DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56041-01C02 | CML-1 | 80-DH-56041-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20924 | Rope Access | 2014-05-18 07:00 | 2014-05-18 08:00 | [36 empty] | 5.35 | CML-1 | CML: type TBC | 3 | 2017-08-01 | 2018-01-25 | 2014-05-18 07:00 | 2.5 | 0.71693 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 9 O'Clock | 80 | 5.49 | 80-DH-56041-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 5.6 | 5.6 | 4.8 | 0.37859
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8875 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 08:00 | 2015-02-25 09:00 | [36 empty] | 5.25 | CML-7 | CML: type TBC | 3 | 2028-12-10 | 2030-08-11 | 2015-02-25 08:00 | 2.5 | 0.19564 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AU-63019-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.3 | 5.3 | 0.057735
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-1 | 80-PW-44034-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23078 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.35 | CML-1 | CML: Fitting | 3 | 2043-10-21 | 2047-05-05 | 2015-05-07 07:00 | 2.5 | 0.09833 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 1.2463 | 5.4 | 5.3 | 5.3 | 5.4 | 0.057735
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-12 | 50-FG-45501-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6595 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.55 | CML-12 | CML: Pipe Length | 3 | 2036-07-22 | 2039-01-15 | 2015-03-30 07:00 | 2.5 | 0.13128 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.1 | 5.5 | 5.3 | 5.3 | 0.37859
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-2 | 100-FH-43104-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12753 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 5.85 | CML-2 | CML: type TBC | 3 | 2016-08-08 | 2016-09-16 | 2014-01-25 07:00 | 2.5 | 1.1029 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 3 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.1 | 5.3 | 6.1 | 5.9 | 0.37859
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56555-01C02 | CML-1 | 50-DH-56555-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21123 | CML-2 avg. WT is 5.0 mm. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. Based on CML’s checked Line is FFS. Action: Update RBI study to include this line. While RBI is updated rest of CMLs to be inspected in 48m. Reviewed 20/11/14. FFS. Re check Oct.18. Review RBI to include this line. | 2014-10-08 07:00 | 2014-10-08 15:00 | [36 empty] | 6.35 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-08 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56555-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.6 | 6.6 | 5.8 | 0.37859
FG02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-FG-45455-01C02-E | CML-47 | 25-FG-45455-01C02-E CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 9134 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 6.25 | CML-47 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.8 | 6 | 6.2 | 6 | 0.37859
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-5 | 50-CG-38452-09C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20399 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 7.45 | CML-5 | CML: Pipe Length | 3 | 2059-07-07 | 2055-11-27 | 2014-10-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 6 O'Clock | 150 | 7.11 | 150-WC-40405-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8 | 7.2 | 7.2 | 7.4 | 0.37859
PG05 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 2520 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.6667 | CML-6 | CML: type TBC | 3 | 2031-07-31 | 2033-07-12 | 2014-04-02 13:00 | 2.5 | 0.16724 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 5.4 |  | 5.4 | 6.1 | 5.5 | 0.37859
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40013-01C02 | CML-7 | 50-WC-40013-01C02 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 1562 | Rope Access | 2014-04-09 10:00 | 2014-04-09 11:00 | [36 empty] | 7.15 | CML-7 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-WC-40013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 8.3 | 7.2 | 7.3 | 5.8 | 1.0279
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-5 | 150-FL-43453-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2249 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 8.9333 | CML-5 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 8.5 | 3 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  |  | 8.5 | 9.1 | 9.2 | 0.37859
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-61 | 350-FL-43512-01C02 CML-61 |  | FPSO 2015 | Pipe Wall Thickness | 6548 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 8.65 | CML-61 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 8.4 | 9 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.6 | 8.4 | 9.2 | 8.4 | 0.37859
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20059-01C02 | CML-2 | 200-PL-20059-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2867 | Rope Access | 2014-03-25 11:00 | 2014-03-25 12:00 | [36 empty] | 7 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-25 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 12 O'Clock | 200 | 6.35 | 200-PL-20059-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.9 | 7.1 | 7.2 | 0.18257
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-3 | 80-CG-38459-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2738 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 15.475 | CML-3 | CML: Pipe Length | 3 | 2096-09-16 | 2070-01-23 | 2014-03-13 09:00 | 2.8 | 0 | A4: Left Quadrant |  | 8.13 | 2.8 | 5.465 | 15.1 | 9 O'Clock | 80 | 11.13 | 80-PG-23050-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.3 |  | 15.2 | 15.8 | 15.8 | 15.1 | 0.37749
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10406 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 7.375 | CML-3 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 7.1 | 6 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.4 | 7.1 | 7.1 | 7.9 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-12 | 200-FH-43012-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2842 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 8.375 | CML-12 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 8.1 | 9 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.76 |  | 8.4 | 8.9 | 8.1 | 8.1 | 0.37749
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-17 | 300-PG-20004-03C03-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23366 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 13.725 | CML-17 | CML: Fitting | 6 | 2032-02-06 | 2028-09-27 | 2015-07-20 07:00 | 4.9 | 0.50116 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 | -0.097599 | 13.2 | 14 | 14 | 13.7 | 0.37749
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-24 | 300-PG-20005-03C03-P CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 22786 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 13.875 | CML-24 | CML: Reducing Tee | 6 | 2040-02-11 | 2035-04-25 | 2015-04-29 07:00 | 4.9 | 0.35071 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 | 0.75005 | 13.6 | 13.9 | 14.4 | 13.6 | 0.37749
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-15 | 100-DH-56088-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 5208 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 8.325 | CML-15 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.9 | 9 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.2 | 8.8 | 8.4 | 7.9 | 0.37749
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-15 | 50-CG-38487-09C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20815 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.825 | CML-15 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9.4 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.3 | 9.7 | 9.9 | 9.4 | 0.37749
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45031-03C03 | CML-1 | 50-PL-45031-03C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10469 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 8.325 | CML-1 | CML: type TBC | 6 | 2017-08-10 | 2017-02-18 | 2013-11-14 | 0.99 | 1.847 | A3: Inside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.9 | 6 O'Clock | 50 | 8.74 | 50-PL-45031-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.91 |  | 8.4 | 8.2 | 7.9 | 8.8 | 0.37749
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12623 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.075 | CML-4 | CML: type TBC | 3 | 2015-10-04 | 2016-01-04 | 2014-01-23 10:00 | 2.5 | 1.2969 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.8 | 5.4 | 4.7 | 5.4 | 0.37749
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40043-01C02 | CML-7 | 300-WC-40043-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1048 |  | 2014-03-20 13:00 | 2014-03-20 14:00 | Check Corrosion Rate of 0.686mm/ yr | [35 empty] | 6.4 | CML-7 | CML: type TBC | 3 | 2019-01-08 | 2018-12-24 | 2014-03-20 13:00 | 2.5 | 0.68623 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 300 | 6.35 | 300-WC-40043-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.1 | 6.6 | 7.1 | 0.57155
FG02 | Montara_Topside | Yes | Potable Water (53) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8292 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.375 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-WD-53003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6.7 | 6.7 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43121-01C02 | CML-2 | 150-FH-43121-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1765 | Rope access | 2014-04-27 09:30 | 2014-04-27 11:00 | [36 empty] | 7.325 | CML-2 | CML: Fitting | 3 | 2026-11-13 | 2025-10-24 | 2014-04-27 09:30 | 2.5 | 0.34247 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 12 O'Clock | 150 | 7.11 | 150-FH-43121-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.4 | 7.7 | 7.4 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43108-01C02 | CML-5 | 200-FH-43108-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12780 |  | 2014-01-18 15:30 | 2014-01-18 16:30 | [36 empty] | 6.675 | CML-5 | CML: Pipe Length | 3 | 2076-12-17 | 2069-04-01 | 2014-01-18 15:30 | 1.34 | 0.07878 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.3 | 12 O'Clock | 200 | 6.35 | 200-FH-43108-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 6.3 | 6.6 | 6.6 | 7.2 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43109-01C02 | CML-7 | 200-FH-43109-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12791 |  | 2014-01-18 14:30 | 2014-01-18 15:30 | [36 empty] | 8.025 | CML-7 | CML: Reducer | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 14:30 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.7 | 6 O'Clock | 150 | 6.35 | 200-FH-43109-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.36 |  | 7.7 | 8.4 | 7.7 | 8.3 | 0.37749
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56065-01C02 | CML-2 | 50-DH-56065-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3410 | Rope Access | 2014-05-11 09:30 | 2014-05-11 11:00 | [36 empty] | 5.925 | CML-2 | CML: type TBC | 3 | 2085-01-28 | 2092-10-07 | 2014-05-11 09:30 | 2.5 | 0.04239 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DH-56065-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.8 | 6.4 | 6 | 0.37749
CG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-CG-38452-09C02-P | CML-35 | 50-CG-38452-09C02-P CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 1441 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 7.575 | CML-35 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8 | 7.7 | 7.5 | 7.1 | 0.37749
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40512-1CG | CML-1 | 150-WC-40512-1CG CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5474 | Rope Access | 2014-05-28 10:00 | 2014-05-28 11:30 | [36 empty] | 12.875 | CML-1 | CML: Elbow | 3 | 2098-02-09 | 2070-10-05 | 2014-05-28 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 7.97 | 2.5 | 5.235 | 12 | 9 O'Clock | 150 | 10.97 | 150-WC-40512-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 13.6 | 13.3 | 12.6 | 12 | 0.71822
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-11 | 100-PW-20021-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21814 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6.025 | CML-11 | CML: Elbow | 3 | 2021-02-22 | 2021-05-26 | 2014-10-11 07:00 | 2.5 | 0.45506 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 6 | 5.4 | 6.8 | 0.57951
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-4 | 200-PL-20010-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 23804 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.85 | CML-4 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.9 | 6.8 | 6.9 | 6.8 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-11 | 200-FH-43003-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12534 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.525 | CML-11 | CML: Pipe Length | 3 | 2026-02-11 | 2024-07-28 | 2014-01-18 11:30 | 1.34 | 0.3942 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.1 | 9 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 6.6 | 7 | 6.4 | 6.1 | 0.37749
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-5 | 80-PW-44035-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21928 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 6.1 | CML-5 | CML: Elbow | 3 | 2058-06-19 | 2063-09-17 | 2014-10-09 07:00 | 2.5 | 0.06632 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.3 | 5.4 | 6 | 6.7 | 0.54772
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-14 | 200-PW-44018-01X01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7837 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:39 | [32 empty] | 5.225 | CML-14 | CML: Pipe Length | 3 | 2027-11-24 | 2029-06-13 | 2015-01-13 13:00 | 2.5 | 0.20979 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.3 | 5.2 | 0.05
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23048-09C02 | CML-4 | 50-PG-23048-09C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20586 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.475 | CML-4 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9 | 9 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.6 | 9.4 | 9.9 | 9 | 0.37749
FL02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FL-43454-01C02-P | CML-1 | 50-FL-43454-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22053 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.625 | CML-1 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.1 | 9 O'Clock | 100 | 6.02 | 100-FG-45041-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.7 | 9.7 | 10 | 9.1 | 0.37749
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-24 | 250-PW-20040-03C03-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21408 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.5 | CML-24 | CML: Fitting | 6 | 2025-05-16 | 2023-07-26 | 2014-07-12 07:30 | 4.1 | 0.71866 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 11.9 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 12.5 | 12.8 | 12.8 | 11.9 | 0.42426
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-2 | 100-DH-56561-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7934 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 10.125 | CML-2 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-17 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.7 | 12 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 10.6 | 10.2 | 10 | 0.37749
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-9 | 80-DH-56140-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21080 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 11.375 | CML-9 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 10.9 | 9 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.5 | 11.3 | 11.8 | 10.9 | 0.37749
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-5 | 50-CG-38470-01C02-P CML-5 | Yes | FPSO 2015 | Pipe Wall Thickness | 23611 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 12.525 | CML-5 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 12.1 | 9 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 12.6 | 13 | 12.4 | 12.1 | 0.37749
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-15 | 250-PW-20022-01C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2058 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.675 | CML-15 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 10.3 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 11 | 10.3 | 10.5 | 10.9 | 0.3304
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23302-01C02 | CML-7 | 80-VA-23302-01C02 CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 22523 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.425 | CML-7 | CML: Elbow | 3 | 2015-10-10 | 2016-01-18 | 2015-04-20 07:00 | 2.5 | 1.2674 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.1 | 9 O'Clock | 50 | 5.49 | 80-VA-23302-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.7 | 3.8 | 3.1 | 0.37749
FH01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-FH-43141-01C02 | CML-8 | 150-FH-43141-01C02 CML-8 | yes | FPSO 2016 | Pipe Wall Thickness | 24284 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 3.725 | CML-8 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 3.4 | 6 O'Clock | 25 | 3.38 | 0100-AI-63L9004-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 4 | 3.4 | 4.1 | 0.37749
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-13 | 80-PW-44016-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21945 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.7 | CML-13 | CML: Elbow | 3 | 2058-07-22 | 2063-10-24 | 2014-10-10 07:00 | 2.5 | 0.06619 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 6.2 | 5.4 | 0.38297
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-10 | 50-PG-23074-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20632 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.475 | CML-10 | CML: Elbow | 3 | 2023-09-14 | 2024-10-22 | 2014-07-26 07:00 | 2.5 | 0.29527 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 6 | 5.2 | 5.2 | 0.37749
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-16 | 200-PL-20034-03C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21613 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.475 | CML-16 | CML: Fitting | 3 | 2040-09-13 | 2036-01-06 | 2014-06-28 13:00 | 3.61 | 0.16737 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 8 | 6 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 |  | 8.4 | 9.3 | 8 | 8.2 | 0.57373
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43513-01C02 | CML-3 | 50-FL-43513-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 7985 | Line is FFS. Current RBI frequency is 48m Action: to recheck line in 24m (Jan. 2017) to confirm CR. RBI frequency to be updated | 2015-01-18 16:00 | 2015-01-18 17:00 |  |  | Administrator | 2015-09-07 14:59 | [32 empty] | 5.325 | CML-3 | CML: Elbow | 3 | 2020-02-16 | 2020-11-05 | 2015-01-18 16:00 | 2.5 | 0.45268 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FL-43513-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.6 | 5.3 | 5.6 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-3 | 100-FH-43507-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7752 |  | 2015-01-11 08:00 | 2015-01-11 09:00 | [36 empty] | 5.325 | CML-3 | CML: type TBC | 3 | 2020-01-17 | 2020-10-02 | 2015-01-11 08:00 | 2.5 | 0.45831 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FH-43507-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.6 | 5.3 | 5.6 | 0.37749
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56053-01C02 | CML-3 | 80-DH-56053-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20942 | Rope Access | 2014-05-21 14:00 | 2014-05-21 15:00 | [36 empty] | 5.175 | CML-3 | CML: Elbow | 3 | 2018-05-02 | 2018-11-28 | 2014-05-21 14:00 | 2.5 | 0.60733 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-DH-56053-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 4.9 | 5.2 | 5.7 | 0.37749
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-3 | 200-PW-44018-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7756 |  | 2015-01-11 09:30 | 2015-01-11 10:30 | [36 empty] | 5.275 | CML-3 | CML: Elbow | 3 | 2027-11-04 | 2029-05-23 | 2015-01-11 09:30 | 2.5 | 0.21055 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-VA-43519-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.3 | 5.2 | 5.3 | 0.05
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-1 | 50-PW-44012-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2015 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 6.075 | CML-1 | CML: Elbow | 3 | 2023-10-19 | 2024-11-29 | 2014-03-27 09:30 | 2.5 | 0.29259 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.3 | 7.3 | 5.4 | 0.93229
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-24 | 250-PW-44006-01X01 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 1921 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 5.975 | CML-24 | CML: Pipe Length | 3 | 2016-05-29 | 2016-05-21 | 2014-03-26 07:00 | 2.5 | 1.2848 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 6.2 | 5.3 | 6.8 | 0.66521
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-11 | 80-PW-44016-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21943 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.7 | CML-11 | CML: Equal Tee | 3 | 2058-07-22 | 2063-10-24 | 2014-10-10 07:00 | 2.5 | 0.06619 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 6.2 | 5.4 | 0.38297
FG02 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 25-FG-45455-01C02-E | CML-10 | 25-FG-45455-01C02-E CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8532 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.275 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.8 | 6.3 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-14 | 200-FH-43003-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12537 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.475 | CML-14 | CML: Pipe Length | 3 | 2034-08-01 | 2032-01-05 | 2014-01-18 11:30 | 1.34 | 0.23652 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.2 | 3 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 6.2 | 6.2 | 6.5 | 7 | 0.37749
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-VA-23057-01C02 | CML-2 | 200-VA-23057-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3146 | Rope Access | 2014-05-02 14:00 | 2014-05-02 15:00 | [36 empty] | 8.175 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-05-02 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 6 O'Clock | 200 | 6.35 | 200-VA-23057-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.6 | 8.3 | 7.7 | 8.1 | 0.37749
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43014-01C02 | CML-4 | 250-FL-43014-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23076 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.375 | CML-4 | CML: Elbow | 3 | 2029-12-08 | 2029-10-25 | 2015-05-07 07:00 | 2.5 | 0.23288 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 0.096828 | 5.9 | 6.5 | 6.8 | 6.3 | 0.37749
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-30 | 250-PW-44006-01X01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 8022 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6 | CML-30 | CML: Pipe Length | 3 | 2019-06-03 | 2019-05-18 | 2015-01-20 08:30 | 2.5 | 0.64051 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0.48657 | 6 | 6.2 | 5.3 | 6.5 | 0.5099
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-8 | 100-DH-56086-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20967 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 6.875 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.4 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.8 | 7 | 7.3 | 6.4 | 0.37749
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45005-03C02-E | CML-6 | 150-FG-45005-03C02-E CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24324 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.375 | CML-6 | CML: Elbow | 3 | 2075-06-12 | 2065-11-14 | 2016-06-01 07:00 | 2.77 | 0.06992 | A2: Right Quadrant |  | 4.11 | 2.77 | 3.44 | 6.9 | 3 O'Clock | 40 | 7.11 | 150-FG-45005-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.13 |  | 7.5 | 6.9 | 7.8 | 7.3 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43075-01C02 | CML-4 | 100-FH-43075-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3163 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 7.675 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 12 O'Clock | 100 | 6.02 | 100-FH-43075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.8 | 8.1 | 7.6 | 0.37749
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24349 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.225 | CML-4 | CML: Elbow | 3 | 2031-04-11 | 2031-02-22 | 2016-06-06 07:00 | 2.5 | 0.21543 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 12 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 6.6 | 6.3 | 0.37749
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-30 | 250-PW-44006-01X01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 23201 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.975 | CML-30 | CML: Pipe Length | 3 | 2020-07-14 | 2020-06-25 | 2015-05-11 07:00 | 2.5 | 0.54033 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0 | 6 | 6.1 | 5.3 | 6.5 | 0.49917
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-6 | 150-FH-43136-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5519 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 6.725 | CML-6 | CML: Elbow | 3 | 2021-12-24 | 2020-06-08 | 2014-06-01 07:00 | 1.03 | 0.70943 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.4 | 9 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 | -0.91345 | 7.1 | 7 | 6.4 | 6.4 | 0.37749
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-5 | 300-PG-20049-03C03-P CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24472 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.409mm/ yr | 39 | Kirstie Albone | 2017-03-23 13:28 | [32 empty] | 13.325 | CML-5 | CML: Elbow | 6 | 2036-04-29 | 2032-03-16 | 2016-07-09 07:00 | 4.9 | 0.40867 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13 | 3 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | 0.20563 | 13 | 13 | 13.6 | 13.7 | 0.37749
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-4 | 250-WC-40017-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2067 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | Check Corrosion Rate of 0.668mm/ yr | [35 empty] | 6.325 | CML-4 | CML: type TBC | 3 | 2019-03-04 | 2019-02-17 | 2014-03-28 09:30 | 2.5 | 0.66828 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 6.8 | 6.4 | 5.8 | 0.4113
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-6 | 250-PW-20041-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21415 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 10.6 | CML-6 | CML: Elbow | 6 | 2018-02-21 | 2017-03-03 | 2014-07-12 07:30 | 2.5 | 2.156 | A3: Inside Quadrant |  | 6.7 | 2.5 | 4.6 | 10.3 | 6 O'Clock | 40 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.8 | 10.4 | 10.3 | 10.9 | 0.29439
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-8 | 200-PG-23006-09C02-PA CML-8 | Yes | FPSO 2014 | Pipe Wall Thickness | 23841 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 18.575 | CML-8 | CML: Fitting | 3 | 2087-03-17 | 2062-08-31 | 2014-09-25 07:00 | 9.3 | 0.12134 | A3: Inside Quadrant |  | 15.26 | 9.3 | 12.28 | 18.1 | 6 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 18.5 | 19 | 18.1 | 18.7 | 0.37749
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20044-03C03-P | CML-2 | 80-PG-20044-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21450 | Protective mesh removed | 2014-06-29 09:30 | 2014-06-29 11:00 | [36 empty] | 10.8 | CML-2 | CML: Pipe Length | 6 | 2026-02-23 | 2024-03-17 | 2014-06-29 09:30 | 2.5 | 0.67731 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.4 | 6 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 11.3 | 10.7 | 10.4 | 10.8 | 0.37417
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-10 | 300-PW-44003-01C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21852 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 10.6 | CML-10 | CML: Reducing Tee | 6 | 436058 | 390329 | 2014-10-19 07:00 | 2.5 | 0.00722 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 10.3 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.6 | 10.8 | 10.7 | 10.3 | 0.21602
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-5 | 50-PL-23041-06C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10218 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.7 | CML-5 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 4.2659 | A2: Right Quadrant |  | 5.07 |  |  | 9.2 | 3 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.1 | 9.2 | 9.7 | 9.8 | 0.37417
FH01 | Montara_Topside | Yes | Potable Water (53) | Pipework | 150-FH-43141-01C02 | CML-5 | 150-FH-43141-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 5109 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 3.7 | CML-5 | CML: type TBC | 0 | 2036-10-14 | 2030-08-10 | 2015-03-06 07:00 | 2.5 | 0.037 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.3 | 12 O'Clock | 25 | 3.38 | 0100-WZ-53L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 4.2 | 3.7 | 3.6 | 0.37417
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-1 | 50-FG-45018-03C02 CML-1 | yes | FPSO 2013 | Pipe Wall Thickness | 10500 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.9 | CML-1 | CML: type TBC | 3 | 2014-10-02 | 2014-09-28 | 2013-11-15 | 2.5 | 2.2731 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.4 | 4.8 | 4.5 | 4.9 | 0.37417
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56025-01C02 | CML-2 | 80-DH-56025-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3486 | Rope Access | 2014-05-14 11:00 | 2014-05-14 12:00 | [36 empty] | 5.1 | CML-2 | CML: type TBC | 3 | 2016-08-11 | 2016-12-25 | 2014-05-14 11:00 | 2.5 | 0.93493 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 9 O'Clock | 80 | 5.49 | 80-DH-56025-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.1 | 5.2 | 5.5 | 4.6 | 0.37417
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-24 | 50-FG-45300-01C02 CML-24 | yes | FPSO 2015 | Pipe Wall Thickness | 7847 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:42 | [32 empty] | 5.2 | CML-24 | CML: Elbow | 3 | 2020-01-26 | 2020-10-12 | 2015-01-13 13:00 | 2.5 | 0.4566 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 5.2 | 5.7 | 4.8 | 0.37417
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-6 | 80-PW-44016-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21938 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.6 | CML-6 | CML: Pipe Length | 3 | 2058-07-22 | 2063-10-24 | 2014-10-10 07:00 | 2.5 | 0.06619 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.4 | 5.5 | 5.5 | 0.2708
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-7 | 200-PL-20034-03C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21604 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.525 | CML-7 | CML: Fitting | 3 | 2040-09-13 | 2036-01-06 | 2014-06-28 13:00 | 3.61 | 0.16737 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 8 | 6 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 |  | 8.5 | 8.9 | 8 | 8.7 | 0.38622
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45004-03C02 | CML-9 | 150-FG-45004-03C02 CML-9 |  | FPSO 2016 | Pipe Wall Thickness | 24341 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. No internal damage in RBI | [31 empty] | 6.1 | CML-9 | CML: Elbow | 3 | 2022-08-15 | 2021-01-05 | 2016-06-06 07:00 | 2.5 | 0.50046 | A1: Outside Quadrant |  | 4.11 | 2.5 | 3.305 | 5.6 | 12 O'Clock | 150 | 7.11 | 150-FG-45004-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.2 | 6.1 | 6.5 | 0.37417
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43125-01C02 | CML-6 | 200-FH-43125-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2760 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 6.5 | CML-6 | CML: Pipe Length | 3 | 2024-08-06 | 2023-03-30 | 2014-03-13 09:00 | 1.34 | 0.44766 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6 | 12 O'Clock | 200 | 6.35 | 200-FH-43125-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 6 | 6.6 | 6.5 | 6.9 | 0.37417
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-2 | 150-WC-40003-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2979 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 1.43mm/ yr | [35 empty] | 6.175 | CML-2 | CML: Elbow | 3 | 2016-08-20 | 2016-05-20 | 2014-05-01 09:30 | 2.5 | 1.4299 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.8 | 3 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0 | 5.9 | 5.8 | 6.6 | 6.4 | 0.38622
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56002-01C02 | CML-1 | 80-DH-56002-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3420 | Rope Access | 2014-05-11 14:00 | 2014-05-11 14:30 | [36 empty] | 5.5 | CML-1 | CML: type TBC | 3 | 2019-03-04 | 2019-11-04 | 2014-05-11 14:00 | 2.5 | 0.51903 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 6 O'Clock | 80 | 5.49 | 80-DH-56002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.9 | 5.5 | 5 | 5.6 | 0.37417
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-10 | 100-PW-20021-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21813 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.625 | CML-10 | CML: Elbow | 3 | 2021-02-22 | 2021-05-26 | 2014-10-11 07:00 | 2.5 | 0.45506 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.5 | 6 | 5.4 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-21 | 50-DH-56062-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 9108 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 6 | CML-21 | CML: type TBC | 3 | 2146-06-10 | 2160-09-18 | 2015-03-02 07:00 | 2.5 | 0.02284 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.4 | 6 | 6.1 | 5.5 | 0.37417
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-15 | 25-FG-45455-01C02-E CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1163 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.5 | CML-15 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 6.6 | 6.5 | 6 | 0.37417
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-14 | 80-DH-56074-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20959 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 7 | CML-14 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-05-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.6 | 6 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 7.5 | 6.6 | 6.9 | 0.37417
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-10 | 150-FL-43174-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12908 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.5 | CML-10 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 3 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8 | 7.1 | 7.5 | 7.4 | 0.37417
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-14 | 50-PL-23040-03C03 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10199 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8 | CML-14 | CML: type TBC | 6 | 2015-08-15 | 2015-07-30 | 2013-11-08 | 2.5 | 2.8287 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 7.5 | 9 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.4 | 8.1 | 8 | 7.5 | 0.37417
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-20 | 80-PW-20024-01C03-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23064 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 10.85 | CML-20 | CML: Elbow | 6 | 2063-11-04 | 2056-02-27 | 2015-05-06 07:00 | 2.5 | 0.17102 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.8 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 10.8 | 10.8 | 11 | 0.1
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40507-1CG | CML-3 | 200-WC-40507-1CG CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8672 | Material Class Not Selectable | 2015-02-12 14:00 | 2015-02-12 15:00 |  |  | Administrator | 2015-09-08 10:53 | [32 empty] | 12.65 | CML-3 | CML: Elbow | 3 | 2048-02-18 | 2035-11-17 | 2015-02-12 14:00 | 2.5 | 0.29361 | A1: Outside Quadrant |  | 9.7 | 2.5 | 6.1 | 12.2 | 12 O'Clock | 200 | 12.7 | 200-WC-40507-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 12.2 | 12.5 | 13.5 | 12.4 | 0.58023
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40508-1CG | CML-2 | 200-WC-40508-1CG CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8667 | Material Class Not Selectable.Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Feb. 2020). RBI to be updated | 2015-02-12 13:00 | 2015-02-12 14:00 |  |  | Administrator | 2015-09-08 10:32 | [32 empty] | 12.55 | CML-2 | CML: Elbow | 3 | 2048-02-17 | 2035-11-17 | 2015-02-12 13:00 | 2.5 | 0.29362 | A1: Outside Quadrant |  | 9.7 | 2.5 | 6.1 | 12.2 | 12 O'Clock | 200 | 12.7 | 200-WC-40508-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 12.2 | 12.4 | 12.7 | 12.9 | 0.31091
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-5 | 300-FL-43080-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2384 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 8.2 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 12 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 8.3 | 8.6 | 8.2 | 0.37417
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56126-01C02 | CML-1 | 80-DH-56126-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21046 | Rope Access | 2014-05-17 07:00 | 2014-05-17 08:00 | [36 empty] | 5.6 | CML-1 | CML: type TBC | 3 | 2023-04-21 | 2024-06-15 | 2014-05-17 07:00 | 2.5 | 0.30218 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-DH-56126-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.5 | 6.1 | 5.6 | 0.37417
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38486-09C02-P |  | 80-CG-38486-09C02-P |  | FPSO 2015 | Pipe Wall Thickness | 23651 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 16.5 | 80-CG-38486-01C02-H | Piping | 3 | 2043-04-25 |  | 2015-10-28 07:00 |  | 0 | A4: Left Quadrant |  |  | 2.5 |  | 16.1 | 9 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.6 |  | 16.4 | 16.5 | 17 | 16.1 | 0.37417
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45044-03C02 | CML-3 | 50-FG-45044-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 24269 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 11.2 | CML-3 | CML: Pipe Length | 3 | 2061-11-30 | 2054-07-28 | 2014-09-24 07:00 | 4.7 | 0.12919 | A4: Left Quadrant |  | 7.97 | 4.7 | 5.6494 | 10.8 | 9 O'Clock | 150 | 10.97 | 150-PG-23045-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 11.1 | 11.2 | 11.7 | 10.8 | 0.37417
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-15 | 250-PG-23004-06C03-A CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23382 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 18.65 | CML-15 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2015-07-21 07:00 | 8.55 | 0 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.3 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.75 | -0.32843 | 18.3 | 18.8 | 19.1 | 18.4 | 0.36968
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-17 | 300-PG-20005-03C03-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 22779 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.25 | CML-17 | CML: Reducing Tee | 6 | 2044-10-18 | 2039-02-26 | 2015-04-29 07:00 | 4.9 | 0.29837 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | -0.50004 | 14.5 | 13.7 | 14.4 | 14.4 | 0.36968
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-5 | 50-PL-23020-01C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10119 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 7.85 | CML-5 | CML: type TBC | 6 | 2015-08-15 | 2015-07-30 | 2013-11-08 | 2.5 | 2.8287 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.5 | 6 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.3 | 7.6 | 7.5 | 8 | 0.36968
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-2 | 150-WC-40003-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22258 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 1.43mm/ yr | [35 empty] | 6.175 | CML-2 | CML: Elbow | 3 | 2016-08-20 | 2016-05-20 | 2014-05-01 09:30 | 2.5 | 1.4299 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.8 | 3 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 5.8 | 6.6 | 6.4 | 0.38622
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24458 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | Check Corrosion Rate of 0.681mm/ yr |  | John Wilson | 2017-03-23 16:25 | Readings appear stable and have never returned values of the nominal value. | [31 empty] | 8.65 | CML-2 | CML: Equal Tee | 6 | 2020-11-17 | 2021-07-19 | 2016-07-05 07:00 | 5.22 | 0.68137 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 8.2 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.98 | 0.41834 | 8.2 | 8.5 | 9 | 8.9 | 0.36968
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-7 | 150-PG-20507-01C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2851 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 11.05 | CML-7 | CML: type TBC | 6 | 2031-06-26 | 2028-11-06 | 2014-03-16 07:00 | 2.5 | 0.46845 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.6 | 12 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.6 | 10.9 | 11.3 | 11.4 | 0.36968
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-13 | 300-PG-23001-03C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10963 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.05 | CML-13 | CML: Pipe Length | 6 | 2021-08-16 | 2020-03-29 | 2014-01-09 | 5.22 | 1.1016 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 13.6 | 6 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.38 |  | 14.3 | 13.9 | 13.6 | 14.4 | 0.36968
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-11 | 80-PG-23025-06C03 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20550 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 11.65 | CML-11 | CML: Tee | 6 | 2096-09-16 | 2085-01-22 | 2014-05-27 08:00 | 2.8 | 0 | A4: Left Quadrant |  | 5.13 | 2.8 | 3.965 | 11.2 | 9 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | 14.0804 | 12 | 11.5 | 11.9 | 11.2 | 0.36968
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-7 | 25-VA-23054-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1476 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 5.35 | CML-7 | CML: type TBC | 3 | 2019-09-14 | 2020-05-18 | 2014-04-29 10:00 | 2.5 | 0.48313 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.2 | 5.9 | 5.2 | 0.36968
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56106-01C02 | CML-2 | 80-DH-56106-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2028 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 6.15 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-27 14:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.3 | 6.4 | 6.3 | 0.36968
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-3 | 250-WC-40017-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2066 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | Check Corrosion Rate of 0.668mm/ yr | [35 empty] | 6.25 | CML-3 | CML: type TBC | 3 | 2019-03-04 | 2019-02-17 | 2014-03-28 09:30 | 2.5 | 0.66828 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.4 | 5.8 | 6.4 | 0.3
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-7 | 50-DH-56109-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20996 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.05 | CML-7 | CML: Elbow | 3 | 2016-07-30 | 2016-12-02 | 2014-05-24 10:30 | 2.5 | 0.95989 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.4 | 5.3 | 4.9 | 0.36968
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-12 | 200-PL-20034-03C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21609 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.3 | CML-12 | CML: Elbow | 3 | 2040-09-13 | 2036-01-06 | 2014-06-28 13:00 | 3.61 | 0.16737 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 8 | 3 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 |  | 8.7 | 8 | 8.2 | 8.3 | 0.29439
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56126-01C02 | CML-3 | 80-DH-56126-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21048 | Rope Access | 2014-05-17 07:00 | 2014-05-17 08:00 | [36 empty] | 5.85 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 3 O'Clock | 80 | 5.49 | 80-DH-56126-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.4 | 5.6 | 5.7 | 5.7 | 0.36968
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38493-01C02 | CML-3 | 25-CG-38493-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10372 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.15 | CML-3 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 9 O'Clock | 25 | 6.35 | 25-CG-38493-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 6.3 | 6.4 | 6.3 | 5.6 | 0.36968
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44036-01C02-P | CML-3 | 80-PW-44036-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21955 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.6 | CML-3 | CML: Reducing Tee | 3 | 2058-07-22 | 2063-10-24 | 2014-10-10 07:00 | 2.5 | 0.06619 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.4 | 5.4 | 5.7 | 0.24495
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-10 | 200-PL-20034-03C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21607 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.3 | CML-10 | CML: Elbow | 3 | 2040-09-13 | 2036-01-06 | 2014-06-28 13:00 | 3.61 | 0.16737 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 8 | 3 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 |  | 8.3 | 8 | 8.4 | 8.5 | 0.21602
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2501 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.55 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 3 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.5 | 7.1 | 7.6 | 8 | 0.36968
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40500-1CG | CML-6 | 400-WC-40500-1CG CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23434 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 13.025 | CML-6 | CML: Elbow | 3 | 2017-11-26 | 2016-01-06 | 2015-07-23 07:00 | 2.5 | 4.2179 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 12.4 | 6 O'Clock | 200 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 | 7.9126 | 13.1 | 13.4 | 12.4 | 13.2 | 0.43493
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-11 | 50-PW-44012-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2025 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 5.7 | CML-11 | CML: Pipe Length | 3 | 2023-10-19 | 2024-11-29 | 2014-03-27 09:30 | 2.5 | 0.29259 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.1 | 6 | 5.4 | 5.3 | 0.40825
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-26 | 100-PW-20021-01C02-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 21829 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.65 | CML-26 | CML: Elbow | 3 | 2021-02-22 | 2021-05-26 | 2014-10-11 07:00 | 2.5 | 0.45506 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.9 | 5.7 | 5.6 | 0.20817
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45035-03C02 | CML-1 | 50-FG-45035-03C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 2578 |  | 2014-04-26 14:00 | 2014-04-26 15:00 | [36 empty] | 5.15 | CML-1 | CML: type TBC | 3 | 2016-09-05 | 2016-08-28 | 2014-04-26 14:00 | 2.5 | 0.93027 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FG-45035-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.5 | 4.7 | 5.4 | 5 | 0.36968
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43116-01C02 | CML-1 | 150-FH-43116-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1771 | Rope access | 2014-04-27 13:00 | 2014-04-27 14:00 | [36 empty] | 5.35 | CML-1 | CML: Elbow | 3 | 2015-03-22 | 2015-01-30 | 2014-04-27 13:00 | 2.5 | 2.5508 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 4.8 | 12 O'Clock | 80 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.6 | 5.5 | 5.5 | 0.36968
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-21 | 250-PW-44006-01X01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 8013 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 5.675 | CML-21 | CML: Fitting | 3 | 2019-06-03 | 2019-05-18 | 2015-01-20 08:30 | 2.5 | 0.64051 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0.24328 | 6 | 5.6 | 5.3 | 5.8 | 0.29861
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23044 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 5.675 | CML-7 | CML: Elbow | 3 | 2020-06-26 | 2020-06-07 | 2015-05-06 07:00 | 2.5 | 0.54416 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 6 O'Clock | 20 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 2.5027 | 5.8 | 5.8 | 5.3 | 5.8 | 0.25
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40009-01C02 | CML-3 | 200-WC-40009-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3122 | Rope Access | 2014-05-04 07:00 | 2014-05-04 08:00 | Check Corrosion Rate of 0.595mm/ yr | [35 empty] | 5.975 | CML-3 | CML: Fitting | 3 | 2019-11-18 | 2019-10-31 | 2014-05-04 07:00 | 2.5 | 0.59518 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 200 | 6.35 | 200-WC-40009-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 5.8 | 5.8 | 6 | 0.23629
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-11 | 50-PW-44015-01X01 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10294 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.5 | CML-11 | CML: Reducer | 3 | 2019-01-13 | 2019-08-21 | 2013-11-10 | 2.5 | 0.54074 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.6 | 5.3 | 5.8 | 0.24495
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-12 | 200-PL-20035-03C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21335 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 8.1 | CML-12 | CML: Fitting | 3 | 2040-08-18 | 2035-12-16 | 2014-06-27 13:00 | 3.61 | 0.1678 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 8 | 9 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 |  | 8.2 | 8 | 8.2 | 8 | 0.11547
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56106-01C02 | CML-12 | 80-DH-56106-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2038 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 6.25 | CML-12 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-27 14:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 6 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 6.6 | 5.8 | 6.5 | 0.36968
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56142-01C02 | CML-1 | 25-DH-56142-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7522 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 6.25 | CML-1 | CML: Reducer | 3 | 2029-05-16 | 2029-04-04 | 2015-04-13 07:00 | 2.5 | 0.24109 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 6 O'Clock | 25 | 6.35 | 25-DH-56142-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 6.4 | 5.9 | 6 | 0.36968
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-13 | 25-FG-45455-01C02-E CML-13 |  | FPSO 2016 | Pipe Wall Thickness | 24358 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.55 | CML-13 | CML: Elbow | 3 | 2046-08-01 | 2046-05-04 | 2016-06-06 07:00 | 2.5 | 0.116 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.7 | 6 | 6.8 | 6.7 | 0.36968
FG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3106 | Rope Access | 2014-05-04 10:00 | 2014-05-04 10:30 | [36 empty] | 6.35 | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-04 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 15 | 5.54 | 50-CG-38005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6.8 | 6.5 | 6 | 0.36968
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-5 | 25-PW-44026-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22737 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 6.45 | CML-5 | CML: Elbow | 3 | 2034-05-21 | 2034-03-26 | 2015-04-28 07:00 | 2.5 | 0.18347 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 25 | 6.35 | 25-PW-44026-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6 | 6.8 | 6.7 | 0.36968
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40011-01C02 | CML-4 | 50-WC-40011-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1889 | Rope Access | 2014-03-25 13:00 | 2014-03-25 14:00 | [36 empty] | 6.075 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.2 | 6.3 | 6 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-9 | 200-FH-43012-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2839 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.25 | CML-9 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 7 | 3 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.66 |  | 7.8 | 7 | 7.1 | 7.1 | 0.36968
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43514-01C02 | CML-4 | 150-FL-43514-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5322 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.15 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 3 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 4.3 | 3.6 | 4.3 | 4.4 | 0.36968
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44027-01X01 | CML-1 | 50-PW-44027-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22743 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.5 | CML-1 | CML: Pipe Length | 3 | 2037-07-24 | 2040-02-26 | 2015-04-28 07:00 | 2.5 | 0.12581 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-PW-44027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 4.5488 | 5.4 | 5.6 | 5.7 | 5.3 | 0.18257
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23049-25C02-P | CML-3 | 100-PG-23049-25C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2753 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 17.35 | CML-3 | CML: Pipe Length | 3 | 2063-09-06 | 2048-04-24 | 2014-03-13 09:00 | 9.4 | 0.15348 | A4: Left Quadrant |  | 14.12 | 9.4 | 11.76 | 17 | 9 O'Clock | 100 | 17.12 | 100-PG-23049-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 17.8 | 17.5 | 17.1 | 17 | 0.36968
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-2 | 200-PG-23051-09C02-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13107 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.575 | CML-2 | CML: type TBC | 3 | 2037-02-20 | 2029-04-01 | 2014-02-07 11:00 | 9.3 | 0.3774 | A3: Inside Quadrant |  | 15.26 | 9.3 | 12.28 | 18 | 6 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 20.3 | 19.9 | 18 | 20.1 | 1.0626
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-5 | 50-PW-44012-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2019 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 5.375 | CML-5 | CML: Elbow | 3 | 2023-10-19 | 2024-11-29 | 2014-03-27 09:30 | 2.5 | 0.29259 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.4 | 5.5 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-20 | 50-DH-56137-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21104 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 5.35 | CML-20 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 4.9 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.8 | 5.3 | 5.4 | 4.9 | 0.36968
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40050-01C02 | CML-2 | 50-WC-40050-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1896 | Rope Access | 2014-03-25 14:00 | 2014-03-25 15:00 | [36 empty] | 6.1 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40050-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.3 | 6.1 | 6.2 | 0.21602
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-5 | 50-WC-40451-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3067 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | [36 empty] | 6.025 | CML-5 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-05-03 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 100 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | -2.4981 | 6 | 6.3 | 5.8 | 6 | 0.20616
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5788 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.95 | CML-2 | CML: Elbow | 3 | 2036-06-15 | 2038-12-05 | 2014-06-23 13:00 | 2.5 | 0.13186 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.1 | 6.1 | 6.2 | 0.36968
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-2 | 200-PL-20010-01C02-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 23802 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.125 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.8 | 8.4 | 9.4 | 6.9 | 1.05
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56006-01C02 | CML-2 | 80-DH-56006-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3445 | Rope Access | 2014-05-12 10:30 | 2014-05-12 11:30 | [36 empty] | 6.15 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-12 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-DH-56006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.2 | 6.1 | 6.6 | 0.36968
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-21 | 50-DH-56070-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 3237 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.05 | CML-21 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 6.6 | 5.9 | 5.8 | 0.36968
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-38 | 250-PW-44006-01X01 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 8030 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 5.325 | CML-38 | CML: Elbow | 3 | 2019-06-03 | 2019-05-18 | 2015-01-20 08:30 | 2.5 | 0.64051 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 9 O'Clock | 50 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | -0.60821 | 5.3 | 5.3 | 5.4 | 5.3 | 0.05
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-5 | 80-PW-44001-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23214 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6 | CML-5 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 3.4928 | 5.5 | 6.5 | 6.1 | 5.9 | 0.41633
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-38 | 50-DH-56070-01C02 CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 3254 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.65 | CML-38 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.1 | 6.4 | 6.8 | 6.3 | 0.36968
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-11 | 200-WC-40008-01C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 7817 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | Check Corrosion Rate of 0.339mm/ yr | [35 empty] | 5.95 | CML-11 | CML: Fitting | 3 | 2024-09-30 | 2024-08-31 | 2015-01-13 09:30 | 2.5 | 0.33945 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 5.9 | 6.2 | 0.17321
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43304-01C02 |  | 150-FL-43304-01C02 |  | FPSO 2016 | Pipe Wall Thickness | 9171 |  | 2016-02-23 07:00 | 2016-02-23 15:00 | [36 empty] | 7.15 | 150-FL-43304-01C02 | Piping | 3 |  |  | 2016-02-23 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.7 | 3 O'Clock | 150 |  | Pipework | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.6 | 6.7 | 7.2 | 7.1 | 0.36968
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-10 | 80-FH-43009-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12588 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.65 | CML-10 | CML: Pipe Length | 3 | 2025-01-24 | 2023-07-31 | 2014-02-05 08:00 | 0.54 | 0.42453 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 5.2 | 5.6 | 6.1 | 5.7 | 0.36968
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-18 | 80-FH-43009-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 12596 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.45 | CML-18 | CML: Elbow | 3 | 2019-02-21 | 2018-05-30 | 2014-02-05 08:00 | 0.54 | 0.8637 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.36 |  | 5.7 | 5.6 | 4.9 | 5.6 | 0.36968
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-9 | 50-WC-40032-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1243 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 5.95 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6 | 6 | 6 | 0.1
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-15 | 250-PW-44006-01X01 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1912 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.3 | CML-15 | CML: Pipe Length | 3 | 2016-09-21 | 2016-09-13 | 2014-03-26 07:00 | 2.5 | 1.1624 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 12 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.2 | 7.3 | 6.3 | 0.77889
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40508-1CG | CML-1 | 200-WC-40508-1CG CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8666 | Material Class Not Selectable.Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Feb. 2020). RBI to be updated | 2015-02-12 13:00 | 2015-02-12 14:00 |  |  | Administrator | 2015-09-08 10:32 | [32 empty] | 13.15 | CML-1 | CML: Elbow | 3 | 2100-03-15 | 2069-07-27 | 2015-02-12 13:00 | 2.5 | 0.11745 | A2: Right Quadrant |  | 9.7 | 2.5 | 6.1 | 12.5 | 3 O'Clock | 200 | 12.7 | 200-WC-40508-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 12.8 | 12.5 | 13.4 | 13.9 | 0.6245
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56087-01C02 | CML-8 | 100-DH-56087-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8038 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:32 | [32 empty] | 10.55 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2015-01-20 14:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.3 | 6 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.4 | 11.1 | 10.3 | 10.4 | 0.36968
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43300-01C02-E | CML-5 | 200-PL-43300-01C02-E CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 8591 | Line is FFS. Action: to recheck in two years (Feb. 2017) to confirm CR. | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-07 16:36 | [32 empty] | 5.575 | CML-5 | CML: Elbow | 3 | 2022-05-01 | 2021-04-01 | 2015-02-08 11:00 | 1.34 | 0.56158 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 5.4 | 6 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.06 |  | 5.6 | 5.6 | 5.4 | 5.7 | 0.12583
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-25 | 80-CG-38459-09C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 20009 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 22.85 | CML-25 | CML: type TBC | 6 | 2117-05-30 | 2095-05-30 | 2014-01-10 | 10.22 | 0 | A2: Right Quadrant |  | 14.62 | 10.22 | 12.42 | 22.6 | 3 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.38 |  | 22.7 | 22.6 | 22.7 | 23.4 | 0.36968
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-6 | 50-PG-23074-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20628 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.475 | CML-6 | CML: Elbow | 3 | 2019-11-23 | 2020-08-03 | 2014-07-26 07:00 | 2.5 | 0.46896 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.5 | 5.9 | 5 | 0.36856
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-5 | 200-PW-44018-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23042 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 6 | CML-5 | CML: Fitting | 3 | 2021-03-25 | 2021-03-04 | 2015-05-06 07:00 | 2.5 | 0.49234 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 12 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.56879 | 5.4 | 6.6 | 5.5 | 6.5 | 0.6377
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57028-01C02 | CML-5 | 50-DC-57028-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20272 | Rope Access | 2014-05-26 08:00 | 2014-05-26 09:00 | Check Corrosion Rate of 0.447mm/ yr | [35 empty] | 5.425 | CML-5 | CML: type TBC | 3 | 2024-12-22 | 2023-04-28 | 2014-05-26 08:00 | 0.37 | 0.44694 | A4: Left Quadrant |  | 2.54 | 0.37 | 1.1087 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.73 |  | 5.8 | 5.3 | 5.5 | 5.1 | 0.29861
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57029-01C02 | CML-1 | 50-DC-57029-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20274 | Rope Access | 2014-05-26 07:00 | 2014-05-26 08:00 | Check Corrosion Rate of 0.447mm/ yr | [35 empty] | 5.45 | CML-1 | CML: type TBC | 3 | 2024-12-21 | 2023-04-28 | 2014-05-26 07:00 | 0.37 | 0.44699 | A4: Left Quadrant |  | 2.54 | 0.37 | 1.1087 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57029-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.73 |  | 5.2 | 5.6 | 5.9 | 5.1 | 0.36968
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-7 | 250-PW-20041-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21416 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 10.3 | CML-7 | CML: Reducer | 6 | 2018-02-21 | 2017-03-03 | 2014-07-12 07:30 | 2.5 | 2.156 | A1: Outside Quadrant |  | 6.7 | 2.5 | 4.6 | 10.3 | 9 O'Clock | 40 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 10.3 | 10.3 | 10.3 | 0
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-7 | 150-WC-40004-01C02 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 1809 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | Check Corrosion Rate of 1.328mm/ yr | [35 empty] | 7.475 | CML-7 | CML: Equal Tee | 3 | 2016-11-18 | 2016-08-11 | 2014-04-29 11:00 | 2.5 | 1.3284 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.9 | 12 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 8.1 | 7.9 | 8 | 1.0532
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43308-01C02-E | CML-3 | 200-PL-43308-01C02-E CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 8796 | LAGGING REMOVAL REQUIRED | 2015-02-15 13:00 | 2015-02-15 15:00 | [36 empty] | 6.7 | CML-3 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2015-02-15 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 3 O'Clock | 200 | 6.35 | 200-PL-43308-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.6 | 6.7 | 6.8 | 0.08165
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-32 | 200-PL-20019-01C02 CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 21283 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.55 | CML-32 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.1 | 8.3 | 7.9 | 0.66081
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-4 | 200-PL-20019-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21255 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.55 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.8 | 7.4 | 8.1 | 6.9 | 0.51962
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-37 | 200-PL-20019-01C02 CML-37 |  | FPSO 2014 | Pipe Wall Thickness | 21288 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.6 | CML-37 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 9 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8.2 | 7.8 | 7.3 | 7.1 | 0.49666
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23302-01C02 | CML-8 | 80-VA-23302-01C02 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 22524 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.875 | CML-8 | CML: Elbow | 3 | 2016-02-10 | 2016-06-04 | 2015-04-20 07:00 | 2.5 | 1.1083 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.4 | 3 O'Clock | 50 | 5.49 | 80-VA-23302-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.9 | 3.4 | 3.9 | 4.3 | 0.36856
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-38 | 200-PL-20019-01C02 CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 21289 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.525 | CML-38 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.6 | 7.1 | 7.4 | 8 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43133-01C02 | CML-3 | 50-FH-43133-01C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 3056 | Rope Access | 2014-05-03 10:30 | 2014-05-03 11:30 | [36 empty] | 4.825 | CML-3 | CML: Elbow | 3 | 2015-11-15 | 2016-02-19 | 2014-05-03 10:30 | 2.5 | 1.2368 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.8 | 5.3 | 4.8 | 4.4 | 0.36856
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-8 | 250-PG-23003-06C02-PA CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2450 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 5.825 | CML-8 | CML: type TBC | 3 | 2030-10-19 | 2032-08-30 | 2014-03-20 09:30 | 2.5 | 0.17476 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 6.3 | 5.8 | 0.36856
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57003-01C02 | CML-6 | 80-DC-57003-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12508 | External Corrosion evident | 2014-02-04 16:00 | 2014-02-04 17:00 | [36 empty] | 5.375 | CML-6 | CML: Pipe Length | 3 | 2031-02-25 | 2028-11-20 | 2014-02-04 16:00 | 0.54 | 0.27889 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.4 | 5.4 | 5.3 | 5.4 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57003-01C02 | CML-5 | 80-DC-57003-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12507 | External Corrosion evident | 2014-02-04 16:00 | 2014-02-04 17:00 | [36 empty] | 5.375 | CML-5 | CML: Pipe Length | 3 | 2031-02-25 | 2028-11-20 | 2014-02-04 16:00 | 0.54 | 0.27889 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.4 | 5.4 | 5.3 | 5.4 | 0.05
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43303-01C02 | CML-7 | 50-FL-43303-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20463 | Reviewed 24/11/14. FFS. Repeat on Oct.18. | 2014-10-05 07:00 | 2014-10-05 15:00 |  |  | Nestor | 2014-11-26 15:03 | [32 empty] | 5.325 | CML-7 | CML: Elbow | 3 | 2019-10-21 | 2020-06-28 | 2014-10-05 07:00 | 2.5 | 0.47548 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-FL-43303-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 4.9 | 5.3 | 5.8 | 0.36856
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-12 | 50-DH-56116-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5222 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.375 | CML-12 | CML: Elbow | 3 | 2018-01-04 | 2018-07-03 | 2014-05-20 09:30 | 2.5 | 0.66102 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.8 | 5.4 | 5.4 | 4.9 | 0.36856
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-2 | 50-FH-43137-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12854 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 5.325 | CML-2 | CML: Elbow | 3 | 2016-06-27 | 2016-10-26 | 2014-01-23 08:00 | 2.5 | 0.98843 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 5.3 | 4.9 | 5.8 | 0.36856
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-24 | 200-FH-43025-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 2497 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 8.9 | CML-24 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.5 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 9.1 | 9.3 | 8.7 | 0.36515
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-2 | 80-FL-43015-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22945 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 6 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 3 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.35096 | 5.8 | 5.6 | 6.2 | 6.4 | 0.36515
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-6 | 50-FG-45300-01C02 CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 7829 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:45 | [32 empty] | 6 | CML-6 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-01-13 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 6.2 | 6.4 | 5.6 | 0.36515
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23030-09C02-P | CML-1 | 50-PG-23030-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20744 | Protective mesh removed/Rope access | 2014-07-02 09:30 | 2014-07-02 11:00 | [36 empty] | 8.9 | CML-1 | CML: type TBC | 3 | 2041-08-19 | 2034-04-22 | 2014-07-02 09:30 | 2.5 | 0.22099 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 3 O'Clock | 50 | 8.74 | 50-PG-23030-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.7 | 8.5 | 9.3 | 9.1 | 0.36515
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-2 | 50-PW-44012-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2016 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 5.825 | CML-2 | CML: Pipe Length | 3 | 2031-03-20 | 2033-02-14 | 2014-03-27 09:30 | 2.5 | 0.17068 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.6 | 5.7 | 5.6 | 0.53151
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-7 | 150-FL-43453-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2251 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.7 | CML-7 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.3 | 6 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.9 | 6.5 | 6.3 | 7.1 | 0.36515
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-4 | 50-DH-56137-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21088 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.8 | CML-4 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.4 | 12 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.6 | 7.2 | 7 | 0.36515
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-9 | 250-PW-20041-03C03-P CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 21418 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.375 | CML-9 | CML: Elbow | 6 | 2027-01-30 | 2025-01-06 | 2014-07-12 07:30 | 4.1 | 0.62883 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 13.2 | 13.3 | 15 | 12 | 1.2339
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-15 | 50-FL-43454-01C02-P CML-15 | Yes | FPSO 2014 | Pipe Wall Thickness | 20518 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 12 | CML-15 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 11.6 | 9 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 12.2 | 11.8 | 12.4 | 11.6 | 0.36515
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56115-01C02 | CML-3 | 50-DH-56115-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5234 | Rope Access | 2014-05-20 13:00 | 2014-05-20 14:00 | [36 empty] | 5.1 | CML-3 | CML: Elbow | 3 | 2016-12-01 | 2017-04-17 | 2014-05-20 13:00 | 2.5 | 0.86722 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DH-56115-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.5 | 5.3 | 4.9 | 0.36515
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-2 | 50-PW-44014-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2004 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 5.9 | CML-2 | CML: Pipe Length | 3 | 2031-03-20 | 2033-02-15 | 2014-03-27 10:00 | 2.5 | 0.17067 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.2 | 6.3 | 5.7 | 5.4 | 0.42426
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-21 | 50-CG-38452-09C02-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 12984 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 7.1 | CML-21 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 6.9 | 7.5 | 7.3 | 0.36515
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-19 | 300-PG-20506-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 13233 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.2 | CML-19 | CML: type TBC | 6 | 2026-12-26 | 2024-07-18 | 2014-02-04 15:00 | 4.9 | 0.68999 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 6 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14.6 | 14.4 | 13.8 | 14 | 0.36515
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-2 | 150-FH-43157-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10658 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.9 | CML-2 | CML: type TBC | 3 | 2016-12-06 | 2016-08-28 | 2013-11-18 | 2.5 | 1.3097 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.5 | 9 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  |  | 7 | 7.2 | 6.5 | 0.36056
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-10 | 80-FH-43007-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12571 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 6.2 | CML-10 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-01-18 07:00 | 0.54 | 0 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.8 | 6 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.26 |  | 6.3 | 6.5 | 5.8 |  | 0.36056
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40013-01C02 | CML-6 | 50-WC-40013-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1561 | Rope Access | 2014-04-09 10:00 | 2014-04-09 11:00 | [36 empty] | 6.95 | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.5 | 7.6 | 6.8 | 5.9 | 0.78528
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-8 | 150-PG-23506-25C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2782 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22 | CML-8 | CML: Pipe Length | 3 | 2027-01-22 | 2023-08-11 | 2014-03-15 09:00 | 15.88 | 0.44454 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 21.6 | 9 O'Clock | 50 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.72 |  | 22.3 | 22.1 |  | 21.6 | 0.36056
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42309-01S01 | CML-1 | 40-CI-42309-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7497 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.55 | CML-1 | CML: type TBC | 1 | 2059-10-24 | 2046-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 6.14 | 2.5 | 3.8737 | 7.3 | 6 O'Clock | 40 | 7.14 | 40-CI-42309-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.7 | 7.5 | 7.3 | 7.7 | 0.19149
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-4 | 50-FG-45024-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12644 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 8.4 | CML-4 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 8 | 12 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.97 |  | 8 | 8.5 | 8.7 |  | 0.36056
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67003-01E01 | CML-6 | 50-GN-67003-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8501 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 7.375 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 3 O'Clock | 50 | 5.54 | 50-GN-67003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.3 | 7.5 | 7.4 | 0.095743
CG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-CG-38459-09C02-P | CML-6 | 80-CG-38459-09C02-P CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10446 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 13.8 | CML-6 | CML: type TBC | 6 | 2090-11-29 | 2082-02-28 | 2013-11-13 | 0.99 | 0 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 13.5 | 12 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.51 |  | 13.5 | 14.2 | 13.7 |  | 0.36056
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69004-01S01 | CML-2 | 80-OL-69004-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8093 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 7.5 | CML-2 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.49 | 2.5 | 3.1519 | 7.3 | 9 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.5 | 7.8 | 7.4 | 7.3 | 0.21602
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-1 | 50-PL-23052-09C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10165 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.275 | CML-1 | CML: type TBC | 6 | 2016-10-25 | 2016-05-08 | 2013-11-09 | 2.81 | 2.4258 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 10 | 3 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.19 |  | 10.8 | 10 | 10.2 | 10.1 | 0.3594
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-2 | 150-PG-23043-06C02-P CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24435 | Re-check as requested by N.Sequera | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.735mm/ yr | [35 empty] | 9.225 | CML-2 | CML: Elbow | 3 | 2021-12-09 | 2020-08-25 | 2016-07-02 07:00 | 4.7 | 0.73499 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.7 | 3 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | -1.5643 | 9.4 | 8.7 | 9.5 | 9.3 | 0.3594
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40051-01C02 | CML-5 | 50-WC-40051-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 904 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 6.825 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.7 | 7 | 6.7 | 5.9 | 0.74554
FG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-FG-45024-01C02 | CML-9 | 50-FG-45024-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2555 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 9.675 | CML-9 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 12 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.9 | 10 | 9.6 | 0.3594
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-11 | 400-FH-43508-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6560 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 11.575 | CML-11 | CML: Reducer | 3 | 2062-08-12 | 2057-12-18 | 2015-03-30 07:00 | 3 | 0 | A2: Right Quadrant |  | 4.92 | 3 | 3.465 | 11.1 | 3 O'Clock | 500 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 11.8 | 11.1 | 11.5 | 11.9 | 0.3594
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-15 | 250-PW-20040-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21399 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.65 | CML-15 | CML: Fitting | 6 | 2027-01-30 | 2025-01-06 | 2014-07-12 07:30 | 4.1 | 0.62883 | A1: Outside Quadrant |  | 6.7 | 4.1 | 5.4 | 12 | 12 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 12 | 13.2 | 12.9 | 12.5 | 0.51962
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-12 | 50-PW-44040-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1987 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.8667 | CML-12 | CML: Equal Tee | 3 | 2075-09-10 | 2082-05-17 | 2014-03-27 07:00 | 2.5 | 0.04878 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  |  | 5.5 | 6.3 | 5.8 | 0.40415
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-1 | 150-PG-20054-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21512 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 11.625 | CML-1 | CML: Elbow | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.1 | 12 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.1 | 11.9 | 11.7 | 11.8 | 0.3594
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-14 | 100-FG-45043-03C02-E CML-14 | yes | FPSO 2015 | Pipe Wall Thickness | 22660 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.125 | CML-14 | CML: Elbow | 3 | 2018-12-19 | 2018-03-15 | 2015-04-27 07:00 | 1.88 | 0.74544 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 4.6 | 12 O'Clock | 50 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 12 O'Clock | 6 O'Clock | 9 O'Clock | 2.72 |  | 5.3 | 4.6 | 5.2 | 5.4 | 0.3594
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23415-01C03 | CML-2 | 100-PG-23415-01C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20782 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 7.75 | CML-2 | CML: type TBC | 6 | 2016-07-01 | 2016-01-19 | 2014-10-02 07:00 | 2.5 | 2.7433 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 7.3 | 9 O'Clock | 150 | 10.97 | 150-PG-23415-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8 | 8 | 7.7 | 7.3 | 0.33166
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-7 | 50-CG-38452-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1122 |  | 2014-03-21 11:30 | 2014-03-21 12:00 | [36 empty] | 7.375 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-21 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 12 O'Clock | 300 | 6.35 | 300-WC-40044-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.2 | 7.3 | 7.9 | 0.3594
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-10 | 250-PG-23005-06C03 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10056 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 16.725 | CML-10 | CML: Elbow | 6 | 2015-08-30 | 2015-03-28 | 2013-11-06 | 8.6 | 4.2968 | A1: Outside Quadrant |  | 12.26 | 8.6 | 10.43 | 16.4 | 12 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 16.4 | 17.2 | 16.8 | 16.5 | 0.3594
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-4 | 250-PW-44006-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7996 | Leak x 2 | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 5.6 | CML-4 | CML: Pipe Length | 3 | 2020-01-20 | 2020-01-03 | 2015-01-20 08:30 | 2.5 | 0.57951 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.85149 | 5.4 | 5.9 | 5.4 | 5.7 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FH-43308-01C02 | CML-3 | 50-FH-43308-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20440 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 7.45 | CML-3 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-07-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 6 O'Clock | 50 | 5.54 | 50-FH-43308-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.8 | 7.3 | 7.4 | 0.23805
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-1 | 200-PW-44021-01X01 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10706 | Deck Level. Line is FFS. High CR. Line rechecked (refer to Jan. 15 values) | 2013-11-10 | 2013-11-10 |  |  | Administrator | 2015-09-04 14:24 | [32 empty] | 5.55 | CML-1 | CML: Elbow | 3 | 2015-03-19 | 2015-03-14 | 2013-11-10 | 2.5 | 2.1404 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 6 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 5.4 | 5.6 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43141-01C02 | CML-5 | 150-FH-43141-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10656 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.675 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-18 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-FH-43141-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7 | 6.6 | 6.9 | 6.2 | 0.3594
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38460-01C02-P | CML-5 | 80-CG-38460-01C02-P CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 20886 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 7.825 | CML-5 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.3 | 3 O'Clock | 80 | 5.49 | 80-CG-38460-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.1 | 7.3 | 7.9 | 8 | 0.3594
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40051-01C02 | CML-5 | 50-WC-40051-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1568 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 6.825 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.7 | 7 | 6.7 | 5.9 | 0.74554
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-17 | 150-PG-20507-01C03-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2861 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.525 | CML-17 | CML: type TBC | 6 | 2020-04-22 | 2019-04-21 | 2014-03-16 07:00 | 2.5 | 1.2281 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10 | 12 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 10.8 | 10.6 | 10.7 | 0.3594
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-5 | 50-PW-44013-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22724 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.625 | CML-5 | CML: Elbow | 3 | 2054-10-23 | 2059-04-03 | 2015-04-28 07:00 | 2.5 | 0.07339 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.23567 | 5.8 | 5.7 | 5.6 | 5.4 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-5 | 50-PW-44015-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22710 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.475 | CML-5 | CML: Pipe Length | 3 | 2054-10-23 | 2059-04-03 | 2015-04-28 07:00 | 2.5 | 0.07339 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.23558 | 5.4 | 5.7 | 5.4 | 5.4 | 0.15
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38460-01C02-P | CML-1 | 80-CG-38460-01C02-P CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 20882 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.525 | CML-1 | CML: Elbow | 3 | 2027-04-04 | 2028-11-12 | 2014-10-04 07:00 | 2.5 | 0.21589 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-CG-38460-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.2 | 5.3 | 6 | 0.3594
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-16 | 250-PW-44006-01X01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8008 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.15 | CML-16 | CML: Pipe Length | 3 | 2020-11-01 | 2020-10-12 | 2015-01-20 08:30 | 2.5 | 0.51851 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 0.85149 | 6.3 | 7.2 | 5.5 | 5.6 | 0.78528
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-11 | 100-DH-56082-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 3379 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 5.775 | CML-11 | CML: type TBC | 3 | 2019-10-12 | 2019-12-28 | 2014-05-10 09:30 | 2.5 | 0.55271 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 6 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 5.7 | 5.5 | 5.6 | 0.3594
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-1 | 50-CG-38474-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23625 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 6.025 | CML-1 | CML: Equal Tee | 3 | 2196-05-18 | 2216-01-06 | 2015-10-28 07:00 | 2.5 | 0.0166 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.2 | 6.3 | 5.5 | 6.1 | 0.3594
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-6 | 100-DH-56009-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3429 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 6.475 | CML-6 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.2 | 3 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.2 | 7 | 6.4 | 0.3594
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40016-01C02 | CML-9 | 250-WC-40016-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20371 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 | Check Corrosion Rate of 0.334mm/ yr |  | Nestor | 2014-11-24 10:38 | [32 empty] | 6.525 | CML-9 | CML: Elbow | 3 | 2024-12-11 | 2024-11-11 | 2014-10-06 07:00 | 2.5 | 0.33364 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 7 | 7 | 5.9 | 0.56199
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-1 | 250-WC-40017-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2064 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | Check Corrosion Rate of 0.547mm/ yr | [35 empty] | 6.675 | CML-1 | CML: type TBC | 3 | 2020-06-14 | 2020-05-26 | 2014-03-28 09:30 | 2.5 | 0.54678 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.1 | 7 | 6.7 | 5.9 | 0.54391
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20394 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 7.475 | CML-4 | CML: Pipe Length | 3 | 2059-07-07 | 2055-11-27 | 2014-10-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 3 O'Clock | 150 | 7.11 | 150-WC-40404-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.4 | 7.2 | 7.3 | 8 | 0.3594
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40045-01C02 | CML-5 | 300-WC-40045-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1066 |  | 2014-03-20 14:30 | 2014-03-20 15:00 | Check Corrosion Rate of 0.561mm/ yr | [35 empty] | 6.45 | CML-5 | CML: type TBC | 3 | 2020-04-08 | 2020-03-21 | 2014-03-20 14:30 | 2.5 | 0.56134 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 300 | 6.35 | 300-WC-40045-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.7 | 6.2 | 7 | 0.49329
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-15 | 25-FG-45455-01C02-E CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1817 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | Check Corrosion Rate of 1.219mm/ yr | [35 empty] | 6.475 | CML-15 | CML: Elbow | 3 | 2017-03-12 | 2016-11-24 | 2014-04-29 11:00 | 2.5 | 1.2187 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6 | 9 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.7 | 6.8 | 6.4 | 6 | 0.3594
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-11 | 50-FG-45024-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1215 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.475 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.4 | 6.8 | 6.7 | 0.3594
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-5 | 150-FH-43026-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12645 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.225 | CML-5 | CML: Pipe Length | 3 | 2022-12-20 | 2021-03-31 | 2014-01-22 07:00 | 1.03 | 0.63602 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.7 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.67 |  | 7.5 | 6.7 | 7.3 | 7.4 | 0.3594
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-7 | 25-VA-23054-01C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10103 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 16.325 | CML-7 | CML: Pipe Length | 6 | 2103-11-30 | 2088-08-29 | 2013-11-07 | 5.22 | 0 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 15.8 | 6 O'Clock | 40 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.58 |  | 16.5 | 16.4 | 15.8 | 16.6 | 0.3594
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-11 | 50-DH-56137-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5865 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 18.825 | CML-11 | CML: Reducer | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 10:30 | 3.3 | 0 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 18.5 | 12 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.2 |  | 18.5 | 19.3 | 18.9 | 18.6 | 0.3594
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-5 | 300-PG-20005-03C03-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22767 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 52.8 | CML-5 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 15.6 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 | 3.6253 | 16.2 | 16.4 | 16.3 | 15.6 | 0.3594
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-19 | 50-DH-56062-01C02 CML-19 | yes | FPSO 2015 | Pipe Wall Thickness | 9106 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.625 | CML-19 | CML: type TBC | 3 | 2017-09-15 | 2018-03-02 | 2015-03-02 07:00 | 2.5 | 0.70797 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 5.1 | 4.4 | 4.7 | 4.3 | 0.3594
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56069-01C02 | CML-1 | 50-DH-56069-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3396 | Rope Access | 2014-05-10 13:00 | 2014-05-10 14:00 | [36 empty] | 5.125 | CML-1 | CML: type TBC | 3 | 2017-04-12 | 2017-09-10 | 2014-05-10 13:00 | 2.5 | 0.78622 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56069-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 5.6 | 4.8 | 5.2 | 0.3594
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-10 | 50-CG-38470-01C02-P CML-10 | Yes | FPSO 2015 | Pipe Wall Thickness | 23616 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 6.375 | CML-10 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 6.3 | 5.9 | 6.7 | 0.3594
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-11 | 200-PL-20008-01C02-H CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 8808 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 7.175 | CML-11 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.4 | 7.8 | 6.8 | 6.7 | 0.51881
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56012-01C02 | CML-1 | 80-DH-56012-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3467 | Rope Access | 2014-05-13 10:30 | 2014-05-13 12:00 | [36 empty] | 5.425 | CML-1 | CML: type TBC | 3 | 2018-03-22 | 2018-10-13 | 2014-05-13 10:30 | 2.5 | 0.62161 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-DH-56012-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.5 | 5.6 | 4.9 | 5.7 | 0.3594
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5787 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.925 | CML-1 | CML: Elbow | 3 | 2036-06-15 | 2038-12-05 | 2014-06-23 13:00 | 2.5 | 0.13186 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.4 | 6.2 | 6.1 | 0.3594
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-49 | 200-PL-20019-01C02 CML-49 |  | FPSO 2014 | Pipe Wall Thickness | 21300 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.375 | CML-49 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.6 | 7.3 | 7.1 | 7.5 | 0.22174
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56129-01C02 | CML-2 | 50-DH-56129-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3285 | Rope Access | 2014-05-09 15:30 | 2014-05-09 16:00 | [36 empty] | 6.125 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 15:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-DH-56129-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 5.8 | 6.2 | 6.6 | 0.3594
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-12 | 200-PL-20008-01C02-H CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8809 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.95 | CML-12 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7 | 7.2 | 6.9 | 6.7 | 0.20817
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-10 | 150-FL-43514-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20503 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.575 | CML-10 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 7.3 | 3 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.5 | 7.3 | 7.4 | 8.1 | 0.3594
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56011-01C02 | CML-2 | 50-DH-56011-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1835 | Rope Access | 2014-05-06 09:30 | 2014-05-06 10:30 | [36 empty] | 7.575 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 12 O'Clock | 50 | 5.54 | 50-DH-56011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.4 | 8.1 | 7.5 | 0.3594
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57063-01C02 | CML-6 | 50-DC-57063-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1391 | Rope access | 2014-04-05 13:00 | 2014-04-05 14:00 | [36 empty] | 7.525 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 3 O'Clock | 50 | 5.54 | 50-DC-57063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.5 | 7.3 | 7.5 | 7.8 | 0.20616
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-8 | 50-DN-56101-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 848 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 7.9333 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-02 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 6 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.5 | 9 | 7.3 |  | 0.92916
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56097-01C02 | CML-4 | 50-DN-56097-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1326 |  | 2014-04-01 07:00 | 2014-04-01 08:00 | [36 empty] | 7.8 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-01 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-DN-56097-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  |  | 7.7 | 8.4 | 7.3 | 0.55678
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56011-01C02 | CML-2 | 50-DH-56011-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22315 | Rope Access | 2014-05-06 09:30 | 2014-05-06 10:30 | [36 empty] | 7.575 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 12 O'Clock | 50 | 5.54 | 50-DH-56011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.4 | 8.1 | 7.5 | 0.3594
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-5 | 200-PL-20018-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 23877 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 7.325 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 9 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.5 | 7.4 | 7.3 | 7.1 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40016-01C02 | CML-11 | 250-WC-40016-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20373 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 | Check Corrosion Rate of 0.334mm/ yr |  | Nestor | 2014-11-24 10:39 | [32 empty] | 6.55 | CML-11 | CML: Elbow | 3 | 2024-12-11 | 2024-11-11 | 2014-10-06 07:00 | 2.5 | 0.33364 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7 | 6.7 | 6.6 | 5.9 | 0.46547
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-8 | 50-PW-44014-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2010 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 6.125 | CML-8 | CML: Elbow | 3 | 2075-09-19 | 2082-05-27 | 2014-03-27 10:00 | 2.5 | 0.04876 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 5.5 | 6.5 | 6.8 | 0.62383
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-4 | 200-PL-20018-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 23876 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 7.275 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 9 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.3 | 7.4 | 7.3 | 7.1 | 0.12583
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-4 | 25-PG-23300-25C02 CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 20671 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 8.625 | CML-4 | CML: Elbow | 3 | 2019-04-10 | 2018-03-21 | 2014-05-27 09:30 | 4.4 | 0.80009 | A4: Left Quadrant |  | 6.09 | 4.4 | 5.245 | 8.3 | 9 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 8.7 | 8.4 | 9.1 | 8.3 | 0.3594
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-14 | 100-PW-20021-01C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21817 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6 | CML-14 | CML: Elbow | 3 | 2022-08-19 | 2022-12-08 | 2014-10-11 07:00 | 2.5 | 0.38167 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.3 | 6.2 | 6 | 0.3559
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-34 | 150-PG-23506-25C02 CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 20661 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | [36 empty] | 20.375 | CML-34 | CML: Pipe Length | 3 | 2016-08-29 | 2015-11-03 | 2014-05-28 07:00 | 15.88 | 1.869 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.1 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.22 | 4.938 | 20.1 | 20.3 | 20.9 | 20.2 | 0.3594
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-14 | 250-PW-20022-01C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2057 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 11.1 | CML-14 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 10.4 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 11.3 | 11.5 | 11.2 | 10.4 | 0.48305
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-8 | 400-FH-43508-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6557 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.6 | CML-8 | CML: Pipe Length | 3 | 2062-08-12 | 2057-12-18 | 2015-03-30 07:00 | 3 | 0 | A1: Outside Quadrant |  | 4.92 | 3 | 3.465 | 9.2 | 12 O'Clock | 500 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.2 | 9.9 | 9.9 | 9.4 | 0.3559
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45052-03C02 | CML-1 | 150-FG-45052-03C02 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24331 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.1 | CML-1 | CML: Elbow | 3 | 2022-08-15 | 2021-01-05 | 2016-06-06 07:00 | 2.5 | 0.50046 | A1: Outside Quadrant |  | 4.11 | 2.5 | 3.305 | 5.6 | 12 O'Clock | 150 | 7.11 | 150-FG-45052-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.4 | 6.3 | 6.1 | 0.3559
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-25 | 80-PW-44001-01C02-P CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 23234 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.875 | CML-25 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 2.2703 | 5.7 | 6.1 | 5.5 | 6.2 | 0.3304
CG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20268 | Rope Access | 2014-05-26 08:00 | 2014-05-26 09:00 | Check Corrosion Rate of 0.549mm/ yr | [35 empty] | 5.3 | CML-1 | CML: type TBC | 3 | 2022-11-01 | 2021-06-27 | 2014-05-26 08:00 | 0.37 | 0.54852 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 5 | 9 O'Clock | 50 | 5.54 | 50-DC-57028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.63 |  | 5 | 5.7 | 5.5 | 5 | 0.3559
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-7 | 80-CG-38459-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 24266 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 19.7 | CML-7 | CML: Reducer | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A4: Left Quadrant |  | 11.27 | 7 | 9.135 | 19.4 | 9 O'Clock | 150 | 14.27 | 150-PG-23026-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.4 |  | 20.2 | 19.5 | 19.7 | 19.4 | 0.3559
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-5 | 80-PW-44016-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21937 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.725 | CML-5 | CML: Pipe Length | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 9 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 6.1 | 5.5 | 5.5 | 0.28723
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56129-01C02 | CML-3 | 50-DH-56129-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3286 | Rope Access | 2014-05-09 15:30 | 2014-05-09 16:00 | [36 empty] | 5.5 | CML-3 | CML: type TBC | 3 | 2021-10-20 | 2022-09-14 | 2014-05-09 15:30 | 2.5 | 0.36218 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-DH-56129-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.7 | 5.9 | 0.3559
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-1 | 150-WC-40004-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1803 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | Check Corrosion Rate of 1.328mm/ yr | [35 empty] | 6.35 | CML-1 | CML: Elbow | 3 | 2016-11-18 | 2016-08-11 | 2014-04-29 11:00 | 2.5 | 1.3284 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.9 | 12 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.4 | 6.6 | 6.5 | 0.31091
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-5 | 50-PL-20033-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21834 |  | 2014-10-12 07:00 | 2014-10-12 12:00 | [36 empty] | 7.9667 | CML-5 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 | -3.6533 | 8.6 | 8 |  | 7.3 | 0.65064
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57024-01C02 | CML-6 | 50-DC-57024-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2878 | Rope Access | 2014-04-24 13:00 | 2014-04-24 14:00 | Check Corrosion Rate of 0.379mm/ yr | [35 empty] | 5.425 | CML-6 | CML: type TBC | 3 | 2027-01-19 | 2025-02-06 | 2014-04-24 13:00 | 0.37 | 0.37888 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.83 |  | 5.2 | 5.6 | 5.6 | 5.3 | 0.20616
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57024-01C02 | CML-3 | 50-DC-57024-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2875 | Rope Access | 2014-04-24 13:00 | 2014-04-24 14:00 | Check Corrosion Rate of 0.379mm/ yr | [35 empty] | 5.2 | CML-3 | CML: type TBC | 3 | 2027-01-19 | 2025-02-06 | 2014-04-24 13:00 | 0.37 | 0.37888 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DC-57024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.83 |  | 5.2 | 5.2 | 5.2 | 5.2 | 0
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-3 | 50-PL-23020-01C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10117 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8 | CML-3 | CML: type TBC | 6 | 2015-08-15 | 2015-07-30 | 2013-11-08 | 2.5 | 2.8287 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.5 | 6 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.2 | 8.3 | 7.5 | 8 | 0.3559
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-8 | 150-WC-40002-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20347 | Reviewed on 18/11/14. Line is FFS. Repeat on Oct.19 | 2014-10-09 07:00 | 2014-10-09 15:00 | Check Corrosion Rate of 0.892mm/ yr |  | Nestor | 2014-11-24 10:27 | [32 empty] | 6.1 | CML-8 | CML: Elbow | 3 | 2018-08-01 | 2018-03-06 | 2014-10-09 07:00 | 2.5 | 0.8917 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.9 | 9 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6 | 6.3 | 5.9 | 0.18257
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-7 | 100-FG-45043-03C02-E CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22653 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 10.5 | CML-7 | CML: Equal Tee | 3 | 2054-10-24 | 2049-02-10 | 2015-04-27 07:00 | 1.88 | 0 | A4: Left Quadrant |  | 3.02 | 1.88 | 2.45 | 10 | 9 O'Clock | 100 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.12 |  | 10.8 | 10.5 | 10.7 | 10 | 0.3559
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45032-03C02 | CML-2 | 100-FG-45032-03C02 CML-2 | yes | FPSO 2013 | Pipe Wall Thickness | 10643 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5 | CML-2 | CML: type TBC | 3 |  |  | 2013-11-18 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 4.5 | 9 O'Clock | 100 |  | 100-FG-45032-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.2 | 5.3 | 5 | 4.5 | 0.3559
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-33 | 250-PW-44006-01X01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 23204 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.075 | CML-33 | CML: Elbow | 3 | 2022-03-18 | 2022-02-23 | 2015-05-11 07:00 | 2.5 | 0.43741 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 2.3031 | 6.5 | 5.5 | 5.8 | 6.5 | 0.5058
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-6 | 200-WC-40008-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7812 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 6.075 | CML-6 | CML: Fitting | 3 | 2027-04-08 | 2027-03-02 | 2015-01-13 09:30 | 2.5 | 0.27773 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 6 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6.2 | 5.9 | 6.2 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40062-01C02 | CML-6 | 100-WC-40062-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 830 |  | 2014-04-02 08:00 | 2014-04-02 09:00 | [36 empty] | 6 | CML-6 | CML: Pipe Length | 3 | 2037-12-08 | 2038-09-30 | 2014-04-02 08:00 | 2.5 | 0.14345 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 3 O'Clock | 100 | 6.02 | 100-WC-40062-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 5.9 | 6 | 6.1 | 0.08165
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-4 | 100-WC-40027-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23424 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 |  |  | Nestor | 2016-04-01 | Description | [31 empty] | 6.1 | CML-4 | CML: Fitting | 3 | 2390-05-19 | 2402-10-30 | 2015-07-23 07:00 | 2.5 | 0.00933 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | -0.38267 | 6.2 | 6 | 6.1 | 6.1 | 0.08165
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-6 | 80-PW-44035-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21929 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 5.775 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 6.1 | 5.9 | 0.27538
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-5 | 100-DH-56082-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3373 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.8 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.3 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7.1 | 7 | 6.8 | 0.3559
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43301-01C02-E | CML-2 | 200-PL-43301-01C02-E CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8599 | Line is FFS. Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-02-09 07:30 | 2015-02-09 15:00 |  |  | Administrator | 2015-09-07 16:33 | [32 empty] | 6.05 | CML-2 | CML: Fitting | 3 | 2024-09-21 | 2023-05-08 | 2015-02-09 07:30 | 1.34 | 0.44274 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 5.6 | 3 O'Clock | 200 | 6.35 | 200-PL-43301-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.26 |  | 6.1 | 5.6 | 6.7 | 5.8 | 0.47958
DH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-DH-56004-01C02 | CML-8 | 80-DH-56004-01C02 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 23243 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 3.6 | CML-8 | CML: Pipe Length | 3 | 2016-01-19 | 2016-05-01 | 2015-05-11 07:00 | 2.5 | 1.1527 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.3 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 | 0.089024 | 3.6 | 4.1 | 3.3 | 3.4 | 0.3559
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-35 | 200-PL-20019-01C02 CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 21286 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.7 | CML-35 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.4 | 7.4 | 7.3 | 7.7 | 0.49666
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-15 | 100-FG-45001-09C02 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10430 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.3 | CML-15 | CML: type TBC | 3 | 2015-12-26 | 2015-04-20 | 2013-11-13 | 4.7 | 2.4997 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 10.7 | 10 | 10 | 10.5 | 0.3559
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-1 | 200-PL-20018-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 23873 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 7.675 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 9 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.6 | 7.8 | 8 | 7.3 | 0.29861
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-17 | 50-PL-45016-03C03 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10457 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 7.8 | CML-17 | CML: type TBC | 6 | 2016-01-11 | 2015-09-25 | 2013-11-13 | 0.99 | 2.9642 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 7.4 | 3 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.41 |  | 7.6 | 7.4 | 8.1 | 8.1 | 0.3559
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-25 | 250-PW-20040-03C03-P CML-25 | yes | FPSO 2014 | Pipe Wall Thickness | 21409 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.6 | CML-25 | CML: Elbow | 6 | 2029-05-11 | 2026-12-13 | 2014-07-12 07:30 | 4.1 | 0.53899 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.1 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 14.1 | 13.4 | 14.8 | 12.1 | 1.1518
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-4 | 50-PG-23024-03C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10036 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 8.4 | CML-4 | CML: Elbow | 6 | 2017-12-16 | 2017-06-10 | 2013-11-06 | 0.97 | 1.7095 | A2: Right Quadrant |  | 2.74 | 0.97 | 1.855 | 8 | 3 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.03 |  | 8.2 | 8 | 8.7 | 8.7 | 0.3559
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-19 | 200-PG-23065-09C02-A CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 433 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.4 | CML-19 | CML: Elbow | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A1: Outside Quadrant |  | 15.26 | 10.17 | 12.715 | 18.9 | 12 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.73 |  | 18.9 | 20.3 | 19.1 | 19.3 | 0.62183
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57003-01C02 | CML-10 | 80-DC-57003-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12512 |  | 2014-02-04 16:00 | 2014-02-04 17:00 | [36 empty] | 5.4 | CML-10 | CML: Pipe Length | 3 | 2050-11-10 | 2046-01-29 | 2014-02-04 16:00 | 0.54 | 0.1321 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57003-01C02 | CML-4 | 80-DC-57003-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12506 |  | 2014-02-04 16:00 | 2014-02-04 17:00 | [36 empty] | 5.625 | CML-4 | CML: Pipe Length | 3 | 2050-11-10 | 2046-01-29 | 2014-02-04 16:00 | 0.54 | 0.1321 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.9 | 5.5 | 5.4 | 5.7 | 0.22174
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-20 | 100-PW-20021-01C02-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 22838 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.9 | CML-20 | CML: Elbow | 3 | 2026-05-10 | 2026-10-14 | 2015-04-30 07:00 | 2.5 | 0.27181 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 0.36318 | 5.5 | 6 | 6.1 | 6 | 0.2708
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-16 | 400-FH-43508-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6565 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.7 | CML-16 | CML: Elbow | 3 | 2032-06-16 | 2029-12-11 | 2015-03-30 07:00 | 2.5 | 0.28443 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.5 | 7.4 | 8.2 | 7.7 | 0.3559
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-20 | 50-CG-38487-09C02-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23589 | Re-check of line as requested by ops supervisor (Additional CML @ corroded location) | 2015-09-10 07:00 | 2015-09-10 09:00 | Check Corrosion Rate of %vmm/ yr |  | John Wilson | 2017-03-24 11:17 | [32 empty] | 8.4 | CML-20 | CML: Pipe Length | 3 | 2030-04-28 | 2025-12-07 | 2015-09-10 07:00 | 2.5 | 0.36882 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 7.9 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.4 | 8.7 | 8.6 | 0.3559
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 |  | 50-PG-23024-03C03 | Yes | FPSO 2013 | Pipe Wall Thickness | 1 |  | 2013-11-06 13:00 | [37 empty] | 8.4 | 50-PG-23024-03C03 | Piping | 6 | 2016-08-21 |  | 2013-11-06 13:00 |  | 1.9339 | A1: Outside Quadrant |  |  | 2.5 |  | 7.9 | 12 O'Clock | 50 | 8.74 | Pipework | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.6 | 8.7 | 8.4 | 0.3559
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-4 | 150-FL-43514-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20497 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 8.9 | CML-4 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 8.4 | 12 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.9 | 9.2 | 9.1 | 0.3559
PL03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PL-57066-01C03 | CML-2 | 50-PL-57066-01C03 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22955 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.6 | CML-2 | CML: Elbow | 6 | 2028-04-13 | 2026-07-24 | 2015-05-04 07:00 | 2.5 | 0.52492 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.3 | 6 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | 1.46 | 9.4 | 10.1 | 9.3 | 9.6 | 0.3559
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-1 | 50-PG-23024-03C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10033 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 8.4 | CML-1 | CML: Elbow | 6 | 2017-06-01 | 2016-12-17 | 2013-11-06 | 0.97 | 1.9405 | A1: Outside Quadrant |  | 2.74 | 0.97 | 1.855 | 7.9 | 12 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.93 |  | 7.9 | 8.6 | 8.7 | 8.4 | 0.3559
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-3 | 100-DH-56088-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5196 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 10.3 | CML-3 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.8 | 9 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.3 | 10.6 | 10.5 | 9.8 | 0.3559
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-18 | 200-PG-23065-09C02-A CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 432 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.2333 | CML-18 | CML: Pipe Length | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 18.9 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.73 |  | 19.6 | 18.9 |  | 19.2 | 0.35119
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-18 | 300-PF-20501-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21694 | Low Reading 300x150mm area to 10mm Outside Radius | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 13.95 | CML-18 | CML: Pipe Length | 6 | 2031-12-16 | 2028-08-15 | 2014-09-28 07:00 | 4.9 | 0.50496 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14.2 | 14.3 | 13.6 | 13.7 | 0.35119
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-29 | 50-DH-56062-01C02 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 9116 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 8.05 | CML-29 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.4 | 8.3 | 7.7 | 7.8 | 0.35119
CG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1374 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 7.4667 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  |  | 7.5 | 7.8 | 7.1 | 0.35119
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40013-01C02 | CML-5 | 50-WC-40013-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1560 | Rope Access | 2014-04-09 10:00 | 2014-04-09 11:00 | [36 empty] | 7.1 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-WC-40013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 8 | 7 | 7.3 | 6.1 | 0.7874
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-13 | 50-DH-56116-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5223 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.05 | CML-13 | CML: Elbow | 3 | 2016-11-30 | 2017-04-17 | 2014-05-20 09:30 | 2.5 | 0.86758 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 5.4 | 4.8 | 4.7 | 0.35119
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56010-01C02 | CML-3 | 50-DH-56010-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22320 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 5.15 | CML-3 | CML: type TBC | 3 | 2017-03-26 | 2017-08-23 | 2014-05-06 10:30 | 2.5 | 0.79573 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.5 | 4.9 | 5.4 | 4.8 | 0.35119
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56010-01C02 | CML-3 | 50-DH-56010-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1840 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 5.15 | CML-3 | CML: type TBC | 3 | 2017-03-26 | 2017-08-23 | 2014-05-06 10:30 | 2.5 | 0.79573 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.5 | 4.9 | 5.4 | 4.8 | 0.35119
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-1 | 50-CG-38466-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 2515 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.4333 | CML-1 | CML: type TBC | 3 | 2019-03-13 | 2019-10-25 | 2014-04-02 13:00 | 2.5 | 0.52562 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 5.1 |  | 5.8 | 5.4 | 5.1 | 0.35119
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-WC-40068-01C02 | CML-2 | 80-WC-40068-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 926 |  | 2014-04-10 11:00 | 2014-04-10 12:00 | [36 empty] | 6.925 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-04-10 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 12 O'Clock | 80 | 5.49 | 80-WC-40068-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 7.9 | 6.8 | 6.9 | 0.74106
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-1 | 80-FH-43151-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2235 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 6.05 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 5.8 | 6.4 | 0.35119
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43035-01C02 | CML-5 | 100-FH-43035-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12664 |  | 2014-01-22 10:00 | 2014-01-22 11:00 | [36 empty] | 6.15 | CML-5 | CML: type TBC | 3 | 2023-09-23 | 2024-01-26 | 2014-01-22 10:00 | 2.5 | 0.3411 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 12 O'Clock | 100 | 6.02 | 100-FH-43035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.4 | 5.9 | 6.5 | 0.35119
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20059-01C02 | CML-3 | 200-PL-20059-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2868 | Rope Access | 2014-03-25 11:00 | 2014-03-25 12:00 | [36 empty] | 7.625 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-25 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 12 O'Clock | 200 | 6.35 | 200-PL-20059-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.7 | 7.7 | 7.8 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43138-01C02 | CML-2 | 50-FH-43138-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12866 |  | 2014-01-21 09:30 | 2014-01-21 10:00 | [36 empty] | 5.25 | CML-2 | CML: Elbow | 3 | 2016-06-18 | 2016-10-15 | 2014-01-21 09:30 | 2.5 | 0.9966 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FH-43138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.6 | 4.9 | 5.5 | 0.35119
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-WC-40068-01C02 | CML-2 | 80-WC-40068-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1590 |  | 2014-04-10 11:00 | 2014-04-10 12:00 | [36 empty] | 6.925 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-04-10 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 12 O'Clock | 80 | 5.49 | 80-WC-40068-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 7.9 | 6.8 | 6.9 | 0.74106
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-5 | 50-WC-40028-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1685 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 6.925 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.9 | 6.1 | 7.6 | 7.1 | 0.62383
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-24 | 200-PL-20010-01C02-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 23824 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.475 | CML-24 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.6 | 9 | 8.9 | 7.4 | 0.73655
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-16 | 150-FH-43518-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2716 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.25 | CML-16 | CML: Pipe Length | 3 | 2035-03-20 | 2031-07-11 | 2014-03-12 09:00 | 1.23 | 0.26954 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.9 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.67 | 0 | 6.9 | 7.6 | 7.5 | 7 | 0.35119
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-16 | 150-FH-43518-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 355 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.25 | CML-16 | CML: Pipe Length | 3 | 2035-03-10 | 2031-07-02 | 2014-03-12 | 1.23 | 0.26989 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.9 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.67 |  | 6.9 | 7.6 | 7.5 | 7 | 0.35119
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56120-01C02 | CML-6 | 50-DH-56120-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21038 | Rope Access | 2014-05-19 08:00 | 2014-05-19 09:00 | [36 empty] | 9.25 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-19 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56120-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9 | 8.9 | 9.5 | 9.6 | 0.35119
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-8 | 50-CG-38487-09C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23577 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 10.65 | CML-8 | CML: Reducer | 3 | 2075-10-24 | 2059-08-12 | 2015-09-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.3 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 | 0.42566 | 10.3 | 10.9 | 10.4 | 11 | 0.35119
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-8 | 200-PG-24001-09C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10264 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 17.65 | CML-8 | CML: Elbow | 3 | 2017-07-29 | 2016-03-08 | 2013-11-09 | 9.2 | 2.1764 | A3: Inside Quadrant |  | 15.26 | 9.2 | 12.23 | 17.3 | 6 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 17.9 | 17.4 | 17.3 | 18 | 0.35119
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-22 | 200-PG-23007-09C03-PA CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 20709 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 |  |  | John Wilson | 2017-03-23 09:52 | [32 empty] | 20.65 | CML-22 | CML: Pipe Length | 6 | 2048-07-09 | 2041-02-04 | 2014-06-30 13:00 | 10.22 | 0.29604 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 20.3 | 12 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.08 |  | 20.3 | 21 | 20.9 | 20.4 | 0.35119
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-32 | 250-PW-44006-01X01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 23203 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.05 | CML-32 | CML: Pipe Length | 3 | 2022-03-18 | 2022-02-23 | 2015-05-11 07:00 | 2.5 | 0.43741 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -0.98704 | 6.4 | 5.8 | 5.5 | 6.5 | 0.47958
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-4 | 0200-DH-56L9003-AC21M-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5089 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 7.975 | CML-4 | CML: type TBC | 3 | 2023-01-29 | 2021-05-07 | 2015-03-06 07:00 | 2.5 | 0.61967 | A3: Inside Quadrant |  | 5.74 | 2.5 | 3.5737 | 7.4 | 6 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.1 | 8.4 | 7.4 | 8 | 0.41932
SD02 | Montara_Topside | No | Steam (55) | Pipework | 50-SL-55003-01C02-P | CML-6 | 50-SL-55003-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8858 |  | 2015-02-24 11:00 | 2015-02-24 12:00 | [36 empty] | 7.8 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-24 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 12 O'Clock | 50 | 5.54 | 50-SL-55003-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.6 | 8 | 8.2 | 0.36515
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40403-01C02 | CML-4 | 100-WC-40403-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20384 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.3 | CML-4 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 9 O'Clock | 80 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.9 | 6.1 | 6.1 | 6.1 | 0.4
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-11 | 100-FG-45001-09C02 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10426 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.375 | CML-11 | CML: type TBC | 3 | 2016-07-15 | 2015-09-15 | 2013-11-13 | 4.7 | 2.0573 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 10.2 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 10.2 | 10.2 | 10.9 | 10.2 | 0.35
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-7 | 250-PW-20040-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21391 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.45 | CML-7 | CML: Elbow | 6 | 2029-05-11 | 2026-12-13 | 2014-07-12 07:30 | 4.1 | 0.53899 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.1 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 13.5 | 13.7 | 14.5 | 12.1 | 0.99833
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-2 | 50-FL-43454-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1858 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.625 | CML-2 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.8 | 9.1 | 9.8 | 9.8 | 0.35
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-20 | 50-PL-45016-03C03 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10460 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.375 | CML-20 | CML: type TBC | 6 | 2018-02-23 | 2017-08-11 | 2013-11-13 | 0.99 | 1.637 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 8 | 3 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.01 |  | 8.2 | 8 | 8.5 | 8.8 | 0.35
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-21 | 250-PW-44006-01X01 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 1918 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 20.025 | CML-21 | CML: Fitting | 3 | 2017-02-11 | 2017-02-01 | 2014-03-26 07:00 | 2.5 | 1.0401 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.5 | 6.2 | 6.1 | 5.5 | 0.41932
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57303-03C03 | CML-3 | 20-DC-57303-03C03 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7928 |  | 2015-01-17 10:30 | 2015-01-17 12:00 | [36 empty] | 7.65 | CML-3 | CML: type TBC | 6 | 2044-01-06 | 2058-09-17 | 2015-01-17 10:30 | 2.5 | 0 | A2: Right Quadrant |  | -0.44 | 2.5 | 1.03 | 7.4 | 3 O'Clock | 20 | 5.56 | 20-DC-57303-03C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.7 | 7.4 | 7.9 | 7.6 | 0.20817
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-13 | 200-PL-20018-01C02-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23477 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 7.925 | CML-13 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2015-07-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 6 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | -1.9402 | 8.1 | 8 | 7.4 | 8.2 | 0.3594
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-9 | 80-CG-38459-09C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23706 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 6.475 | CML-9 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 12 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.6 | 6.3 | 6.9 | 0.35
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-8 | 200-PL-20018-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 23880 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 7.675 | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 12 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.7 | 8.1 | 7.5 | 0.30957
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45051-03C02 | CML-7 | 150-FG-45051-03C02 CML-7 | yes | FPSO 2016 | Pipe Wall Thickness | 24381 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.325 | CML-7 | CML: Elbow | 3 | 2024-01-10 | 2022-03-04 | 2016-06-06 07:00 | 2.5 | 0.43417 | A2: Right Quadrant |  | 4.11 | 2.5 | 3.305 | 5.8 | 3 O'Clock | 150 | 7.11 | 150-FG-45051-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 5.8 | 6.5 | 6.5 | 0.35
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML90 | 150-FH-43141-01C02 CML90 | yes | FPSO 2015 | Pipe Wall Thickness | 7335 |  | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 3.775 | CML90 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.9 | 4.2 | 3.4 | 3.6 | 0.35
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-13 | 50-CG-38465-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20876 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 8.725 | CML-13 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 6 O'Clock | 80 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 10.7 | 8.3 | 7.4 | 8.5 | 1.4009
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-22 | 50-DH-56137-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21106 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.025 | CML-22 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.5 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.2 | 6.2 | 6.2 | 5.5 | 0.35
FL02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-FL-43454-01C02-P | CML-12 | 50-FL-43454-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1653 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.525 | CML-12 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.1 | 9 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.4 | 9.9 | 9.7 | 9.1 | 0.35
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-15 | 50-FG-45024-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1198 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 10.075 | CML-15 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.7 | 12 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 10.5 | 10.2 | 9.9 | 0.35
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-7 | 300-PW-44003-01C03 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21849 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 10.95 | CML-7 | CML: Reducing Tee | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.5 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11.1 | 11.7 | 10.5 | 10.5 | 0.57446
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-9 | 200-PG-20300-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5874 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | [36 empty] | 12.975 | CML-9 | CML: Fitting | 6 | 2113-08-19 | 2095-07-04 | 2014-06-25 09:30 | 3.3 | 0.09373 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 12.6 | 12 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.6 | 13.1 | 12.8 | 13.4 | 0.35
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38489-01C02-P | CML-3 | 50-CG-38489-01C02-P CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 20860 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 5.225 | CML-3 | CML: Elbow | 3 | 2018-11-27 | 2019-07-01 | 2014-10-02 07:00 | 2.5 | 0.55315 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-CG-38489-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 4.8 | 5.4 | 5.6 | 0.35
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-5 | 50-PG-23074-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20627 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.725 | CML-5 | CML: Elbow | 3 | 2027-12-28 | 2029-07-22 | 2014-07-26 07:00 | 2.5 | 0.20843 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.3 | 6.1 | 5.6 | 0.35
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-1 | 80-FH-43005-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 12551 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 4.625 | CML-1 | CML: type TBC | 3 | 2014-11-24 | 2015-01-26 | 2014-01-20 10:00 | 2.5 | 2.0172 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.2 | 12 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.8 | 5 | 4.5 | 0.35
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-6 | 50-FG-45018-03C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2588 | Rope Access | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 5.125 | CML-6 | CML: type TBC | 3 | 2016-09-04 | 2016-08-27 | 2014-04-26 07:00 | 2.5 | 0.93109 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | -1.1245 | 5.5 | 4.7 | 5.3 | 5 | 0.35
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-4 | 50-FG-45021-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2616 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.175 | CML-4 | CML: type TBC | 3 | 2017-02-13 | 2017-02-04 | 2014-04-26 10:45 | 2.5 | 0.81986 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.90432 | 5.6 | 5 | 5.3 | 4.8 | 0.35
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-28 | 250-PW-44006-01X01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 8020 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.05 | CML-28 | CML: Fitting | 3 | 2020-11-01 | 2020-10-12 | 2015-01-20 08:30 | 2.5 | 0.51851 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -0.36492 | 6.2 | 6.3 | 5.5 | 6.2 | 0.36968
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-2 | 100-DH-56009-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3425 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.575 | CML-2 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.2 | 6 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.7 | 5.2 | 6 | 0.35
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-6 | 80-PW-44035-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23270 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.625 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 0 | 5.9 | 5.5 | 5.5 | 5.6 | 0.1893
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-20 | 100-DH-56082-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 3388 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.325 | CML-20 | CML: type TBC | 3 | 2040-12-28 | 2041-11-26 | 2014-05-10 09:30 | 2.5 | 0.12755 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 6.5 | 6.2 | 5.9 | 0.35
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-18 | 200-PL-20035-03C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21350 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 9.575 | CML-18 | CML: Pipe Length | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 8.6 | 9 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.99 |  | 9.4 | 9.9 | 10.4 | 8.6 | 0.76757
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-23 | 250-WC-40017-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 2086 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | Check Corrosion Rate of 0.304mm/ yr | [35 empty] | 6.4 | CML-23 | CML: type TBC | 3 | 2026-01-30 | 2025-12-27 | 2014-03-28 09:30 | 2.5 | 0.30377 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.5 | 6.2 | 6.8 | 6.1 | 0.31623
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40045-01C02 | CML-2 | 300-WC-40045-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1063 |  | 2014-03-20 14:30 | 2014-03-20 15:00 | Check Corrosion Rate of 0.312mm/ yr | [35 empty] | 6.4 | CML-2 | CML: type TBC | 3 | 2025-10-02 | 2025-08-30 | 2014-03-20 14:30 | 2.5 | 0.31185 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 300 | 6.35 | 300-WC-40045-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.6 | 6.3 | 6.6 | 0.24495
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38460-01C02-P | CML-2 | 80-CG-38460-01C02-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 20883 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 7.075 | CML-2 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-10-04 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.7 | 9 O'Clock | 80 | 5.49 | 80-CG-38460-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.9 | 7.5 | 7.2 | 6.7 | 0.35
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-11 | 150-FL-43174-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12909 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.425 | CML-11 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 9 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.6 | 7.8 | 7.3 | 7 | 0.35
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-9 | 150-FL-43174-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12907 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.425 | CML-9 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 9 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.6 | 7.8 | 7.3 | 7 | 0.35
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23038 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 5.925 | CML-1 | CML: Fitting | 3 | 2022-02-24 | 2022-01-31 | 2015-05-06 07:00 | 2.5 | 0.44051 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 0.34128 | 5.9 | 5.9 | 5.5 | 6.4 | 0.36856
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20962 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 7.625 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.8 | 8 | 7.5 | 7.2 | 0.35
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-21 | 50-CG-38452-09C02-P CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 23761 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.825 | CML-21 | CML: Elbow | 3 | 2057-09-12 | 2046-03-15 | 2015-10-30 07:00 | 2.5 | 0.14082 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.7 | 9 | 9.2 | 0.35
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-13 | 50-PL-23516-03C03 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7801 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 15:58 | [32 empty] | 8.825 | CML-13 | CML: Elbow | 6 | 2043-02-15 | 2042-07-22 | 2015-01-13 07:00 | 2.5 | 0.20988 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9 | 9.2 | 8.7 | 0.35
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-2 | 200-PW-44020-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23009 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 6 | CML-2 | CML: Reducing Tee | 3 | 2022-02-19 | 2022-01-27 | 2015-05-05 07:00 | 2.5 | 0.44114 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 12 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 0.57083 | 5.5 | 6.1 | 6.2 | 6.2 | 0.33665
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-22 | 400-FH-43508-01C02 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6571 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.225 | CML-22 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 8.8 | 12 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9.6 | 9.4 | 9.1 | 0.35
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-23 | 100-DH-56082-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 3391 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.425 | CML-23 | CML: type TBC | 3 | 2040-12-28 | 2041-11-26 | 2014-05-10 09:30 | 2.5 | 0.12755 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 6.6 | 5.9 | 6.6 | 0.35
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-4 | 50-DC-57451-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1375 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 7.5667 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  |  | 7.7 | 7.4 | 7.6 | 0.15275
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-13 | 50-CG-38487-09C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20813 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 11.675 | CML-13 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 11.5 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 11.5 | 12.2 | 11.5 | 11.5 | 0.35
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-30 | 200-PG-23007-09C03-PA CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 20717 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 |  |  | John Wilson | 2017-03-23 09:35 | [32 empty] | 20.825 | CML-30 | CML: Equal Tee | 6 | 2048-07-09 | 2041-02-04 | 2014-06-30 13:00 | 10.22 | 0.29604 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 20.3 | 12 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.08 |  | 20.3 | 21 | 21 | 21 | 0.35
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-26 | 80-CG-38459-09C02-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 20010 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 22.875 | CML-26 | CML: type TBC | 6 | 2117-05-30 | 2095-05-30 | 2014-01-10 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 22.7 | 6 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.48 |  | 22.7 | 22.7 | 22.7 | 23.4 | 0.35
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-6 | 50-DH-56137-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22768 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 19.675 | CML-6 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 19.5 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.6 | 1.7501 | 19.5 | 19.5 | 19.5 | 20.2 | 0.35
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-21 | 200-PG-24001-09C02 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10277 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 17.975 | CML-21 | CML: Pipe Length | 3 | 2019-06-20 | 2017-06-10 | 2013-11-09 | 9.2 | 1.4963 | A2: Right Quadrant |  | 15.26 | 9.2 | 12.23 | 17.6 | 3 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 17.8 | 17.6 | 18.1 | 18.4 | 0.35
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20043 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 20.8 | CML-6 | CML: Pipe Length | 3 | 2017-07-26 | 2016-07-08 | 2014-05-29 07:00 | 15.88 | 1.4608 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 9 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 | 0 | 21.1 | 20.5 | 21.1 | 20.5 | 0.34641
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-17 | 200-FH-43003-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12540 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 10.1 | CML-17 | CML: Tee | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 11:30 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 9.7 | 12 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.36 |  | 9.7 | 10.3 | 10.3 |  | 0.34641
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-8 | 50-PL-23023-03C03 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10208 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.3 | CML-8 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.8 | 8.2 | 8.2 | 8 | 0.34641
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-3 | 300-PF-20500-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21623 | Protective mesh removed | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.3 | CML-3 | CML: Fitting | 6 | 2059-05-03 | 2051-01-28 | 2014-09-27 07:00 | 4.9 | 0.20391 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 14.2 | 14.2 | 14.8 | 14 | 0.34641
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-9 | 50-PW-44012-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2023 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 5.725 | CML-9 | CML: Pipe Length | 3 | 2075-09-18 | 2082-05-26 | 2014-03-27 09:30 | 2.5 | 0.04876 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 5.6 | 6.2 | 0.32016
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-6 | 100-DH-56088-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5199 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 7.1 | CML-6 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 9 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.4 | 7.2 | 7.2 | 6.6 | 0.34641
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20013-01C02-P | CML-5 | 200-PL-20013-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21215 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.55 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 9 O'Clock | 200 | 6.35 | 200-PL-20013-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 9.2 | 9 | 8.5 | 7.5 | 0.75939
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-50 | 300-PF-20001-03C03-P CML-50 |  | FPSO 2014 | Pipe Wall Thickness | 21188 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [35 empty] | Low alarm breach | 7.8 | CML-50 | CML: Reducer | 6 | 2015-05-15 | 2014-11-21 | 2014-07-16 07:30 | 2.5 | 6.0224 | A1: Outside Quadrant |  | 8.27 | 2.5 | 5.385 | 7.5 | 12 O'Clock | 20 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.7 | 8.3 | 7.7 | 0.34641
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-22 | 150-FG-45505-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 22362 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 8 | CML-22 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 3 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.3 | 7.5 | 8.1 | 8.1 | 0.34641
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-3 | 200-WC-40008-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7809 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 6.325 | CML-3 | CML: Fitting | 3 | 2038-05-08 | 2038-03-02 | 2015-01-13 09:30 | 2.5 | 0.1543 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 6.4 | 6.6 | 0.22174
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-17 | 80-CG-38459-09C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21583 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.1 | CML-17 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 3 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.2 | 8.6 | 9.2 | 9.4 | 0.34641
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57012-01C02 | CML-4 | 50-DC-57012-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2883 | Rope Access | 2014-04-24 14:00 | 2014-04-24 15:00 | [36 empty] | 5.45 | CML-4 | CML: type TBC | 3 | 2032-09-25 | 2029-12-22 | 2014-04-24 14:00 | 0.37 | 0.26741 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DC-57012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.93 |  | 5.3 | 5.3 | 5.4 | 5.8 | 0.23805
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40011-01C02 | CML-2 | 50-WC-40011-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1887 | Rope Access | 2014-03-25 13:00 | 2014-03-25 14:00 | [36 empty] | 6.25 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-WC-40011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.4 | 6.4 | 6.1 | 0.17321
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45036-03C02 | CML-3 | 50-FG-45036-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2575 |  | 2014-04-26 13:00 | 2014-04-26 14:00 | [36 empty] | 5.3 | CML-3 | CML: type TBC | 3 | 2017-02-13 | 2017-02-04 | 2014-04-26 13:00 | 2.5 | 0.81962 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45036-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 5.6 | 4.8 | 5.4 | 0.34641
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-2 | 200-PW-44021-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7699 | Re-check. This point has increased CR when compared to CR in 2013. To be rechecked | 2015-01-08 15:30 | 2015-01-08 16:30 |  |  | Administrator | 2015-09-04 14:23 | [32 empty] | 5.875 | CML-2 | CML: Reducing Tee | 3 | 2020-09-09 | 2020-08-20 | 2015-01-08 15:30 | 2.5 | 0.52885 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 9 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 1.3753 | 6.2 | 5.8 | 6 | 5.5 | 0.29861
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-23 | 300-FL-43070-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 12716 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.2 | CML-23 | CML: type TBC | 3 | 2019-03-01 | 2019-02-13 | 2014-02-01 09:00 | 2.5 | 0.66938 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.1 | 6.1 | 6.7 | 0.34641
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-1 | 250-PW-44007-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23134 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.825 | CML-1 | CML: Pipe Length | 3 | 2022-03-14 | 2022-02-18 | 2015-05-10 07:00 | 2.5 | 0.43803 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -0.2672 | 5.8 | 6.2 | 5.5 | 5.8 | 0.28723
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-9 | 50-DH-56116-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5219 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.2 | CML-9 | CML: Elbow | 3 | 2016-11-30 | 2017-04-17 | 2014-05-20 09:30 | 2.5 | 0.86758 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 5.5 | 5.3 | 4.7 | 0.34641
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-3 | 100-FL-43455-01C02-P CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 20486 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 5.3 | CML-3 | CML: Elbow | 3 | 2018-01-14 | 2018-03-11 | 2014-10-03 07:00 | 2.5 | 0.7609 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 3 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5.2 | 5.8 | 0.34641
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40062-01C02 | CML-2 | 100-WC-40062-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 826 |  | 2014-04-02 08:00 | 2014-04-02 09:00 | [36 empty] | 6.225 | CML-2 | CML: Fitting | 3 | 2048-08-12 | 2049-10-10 | 2014-04-02 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 6 O'Clock | 100 | 6.02 | 100-WC-40062-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.4 | 6.1 | 6.3 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40402-01C02 | CML-7 | 100-WC-40402-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20380 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.225 | CML-7 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 9 O'Clock | 100 | 6.02 | 100-WC-40402-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.4 | 6.2 | 6.1 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57003-01C02 | CML-9 | 80-DC-57003-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12511 |  | 2014-02-04 16:00 | 2014-02-04 17:00 | [36 empty] | 6.025 | CML-9 | CML: Elbow | 3 | 2062-11-29 | 2056-08-05 | 2014-02-04 16:00 | 0.54 | 0 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 6.6 | 5.9 | 5.5 | 6.1 | 0.45735
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57003-01C02 | CML-7 | 80-DC-57003-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12509 |  | 2014-02-04 16:00 | 2014-02-04 17:00 | [36 empty] | 5.825 | CML-7 | CML: Elbow | 3 | 2062-11-29 | 2056-08-05 | 2014-02-04 16:00 | 0.54 | 0 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 6.1 | 5.6 | 5.5 | 6.1 | 0.32016
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57003-01C02 | CML-1 | 80-DC-57003-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12503 |  | 2014-02-04 16:00 | 2014-02-04 17:00 | [36 empty] | 5.95 | CML-1 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-02-04 16:00 | 0.54 | 0 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 5.9 | 6.2 | 5.5 | 6.2 | 0.33166
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-21 | 80-PW-44001-01C02-P CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 23230 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.425 | CML-21 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 1.5718 | 5.6 | 6.6 | 7.2 | 6.3 | 0.66521
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-12 | 100-PG-23503-03C03-A CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5514 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 10.8 | CML-12 | CML: Pipe Length | 6 | 2022-02-05 | 2022-07-09 | 2014-06-01 07:00 | 5.66 | 0.6295 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.5 | 3 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.84 | -0.45673 | 10.5 | 10.5 | 11.1 | 11.1 | 0.34641
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-2 | 50-CG-38466-01C02 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 2516 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.4 | CML-2 | CML: type TBC | 3 | 2020-11-22 | 2021-09-12 | 2014-04-02 13:00 | 2.5 | 0.40616 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 5.2 |  | 5.8 | 5.2 | 5.2 | 0.34641
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43300-01C02-E | CML-8 | 200-PL-43300-01C02-E CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8594 | Line is FFS. Action: to recheck in two years (Feb. 2017) to confirm CR. | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-07 16:36 | [32 empty] | 5.8 | CML-8 | CML: Fitting | 3 | 2024-09-15 | 2023-05-03 | 2015-02-08 11:00 | 1.34 | 0.44335 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 5.6 | 9 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.26 |  | 6 | 5.9 | 5.7 | 5.6 | 0.18257
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-11 | 80-CG-38459-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 3009 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.7 | CML-11 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.4 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.79 | 0 | 8.4 | 9 | 9 | 8.4 | 0.34641
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-11 | 80-CG-38459-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 22288 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.7 | CML-11 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.4 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.79 |  | 8.4 | 9 | 9 | 8.4 | 0.34641
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-5 | 200-FH-43114-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12813 |  | 2014-02-01 12:00 | 2014-02-01 14:00 | [36 empty] | 9.3 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 12:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.9 | 6 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  |  | 9.5 | 8.9 | 9.5 | 0.34641
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-7 | 50-WC-40032-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1241 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 6.225 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 6.3 | 6.3 | 0.095743
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20031-01C03-P | CML-1 | 150-PG-20031-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 23863 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.65 | CML-1 | CML: Elbow | 6 | 2027-12-10 | 2025-10-27 | 2014-09-26 07:00 | 2.5 | 0.58274 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.2 | 12 O'Clock | 150 | 10.97 | 150-PG-20031-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.2 | 10.6 | 11 | 10.8 | 0.34157
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-18 | 300-PG-23001-03C03 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 10968 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 13.85 | CML-18 | CML: Elbow | 6 | 2020-07-23 | 2019-05-10 | 2014-01-09 | 5.22 | 1.266 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 13.5 | 12 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.28 |  | 13.5 | 13.9 | 14.3 | 13.7 | 0.34157
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-16 | 200-PG-23007-09C03-PA CML-16 |  | FPSO 2016 | Pipe Wall Thickness | 24450 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | Check Corrosion Rate of 0.621mm/ yr |  | John Wilson | 2017-03-23 09:16 | Loss within CA no further action required | [31 empty] | 19.15 | CML-16 | CML: Fitting | 6 | 2030-02-23 | 2026-08-10 | 2016-07-03 07:00 | 10.22 | 0.62112 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 18.7 | 6 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.48 | 0.31556 | 19.3 | 19.1 | 18.7 | 19.5 | 0.34157
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-2 | 200-PW-44021-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23017 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 5.925 | CML-2 | CML: Reducing Tee | 3 | 2022-02-19 | 2022-01-27 | 2015-05-05 07:00 | 2.5 | 0.44114 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 0 | 6 | 6.1 | 5.5 | 6.1 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-7 | 50-PW-44014-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2009 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 5.825 | CML-7 | CML: Elbow | 3 | 2075-09-19 | 2082-05-27 | 2014-03-27 10:00 | 2.5 | 0.04876 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.9 | 6.1 | 5.8 | 0.25
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45024-01C02 | CML-2 | 50-FG-45024-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1874 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.55 | CML-2 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.2 | 12 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.4 | 10 | 9.6 | 0.34157
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-4 | 200-PW-44021-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7701 | Re-check. Line is FFS. This point has increased CR when compared to CR in 2013. To be rechecked | 2015-01-08 15:30 | 2015-01-08 16:30 |  |  | Administrator | 2015-09-13 11:01 | [32 empty] | 5.7 | CML-4 | CML: Reducer | 3 | 2020-09-09 | 2020-08-20 | 2015-01-08 15:30 | 2.5 | 0.52885 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 1.2893 | 5.6 | 5.7 | 5.5 | 6 | 0.21602
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56084-01C02 | CML-5 | 100-DH-56084-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3347 | Rope Access | 2014-05-08 13:00 | 2014-05-08 14:00 | [36 empty] | 8.45 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.1 | 12 O'Clock | 100 | 6.02 | 100-DH-56084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.3 | 8.5 | 8.9 | 0.34157
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38486-09C02-P |  | 80-CG-38486-09C02-P |  | FPSO 2015 | Pipe Wall Thickness | 23649 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 11.55 | 80-CG-38486-01C02-H | Piping | 3 | 2043-04-25 |  | 2015-10-28 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 11.2 | 3 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.4 | 11.2 | 11.6 | 12 | 0.34157
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44036-01C02-P | CML-5 | 80-PW-44036-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21957 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 6.5 | CML-5 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.5 | 7.1 | 6.8 | 0.64807
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-16 | 80-PW-44001-01C02-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23225 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.15 | CML-16 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 2.445 | 5.6 | 6 | 6.8 | 6.2 | 0.5
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40045-01C02 | CML-1 | 300-WC-40045-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1062 |  | 2014-03-20 14:30 | 2014-03-20 15:00 | Check Corrosion Rate of 0.312mm/ yr | [35 empty] | 6.2 | CML-1 | CML: type TBC | 3 | 2025-10-02 | 2025-08-30 | 2014-03-20 14:30 | 2.5 | 0.31185 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 300 | 6.35 | 300-WC-40045-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 6.3 | 6.2 | 0.08165
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-18 | 50-FL-43454-01C02-P CML-18 | Yes | FPSO 2014 | Pipe Wall Thickness | 20521 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 19.7 | CML-18 | CML: Reducing Tee | 3 | 2042-08-16 | 2045-10-03 | 2014-10-05 07:00 | 2.5 | 0.10401 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 6.2 | 5.4 | 5.6 | 0.34157
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44027-01X01 | CML-2 | 50-PW-44027-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21904 |  | 2014-06-19 08:30 | 2014-06-19 09:00 | [36 empty] | 5.65 | CML-2 | CML: Reducer | 3 | 2093-03-07 | 2101-09-29 | 2014-06-19 08:30 | 2.5 | 0.03808 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-PW-44027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.6 | 5.9 | 5.5 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-10 | 200-FH-43004-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12550 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 6.75 | CML-10 | CML: type TBC | 3 | 2065-02-15 | 2064-09-30 | 2014-02-01 07:00 | 2.5 | 0.0744 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 7.1 | 6.9 | 6.3 | 0.34157
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-13 | 50-FL-43454-01C02-P CML-13 | High Priority | FPSO 2014 | Pipe Wall Thickness | 20516 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.35 | CML-13 | CML: Elbow | 3 | 2019-10-21 | 2020-06-28 | 2014-10-05 07:00 | 2.5 | 0.47548 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.5 | 5.3 | 5.7 | 4.9 | 0.34157
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43171-01C02 | CML-2 | 80-FL-43171-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20524 |  | 2014-10-06 07:00 | 2014-10-06 15:00 | [36 empty] | 5.45 | CML-2 | CML: Elbow | 3 | 2021-08-21 | 2022-08-06 | 2014-10-06 07:00 | 2.5 | 0.3633 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-FL-43171-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5.4 | 5.6 | 5 | 0.34157
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44027-01X01 | CML-2 | 50-PW-44027-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5575 |  | 2014-06-19 08:30 | 2014-06-19 09:00 | [36 empty] | 5.65 | CML-2 | CML: Reducer | 3 | 2093-03-07 | 2101-09-29 | 2014-06-19 08:30 | 2.5 | 0.03808 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-PW-44027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 5.3006 | 5.6 | 5.6 | 5.9 | 5.5 | 0.17321
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57303-03C03 | CML-2 | 20-DC-57303-03C03 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7927 |  | 2015-01-17 10:30 | 2015-01-17 12:00 | [36 empty] | 7.6 | CML-2 | CML: type TBC | 6 | 2044-01-06 | 2058-09-17 | 2015-01-17 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | -0.44 | 2.5 | 1.03 | 7.5 | 6 O'Clock | 20 | 5.56 | 20-DC-57303-03C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.6 | 7.6 | 7.5 | 7.7 | 0.08165
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-14 | 50-DH-56070-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 3230 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.15 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 6.3 | 5.7 | 6.1 | 0.34157
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-25 | 200-PL-20010-01C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 23825 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.5 | CML-25 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.6 | 8.6 | 9.3 | 7.5 | 0.74386
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-5 | 80-DC-57002-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20234 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.875 | CML-5 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.5 | 3 O'Clock | 20 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.3 | 7.5 | 7.8 | 7.9 | 0.3304
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-8 | 100-FH-43507-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7872 | Line is FFS. It has been check twice. The higher values reported here are from the data collected in Apr. 2014. The rechecked CR’s from data from Jan. 2015 are lower. Current RBI frequency is 48m. Action: to recheck line in a 24m (Jan. 2017) to confirm CR. | 2015-01-14 09:30 | 2015-01-14 10:30 |  |  | Administrator | 2015-09-07 17:07 | [32 empty] | 6.85 | CML-8 | CML: Fitting | 3 | 2023-12-12 | 2023-02-14 | 2015-01-14 09:30 | 2.5 | 0.43746 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.2 | 7 | 6.4 | 6.8 | 0.34157
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43116-01C02 | CML-5 | 150-FH-43116-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7869 | Line is FFS. It has been check twice. The higher values reported here are from the data collected in Apr. 2014. The rechecked CR’s from data from Jan. 2015 are lower. Current RBI frequency is 48m. Action: to recheck line in a 24m (Jan. 2017) to confirm CR. | 2015-01-14 09:30 | 2015-01-14 10:30 |  |  | Administrator | 2015-09-07 17:06 | [32 empty] | 7.05 | CML-5 | CML: Pipe Length | 3 | 2031-08-26 | 2030-03-23 | 2015-01-14 09:30 | 2.5 | 0.25262 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 12 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 | -0.13939 | 6.7 | 7.1 | 7.5 | 6.9 | 0.34157
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-12 | 300-FL-43080-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2391 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 7.15 | CML-12 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 6 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7 | 7.6 | 6.8 | 7.2 | 0.34157
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-10 | 250-PW-44006-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8002 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.15 | CML-10 | CML: Pipe Length | 3 | 2021-10-28 | 2021-10-06 | 2015-01-20 08:30 | 2.5 | 0.4575 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.48657 | 6.7 | 6.6 | 5.6 | 5.7 | 0.58023
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40047-01C02 | CML-4 | 50-WC-40047-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1704 | Rope Access | 2014-04-13 10:15 | 2014-04-13 11:15 | [36 empty] | 7.2333 | CML-4 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 10:15 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40047-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  |  | 7.7 | 6.2 | 7.8 | 0.89629
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-19 | 50-CG-38452-09C02-P CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 23759 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.25 | CML-19 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.8 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.2 | 8.8 | 9.4 | 9.6 | 0.34157
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-2 | 300-FH-43001-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12514 |  | 2014-01-24 13:00 | 2014-01-24 15:00 | [36 empty] | 10.25 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-24 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.8 | 6 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.2 | 10.4 | 9.8 | 10.6 | 0.34157
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56018-01C02 | CML-1 | 80-DH-56018-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3477 | Rope Access | 2014-05-13 14:00 | 2014-05-13 15:00 | [36 empty] | 10.75 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-13 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 10.4 | 12 O'Clock | 80 | 5.49 | 80-DH-56018-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 10.8 | 10.6 | 11.2 | 0.34157
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23032-01C03 | CML-2 | 50-PL-23032-01C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20786 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 8.65 | CML-2 | CML: Elbow | 6 | 2032-09-07 | 2032-04-24 | 2014-10-10 07:00 | 2.5 | 0.3236 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 12 O'Clock | 50 | 8.74 | 50-PL-23032-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.1 | 8.5 | 8.7 | 0.34157
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-21 | 80-PW-20024-01C03-P CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 23065 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 16.275 | CML-21 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2015-05-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 16 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.5 |  | 16.6 | 16.4 | 16.1 | 16 | 0.27538
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23743 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 12.35 | CML-3 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 11.9 | 12 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 11.9 | 12.3 | 12.5 | 12.7 | 0.34157
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23018-09C03-A | CML-4 | 200-PG-23018-09C03-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13065 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 20.05 | CML-4 | CML: type TBC | 6 | 2019-09-05 | 2018-05-06 | 2014-01-10 07:00 | 10.17 | 1.6673 | A2: Right Quadrant |  | 14.62 | 10.17 | 12.395 | 19.6 | 3 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.43 |  | 20 | 19.6 | 20.4 | 20.2 | 0.34157
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-16 | 50-CG-38452-09C02-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23756 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.325 | CML-16 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 9 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.2 | 9 | 9.3 | 9.8 | 0.34034
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-1 | 80-PG-20046-03C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23337 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-19 07:00 | 2015-07-19 15:00 | [36 empty] | 10.825 | CML-1 | CML: Pipe Length | 6 | 2042-08-09 | 2038-02-26 | 2015-07-19 07:00 | 2.5 | 0.29545 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.5 | 12 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | -0.28371 | 10.5 | 10.8 | 11.3 | 10.7 | 0.34034
PF02 | Montara_Topside | No | Separation (20) | Pipework | 50-PF-20063-03S01-P | CML-2 | 50-PF-20063-03S01-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21544 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 8.15 | CML-2 | CML: Reducer | 1 | 2027-07-07 | 2025-06-19 | 2014-07-13 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.91 | 2.5 | 2.705 | 7.5 | 9 O'Clock | 150 | 3.91 | 50-PF-20063-03S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.2 | 8.7 | 8.2 | 7.5 | 0.49329
PF02 | Montara_Topside | No | Separation (20) | Pipework | 50-PF-20063-03S01-P | CML-1 | 50-PF-20063-03S01-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21543 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 8.075 | CML-1 | CML: Reducer | 1 | 2027-07-07 | 2025-06-19 | 2014-07-13 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.91 | 2.5 | 2.705 | 7.5 | 3 O'Clock | 100 | 3.91 | 50-PF-20063-03S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8 | 7.5 | 8.5 | 8.3 | 0.43493
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-23 | 200-PG-23013-09C03-A CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 20007 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 20.525 | CML-23 | CML: type TBC | 6 | 2028-07-13 | 2025-05-02 | 2014-01-10 | 10.22 | 0.68744 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 20.2 | 9 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.98 |  | 20.5 | 21 | 20.4 | 20.2 | 0.34034
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-3 | 200-PG-23008-15S01-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3178 | Rope Access | 2014-05-07 13:00 | 2014-05-07 14:00 | [36 empty] | 5.425 | CML-3 | CML: type TBC | 3 | 2019-11-09 | 2020-07-19 | 2014-05-07 13:00 | 2.5 | 0.4716 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DH-56052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.9 | 5.1 | 5.3 | 5.4 | 0.34034
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-3 | 200-PG-23008-15S01-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20130 | Rope Access | 2014-05-07 13:00 | 2014-05-07 14:00 | [36 empty] | 5.425 | CML-3 | CML: type TBC | 3 | 2019-11-09 | 2020-07-19 | 2014-05-07 13:00 | 2.5 | 0.4716 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 1751.9996 | 5.9 | 5.1 | 5.3 | 5.4 | 0.34034
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-4 | 150-WC-40004-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1806 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | Check Corrosion Rate of 0.999mm/ yr | [35 empty] | 6.95 | CML-4 | CML: Elbow | 3 | 2018-01-10 | 2017-08-31 | 2014-04-29 11:00 | 2.5 | 0.99907 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.2 | 6 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.3 | 6.5 | 6.2 | 7.8 | 0.73258
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-6 | 80-FL-43015-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22949 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.925 | CML-6 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.35096 | 5.6 | 5.8 | 6.4 | 5.9 | 0.34034
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40016-01C02 | CML-3 | 250-WC-40016-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20365 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-24 10:37 | [32 empty] | 6.6 | CML-3 | CML: Pipe Length | 3 | 2048-01-04 | 2047-10-04 | 2014-10-06 07:00 | 2.5 | 0.11121 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 7.4 | 6.2 | 6.2 | 0.56569
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-5 | 50-PL-23042-09C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10070 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.075 | CML-5 | CML: type TBC | 6 | 2015-12-14 | 2015-07-28 | 2013-11-07 | 2.5 | 3.3745 | A2: Right Quadrant |  | 5.07 | 2.5 | 3.785 | 9.6 | 3 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.4 | 9.6 | 10.2 | 10.1 | 0.34034
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-24 | 350-FL-43511-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 2305 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 7.975 | CML-24 | CML: type TBC | 3 | 2023-08-21 | 2022-04-16 | 2014-03-17 08:00 | 2.5 | 0.52984 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.5 | 3 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8 | 7.5 | 8.3 | 8.1 | 0.34034
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43115-01C02 | CML-7 | 80-FH-43115-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12827 |  | 2014-01-20 09:00 | 2014-01-20 10:00 | [36 empty] | 8.425 | CML-7 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-20 09:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.1 | 6 O'Clock | 80 | 5.49 | 80-FH-43115-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.9 | 8.4 | 8.1 | 8.3 | 0.34034
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-7 | 50-FG-45020-03C02 CML-7 | yes | FPSO 2013 | Pipe Wall Thickness | 10579 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.925 | CML-7 | CML: type TBC | 3 | 2014-10-08 | 2014-10-04 | 2013-11-17 | 2.5 | 2.2462 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.8 | 5.2 | 5.2 | 4.5 | 0.34034
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-6 | 200-PG-23008-15S01-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21044 | Rope Access | 2014-05-19 07:00 | 2014-05-19 08:00 | [36 empty] | 5.375 | CML-6 | CML: type TBC | 3 | 2020-01-30 | 2020-10-17 | 2014-05-19 07:00 | 2.5 | 0.45587 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56121-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.8 | 5.1 | 5.5 | 5.1 | 0.34034
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43144-01C02 | CML-2 | 100-FH-43144-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10525 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.725 | CML-2 | CML: type TBC | 3 | 2015-08-26 | 2015-09-22 | 2013-11-15 | 2.5 | 1.5736 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 12 O'Clock | 100 | 6.02 | 100-FH-43144-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6 | 6 | 5.6 | 0.34034
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-16 | 200-PL-20010-01C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 23816 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.4 | CML-16 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.5 | 8.7 | 8.9 | 7.5 | 0.62183
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-11 | 200-FH-43012-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2841 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.275 | CML-11 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7 | 9 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.66 |  | 7.7 | 7.4 | 7 | 7 | 0.34034
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56113-01C02 | CML-4 | 50-DH-56113-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5243 | Rope Access | 2014-05-20 14:00 | 2014-05-20 15:00 | [36 empty] | 5.275 | CML-4 | CML: Elbow | 3 | 2017-05-23 | 2017-10-26 | 2014-05-20 14:00 | 2.5 | 0.76389 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-DH-56113-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.6 | 4.8 | 5.4 | 5.3 | 0.34034
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56115-01C02 | CML-5 | 50-DH-56115-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5236 | Rope Access | 2014-05-20 13:00 | 2014-05-20 14:00 | [36 empty] | 5.275 | CML-5 | CML: Elbow | 3 | 2017-05-23 | 2017-10-26 | 2014-05-20 13:00 | 2.5 | 0.76398 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56115-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 5.4 | 5.6 | 4.8 | 0.34034
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-11 | 50-DH-56116-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5221 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.225 | CML-11 | CML: Elbow | 3 | 2018-01-04 | 2018-07-03 | 2014-05-20 09:30 | 2.5 | 0.66102 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 5.2 | 5.7 | 4.9 | 0.34034
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-22 | 100-DH-56086-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 20981 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 5.775 | CML-22 | CML: type TBC | 3 | 2018-02-03 | 2018-04-01 | 2014-05-16 13:00 | 2.5 | 0.75184 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.8 | 6.1 | 5.3 | 0.34034
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43021-01C02 | CML-2 | 80-FH-43021-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23521 | Re-check on line as Per RBI 2014 Report | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 5.725 | CML-2 | CML: Elbow | 3 | 2085-01-09 | 2093-05-12 | 2015-07-28 07:00 | 2.5 | 0.04173 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-FH-43021-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.61864 | 5.7 | 5.4 | 6.2 | 5.6 | 0.34034
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML3 | 50-CG-38452-09C02-P CML3 |  | FPSO 2015 | Pipe Wall Thickness | 7532 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.525 | CML3 |  | 3 | 2051-11-30 | 2051-08-19 | 2015-04-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 9 O'Clock | 25 | 6.35 | 25-DH-56143-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.8 | 7.8 | 7.4 | 7.1 | 0.34034
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56120-01C02 | CML-3 | 50-DH-56120-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21035 | Rope Access | 2014-05-19 08:00 | 2014-05-19 09:00 | [36 empty] | 5.175 | CML-3 | CML: type TBC | 3 | 2016-11-27 | 2017-04-12 | 2014-05-19 08:00 | 2.5 | 0.8702 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-DH-56120-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.5 | 4.7 | 5.3 | 5.2 | 0.34034
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-1 | 200-PW-44019-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21892 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 6.05 | CML-1 | CML: Fitting | 3 | 2018-10-21 | 2018-10-06 | 2014-06-19 09:30 | 2.5 | 0.71401 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.6 | 5.9 | 5.6 | 6.1 | 0.42032
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-48 | 200-PL-20019-01C02 CML-48 |  | FPSO 2014 | Pipe Wall Thickness | 21299 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.875 | CML-48 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.8 | 8.6 | 7.6 | 0.49917
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38460-01C02-P | CML-8 | 80-CG-38460-01C02-P CML-8 | yes | FPSO 2014 | Pipe Wall Thickness | 20889 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.525 | CML-8 | CML: Fitting | 3 | 2027-04-04 | 2028-11-12 | 2014-10-04 07:00 | 2.5 | 0.21589 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 50 | 5.49 | 80-CG-38460-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.5 | 6 | 0.34034
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-16 | 80-CG-38459-09C02-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23713 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.625 | CML-16 | CML: Elbow | 3 | 2051-05-21 | 2055-10-22 | 2015-10-30 07:00 | 2.5 | 0.07869 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 20 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 6.1 | 5.6 | 0.34034
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-42 | 50-DH-56070-01C02 CML-42 |  | FPSO 2014 | Pipe Wall Thickness | 3258 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.825 | CML-42 | CML: type TBC | 3 | 2084-08-21 | 2092-04-12 | 2014-05-09 07:00 | 2.5 | 0.04265 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 5.5 | 5.7 | 5.8 | 0.34034
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-33 | 100-DC-57036-01C02 CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 1439 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 8.375 | CML-33 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.5 | 6 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 9.5 | 8.9 | 7.5 | 7.6 | 0.98446
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-6 | 50-DC-57451-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1377 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 7.9667 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  |  | 8 | 8.4 | 7.5 | 0.45092
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43113-01C02 | CML-2 | 80-FH-43113-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20429 | Rope Access | 2014-05-25 14:00 | 2014-05-25 15:00 | [36 empty] | 6.025 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-25 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 6 O'Clock | 80 | 5.49 | 80-FH-43113-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 6.5 | 5.7 | 5.9 | 0.34034
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-3 | 250-PW-44004-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22747 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 6.1 | CML-3 | CML: Pipe Length | 3 | 2023-03-20 | 2023-02-22 | 2015-04-29 07:00 | 2.5 | 0.39259 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.1351 | 6.4 | 6.6 | 5.6 | 5.8 | 0.4761
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-1 | 200-PW-44019-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5567 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 6.05 | CML-1 | CML: Fitting | 3 | 2018-10-21 | 2018-10-06 | 2014-06-19 09:30 | 2.5 | 0.71401 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.6 | 5.9 | 5.6 | 6.1 | 0.42032
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-3 | 50-DC-57056-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1135 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 7.5667 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 7.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  |  | 7.6 | 7.5 | 7.6 | 0.057735
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24347 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.375 | CML-2 | CML: Elbow | 3 | 2039-03-19 | 2039-01-09 | 2016-06-06 07:00 | 2.5 | 0.14914 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.5 | 6.4 | 6.7 | 0.34034
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40045-01C02 | CML-3 | 300-WC-40045-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1064 |  | 2014-03-20 14:30 | 2014-03-20 15:00 | [36 empty] | 6.6 | CML-3 | CML: type TBC | 3 | 2033-12-23 | 2033-10-29 | 2014-03-20 14:30 | 2.5 | 0.18711 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 300 | 6.35 | 300-WC-40045-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.2 | 7.4 | 6.3 | 0.54772
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-3 | 50-PL-23021-03C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10235 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 7.625 | CML-3 | CML: type TBC | 6 | 2015-04-25 | 2015-04-12 | 2013-11-08 | 2.5 | 3.285 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.3 | 3 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.5 | 7.3 | 7.6 | 8.1 | 0.34034
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-7 | 150-FH-43518-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2707 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 6.975 | CML-7 | CML: Pipe Length | 3 | 2020-12-02 | 2019-08-26 | 2014-03-12 09:00 | 1.23 | 0.78294 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.5 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.27 | 0 | 6.5 | 7 | 7.3 | 7.1 | 0.34034
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-7 | 150-FH-43518-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 346 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 6.975 | CML-7 | CML: Pipe Length | 3 | 2020-11-28 | 2019-08-23 | 2014-03-12 | 1.23 | 0.78398 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.5 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.27 |  | 6.5 | 7 | 7.3 | 7.1 | 0.34034
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-16 | 50-FG-45024-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23515 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 7.775 | CML-16 | CML: Elbow | 3 | 2074-03-18 | 2063-04-04 | 2015-07-28 07:00 | 1.03 | 0 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.5 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.47 | -0.066123 | 7.9 | 7.5 | 8.2 | 7.5 | 0.34034
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-13 | 50-PL-23040-03C03 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10198 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.675 | CML-13 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 10.4 | 6 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 11.1 | 10.4 | 10.8 | 0.34034
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-33 | 50-FG-45501-01C02 CML-33 | Yes | FPSO 2015 | Pipe Wall Thickness | 23552 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 5.325 | CML-33 | CML: Pipe Length | 3 | 2023-10-28 | 2024-12-09 | 2015-08-10 07:30 | 2.5 | 0.29189 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.6 | 5.6 | 5.2 | 0.34034
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-20 | 100-FG-45001-09C02 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10435 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.375 | CML-20 | CML: type TBC | 3 | 2015-10-11 | 2015-02-23 | 2013-11-13 | 4.7 | 2.7209 | A3: Inside Quadrant |  | 8.13 | 4.7 | 6.415 | 9.9 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 10.5 | 10.7 | 9.9 | 10.4 | 0.34034
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-16 | 150-PG-20054-01C03-P CML-16 |  | FPSO 2016 | Pipe Wall Thickness | 24463 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | [36 empty] | 8.225 | CML-16 | CML: Pipe Length | 6 | 2021-12-14 | 2020-09-15 | 2016-07-05 07:00 | 2.5 | 0.99138 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 7.9 | 3 O'Clock | 100 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 0.20798 | 8.1 | 7.9 | 8.2 | 8.7 | 0.34034
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40506-1CG | CML-3 | 250-WC-40506-1CG CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8626 | Rope Access / Material Class Not Selectable. Line is FFS. Action: to recheck in a year(Feb. 2016) to confirm CR. | 2015-02-10 07:00 | 2015-02-10 08:00 | Check Corrosion Rate of 1.526mm/ yr |  | Administrator | 2015-09-08 10:06 | [32 empty] | 13.15 | CML-3 | CML: Elbow | 3 | 2021-08-28 | 2018-07-08 | 2015-02-10 07:00 | 2.5 | 1.5265 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 12.5 | 6 O'Clock | 250 | 15.09 | 250-WC-40506-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 13.4 | 13.4 | 12.5 | 13.3 | 0.43589
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20013-01C02-P | CML-7 | 200-PL-20013-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21217 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 7.8 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 6 O'Clock | 200 | 6.35 | 200-PL-20013-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.3 | 7.7 | 7.5 | 7.7 | 0.34641
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-1 | 250-PW-44010-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21918 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 10.375 | CML-1 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 9.9 | 9 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.7 | 10.4 | 10.5 | 9.9 | 0.34034
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-1 | 250-PW-44010-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5820 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 10.375 | CML-1 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 9.9 | 9 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.7 | 10.4 | 10.5 | 9.9 | 0.34034
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40403-01C02 | CML-10 | 100-WC-40403-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20390 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.525 | CML-10 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 6 O'Clock | 100 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.3 | 6.2 | 6.2 | 6.4 | 0.5252
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38492-01C02 | CML-2 | 50-CG-38492-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2536 |  | 2014-04-03 08:00 | 2014-04-03 09:00 | [36 empty] | 7.9 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-03 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 3 O'Clock | 50 | 5.54 | 50-CG-38492-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.8 | 7.5 | 8.3 | 8 | 0.33665
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-2 | 80-FH-43158-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12883 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.5 | CML-2 | CML: type TBC | 3 | 2018-05-11 | 2018-12-07 | 2014-01-22 11:00 | 2.5 | 0.60457 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 9 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.9 | 5.6 | 5.4 | 5.1 | 0.33665
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-31 | 400-FH-43508-01C02 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6580 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.5 | CML-31 | CML: Elbow | 3 | 2025-06-28 | 2023-11-24 | 2015-03-30 07:00 | 2.5 | 0.44853 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.1 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.9 | 7.1 | 7.4 | 7.6 | 0.33665
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-49 | 80-CG-38459-09C02-P CML-49 |  | FPSO 2014 | Pipe Wall Thickness | 21187 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 11.4 | CML-49 | CML: Elbow | 6 | 2017-06-16 | 2016-06-19 | 2014-07-16 07:30 | 2.5 | 2.9089 | A3: Inside Quadrant |  | 8.27 | 2.5 | 5.385 | 11 | 6 O'Clock | 40 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11.8 | 11.3 | 11 | 11.5 | 0.33665
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-7 | 250-PG-23003-06C02-PA CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10674 | Deck Level.High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.5849 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 16:16 | [32 empty] | 5.1 | CML-7 | CML: Elbow | 3 | 2014-11-29 | 2015-01-27 | 2013-11-17 | 2.5 | 2.0302 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.2 | 5.3 | 5.3 | 4.6 | 0.33665
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43081-01C02 | CML-4 | 80-FH-43081-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12726 |  | 2014-01-27 08:00 | 2014-01-27 09:00 |  |  | Nestor | 2014-11-19 17:18 | [32 empty] | 5.5 | CML-4 | CML: type TBC | 3 | 2017-06-06 | 2017-11-24 | 2014-01-27 08:00 | 2.5 | 0.74417 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-FH-43081-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.6 | 5.7 | 5.7 | 0.33665
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80002-01C02 | CML-9 | 100-VA-80002-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2169 | Rope Access | 2014-03-30 09:30 | 2014-03-30 11:00 | [36 empty] | 5.5 | CML-9 | CML: type TBC | 3 | 2017-06-18 | 2017-08-06 | 2014-03-30 09:30 | 2.5 | 0.86906 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 6 O'Clock | 100 | 6.02 | 100-VA-80002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.3 | 6 | 0.33665
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-7 | 250-PW-44007-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23140 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 6.05 | CML-7 | CML: Pipe Length | 3 | 2023-05-15 | 2023-04-19 | 2015-05-10 07:00 | 2.5 | 0.38649 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.53439 | 6.4 | 5.8 | 5.6 | 6.4 | 0.41231
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57028-01C02 | CML-4 | 50-DC-57028-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20271 | Rope Access | 2014-05-26 08:00 | 2014-05-26 09:00 | [36 empty] | 5.55 | CML-4 | CML: type TBC | 3 | 2049-09-29 | 2044-07-21 | 2014-05-26 08:00 | 0.37 | 0.14221 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DC-57028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.03 |  | 5.4 | 5.7 | 5.5 | 5.6 | 0.1291
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57029-01C02 | CML-3 | 50-DC-57029-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20276 | Rope Access | 2014-05-26 07:00 | 2014-05-26 08:00 | [36 empty] | 5.525 | CML-3 | CML: type TBC | 3 | 2049-09-28 | 2044-07-20 | 2014-05-26 07:00 | 0.37 | 0.14222 | A4: Left Quadrant |  | 2.54 | 0.37 | 1.1087 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57029-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.03 |  | 5.5 | 5.6 | 5.6 | 5.4 | 0.095743
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-9 | 25-FG-45455-01C02-E CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 23881 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.5 | CML-9 | CML: Fitting | 3 | 2027-12-10 | 2027-11-01 | 2014-09-26 07:00 | 2.5 | 0.26488 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.7 | 6.6 | 6.7 | 0.33665
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40045-01C02 | CML-4 | 300-WC-40045-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1065 |  | 2014-03-20 14:30 | 2014-03-20 15:00 | [36 empty] | 6.5 | CML-4 | CML: type TBC | 3 | 2033-12-23 | 2033-10-29 | 2014-03-20 14:30 | 2.5 | 0.18711 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 300 | 6.35 | 300-WC-40045-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.2 | 6.2 | 6.4 | 6.2 | 0.4761
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-26 | 250-PW-44006-01X01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 23197 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.175 | CML-26 | CML: Pipe Length | 3 | 2023-05-21 | 2023-04-24 | 2015-05-11 07:00 | 2.5 | 0.38595 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.65803 | 5.6 | 6.5 | 6.2 | 6.4 | 0.40311
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-8 | 50-CG-38474-01C02-P CML-8 |  | FPSO 2016 | Pipe Wall Thickness | 24469 | Re-check as requested by N.Sequera | 2016-07-07 07:00 | 2016-07-07 15:00 | Check Corrosion Rate of 0.335mm/ yr | [35 empty] | 4.9 | CML-8 | CML: Pipe Length | 3 | 2022-06-23 | 2023-06-13 | 2016-07-07 07:00 | 2.5 | 0.33525 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | -0.28854 | 5.3 | 4.8 | 4.5 | 5 | 0.33665
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-9 | 100-PW-20021-01C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22827 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.975 | CML-9 | CML: Elbow | 3 | 2029-06-09 | 2029-12-19 | 2015-04-30 07:00 | 2.5 | 0.21954 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.18159 | 5.6 | 6.4 | 5.9 | 6 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40403-01C02 | CML-7 | 100-WC-40403-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20387 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.625 | CML-7 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 3 O'Clock | 100 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.2 | 6.2 | 6.4 | 6.7 | 0.43493
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43081-01C02 | CML-1 | 80-FH-43081-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20418 | CML Reviewed 19-11-14. Line is FFS. Repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-19 17:18 | [32 empty] | 5.4 | CML-1 | CML: Pipe Length | 3 | 2021-08-21 | 2022-08-06 | 2014-10-06 07:00 | 2.5 | 0.3633 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-FH-43081-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.4346 | 5 | 5.8 | 5.3 | 5.5 | 0.33665
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43074-01C02 | CML-8 | 50-FL-43074-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1793 | Rope access | 2014-04-28 09:30 | 2014-04-28 10:30 | [36 empty] | 5.6 | CML-8 | CML: Elbow | 3 | 2021-07-12 | 2022-05-26 | 2014-04-28 09:30 | 2.5 | 0.37448 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FL-43074-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 6 | 5.7 | 5.2 | 0.33665
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-11 | 100-PW-20021-01C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22829 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.775 | CML-11 | CML: Elbow | 3 | 2029-06-09 | 2029-12-19 | 2015-04-30 07:00 | 2.5 | 0.21954 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | -0.36318 | 6 | 5.6 | 5.9 | 5.6 | 0.20616
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-12 | 25-FG-45455-01C02-E CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1145 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.4 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 6 | 6 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6.8 | 6 | 6.5 | 0.33665
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-1 | 200-FH-43025-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2474 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 7.1 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.5 | 7.2 | 7 | 6.7 | 0.33665
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40045-01C02 | CML-8 | 300-WC-40045-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1069 | Rope Access | 2014-03-20 14:30 | 2014-03-20 15:00 | [36 empty] | 6.5 | CML-8 | CML: type TBC | 3 | 2033-12-23 | 2033-10-29 | 2014-03-20 14:30 | 2.5 | 0.18711 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 300 | 6.35 | 300-WC-40045-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.2 | 7 | 6.2 | 0.38297
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38452-09C02-P | CML-18 | 50-CG-38452-09C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 22358 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.6 | CML-18 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.5 | 7.7 | 8 | 7.2 | 0.33665
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-2 | 350-FL-43511-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2283 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 11.3 | CML-2 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 10.9 | 12 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 10.9 | 11.7 | 11.4 | 11.2 | 0.33665
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40016-01C02 | CML-10 | 250-WC-40016-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20372 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-24 10:39 | [32 empty] | 6.575 | CML-10 | CML: Fitting | 3 | 2048-01-04 | 2047-10-04 | 2014-10-06 07:00 | 2.5 | 0.11121 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.7 | 7 | 0.35
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40043-01C02 | CML-2 | 300-WC-40043-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1043 |  | 2014-03-20 13:00 | 2014-03-20 14:00 | [36 empty] | 6.45 | CML-2 | CML: type TBC | 3 | 2033-12-21 | 2033-10-27 | 2014-03-20 13:00 | 2.5 | 0.18715 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 300 | 6.35 | 300-WC-40043-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.2 | 6.9 | 6.4 | 0.31091
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-14 | 25-FG-45455-01C02-E CML-14 |  | FPSO 2016 | Pipe Wall Thickness | 24359 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.4 | CML-14 | CML: Elbow | 3 | 2039-03-19 | 2039-01-09 | 2016-06-06 07:00 | 2.5 | 0.14914 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 3 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 5.9 | 6.5 | 6.6 | 0.33665
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-23 | 150-FG-45505-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 22363 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.9 | CML-23 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.4 | 3 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.1 | 7.4 | 8.1 | 8 | 0.33665
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43301-01C02-E | CML-3 | 200-PL-43301-01C02-E CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8600 | Line is FFS. Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-02-09 07:30 | 2015-02-09 15:00 |  |  | Administrator | 2015-09-07 16:33 | [32 empty] | 5.7 | CML-3 | CML: Elbow | 3 | 2024-09-21 | 2023-05-08 | 2015-02-09 07:30 | 1.34 | 0.44274 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 5.6 | 9 O'Clock | 200 | 6.35 | 200-PL-43301-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.26 |  | 5.8 | 5.8 | 5.6 | 5.6 | 0.11547
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-5 | 250-PW-44006-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7997 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.15 | CML-5 | CML: Fitting | 3 | 2021-10-28 | 2021-10-06 | 2015-01-20 08:30 | 2.5 | 0.4575 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.48657 | 5.6 | 6.4 | 6.2 | 6.4 | 0.37859
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40507-1CG | CML-2 | 200-WC-40507-1CG CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8671 | Material Class Not Selectable | 2015-02-12 14:00 | 2015-02-12 15:00 |  |  | Administrator | 2015-09-08 10:53 | [32 empty] | 12.775 | CML-2 | CML: Elbow | 3 | 2187-01-01 | 2125-09-26 | 2015-02-12 14:00 | 2.5 | 0.05872 | A1: Outside Quadrant |  | 9.7 | 2.5 | 6.1 | 12.6 | 9 O'Clock | 200 | 12.7 | 200-WC-40507-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.1 |  | 12.6 | 12.9 | 13 | 12.6 | 0.20616
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-14 | 80-PG-23025-06C03 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 13085 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 10.9 | CML-14 | CML: Elbow | 6 | 2021-04-09 | 2020-03-04 | 2014-02-07 11:00 | 2.8 | 1.0596 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 10.4 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.4 | 11 | 11.1 | 11.1 | 0.33665
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-25 | 300-PW-44003-01C03 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 21867 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 17:09 | [32 empty] | 10.8 | CML-25 | CML: Pipe Length | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.5 | 12 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.5 | 11 | 10.9 | 10.8 | 0.21602
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-32 | 200-PG-23007-09C03-PA CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 23408 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 19.7 | CML-32 | CML: Fitting | 6 | 2033-04-11 | 2029-01-28 | 2015-07-22 07:00 | 10.22 | 0.52324 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 19.5 | 3 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.28 | 0.18875 | 19.5 | 19.5 | 19.6 | 20.2 | 0.33665
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40402-01C02 | CML-4 | 100-WC-40402-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20377 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.525 | CML-4 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 12 O'Clock | 100 | 6.02 | 100-WC-40402-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.8 | 6.4 | 6.7 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-20 | 400-FH-43508-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6569 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 8.85 | CML-20 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 8.6 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.9 | 9.3 | 8.6 | 0.33166
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-22 | 50-CG-38001-09C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 10936 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.35 | CML-22 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.057 | A1: Outside Quadrant |  | 5.74 |  |  | 8.1 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.1 | 8.1 | 8.8 | 8.4 | 8.1 | 0.33166
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-35 | 300-PF-20501-03C03-P CML-35 | yes | FPSO 2014 | Pipe Wall Thickness | 21711 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 47.175 | CML-35 | CML: type TBC | 6 | 2190-11-25 | 2158-12-26 | 2014-09-28 07:00 | 4.9 | 0.05276 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.5 | 14.5 | 15 | 14.2 | 0.33166
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-3 | 100-PG-23028-25C02-P CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 20552 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 15.95 | CML-3 | CML: Pipe Length | 3 | 2018-02-26 | 2016-09-15 | 2014-05-30 09:30 | 9.4 | 1.6272 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 15.5 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 0.4619 | 16 | 15.5 | 16 | 16.3 | 0.33166
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-14 | 200-PL-20018-01C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 23886 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 7.725 | CML-14 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 3 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 | 0 | 7.5 | 7.5 | 8.1 | 7.8 | 0.28723
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-13 | 80-CG-38459-09C02-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23710 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 10.55 | CML-13 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 10.2 | 9 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.5 | 11 | 10.5 | 10.2 | 0.33166
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-33 | 80-CG-38459-09C02-P CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 23496 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 14.05 | CML-33 | CML: Pipe Length | 6 | 2043-07-10 | 2038-02-08 | 2015-07-27 07:00 | 4.9 | 0.31102 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 | -0.36139 | 13.6 | 14.1 | 14.1 | 14.4 | 0.33166
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-32 | 50-FG-45501-01C02 CML-32 | Yes | FPSO 2015 | Pipe Wall Thickness | 23551 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 5.35 | CML-32 | CML: Pipe Length | 3 | 2028-07-21 | 2030-03-06 | 2015-08-10 07:30 | 2.5 | 0.20067 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.8 | 5.4 | 5.1 | 0.33166
PG06 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-23008-15S01-A | CML-3 | 200-PG-23008-15S01-A CML-3 | no | FPSO 2014 | Pipe Wall Thickness | 21806 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.35 | CML-3 | CML: Elbow | 3 | 2018-08-16 | 2018-10-18 | 2014-10-11 07:00 | 2.5 | 0.67526 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.4 | 5.1 | 5.8 | 0.33166
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57008-01C02 | CML-7 | 80-DC-57008-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23279 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 7.8 | CML-7 | CML: Reducing Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.6 | 12 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 7.8 | 7.9 | 7.9 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43035-01C02 | CML-2 | 100-FH-43035-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12661 |  | 2014-01-22 10:00 | 2014-01-22 11:00 | [36 empty] | 5.35 | CML-2 | CML: type TBC | 3 | 2015-11-18 | 2015-12-18 | 2014-01-22 10:00 | 2.5 | 1.4264 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 6 O'Clock | 100 | 6.02 | 100-FH-43035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.4 | 5.1 | 5.8 | 0.33166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43122-01C02 | CML-1 | 50-FH-43122-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1759 | Rope access | 2014-04-27 08:30 | 2014-04-27 09:00 | [36 empty] | 5.75 | CML-1 | CML: Fitting | 3 | 2024-11-14 | 2026-02-06 | 2014-04-27 08:30 | 2.5 | 0.26517 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FH-43122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6 | 5.7 | 6 | 5.3 | 0.33166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43127-01C02 | CML-6 | 150-FH-43127-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1799 | Rope access | 2014-04-28 10:30 | 2014-04-28 12:00 | [36 empty] | 7.15 | CML-6 | CML: Pipe Length | 3 | 2023-08-14 | 2022-10-27 | 2014-04-28 10:30 | 2.5 | 0.45152 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 3 O'Clock | 150 | 7.11 | 150-FH-43127-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.1 | 6.7 | 7.4 | 7.4 | 0.33166
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42309-01S01 | CML-4 | 40-CI-42309-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7500 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 8.025 | CML-4 | CML: type TBC | 1 | 2059-10-24 | 2046-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 6.14 | 2.5 | 3.8737 | 7.6 | 3 O'Clock | 40 | 7.14 | 40-CI-42309-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 9 | 7.6 | 7.7 | 7.8 | 0.65511
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-14 | 200-PL-20018-01C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21250 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 7.725 | CML-14 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 3 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.5 | 8.1 | 7.8 | 0.28723
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-14 | 0200-DH-56L9003-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5099 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.875 | CML-14 | CML: type TBC | 3 | 2024-11-04 | 2022-10-22 | 2015-03-06 07:00 | 2.5 | 0.52718 | A4: Left Quadrant |  | 5.74 | 2.5 | 3.5737 | 7.6 | 9 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 10 | 8.9 | 9 | 7.6 | 0.98446
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-13 | 0200-DH-56L9003-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5098 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 7.8 | CML-13 | CML: type TBC | 3 | 2024-11-04 | 2022-10-22 | 2015-03-06 07:00 | 2.5 | 0.52718 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 7.6 | 12 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 8.1 | 7.7 | 7.8 | 0.21602
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-4 | 50-FG-45019-03C02 CML-4 | yes | FPSO 2013 | Pipe Wall Thickness | 10486 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.95 | CML-4 | CML: type TBC | 3 | 2014-10-02 | 2014-09-28 | 2013-11-15 | 2.5 | 2.2731 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.9 | 5.2 | 5.2 | 0.33166
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-17 | 50-FG-45018-03C02 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10516 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.25 | CML-17 | CML: type TBC | 3 | 2015-12-28 | 2015-12-21 | 2013-11-15 | 2.5 | 1.1802 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 3 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5.7 | 5.3 | 0.33166
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-3 | 200-PL-20020-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21307 | Reading on larger diameter | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 7.825 | CML-3 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 6 O'Clock | 150 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.8 | 7.9 | 7.5 | 8.1 | 0.25
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-6 | 250-WC-40017-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2069 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 6.525 | CML-6 | CML: type TBC | 3 | 2034-07-11 | 2034-05-15 | 2014-03-28 09:30 | 2.5 | 0.18226 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.2 | 6.5 | 6.8 | 0.25
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43175-01C02 | CML-4 | 150-FL-43175-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12915 |  | 2014-02-03 07:00 | 2014-02-03 08:00 | [36 empty] | 7.05 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.8 | 6 O'Clock | 100 | 6.02 | 100-FL-43175-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.5 | 6.8 | 6.8 | 7.1 | 0.33166
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45038-03C02 | CML-1 | 150-FG-45038-03C02 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24342 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.45 | CML-1 | CML: Pipe Length | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 3.305 | 7.2 | 3 O'Clock | 150 | 7.11 | 150-FG-45038-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.2 | 7.5 | 7.9 | 0.33166
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-6 | 250-PW-44006-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1903 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.1 | CML-6 | CML: Pipe Length | 3 | 2017-08-10 | 2017-07-30 | 2014-03-26 07:00 | 2.5 | 0.91773 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.2 | 6.2 | 6.4 | 0.34641
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-7 | 50-CG-38474-01C02-P CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24468 | Re-check as requested by N.Sequera | 2016-07-07 07:00 | 2016-07-07 15:00 | Check Corrosion Rate of 0.4mm/ yr | [35 empty] | 4.75 | CML-7 | CML: Elbow | 3 | 2021-01-05 | 2021-10-30 | 2016-07-07 07:00 | 2.5 | 0.39972 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 3 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | -0.14427 | 4.8 | 4.3 | 5.1 | 4.8 | 0.33166
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-5 | 250-WC-40017-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2068 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 6.4 | CML-5 | CML: type TBC | 3 | 2034-07-11 | 2034-05-15 | 2014-03-28 09:30 | 2.5 | 0.18226 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.2 | 6.7 | 6.4 | 0.21602
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-2 | 25-PG-23300-25C02 CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 20669 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 8.25 | CML-2 | CML: Elbow | 3 | 2017-01-01 | 2016-05-10 | 2014-05-27 09:30 | 4.4 | 1.3065 | A1: Outside Quadrant |  | 6.09 | 4.4 | 5.245 | 7.8 | 12 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.8 | 8.6 | 8.3 | 8.3 | 0.33166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-7 | 150-FH-43518-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5522 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 6.95 | CML-7 | CML: Pipe Length | 3 | 2023-01-21 | 2021-06-03 | 2014-06-01 07:00 | 1.23 | 0.60951 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.5 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.27 | 0 | 6.5 | 7 | 7.3 | 7 | 0.33166
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23302-01C02 | CML-3 | 80-VA-23302-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 22519 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.55 | CML-3 | CML: Elbow | 3 | 2015-11-16 | 2016-02-29 | 2015-04-20 07:00 | 2.5 | 1.2144 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.2 | 12 O'Clock | 50 | 5.49 | 80-VA-23302-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.5 | 3.5 | 4 | 0.33166
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-11 | 80-PW-44001-01C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23220 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.775 | CML-11 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 1.3971 | 5.7 | 5.8 | 6 | 5.6 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40011-01C02 | CML-7 | 50-WC-40011-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1892 | Rope Access | 2014-03-25 13:00 | 2014-03-25 14:00 | [36 empty] | 6.375 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 3 O'Clock | 50 | 5.54 | 50-WC-40011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.3 | 6.6 | 0.17078
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38005-01C02 | CML-3 | 50-CG-38005-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3103 | Rope Access | 2014-05-04 10:00 | 2014-05-04 10:30 | [36 empty] | 5.95 | CML-3 | CML: Elbow | 3 | 2083-08-16 | 2091-02-27 | 2014-05-04 10:00 | 2.5 | 0.04327 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 15 | 5.54 | 50-CG-38005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 6 | 6 | 5.5 | 0.33166
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23301-01C02 | CML-6 | 80-VA-23301-01C02 CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 22513 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.65 | CML-6 | CML: Elbow | 3 | 2015-11-16 | 2016-02-29 | 2015-04-20 07:00 | 2.5 | 1.2144 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.2 | 12 O'Clock | 50 | 5.49 | 80-VA-23301-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.6 | 3.9 | 3.9 | 0.33166
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-33 | 80-CG-38459-09C02-P CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 21653 | Reviewed on 27/11/14. FFS. Recheck on Sep. 15 | 2014-09-27 07:00 | 2014-09-27 15:00 |  |  | Nestor | 2014-11-27 17:38 | [32 empty] | 13.75 | CML-33 | CML: Pipe Length | 6 | 2026-03-13 | 2023-11-24 | 2014-09-27 07:00 | 4.9 | 0.73258 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 13.3 | 13.8 | 13.8 | 14.1 | 0.33166
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-25 | 80-CG-38459-09C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 21645 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.65 | CML-25 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.3 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 14.3 | 14.6 | 15.1 | 14.6 | 0.33166
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-4 | 100-FG-45001-09C02 CML-4 | Yes | FPSO 2015 | Pipe Wall Thickness | 23309 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 16.65 | CML-4 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A4: Left Quadrant |  | 8.13 | 4.7 | 6.415 | 16.2 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 | -0.1206 | 16.9 | 16.9 | 16.6 | 16.2 | 0.33166
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-10 | 80-CG-38459-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21496 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | [36 empty] | 17.725 | CML-10 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-06-28 10:45 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 17.4 | 9 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.5 |  | 17.9 | 17.5 | 18.1 | 17.4 | 0.3304
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-14 | 80-CG-38486-09C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21484 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 18.225 | CML-14 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-06-28 09:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.9 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13 |  | 17.9 | 18.6 | 18 | 18.4 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-10 | 150-WC-40002-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20349 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 6.425 | CML-10 | CML: Elbow | 3 | 2020-04-14 | 2019-09-30 | 2014-10-09 07:00 | 2.5 | 0.67061 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.2 | 3 O'Clock | 80 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.5 | 6.6 | 0.17078
FL02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-FL-43454-01C02-P | CML-6 | 50-FL-43454-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2314 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | [36 empty] | 9.575 | CML-6 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 9.1 | 12 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.8 | 9.6 | 9.8 | 0.3304
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44037-01C03 | CML-4 | 300-PW-44037-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21914 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 12.65 | CML-4 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-10-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 12.3 | 3 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 12.5 | 12.3 | 12.5 | 13.3 | 0.44347
FG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-FG-45024-01C02 | CML-4 | 50-FG-45024-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13163 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 9.425 | CML-4 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-01-18 15:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 9 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.4 | 9.9 | 9.2 | 9.2 | 0.3304
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20045-03C03-P | CML-2 | 80-PG-20045-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21458 | Protective mesh removed | 2014-06-29 11:00 | 2014-06-29 12:00 | [36 empty] | 11.075 | CML-2 | CML: Fitting | 6 | 2035-01-13 | 2031-09-28 | 2014-06-29 11:00 | 2.5 | 0.3989 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 10.7 | 9 O'Clock | 80 | 11.13 | 80-PG-20045-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11.3 | 11.4 | 10.9 | 10.7 | 0.3304
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38463-01C02 | CML-6 | 50-CG-38463-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3117 | Rope Access | 2014-05-04 08:00 | 2014-05-04 09:00 | [36 empty] | 4.975 | CML-6 | CML: Elbow | 3 | 2016-05-26 | 2016-09-21 | 2014-05-04 08:00 | 2.5 | 1.0171 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-CG-38463-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 5 | 4.6 | 5.4 | 0.3304
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43074-01C02 | CML-6 | 50-FL-43074-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1791 | Rope access | 2014-04-28 09:30 | 2014-04-28 10:30 | [36 empty] | 5.525 | CML-6 | CML: Pipe Length | 3 | 2019-09-07 | 2020-05-10 | 2014-04-28 09:30 | 2.5 | 0.48462 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-FL-43074-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.1 | 5.9 | 5.5 | 0.3304
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-5 | 80-PW-44016-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22907 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 18.025 | CML-5 | CML: Pipe Length | 3 | 2043-04-25 | 2046-10-17 | 2015-05-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 3 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | -0.17892 | 5.8 | 5.6 | 5.5 | 5.7 | 0.1291
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-5 | 80-DH-56074-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20950 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 6.025 | CML-5 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 6.1 | 5.6 | 6.4 | 0.3304
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-2 | 80-PL-44008-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5739 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 7.675 | CML-2 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.5 | 3 O'Clock | 50 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.7 | 7.5 | 7.7 | 7.8 | 0.12583
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43076-01C02 | CML-1 | 150-FL-43076-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2342 | Rope Access | 2014-03-17 11:00 | 2014-03-17 11:30 | [36 empty] | 7.875 | CML-1 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-03-17 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 9 O'Clock | 150 | 7.11 | 150-FL-43076-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.8 | 8.3 | 7.9 | 7.5 | 0.3304
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-10 | 100-FG-45001-09C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10425 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.375 | CML-10 | CML: type TBC | 3 | 2015-12-26 | 2015-04-20 | 2013-11-13 | 4.7 | 2.4997 | A3: Inside Quadrant |  | 8.13 | 4.7 | 6.415 | 10 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 10.4 | 10.3 | 10 | 10.8 | 0.3304
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-14 | 400-FH-43500-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 5650 | Readings taking at weld | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 8.475 | CML-14 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 8.1 | 3 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.4 | 8.1 | 8.9 | 8.5 | 0.3304
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43084-01C02 | CML-7 | 150-FL-43084-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2572 | Rope Access | 2014-04-08 07:30 | 2014-04-08 08:30 | [36 empty] | 8.925 | CML-7 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-04-08 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.5 | 6 O'Clock | 150 | 7.11 | 150-FL-43084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.9 | 9 | 8.5 | 9.3 | 0.3304
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-29 | 100-DC-57036-01C02 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 1435 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 7.825 | CML-29 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.6 | 3 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.9 | 7.6 | 7.9 | 7.9 | 0.15
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-1 | 100-PG-23071-01C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2399 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 9.075 | CML-1 | CML: type TBC | 6 | 2016-05-23 | 2015-12-17 | 2014-03-19 13:00 | 2.5 | 2.842 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 8.7 | 3 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9 | 8.7 | 9.5 | 9.1 | 0.3304
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43108-01C02 | CML-9 | 200-FH-43108-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12784 |  | 2014-01-18 15:30 | 2014-01-18 16:30 | [36 empty] | 7.925 | CML-9 | CML: Reducer | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 15:30 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.6 | 12 O'Clock | 150 | 6.35 | 200-FH-43108-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.26 |  | 7.6 | 8.1 | 7.7 | 8.3 | 0.3304
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43302-01C02-E | CML-2 | 200-PL-43302-01C02-E CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8603 |  | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6.6 | CML-2 | CML: type TBC | 3 | 2026-06-18 | 2024-11-17 | 2015-02-09 07:30 | 1.34 | 0.38371 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 5.7 | 12 O'Clock | 200 | 6.35 | 200-PL-43302-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.36 |  | 5.7 | 6.6 | 7.2 | 6.9 | 0.64807
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-13 | 50-PG-23024-03C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10045 | Rope Access | 2014-01-06 | 2014-01-06 | [36 empty] | 9.075 | CML-13 | CML: Elbow | 6 | 2129-11-20 | 2116-08-15 | 2014-01-06 | 0.97 | 0.06667 | A3: Inside Quadrant |  | 2.74 | 0.97 | 1.855 | 8.7 | 6 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.73 |  | 9.1 | 9 | 8.7 | 9.5 | 0.3304
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-7 | 50-PL-23041-06C03 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10220 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.975 | CML-7 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 3.3534 | A3: Inside Quadrant |  | 5.07 |  |  | 9.6 | 6 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10 | 9.9 | 9.6 | 10.4 | 0.3304
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-5 | 200-PW-44021-01X01 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10710 | Deck Level. Line is FFS. High CR. Line rechecked (refer to Jan. 15 values) | 2013-11-10 | 2013-11-10 |  |  | Administrator | 2015-09-13 11:06 | [32 empty] | 6 | CML-5 | CML: Elbow | 3 | 2015-09-10 | 2015-09-04 | 2013-11-10 | 2.5 | 1.6898 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 3 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 5.6 | 6.1 | 6.3 | 0.29439
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-9 | 200-FH-43003-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12532 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 8.425 | CML-9 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 11:30 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 8 | 12 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.66 |  | 8 | 8.4 | 8.8 | 8.5 | 0.3304
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-17 | 50-FL-43454-01C02-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 22882 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.625 | CML-17 | CML: Elbow | 6 | 2026-11-20 | 2025-04-29 | 2015-05-01 07:00 | 2.5 | 0.57937 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 12 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | -0.56443 | 9.2 | 9.6 | 10 | 9.7 | 0.3304
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-2 | 25-VA-23054-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5877 |  | 2014-06-25 13:00 | 2014-06-25 14:00 | [36 empty] | 14.125 | CML-2 | CML: Cap End | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 13:00 | 3.3 | 0 | A3: Inside Quadrant |  | 6.7 | 3.3 | 5 | 13.7 | 6 O'Clock | 200 | 12.7 | 200-PG-20303-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 14.1 | 14.5 | 13.7 | 14.2 | 0.3304
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-21 | 200-PL-20034-03C02-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21618 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 9.45 | CML-21 | CML: Fitting | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 8.7 | 12 O'Clock | 250 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 |  | 8.7 | 9.4 | 9.5 | 10.2 | 0.61373
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56092-01C02 | CML-2 | 80-DH-56092-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20985 | Rope Access | 2014-05-17 13:00 | 2014-05-17 15:00 | [36 empty] | 5.025 | CML-2 | CML: type TBC | 3 | 2017-01-17 | 2017-06-21 | 2014-05-17 13:00 | 2.5 | 0.82258 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 9 O'Clock | 80 | 5.49 | 80-DH-56092-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.4 | 5.2 | 4.8 | 4.7 | 0.3304
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-12 | 250-PW-44004-01C02 CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 5631 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 8.025 | CML-12 | CML: Reducing Tee | 3 | 2019-08-26 | 2019-08-10 | 2014-06-20 13:00 | 2.5 | 0.61697 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 9.2 | 8.6 | 8.6 | 5.7 | 1.5756
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-2 | 50-DH-56070-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3218 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.025 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 6.4 | 5.7 | 6.2 | 0.3304
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-20 | 200-PL-20034-03C02-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21617 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.75 | CML-20 | CML: Reducer | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 8.7 | 9 O'Clock | 250 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 |  | 8.8 | 8.7 | 8.8 | 8.7 | 0.057735
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-1 | 150-FL-43514-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20494 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.175 | CML-1 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.8 | 6 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.5 | 7.4 | 6.8 | 7 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40016-01C02 | CML-8 | 250-WC-40016-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20370 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-24 10:38 | [32 empty] | 6.375 | CML-8 | CML: Fitting | 3 | 2048-01-04 | 2047-10-04 | 2014-10-06 07:00 | 2.5 | 0.11121 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.5 | 6.2 | 6.3 | 0.15
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43300-01C02-E | CML-6 | 200-PL-43300-01C02-E CML-6 | Yes | FPSO 2015 | Pipe Wall Thickness | 8592 | Line is FFS. Action: to recheck in two years (Feb. 2017) to confirm CR. | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-07 16:36 | [32 empty] | 5.85 | CML-6 | CML: Fitting | 3 | 2026-06-12 | 2024-11-11 | 2015-02-08 11:00 | 1.34 | 0.38424 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 5.7 | 9 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.36 |  | 6.2 | 5.7 | 5.8 | 5.7 | 0.23805
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-8 | 300-PG-23002-03C03-A CML-8 | Yes | FPSO 2013 | Pipe Wall Thickness | 10104 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 12.975 | CML-8 | CML: Elbow | 6 | 2015-10-10 | 2015-05-18 | 2013-11-07 | 5.22 | 3.8337 | A2: Right Quadrant |  | 8.27 | 5.22 | 6.745 | 12.6 | 3 O'Clock | 40 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.38 |  | 12.8 | 12.6 | 13.2 | 13.3 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40402-01C02 | CML-1 | 100-WC-40402-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20374 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.225 | CML-1 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-WC-40402-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.2 | 6.2 | 6.2 | 0.05
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-3 | 50-DH-56070-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3219 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.425 | CML-3 | CML: type TBC | 3 | 2021-10-17 | 2022-09-10 | 2014-05-09 07:00 | 2.5 | 0.36256 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.9 | 5.2 | 0.3304
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80002-01C02 | CML-3 | 100-VA-80002-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2163 | Rope Access | 2014-03-30 09:30 | 2014-03-30 11:00 | [36 empty] | 5.525 | CML-3 | CML: type TBC | 3 | 2017-06-18 | 2017-08-06 | 2014-03-30 09:30 | 2.5 | 0.86906 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 3 O'Clock | 100 | 6.02 | 100-VA-80002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.5 | 6 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40013-01C02 | CML-3 | 50-WC-40013-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1558 | Rope Access | 2014-04-09 10:00 | 2014-04-09 11:00 | [36 empty] | 7 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.9 | 6.6 | 7.2 | 6.3 | 0.70711
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-9 | 150-FH-43136-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5520 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 7.075 | CML-9 | CML: Elbow | 3 | 2025-05-03 | 2023-03-11 | 2014-06-01 07:00 | 1.03 | 0.50959 | A4: Left Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.6 | 9 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.57 | -1.3702 | 7.1 | 7.3 | 7.3 | 6.6 | 0.3304
FL02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-FL-43454-01C02-P | CML-7 | 50-FL-43454-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21045 | Rope Access | 2014-05-19 07:00 | 2014-05-19 08:00 | [36 empty] | 9.475 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56121-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.7 | 9.3 | 9.8 | 9.1 | 0.3304
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-17 | 150-PG-20054-01C03-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21528 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 8.225 | CML-17 | CML: Pipe Length | 6 | 2016-04-09 | 2015-11-09 | 2014-06-26 13:00 | 2.5 | 2.9627 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 7.8 | 12 O'Clock | 100 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.6 | 8.3 | 8.2 | 0.3304
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-12 | 50-FL-43454-01C02-P CML-12 | High Priority | FPSO 2014 | Pipe Wall Thickness | 20515 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 17.475 | CML-12 | CML: Elbow | 3 | 2019-10-21 | 2020-06-28 | 2014-10-05 07:00 | 2.5 | 0.47548 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5.7 | 5.3 | 0.3304
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45017-03C02 | CML-12 | 100-FG-45017-03C02 CML-12 | yes | FPSO 2013 | Pipe Wall Thickness | 10636 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 4.875 | CML-12 | CML: type TBC | 3 | 2014-06-29 | 2014-05-31 | 2013-11-18 | 2.5 | 3.2635 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.76 | 4.5 | 9 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.8 | 5.3 | 4.9 | 4.5 | 0.3304
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57017-01C02 | CML-3 | 20-DC-57017-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2898 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 5.95 | CML-3 | CML: type TBC | 3 | 2032-02-01 | 2029-02-19 | 2014-04-25 08:00 | 0.16 | 0.28904 | A4: Left Quadrant |  | 2.56 | 0.16 | 1.0125 | 5.3 | 9 O'Clock | 20 | 5.56 | 20-DC-57017-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.14 |  | 5.5 | 5.9 | 7.1 | 5.3 | 0.80623
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-5 | 50-DH-56109-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20994 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.125 | CML-5 | CML: Elbow | 3 | 2016-12-15 | 2017-05-03 | 2014-05-24 10:30 | 2.5 | 0.85777 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 5.2 | 5.5 | 4.7 | 0.3304
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56059-01C02 | CML-3 | 50-DH-56059-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3341 | Rope Access | 2014-05-08 11:00 | 2014-05-08 12:00 | [36 empty] | 5.125 | CML-3 | CML: type TBC | 3 | 2016-10-18 | 2017-02-28 | 2014-05-08 11:00 | 2.5 | 0.89791 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56059-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 5.2 | 4.7 | 5.5 | 0.3304
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-1 | 80-PW-44001-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23210 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.25 | CML-1 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 3 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 1.9211 | 5.8 | 5.7 | 6.5 | 7 | 0.61373
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-9 | 80-FH-43005-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12559 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 5.375 | CML-9 | CML: type TBC | 3 | 2017-04-25 | 2017-10-08 | 2014-01-20 10:00 | 2.5 | 0.76623 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.6 | 5.2 | 5.7 | 0.3304
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43123-01C02 | CML-2 | 50-FH-43123-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1778 |  | 2014-04-28 14:30 | 2014-04-28 15:00 | [36 empty] | 5.375 | CML-2 | CML: Elbow | 3 | 2018-07-11 | 2019-01-28 | 2014-04-28 14:30 | 2.5 | 0.59438 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FH-43123-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.3 | 5.8 | 5.4 | 0.3304
FG03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 80-FG-45045-06S01-E | CML-3 | 80-FG-45045-06S01-E CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24404 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 8.575 | CML-3 | CML: Reducing Tee | 1 | 2043-01-05 | 2033-03-19 | 2016-06-08 07:00 | 2.53 | 0 | A4: Left Quadrant |  | 4.49 | 2.53 | 3.51 | 7.7 | 9 O'Clock | 80 | 5.49 | 80-FG-45045-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.17 |  | 9.1 | 8.6 | 8.9 | 7.7 | 0.61847
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-6 | 200-PW-44021-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23021 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 5.8 | CML-6 | CML: Reducing Tee | 3 | 2023-04-20 | 2023-03-24 | 2015-05-05 07:00 | 2.5 | 0.38924 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 9 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.31291 | 6.2 | 5.7 | 5.7 | 5.6 | 0.2708
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-7 | 80-DH-56074-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20952 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 5.625 | CML-7 | CML: Elbow | 3 | 2023-07-02 | 2024-09-03 | 2014-05-24 07:00 | 2.5 | 0.29626 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.7 | 5.2 | 6 | 0.3304
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-23 | 100-PW-20021-01C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21826 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6 | CML-23 | CML: Elbow | 3 | 2028-05-23 | 2028-11-19 | 2014-10-11 07:00 | 2.5 | 0.23487 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.2 | 6.4 | 5.7 | 0.3559
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-13 | 250-WC-40026-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1289 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.05 | CML-13 | CML: type TBC | 3 | 2075-09-09 | 2075-03-27 | 2014-03-23 09:30 | 2.5 | 0.06178 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7.3 | 7.5 | 7.1 | 0.52599
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-8 | 80-FH-43005-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12558 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 6.075 | CML-8 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-20 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 3 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 5.7 | 6.3 | 6.4 | 0.3304
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-10 | 50-DH-56137-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21094 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.125 | CML-10 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.7 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 6.2 | 6.1 | 5.7 | 0.3304
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-5 | 50-PW-44013-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5729 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 5.875 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-22 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 1.7881 | 5.9 | 5.6 | 6 | 6 | 0.1893
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-14 | 200-PL-20010-01C02-P CML-14 | yes | FPSO 2014 | Pipe Wall Thickness | 23814 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 9.5 | CML-14 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 12 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 9.2 | 10.7 | 10.5 | 1.4306
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2894 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 6.425 | CML-4 | CML: Elbow | 3 | 2023-04-21 | 2023-03-26 | 2014-04-25 08:00 | 2.5 | 0.38909 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.4 | 6.8 | 6.5 | 0.3304
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20017-01C02-P | CML-7 | 200-PL-20017-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21246 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.575 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 9 O'Clock | 200 | 6.35 | 200-PL-20017-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 9.4 | 8.6 | 8.7 | 7.6 | 0.74106
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40045-01C02 | CML-6 | 300-WC-40045-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1067 |  | 2014-03-20 14:30 | 2014-03-20 15:00 | [36 empty] | 6.55 | CML-6 | CML: type TBC | 3 | 2075-02-06 | 2074-08-25 | 2014-03-20 14:30 | 2.5 | 0.06237 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 6 O'Clock | 300 | 6.35 | 300-WC-40045-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.4 | 7.1 | 6.3 | 6.4 | 0.36968
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-5 | 200-FH-43025-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2478 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 6.875 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7.3 | 6.8 | 6.9 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40011-01C02 | CML-8 | 50-WC-40011-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1893 | Rope Access | 2014-03-25 13:00 | 2014-03-25 14:00 | [36 empty] | 6.5 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.9 | 6.4 | 6.4 | 6.3 | 0.2708
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43108-01C02 | CML-3 | 200-FH-43108-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12778 |  | 2014-01-18 15:30 | 2014-01-18 16:30 | [36 empty] | 6.375 | CML-3 | CML: Pipe Length | 3 | 2022-06-29 | 2021-05-23 | 2014-01-18 15:30 | 1.34 | 0.55149 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6 | 6 O'Clock | 200 | 6.35 | 200-FH-43108-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 6.7 | 6.2 | 6 | 6.6 | 0.3304
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-3 | 150-FH-43026-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12643 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.375 | CML-3 | CML: Pipe Length | 3 | 2049-01-08 | 2042-08-09 | 2014-01-22 07:00 | 1.03 | 0.17064 | A4: Left Quadrant |  | 4.11 | 1.03 | 2.1256 | 7 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 |  | 7.4 | 7.3 | 7.8 | 7 | 0.3304
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56029-01C02 | CML-2 | 80-DH-56029-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20908 | Rope Access | 2014-05-22 09:30 | 2014-05-22 11:00 | [36 empty] | 5.425 | CML-2 | CML: Elbow | 3 | 2019-05-09 | 2020-01-17 | 2014-05-22 09:30 | 2.5 | 0.50324 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-DH-56029-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5.5 | 5.4 | 5 | 0.3304
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1828 |  | 2014-04-29 14:30 | 2014-04-29 15:00 | [36 empty] | 5.775 | CML-3 | CML: Pipe Length | 3 | 2033-03-10 | 2035-04-24 | 2014-04-29 14:30 | 2.5 | 0.15364 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DH-56123-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.4 | 5.7 | 6.2 | 0.3304
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-35 | 50-CG-38001-09C02 CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 10950 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.175 | CML-35 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.5525 | A1: Outside Quadrant |  | 5.74 |  |  | 7.8 | 12 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.8 | 7.8 | 8.1 | 8.2 | 8.6 | 0.3304
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56028-01C02 | CML-1 | 80-DH-56028-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20898 | Rope Access | 2014-05-22 07:00 | 2014-05-22 08:00 | [36 empty] | 5.225 | CML-1 | CML: Equal Tee | 3 | 2018-05-06 | 2018-12-02 | 2014-05-22 07:00 | 2.5 | 0.60612 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 9 O'Clock | 80 | 5.49 | 80-DH-56028-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 5.6 | 5 | 4.9 | 0.3304
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-4 | 50-CG-38467-01C02 CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 22275 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.275 | CML-4 | CML: Elbow | 3 | 2017-10-06 | 2018-03-26 | 2014-05-01 11:00 | 2.5 | 0.69844 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0 | 4.9 | 5.6 | 5.1 | 5.5 | 0.3304
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-4 | 50-CG-38467-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2996 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.275 | CML-4 | CML: Elbow | 3 | 2017-10-06 | 2018-03-26 | 2014-05-01 11:00 | 2.5 | 0.69844 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.6 | 5.1 | 5.5 | 0.3304
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42310-01S01 | CML-6 | 40-CI-42310-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7495 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 9.5 | CML-6 | CML: type TBC | 1 | 2059-10-24 | 2046-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 6.14 | 2.5 | 3.8737 | 7.7 | 6 O'Clock | 40 | 7.14 | 40-CI-42310-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.3 | 10.6 | 7.7 | 11.4 | 1.7795
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-24 | 80-PW-44001-01C02-P CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 23233 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.175 | CML-24 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 2.2703 | 6.2 | 6.5 | 5.7 | 6.3 | 0.34034
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20015-01C02-P | CML-5 | 200-PL-20015-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21230 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.6 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 6 O'Clock | 200 | 6.35 | 200-PL-20015-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 9.2 | 8.6 | 7.6 | 9 | 0.71181
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-14 | 250-PW-20041-03C03-P CML-14 | yes | FPSO 2014 | Pipe Wall Thickness | 21423 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.55 | CML-14 | CML: Elbow | 6 | 2032-07-19 | 2029-08-28 | 2014-07-12 07:30 | 4.1 | 0.44916 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.2 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 13.6 | 13.7 | 14.7 | 12.2 | 1.0279
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-13 | 50-PL-23300-09C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 13129 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 11.875 | CML-13 | CML: type TBC | 6 | 2096-01-05 | 2084-09-16 | 2014-02-04 07:00 | 2.81 | 0 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 11.5 | 6 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.69 |  | 12.2 | 12.1 | 11.5 | 11.7 | 0.3304
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23072-03C03 | CML-2 | 100-PG-23072-03C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20606 | Rope Access.Line is FFS | 2014-05-25 10:30 | 2014-05-25 11:30 |  |  | Administrator | 2015-09-08 08:12 | [32 empty] | 11.625 | CML-2 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-05-25 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 11.3 | 3 O'Clock | 100 | 11.13 | 100-PG-23072-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 11.4 | 11.3 | 11.8 | 12 | 0.3304
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-6 | 25-VA-23054-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5871 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | [36 empty] | 14.175 | CML-6 | CML: Equal Tee | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 09:30 | 3.3 | 0 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 13.8 | 12 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.5 |  | 13.8 | 14.4 | 14.5 | 14 | 0.3304
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-31 | 80-CG-38459-09C02-P CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 21597 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 16.125 | CML-31 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 15.8 | 6 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.3 |  | 16.5 | 15.9 | 15.8 | 16.3 | 0.3304
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21803 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 7.825 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 7.7 | 3 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.8 | 7.7 | 7.9 | 7.9 | 0.095743
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21802 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 7.8 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.7 | 12 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 7.8 | 7.9 | 0.08165
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21801 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 7.75 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.7 | 3 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.7 | 7.8 | 7.8 | 0.057735
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21800 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.125 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.7 | 3 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.7 | 8.5 | 8.6 | 0.49244
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-1 | 200-PW-44019-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23029 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 5.675 | CML-1 | CML: Fitting | 3 | 2023-04-25 | 2023-03-29 | 2015-05-06 07:00 | 2.5 | 0.38869 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 3 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0 | 5.6 | 5.6 | 5.8 | 5.7 | 0.095743
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-12 | 150-PG-20054-01C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21523 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 12.525 | CML-12 | CML: Fitting | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 12.3 | 6 O'Clock | 200 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 13 | 12.3 | 12.3 | 12.5 | 0.3304
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23405-03C02-P | CML-1 | 100-PG-23405-03C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 23853 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 8.825 | CML-1 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A3: Inside Quadrant |  |  | 2.7 |  | 7.9 | 6 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9.3 | 8.9 | 7.9 | 9.2 | 0.63966
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-21 | 50-CG-38452-09C02-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21353 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 8.525 | CML-21 | CML: Reducer | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 8.3 | 9 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.69 |  | 9 | 8.5 | 8.3 | 8.3 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40402-01C02 | CML-5 | 100-WC-40402-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5485 |  | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 6.55 | CML-5 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2015-03-15 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.3 | 9 O'Clock | 100 | 6.02 | 100-WC-40402-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | 0.49324 | 6.6 | 6.5 | 6.8 | 6.3 | 0.20817
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-18 | 50-PL-23021-03C03 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10250 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 7.975 | CML-18 | CML: type TBC | 6 | 2015-08-15 | 2015-07-30 | 2013-11-08 | 2.5 | 2.8287 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 7.5 | 9 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.2 | 8.2 | 8 | 7.5 | 0.3304
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-21 | 250-PW-44006-01X01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 23192 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.625 | CML-21 | CML: Fitting | 3 | 2023-05-21 | 2023-04-24 | 2015-05-11 07:00 | 2.5 | 0.38595 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | -0.98704 | 5.6 | 5.6 | 5.6 | 5.7 | 0.05
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23034-01C03 | CML-9 | 50-PL-23034-01C03 CML-9 | no | FPSO 2014 | Pipe Wall Thickness | 20577 | Reviewed on 26/11/14.FFS. Repeat Oct.19 | 2014-10-12 07:00 | 2014-10-12 12:00 |  |  | Nestor | 2014-11-26 16:20 | [32 empty] | 8.875 | CML-9 | CML: Elbow | 6 | 2038-06-15 | 2037-12-21 | 2014-10-12 07:00 | 2.5 | 0.24905 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-PL-23034-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.9 | 9.1 | 9.1 | 0.3304
PF02 | Montara_Topside | No | Separation (20) | Pipework | 50-PF-20063-03S01-P | CML-3 | 50-PF-20063-03S01-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21545 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 7.95 | CML-3 | CML: Pipe Length | 1 | 2027-07-07 | 2025-06-19 | 2014-07-13 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.91 | 2.5 | 2.705 | 7.7 | 6 O'Clock | 150 | 3.91 | 50-PF-20063-03S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8 | 8.2 | 7.7 | 7.9 | 0.20817
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-12 | 100-PG-23028-25C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 451 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 15.975 | CML-12 | CML: Pipe Length | 3 | 2017-02-15 | 2015-12-28 | 2014-03-12 09:00 | 9.4 | 2.0793 | A3: Inside Quadrant |  | 14.12 | 9.4 | 11.76 | 15.5 | 6 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 16 | 16.2 | 15.5 | 16.2 | 0.3304
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-5 | 300-PG-23001-03C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10955 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.025 | CML-5 | CML: Elbow | 6 | 2025-02-12 | 2023-02-23 | 2014-01-09 | 5.22 | 0.77275 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.58 |  | 14.5 | 14 | 13.8 | 13.8 | 0.3304
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56059-01C02 | CML-2 | 50-DH-56059-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3340 | Rope Access | 2014-05-08 11:00 | 2014-05-08 12:00 | [36 empty] | 7.825 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-08 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56059-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.9 | 7.8 | 8.2 | 0.3304
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-12 | 80-CG-38459-09C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 3010 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.275 | CML-12 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 8.9 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.29 | 0 | 9.3 | 8.9 | 9.2 | 9.7 | 0.3304
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-12 | 80-CG-38459-09C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 22289 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.275 | CML-12 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 8.9 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.29 |  | 9.3 | 8.9 | 9.2 | 9.7 | 0.3304
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-3 | 50-CG-38487-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20842 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.775 | CML-3 | CML: Pipe Length | 3 | 2037-12-13 | 2031-08-01 | 2014-10-02 07:00 | 2.5 | 0.25415 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 1.444 | 9.2 | 8.8 | 8.7 | 8.4 | 0.3304
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38477-01C02-P | CML-1 | 50-CG-38477-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20891 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 9.825 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-10-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 6 O'Clock | 25 | 6.35 | 25-CG-38485-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.2 | 9.9 | 9.4 | 9.8 | 0.3304
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38491-09C02 | CML-4 | 50-CG-38491-09C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2543 |  | 2014-04-03 10:00 | 2014-04-03 11:00 | [36 empty] | 9.825 | CML-4 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.4 | 6 O'Clock | 50 | 8.74 | 50-CG-38491-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.8 | 10.2 | 9.4 | 9.9 | 0.3304
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-9 | 100-PW-20021-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21812 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6.1 | CML-9 | CML: Elbow | 3 | 2028-05-23 | 2028-11-19 | 2014-10-11 07:00 | 2.5 | 0.23487 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6 | 6.2 | 6.5 | 0.33665
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-6 | 50-CG-38001-09C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10919 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.275 | CML-6 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.3873 | A2: Right Quadrant |  | 5.74 |  |  | 7.9 | 3 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.9 | 8.7 | 7.9 | 8.2 | 8.3 | 0.3304
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-23 | 80-CG-38459-09C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 3021 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.325 | CML-23 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.9 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.29 | 0 | 8.9 | 9.3 | 9.7 | 9.4 | 0.3304
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-23 | 50-PF-20301-03C03-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 22300 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.325 | CML-23 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.9 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.29 |  | 8.9 | 9.3 | 9.7 | 9.4 | 0.3304
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-10 | 50-CG-38452-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20047 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 20.825 | CML-10 | CML: type TBC | 3 | 2017-07-26 | 2016-07-08 | 2014-05-29 07:00 | 15.88 | 1.4608 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 3 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 | 0 | 21 | 20.5 | 20.6 | 21.2 | 0.3304
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-16 | 250-PW-20040-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21400 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.925 | CML-16 | CML: Reducer | 6 | 2032-07-19 | 2029-08-28 | 2014-07-12 07:30 | 4.1 | 0.44916 | A3: Inside Quadrant |  | 6.7 | 4.1 | 5.4 | 12.2 | 6 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 13.4 | 13.7 | 12.2 | 12.4 | 0.73655
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56022-01C02 | CML-1 | 80-DH-56022-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 3482 | Rope Access | 2014-05-14 09:30 | 2014-05-14 11:00 | [36 empty] | 4.7 | CML-1 | CML: type TBC | 3 | 2015-10-21 | 2016-01-31 | 2014-05-14 09:30 | 2.5 | 1.2503 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.3 | 9 O'Clock | 80 | 5.49 | 80-DH-56022-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.7 | 5.1 | 4.7 | 4.3 | 0.3266
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-9 | 50-PW-44015-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22714 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 7.6 | CML-9 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-04-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 2.238 | 7.8 | 5.7 | 8.8 | 8.1 | 1.3342
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-10 | 50-CG-38466-01C02 CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 2524 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.2 | CML-10 | CML: type TBC | 3 | 2016-11-07 | 2017-03-21 | 2014-04-02 13:00 | 2.5 | 0.884 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 4.8 | 5.6 | 5.2 | 5.2 | 4.8 | 0.3266
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-20 | 100-PW-20021-01C02-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21823 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6.025 | CML-20 | CML: Elbow | 3 | 2028-05-23 | 2028-11-19 | 2014-10-11 07:00 | 2.5 | 0.23487 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 6.2 | 5.7 | 6.2 | 0.23629
FG02 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 25-FG-45455-01C02-E | CML-16 | 25-FG-45455-01C02-E CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8137 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.4 | CML-16 | CML: type TBC | 1 | 2303-03-05 | 2230-06-04 | 2015-01-23 07:30 | 2.5 | 0.01214 | A4: Left Quadrant |  | 5.02 | 2.5 | 3.3838 | 6 | 9 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 6.8 | 6.4 | 6 | 0.3266
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-13 | 50-CG-38452-09C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21084 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 7.6 | CML-13 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.2 | 12 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.6 | 7.6 | 8 | 0.3266
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40049-01C02 | CML-2 | 50-WC-40049-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1231 |  | 2014-03-22 08:30 | 2014-03-22 09:00 | [36 empty] | 6.525 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 08:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40049-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.6 | 6.3 | 6.5 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43110-01C02 | CML-2 | 200-FH-43110-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12793 |  | 2014-01-18 13:30 | 2014-01-18 14:30 | [36 empty] | 8.1 | CML-2 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 13:30 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.7 | 3 O'Clock | 200 | 6.35 | 200-FH-43110-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.36 |  | 8.5 | 7.7 | 8.1 | 8.1 | 0.3266
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43036-01C02 | CML-4 | 100-FH-43036-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12668 |  | 2014-01-26 10:00 | 2014-01-26 11:00 | [36 empty] | 10.9333 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-26 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.7 | 12 O'Clock | 100 | 6.02 | 100-FH-43036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.7 | 11.3 | 10.8 |  | 0.32146
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-13 | 80-FH-43158-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12894 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 7.0333 | CML-13 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-22 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 12 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.9 | 7.4 |  | 0.32146
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-30 | 250-PW-44006-01X01 CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 1927 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.1 | CML-30 | CML: Pipe Length | 3 | 2018-04-02 | 2018-03-20 | 2014-03-26 07:00 | 2.5 | 0.79536 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 6.4 | 5.7 | 5.8 | 0.40825
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-5 | 100-FH-43104-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12756 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 8.0333 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.8 | 12 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.4 | 7.9 |  | 0.32146
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-45 | 150-PG-23506-25C02 CML-45 |  | FPSO 2014 | Pipe Wall Thickness | 2819 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.125 | CML-45 | CML: Pipe Length | 3 | 2108-12-07 | 2084-10-10 | 2014-03-15 09:00 | 15.88 | 0.06351 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 21.9 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.02 |  | 22 | 22 | 22.6 | 21.9 | 0.32016
PG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45303-03C03-P | CML-2 | 80-FG-45303-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22056 | Protective mesh removed | 2014-06-30 07:00 | 2014-06-30 08:00 | [36 empty] | 10.675 | CML-2 | CML: Pipe Length | 6 | 2023-06-07 | 2021-11-27 | 2014-06-30 07:00 | 2.5 | 0.86091 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 10.2 | 9 O'Clock | 80 | 11.13 | 80-FG-45303-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.9 | 10.8 | 10.8 | 10.2 | 0.32016
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40507-1CG | CML-1 | 200-WC-40507-1CG CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8670 | Material Class Not Selectable | 2015-02-12 14:00 | 2015-02-12 15:00 |  |  | Administrator | 2015-09-08 10:53 | [32 empty] | 13.175 | CML-1 | CML: Pipe Length | 3 | 2115-05-31 | 2079-05-31 | 2015-02-12 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 9.7 | 2.5 | 6.1 | 12.7 | 6 O'Clock | 200 | 12.7 | 200-WC-40507-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 13.3 | 13.4 | 12.7 | 13.3 | 0.32016
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-25 | 150-PG-23506-25C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 2799 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.475 | CML-25 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.2 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.32 |  | 22.2 | 22.2 | 22.8 | 22.7 | 0.32016
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-20 | 150-FG-45505-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 22360 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.825 | CML-20 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.6 | 9 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.3 | 7.7 | 7.7 | 7.6 | 0.32016
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20057-01C02-P | CML-3 | 100-PW-20057-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22816 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.875 | CML-3 | CML: Reducing Tee | 3 | 2034-06-12 | 2035-02-20 | 2015-04-30 07:00 | 2.5 | 0.16727 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 1.8434 | 5.7 | 6 | 5.8 | 6 | 0.15
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56120-01C02 | CML-4 | 50-DH-56120-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21036 | Rope Access | 2014-05-19 08:00 | 2014-05-19 09:00 | [36 empty] | 5.275 | CML-4 | CML: type TBC | 3 | 2017-05-18 | 2017-10-20 | 2014-05-19 08:00 | 2.5 | 0.7666 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56120-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.5 | 5.4 | 4.8 | 5.4 | 0.32016
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-2 | 50-FH-43016-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12601 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.375 | CML-2 | CML: Elbow | 3 | 2017-11-21 | 2018-05-15 | 2014-01-23 13:00 | 2.5 | 0.67895 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.6 | 5.7 | 5.1 | 0.32016
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-20 | 250-WC-40017-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 2083 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 6.475 | CML-20 | CML: type TBC | 3 | 2076-09-28 | 2076-04-12 | 2014-03-28 09:30 | 2.5 | 0.06075 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 6 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 6.6 | 6.3 | 6.5 | 0.12583
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-5 | 150-FG-45002-03C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10408 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 8.6 | CML-5 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.7 | 12 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 8.8 | 9.4 | 8.5 | 0.70711
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-6 | 200-PW-44019-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21897 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 6.05 | CML-6 | CML: Fitting | 3 | 2019-08-19 | 2019-08-03 | 2014-06-19 09:30 | 2.5 | 0.61881 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 0 | 6.6 | 5.9 | 5.7 | 6 | 0.3873
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40050-01C02 | CML-3 | 50-WC-40050-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1897 | Rope Access | 2014-03-25 14:00 | 2014-03-25 15:00 | [36 empty] | 6.4 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40050-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.4 | 6.4 | 6.5 | 6.3 | 0.08165
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-19 | 50-DH-56070-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 3235 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.275 | CML-19 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.5 | 5.8 | 6.4 | 0.32016
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-6 | 200-PW-44019-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5572 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 6.05 | CML-6 | CML: Fitting | 3 | 2019-08-19 | 2019-08-03 | 2014-06-19 09:30 | 2.5 | 0.61881 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.6 | 5.9 | 5.7 | 6 | 0.3873
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML 2 | 200-PW-44021-01X01 CML 2 |  | FPSO 2014 | Pipe Wall Thickness | 22366 |  | 2014-06-19 13:00 | 2014-06-19 14:00 | [36 empty] | 6.175 | CML 2 | CML: Fitting | 3 | 2019-08-20 | 2019-08-04 | 2014-06-19 13:00 | 2.5 | 0.61858 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 9 O'Clock | 200 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 6.4 | 6.1 | 5.7 | 0.3594
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-3 | 300-PF-20003-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21741 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 20.675 | CML-3 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 20.2 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.3 |  | 20.8 | 20.8 | 20.9 | 20.2 | 0.32016
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-14 | 300-PF-20001-03C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21152 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 20.975 | CML-14 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 20.5 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.6 |  | 20.5 | 21.1 | 21.2 | 21.1 | 0.32016
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-4 | 50-PL-23515-01C03 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8653 |  | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:50 | [32 empty] | 9.075 | CML-4 | CML: Elbow | 6 | 2089-03-25 | 2087-10-10 | 2015-02-12 07:00 | 2.5 | 0.08225 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.2 | 9.2 | 9.3 | 0.32016
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-9 | 300-PL-20011-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 23794 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 7.875 | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 3 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.1 | 7.6 | 7.8 | 8 | 0.22174
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-10 | 250-PG-23003-06C02-PA CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 7689 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:57 | [32 empty] | 4.475 | CML-10 | CML: Elbow | 3 | 2016-08-01 | 2016-12-04 | 2015-01-08 13:00 | 2.5 | 0.95833 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4 | 3 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 0.87416 | 4.6 | 4 | 4.6 | 4.7 | 0.32016
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56141-01C02 | CML-5 | 50-DH-56141-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21072 | Rope Access | 2014-05-15 08:00 | 2014-05-15 09:00 | [36 empty] | 5.025 | CML-5 | CML: type TBC | 3 |  |  | 2014-05-15 08:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 4.8 | 9 O'Clock | 80 |  | 80-DH-56141-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 5.5 | 4.9 | 4.8 | 0.32016
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40011-01C02 | CML-5 | 50-WC-40011-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1890 | Rope Access | 2014-03-25 13:00 | 2014-03-25 14:00 | [36 empty] | 6.35 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.4 | 6.3 | 6.3 | 6.4 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-3 | 50-FH-43011-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7953 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.175 | CML-3 | CML: Elbow | 3 | 2017-05-26 | 2016-11-15 | 2015-01-18 08:00 | 2.5 | 1.3588 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 5.7 | 3 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.3 | 5.7 | 6.3 | 6.4 | 0.32016
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43106-01C02 | CML-1 | 100-FH-43106-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12770 |  | 2014-01-25 10:00 | 2014-01-25 11:00 | [36 empty] | 6.325 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-25 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 12 O'Clock | 100 | 6.02 | 100-FH-43106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 6.2 | 6.8 | 0.32016
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-8 | 150-FH-43136-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2769 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.175 | CML-8 | CML: Pipe Length | 3 | 2024-12-31 | 2022-11-30 | 2014-03-13 09:00 | 1.03 | 0.5244 | A4: Left Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.7 | 9 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.67 |  | 7.3 | 7.3 | 7.4 | 6.7 | 0.32016
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56012-01C02 | CML-8 | 80-DH-56012-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3474 | Rope Access | 2014-05-13 10:30 | 2014-05-13 12:00 | [36 empty] | 5.325 | CML-8 | CML: type TBC | 3 | 2019-03-15 | 2019-11-17 | 2014-05-13 10:30 | 2.5 | 0.51625 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 6 O'Clock | 80 | 5.49 | 80-DH-56012-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.6 | 5 | 5.6 | 0.32016
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-6 | 250-PW-44006-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7998 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 5.975 | CML-6 | CML: Pipe Length | 3 | 2023-02-13 | 2023-01-18 | 2015-01-20 08:30 | 2.5 | 0.3965 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | -0.12164 | 6.4 | 6 | 5.8 | 5.7 | 0.30957
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-4 | 50-FH-43011-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7954 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.325 | CML-4 | CML: Elbow | 3 | 2018-01-09 | 2017-06-01 | 2015-01-18 08:00 | 2.5 | 1.1752 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 6 | 12 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.6 | 6.6 | 0.32016
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57017-01C02 | CML-2 | 20-DC-57017-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2897 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 5.9 | CML-2 | CML: type TBC | 3 | 2043-10-03 | 2038-12-18 | 2014-04-25 08:00 | 0.16 | 0.17787 | A3: Inside Quadrant |  | 2.56 | 0.16 | 1.0125 | 5.4 | 6 O'Clock | 20 | 5.56 | 20-DC-57017-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.24 |  | 6.7 | 5.5 | 5.4 | 6 | 0.59442
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-8 | 300-PL-20011-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 23793 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 7.75 | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 6 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.7 | 7.9 | 7.6 | 7.8 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43124-01C02 | CML-8 | 80-FH-43124-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12850 |  | 2014-02-05 11:00 | 2014-02-05 13:00 | [36 empty] | 5.275 | CML-8 | CML: Elbow | 3 | 2020-04-25 | 2019-06-08 | 2014-02-05 11:00 | 0.54 | 0.71695 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5 | 6 O'Clock | 80 | 5.49 | 80-FH-43124-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.46 |  | 5 | 5.5 | 5 | 5.6 | 0.32016
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2282 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 7.475 | CML-1 | CML: type TBC | 3 | 2019-05-19 | 2018-08-04 | 2014-03-17 08:00 | 2.5 | 0.90829 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.2 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.8 | 7.7 | 7.2 | 7.2 | 0.32016
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38492-01C02 | CML-4 | 50-CG-38492-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2538 |  | 2014-04-03 08:00 | 2014-04-03 09:00 | [36 empty] | 8.225 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-03 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 9 O'Clock | 50 | 5.54 | 50-CG-38492-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8 | 8.5 | 8.5 | 7.9 | 0.32016
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-7 | 50-CG-38487-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20807 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 8.725 | CML-7 | CML: Pipe Length | 3 | 2034-02-20 | 2028-10-04 | 2014-07-18 11:00 | 2.5 | 0.30088 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9 | 8.4 | 9 | 8.5 | 0.32016
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-16 | 100-FG-45001-09C02 CML-16 | Yes | FPSO 2015 | Pipe Wall Thickness | 23321 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.625 | CML-16 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 11.3 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | -1.0251 | 11.4 | 11.3 | 11.9 | 11.9 | 0.32016
FL02 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FL-43454-01C02-P | CML-4 | 50-FL-43454-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23102 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.425 | CML-4 | CML: Pipe Length | 6 | 2090-08-22 | 2086-04-01 | 2015-05-10 07:00 | 2.5 | 0.08761 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.1 | 6 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | 0.62623 | 9.7 | 9.2 | 9.1 | 9.7 | 0.32016
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40051-01C02 | CML-4 | 50-WC-40051-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 903 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 7.275 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.9 | 6.4 | 7.1 | 8.7 | 0.99457
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-21 | 250-PW-20040-03C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21405 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.775 | CML-21 | CML: Fitting | 6 | 2032-07-19 | 2029-08-28 | 2014-07-12 07:30 | 4.1 | 0.44916 | A3: Inside Quadrant |  | 6.7 | 4.1 | 5.4 | 12.2 | 6 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 12.5 | 13.5 | 12.2 | 12.9 | 0.56199
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43146-01C02 | CML-2 | 80-FH-43146-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10555 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.125 | CML-2 | CML: type TBC | 3 | 2015-09-30 | 2016-01-07 | 2013-11-16 | 2.5 | 1.2818 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-FH-43146-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 4.9 | 5 | 5 | 0.32016
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-17 | 80-FH-43009-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12595 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.625 | CML-17 | CML: Pipe Length | 3 | 2050-12-17 | 2046-03-02 | 2014-02-05 08:00 | 0.54 | 0.13175 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.5 | 5.5 | 5.4 | 6.1 | 0.32016
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-32 | 300-PF-20501-03C03-P CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 21708 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.375 | CML-32 | CML: type TBC | 6 | 2046-12-29 | 2040-12-14 | 2014-09-28 07:00 | 4.9 | 0.27886 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.5 | 14.6 | 14.5 | 13.9 | 0.32016
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-11 | 50-FG-45301-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5797 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.875 | CML-11 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7 | 7 | 6.4 | 7.1 | 0.32016
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56010-01C02 | CML-2 | 50-DH-56010-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22319 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 6.875 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7 | 7 | 7.1 | 0.32016
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56010-01C02 | CML-2 | 50-DH-56010-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1839 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 6.875 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7 | 7 | 7.1 | 0.32016
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-7 | 200-PG-23008-15S01-A CML-7 | Yes | FPSO 2013 | Pipe Wall Thickness | 10093 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 20.275 | CML-7 | CML: Pipe Length | 1 | 2014-08-18 | 2014-02-02 | 2013-11-07 | 14.06 | 7.3689 | A4: Left Quadrant |  | 22.01 | 14.06 | 18.035 | 19.8 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.74 |  | 20.4 | 20.5 | 20.4 | 19.8 | 0.32016
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40051-01C02 | CML-4 | 50-WC-40051-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1567 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 7.275 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.9 | 6.4 | 7.1 | 8.7 | 0.99457
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-6 | 300-PG-23400-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 523 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.775 | CML-6 | CML: Pipe Length | 6 | 2064-04-24 | 2068-11-11 | 2014-03-13 09:00 | 5.22 | 0 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 10.5 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.28 |  | 10.5 | 10.6 | 10.9 | 11.1 | 0.27538
FG03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-FG-45055-06S01-E | CML-3 | 50-FG-45055-06S01-E CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24387 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.825 | CML-3 | CML: Equal Tee | 1 | 2035-06-01 | 2029-05-31 | 2016-06-07 07:00 | 1.71 | 0 | A2: Right Quadrant |  | 2.91 | 1.71 | 2.31 | 7 | 3 O'Clock | 50 | 3.91 | 50-FG-45055-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.29 |  | 7.7 | 7 | 8.2 | 8.4 | 0.62383
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-5 | 80-CG-38486-09C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21743 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.6 | CML-5 | CML: Pipe Length | 6 | 2192-01-01 | 2159-11-20 | 2014-10-01 07:00 | 4.9 | 0.05243 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.8 | 14.5 | 14.9 | 14.2 | 0.31623
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-1 | 100-PW-20021-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22819 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.925 | CML-1 | CML: Pipe Length | 3 | 2034-06-12 | 2035-02-20 | 2015-04-30 07:00 | 2.5 | 0.16727 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 9.806 | 5.7 | 6 | 6 | 6 | 0.15
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56084-01C02 | CML-4 | 100-DH-56084-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3346 | Rope Access | 2014-05-08 13:00 | 2014-05-08 14:00 | [36 empty] | 5.7 | CML-4 | CML: type TBC | 3 | 2017-12-26 | 2018-02-19 | 2014-05-08 13:00 | 2.5 | 0.76945 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 6 O'Clock | 100 | 6.02 | 100-DH-56084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.9 | 5.3 | 6 | 0.31623
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-14 | 100-DH-56561-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7946 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 5.8 | CML-14 | CML: Pipe Length | 3 | 2024-06-14 | 2024-10-25 | 2015-01-17 13:00 | 2.5 | 0.3187 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 9 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 6.2 | 5.6 | 5.5 | 0.31623
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56030-01C02 | CML-1 | 80-DH-56030-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20910 | Rope Access | 2014-05-22 08:00 | 2014-05-22 09:00 | [36 empty] | 5.8 | CML-1 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-22 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-DH-56030-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 6.2 | 5.5 | 5.9 | 0.31623
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43306-01C02 | CML-8 | 80-FH-43306-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5767 | Rope access | 2014-06-23 09:30 | 2014-06-23 11:00 | [36 empty] | 5.2 | CML-8 | CML: Elbow | 3 | 2021-01-09 | 2020-01-20 | 2014-06-23 09:30 | 0.54 | 0.65011 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 4.8 | 3 O'Clock | 80 | 5.49 | 80-FH-43306-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.26 |  | 5.1 | 4.8 | 5.5 | 5.4 | 0.31623
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40013-01C02 | CML-4 | 50-WC-40013-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1559 | Rope Access | 2014-04-09 10:00 | 2014-04-09 11:00 | [36 empty] | 7.45 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 8 | 7.9 | 7.5 | 6.4 | 0.73258
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-10 | 50-CG-24002-09C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2556 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 8.5 | CML-10 | CML: type TBC | 3 | 2021-08-06 | 2019-06-22 | 2014-04-03 13:00 | 2.5 | 0.76205 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.8 | 8.1 | 8.4 | 8.7 | 0.31623
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-3 | 100-FG-45001-09C02 CML-3 | Yes | FPSO 2015 | Pipe Wall Thickness | 23308 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11 | CML-3 | CML: type TBC | 3 | 2039-01-01 | 2032-03-05 | 2015-07-11 07:00 | 4.7 | 0.25114 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.6 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | -0.48241 | 11.3 | 10.6 | 10.9 | 11.2 | 0.31623
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-20 | 80-PW-44001-01C02-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 22011 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.325 | CML-20 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.6 | 6.6 | 6.3 | 5.8 | 0.37749
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-23 | 250-PW-20041-03C03-P CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 23493 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 12.475 | CML-23 | CML: Fitting | 6 | 2050-06-11 | 2044-11-04 | 2015-07-27 07:00 | 4.1 | 0.2321 | A3: Inside Quadrant |  | 6.7 | 4.1 | 5.4 | 12.2 | 6 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | -0.48029 | 12.4 | 12.8 | 12.2 | 12.5 | 0.25
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-23 | 80-PW-20024-01C03-P CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 23067 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 11.55 | CML-23 | CML: Elbow | 6 | 244027 | 213155 | 2015-05-06 07:00 | 2.5 | 0.01555 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.1 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.1 | 11.8 | 11.6 | 11.7 | 0.31091
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-10 | 50-FL-43454-01C02-P CML-10 | Yes | FPSO 2014 | Pipe Wall Thickness | 20513 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.5 | CML-10 | CML: Fitting | 3 | 2022-09-16 | 2023-09-15 | 2014-10-05 07:00 | 2.5 | 0.32689 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.8 | 5.4 | 5.1 | 0.31623
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-11 | 250-PW-44007-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23144 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 6.025 | CML-11 | CML: Pipe Length | 3 | 2024-11-25 | 2024-10-25 | 2015-05-10 07:00 | 2.5 | 0.33496 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 9 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 0.44533 | 6 | 6.4 | 6 | 5.7 | 0.28723
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43513-01C02 | CML-2 | 50-FL-43513-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 7984 | Line is FFS. Current RBI frequency is 48m Action: to recheck line in 24m (Jan. 2017) to confirm CR. RBI frequency to be updated | 2015-01-18 16:00 | 2015-01-18 17:00 |  |  | Administrator | 2015-09-07 14:58 | [32 empty] | 5.1 | CML-2 | CML: Elbow | 3 | 2019-04-30 | 2019-12-18 | 2015-01-18 16:00 | 2.5 | 0.51385 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-FL-43513-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 5.4 | 5.3 | 4.7 | 0.31623
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-2 | 100-FH-43507-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7751 |  | 2015-01-11 08:00 | 2015-01-11 09:00 | [36 empty] | 5.1 | CML-2 | CML: type TBC | 3 | 2019-04-03 | 2019-11-18 | 2015-01-11 08:00 | 2.5 | 0.52025 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-FH-43507-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 5.4 | 5.3 | 4.7 | 0.31623
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56130-01C02 | CML-1 | 50-DH-56130-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21053 | Rope Access | 2014-05-15 13:00 | 2014-05-15 14:00 | [36 empty] | 5.9 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-15 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56130-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 5.6 | 5.7 | 6.3 | 0.31623
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-9 | 0200-DH-56L9003-AC21M-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5094 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.125 | CML-9 | CML: type TBC | 3 | 2027-05-12 | 2024-11-21 | 2015-03-06 07:00 | 2.5 | 0.43469 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 7.8 | 12 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8 | 8 | 8.7 | 0.39476
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-6 | 0200-DH-56L9003-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5091 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.875 | CML-6 | CML: type TBC | 3 | 2027-05-12 | 2024-11-21 | 2015-03-06 07:00 | 2.5 | 0.43469 | A2: Right Quadrant |  | 5.74 | 2.5 | 3.5737 | 7.8 | 3 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.8 | 7.8 | 8.7 | 10.2 | 0.99121
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-3 | 0200-DH-56L9003-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5088 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.475 | CML-3 | CML: type TBC | 3 | 2027-05-12 | 2024-11-21 | 2015-03-06 07:00 | 2.5 | 0.43469 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 7.8 | 12 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.7 | 8.7 | 8.7 | 0.45
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-16 | 50-FG-45301-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 5802 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.1 | CML-16 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.5 | 5.9 | 6.2 | 0.31623
SD02 | Montara_Topside | No | Steam (55) | Pipework | 50-SL-55006-01C02-P | CML-3 | 50-SL-55006-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8861 |  | 2015-02-24 13:00 | 2015-02-24 14:00 | [36 empty] | 8.5 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-24 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.8 | 12 O'Clock | 50 | 5.54 | 50-SL-55006-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 9 | 8.6 | 8.6 | 0.50332
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-3 | 250-WC-40026-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1279 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.175 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.4 | 7.5 | 7.4 | 0.51881
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-18 | 250-WC-40026-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1294 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.075 | CML-18 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 6 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.3 | 7.2 | 6.4 | 7.4 | 0.45735
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-25 | 200-PL-20035-03C02-P CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 23474 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 9.05 | CML-25 | CML: Fitting | 3 | 2059-02-11 | 2051-04-06 | 2015-07-24 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 8.8 | 6 O'Clock | 250 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.19 | -0.93172 | 9.4 | 9.1 | 8.8 | 8.9 | 0.26458
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-7 | 250-PW-44004-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5626 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 6.075 | CML-7 | CML: Elbow | 3 | 2020-10-13 | 2020-09-24 | 2014-06-20 13:00 | 2.5 | 0.52205 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 6.5 | 6.1 | 5.8 | 0.30957
CG04 | Montara_Topside | Yes | Steam (55) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8838 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 7.6 | CML-8 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.2 | 6 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.8 | 7.5 | 7.2 | 7.9 | 0.31623
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-7 | 200-FH-43003-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12530 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.6 | CML-7 | CML: Pipe Length | 3 | 2034-08-01 | 2032-01-05 | 2014-01-18 11:30 | 1.34 | 0.23652 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.2 | 12 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 6.2 | 6.5 | 6.8 | 6.9 | 0.31623
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-5 | 25-PG-23300-25C02 CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 20672 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 8.7 | CML-5 | CML: Elbow | 3 | 2020-02-14 | 2018-11-30 | 2014-05-27 09:30 | 4.4 | 0.69881 | A3: Inside Quadrant |  | 6.09 | 4.4 | 5.245 | 8.4 | 6 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 9.1 | 8.8 | 8.4 | 8.5 | 0.31623
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21798 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.8 | 6 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.7 | 7.8 | 11.7 | 1.8493
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21794 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.025 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 7.8 | 3 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.5 | 7.8 | 7.9 | 7.9 | 0.32016
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-11 | 25-FG-45455-01C02-E CML-11 |  | FPSO 2016 | Pipe Wall Thickness | 24356 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 8.3 | CML-11 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 9 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.4 | 8.7 | 8.1 | 8 | 0.31623
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23741 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.7 | CML-1 | CML: Elbow | 3 | 2057-09-12 | 2046-03-15 | 2015-10-30 07:00 | 2.5 | 0.14082 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.5 | 8.4 | 8.8 | 9.1 | 0.31623
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-15 | 50-PL-45016-03C03 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10455 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 7.8 | CML-15 | CML: type TBC | 6 | 2016-03-28 | 2015-12-02 | 2013-11-13 | 0.99 | 2.743 | A3: Inside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.5 | 6 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.51 |  | 7.9 | 7.6 | 7.5 | 8.2 | 0.31623
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-4 | 200-PW-44019-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23032 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 5.9 | CML-4 | CML: Fitting | 3 | 2024-11-01 | 2024-10-02 | 2015-05-06 07:00 | 2.5 | 0.33686 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 3 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 0.11374 | 6.2 | 5.7 | 5.9 | 5.8 | 0.21602
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-17 | 200-PG-23013-09C03-A CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20001 | Rope Access | 2014-01-10 | 2014-01-10 | [35 empty] | Low alarm breach | 14.9 | CML-17 | CML: type TBC | 6 | 2014-06-14 | 2014-03-26 | 2014-01-10 | 10.22 | 10.017 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 14.5 | 9 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.28 |  | 15.2 | 15.1 | 14.8 | 14.5 | 0.31623
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-1 | 150-FL-43453-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2245 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 8.4 | CML-1 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 8 | 3 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.6 | 8 | 8.3 | 8.7 | 0.31623
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-3 | 250-PW-20040-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21387 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.15 | CML-3 | CML: Elbow | 6 | 2037-05-01 | 2033-09-19 | 2014-07-12 07:30 | 4.1 | 0.35933 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.3 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 12.8 | 13.3 | 14.2 | 12.3 | 0.81035
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-6 | 50-WC-40032-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1240 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 6.7 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.8 | 7.2 | 6.4 | 0.38297
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-2 | 200-WC-40008-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7808 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 6.825 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.7 | 7 | 7.2 | 0.35
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-6 | 50-PL-23021-03C03 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10238 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.9 | CML-6 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 10.5 | 12 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.5 | 11.1 | 11.2 | 10.8 | 0.31623
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-6 | 50-PG-44022-01C03-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22981 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 11.1 | CML-6 | CML: Reducing Tee | 6 | 2075-10-24 | 2074-08-12 | 2015-05-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 10.8 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 | 1.516 | 11.2 | 10.9 | 10.8 | 11.5 | 0.31623
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-1 | 80-CG-38486-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21677 | Protective mesh removed | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 16.1 | CML-1 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 15.8 | 12 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 15.8 | 15.9 | 16.5 | 16.2 | 0.31623
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-23 | 300-PG-20005-03C03-P CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 22785 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 16.65 | CML-23 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 16.4 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 | -0.75005 | 16.6 | 16.5 | 17.1 | 16.4 | 0.31091
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-31 | 80-CG-38486-09C02-P CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 3029 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.95 | CML-31 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.7 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 | 0 | 8.7 | 8.9 | 8.8 | 9.4 | 0.31091
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-31 | 50-DH-56137-01C02 CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 22308 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.95 | CML-31 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.7 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 |  | 8.7 | 8.9 | 8.8 | 9.4 | 0.31091
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-4 | 300-PG-20502-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 23891 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 9.95 | CML-4 | CML: Pipe Length | 6 | 2030-04-27 | 2028-05-12 | 2014-09-26 07:00 | 2.5 | 0.46165 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 9.8 | 10.4 | 9.9 | 0.31091
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-4 | 300-PG-20502-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20751 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 9.95 | CML-4 | CML: type TBC | 6 | 2030-04-27 | 2028-05-12 | 2014-09-26 07:00 | 2.5 | 0.46165 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 9.8 | 10.4 | 9.9 | 0.31091
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-2 | 300-PG-20037-03C03-PA CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23341 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.05 | CML-2 | CML: Pipe Length | 6 | 2046-11-17 | 2041-05-17 | 2015-07-20 07:00 | 5.33 | 0.26697 | A1: Outside Quadrant |  | 8.27 | 5.33 | 6.8 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.37 | 0.094621 | 13.7 | 14.4 | 13.9 | 14.2 | 0.31091
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-6 | 250-PW-20040-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21390 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.875 | CML-6 | CML: Fitting | 6 | 2037-05-01 | 2033-09-19 | 2014-07-12 07:30 | 4.1 | 0.35933 | A1: Outside Quadrant |  | 6.7 | 4.1 | 5.4 | 12.3 | 12 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 12.3 | 13 | 13.7 | 12.5 | 0.62383
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40502-1CG | CML-2 | 250-WC-40502-1CG CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 5618 | Material typre 1CG (no option in drop down box) | 2014-06-20 11:00 | 2014-06-20 12:00 | Check Corrosion Rate of 1.794mm/ yr | [35 empty] | 14.625 | CML-2 | CML: Elbow | 3 | 2020-06-05 | 2017-10-03 | 2014-06-20 11:00 | 2.5 | 1.7943 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 13.2 | 9 O'Clock | 250 | 15.09 | 250-WC-40502-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 14.2 | 15.7 | 15.4 | 13.2 | 1.15
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-14 | 250-PW-20040-03C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21398 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.7 | CML-14 | CML: Fitting | 6 | 2037-05-01 | 2033-09-19 | 2014-07-12 07:30 | 4.1 | 0.35933 | A1: Outside Quadrant |  | 6.7 | 4.1 | 5.4 | 12.3 | 12 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 12.3 | 13.3 | 12.5 | 12.7 | 0.43205
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-19 | 50-PL-23041-06C03 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10232 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.55 | CML-19 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 2.2128 | A4: Left Quadrant |  | 5.07 |  |  | 10.1 | 9 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.7 | 10.6 | 10.8 | 10.1 | 0.31091
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45046-03C02-E | CML-4 | 80-FG-45046-03C02-E CML-4 | yes | FPSO 2016 | Pipe Wall Thickness | 24410 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.95 | CML-4 | CML: Elbow | 3 | 2024-11-05 | 2024-11-12 | 2016-06-08 07:00 | 2.5 | 0.26135 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.495 | 4.7 | 12 O'Clock | 80 | 5.49 | 80-FG-45046-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.4 | 4.9 | 4.8 | 0.31091
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56118-01C02 | CML-7 | 50-DH-56118-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21026 | Rope Access | 2014-05-19 11:00 | 2014-05-19 12:00 | [36 empty] | 4.95 | CML-7 | CML: type TBC | 3 | 2016-11-27 | 2017-04-13 | 2014-05-19 11:00 | 2.5 | 0.86989 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-DH-56118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.8 | 4.7 | 5.4 | 4.9 | 0.31091
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-4 | 200-PG-23008-15S01-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3179 | Rope Access | 2014-05-07 13:00 | 2014-05-07 14:00 | [36 empty] | 5.55 | CML-4 | CML: type TBC | 3 | 2019-11-09 | 2020-07-19 | 2014-05-07 13:00 | 2.5 | 0.4716 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.8 | 5.7 | 5.6 | 5.1 | 0.31091
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-4 | 200-PG-23008-15S01-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20131 | Rope Access | 2014-05-07 13:00 | 2014-05-07 14:00 | [36 empty] | 5.55 | CML-4 | CML: type TBC | 3 | 2019-11-09 | 2020-07-19 | 2014-05-07 13:00 | 2.5 | 0.4716 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | -525.5985 | 5.8 | 5.7 | 5.6 | 5.1 | 0.31091
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-15 | 250-PW-44006-01X01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23186 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6 | CML-15 | CML: Pipe Length | 3 | 2024-12-01 | 2024-10-31 | 2015-05-11 07:00 | 2.5 | 0.33449 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 9 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 0.32901 | 6.2 | 6.1 | 6 | 5.7 | 0.21602
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38477-01C02-P | CML-1 | 50-CG-38477-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21328 | Protective mesh removed | 2014-06-27 08:00 | 2014-06-27 09:00 | [36 empty] | 7.45 | CML-1 | CML: Reducer | 1 | 2038-04-25 | 2030-11-12 | 2014-06-27 08:00 | 3.86 | 0 | A2: Right Quadrant |  | 5.35 | 3.86 | 4.605 | 7.2 | 3 O'Clock | 350 | 6.35 | 300-PG-20028-03D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.34 |  | 7.3 | 7.2 | 7.4 | 7.9 | 0.31091
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-1 | 250-PW-44004-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22745 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 6.1 | CML-1 | CML: Pipe Length | 3 | 2026-10-12 | 2026-09-06 | 2015-04-29 07:00 | 2.5 | 0.2879 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.35012 | 6.2 | 6.2 | 5.8 | 6.2 | 0.2
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-9 | 200-WC-40008-01C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7815 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 6.825 | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.2 | 6.8 | 6.9 | 6.4 | 0.3304
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-10 | 50-CH-98806-1CG CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10893 | Deck Level | 2014-01-04 | 2014-01-04 | Low Reading | [35 empty] | 5.75 | CML-10 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 0.23548 | A2: Right Quadrant |  | 2.54 |  |  | 5.4 | 3 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 5.6 | 5.4 | 5.7 | 6.3 | 0.3873
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-13 | 100-FG-45043-03C02-E CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22659 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.95 | CML-13 | CML: Elbow | 3 | 2038-01-16 | 2034-08-26 | 2015-04-27 07:00 | 1.88 | 0.16799 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 5.7 | 3 O'Clock | 50 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.82 |  | 5.8 | 5.7 | 5.9 | 6.4 | 0.31091
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-9 | 50-DN-56101-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 849 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 8.1333 | CML-9 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-02 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.8 | 6 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.1 | 8.5 | 7.8 |  | 0.35119
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-4 | 50-DN-56101-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 844 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 8.3667 | CML-4 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-02 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.8 | 12 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 9.3 | 8 |  | 0.81445
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-21 | 200-PL-20008-01C02-H CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 8818 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 7.425 | CML-21 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 3 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.3 | 6.9 | 7.2 | 8.3 | 0.60759
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-11 | 80-DH-56004-01C02 CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 6889 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.65 | CML-11 | CML: type TBC | 0.5 | 2022-08-19 | 2020-04-29 | 2015-04-05 07:00 | 3.5 | 0.10842 | A2: Right Quadrant |  | 4 | 3.5 | 3.75 | 4.3 | 3 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 5 | 4.3 | 4.5 | 4.8 | 0.31091
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45036-03C02 | CML-1 | 50-FG-45036-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2573 |  | 2014-04-26 13:00 | 2014-04-26 14:00 | [36 empty] | 5.15 | CML-1 | CML: type TBC | 3 | 2017-02-13 | 2017-02-04 | 2014-04-26 13:00 | 2.5 | 0.81962 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-FG-45036-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 4.8 | 5.3 | 5.5 | 0.31091
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-13 | 100-DH-56561-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7945 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 5.55 | CML-13 | CML: Pipe Length | 3 | 2021-05-21 | 2021-08-25 | 2015-01-17 13:00 | 2.5 | 0.44128 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 12 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 6 | 5.5 | 0.31091
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43128-01C02 | CML-2 | 50-FH-43128-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1801 |  | 2014-04-28 14:00 | 2014-04-28 14:30 | [36 empty] | 6.15 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-28 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-FH-43128-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.3 | 6.5 | 6 | 0.31091
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-7 | 25-FG-45455-01C02-E CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21209 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 6.35 | CML-7 | CML: Fitting | 3 | 2025-09-28 | 2025-08-26 | 2014-07-15 07:30 | 2.5 | 0.31211 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 200 | 6.35 | 200-PL-20012-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.5 | 6 | 6.7 | 0.31091
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-11 | 200-FH-43037-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12680 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 6.45 | CML-11 | CML: type TBC | 3 | 2020-12-16 | 2020-11-25 | 2014-02-06 11:00 | 2.5 | 0.51006 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.7 | 6.6 | 6 | 6.5 | 0.31091
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-9 | 50-CH-98806-1CG CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10891 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 6.075 | CML-9 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 0.57189 | A3: Inside Quadrant |  | 2.54 |  |  | 5.2 | 6 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.6 | 6.2 | 5.2 | 6.3 | 0.60759
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-8 | 150-FH-43157-01C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10664 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.85 | CML-8 | CML: type TBC | 3 | 2016-12-06 | 2016-08-28 | 2013-11-18 | 2.5 | 1.3097 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.5 | 12 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.7 | 7 | 7.2 | 0.31091
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-29 | 50-CG-38452-09C02-P CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 21280 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.55 | CML-29 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.4 | 7.9 | 7.7 | 0.31091
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43109-01C02 | CML-4 | 200-FH-43109-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12788 |  | 2014-01-18 14:30 | 2014-01-18 15:30 | [36 empty] | 6.45 | CML-4 | CML: Pipe Length | 3 | 2026-02-14 | 2024-07-30 | 2014-01-18 14:30 | 1.34 | 0.39399 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.1 | 3 O'Clock | 200 | 6.35 | 200-FH-43109-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 6.8 | 6.1 | 6.3 | 6.6 | 0.31091
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40016-01C02 | CML-7 | 250-WC-40016-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20369 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-24 10:38 | [32 empty] | 6.65 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 3 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.4 | 7.1 | 6.5 | 0.31091
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-17 | 150-FH-43026-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23516 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 6.95 | CML-17 | CML: Fitting | 3 | 2034-11-25 | 2031-01-11 | 2015-07-28 07:00 | 1.03 | 0.2828 | A4: Left Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.5 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.47 | 0.43246 | 7.1 | 7 | 7.2 | 6.5 | 0.31091
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40023-01C02 | CML-2 | 50-WC-40023-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1250 |  | 2014-03-23 08:30 | 2014-03-23 09:00 | [36 empty] | 6.575 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-WC-40023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 6.5 | 7 | 0.28723
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38483-01C02 | CML-4 | 25-CG-38483-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10393 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.15 | CML-4 | CML: type TBC | 3 | 2016-01-28 | 2016-01-21 | 2013-11-12 | 2.5 | 1.4466 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 12 O'Clock | 25 | 6.35 | 25-CG-38483-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 5.7 | 5.7 | 6.3 | 6.4 | 6.2 | 0.31091
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-6 | 200-PW-44021-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7703 | Re-check.This point has increased CR when compared to CR in 2013. To be rechecked | 2015-01-08 15:30 | 2015-01-08 16:30 |  |  | Administrator | 2015-09-06 00:36 | [32 empty] | 5.75 | CML-6 | CML: Reducing Tee | 3 | 2022-12-05 | 2022-11-10 | 2015-01-08 15:30 | 2.5 | 0.40442 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 9 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 1.4612 | 5.8 | 5.8 | 5.7 | 5.7 | 0.057735
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-2 | 100-PG-23071-01C03 CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 2400 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 8.25 | CML-2 | CML: type TBC | 6 | 2015-08-14 | 2015-04-19 | 2014-03-19 13:00 | 2.5 | 3.8435 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 7.9 | 6 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.1 | 8.6 | 7.9 | 8.4 | 0.31091
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45024-01C02 | CML-6 | 50-FG-45024-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 24275 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 11.75 | CML-6 | CML: Reducer | 3 | 2076-02-10 | 2066-08-14 | 2014-09-24 07:00 | 4.7 | 0 | A1: Outside Quadrant |  | 7.97 | 4.7 | 5.6494 | 11.4 | 12 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 11.4 | 11.6 | 11.9 | 12.1 | 0.31091
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-10 | 300-PG-20005-03C03-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22772 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.35 | CML-10 | CML: Pipe Length | 6 | 2079-09-01 | 2067-10-02 | 2015-04-29 07:00 | 4.9 | 0.14133 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 | 0.62504 | 14.5 | 14.7 | 14 | 14.2 | 0.31091
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-29 | 50-CG-38001-09C02 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 10944 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 9.15 | CML-29 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0 | A4: Left Quadrant |  | 5.74 |  |  | 8.8 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.8 | 9.5 | 9 | 9.3 | 8.8 | 0.31091
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-16 | 250-WC-40017-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2079 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 6.775 | CML-16 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7 | 6.9 | 6.8 | 6.4 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-5 | 150-WC-40003-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2982 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 6.675 | CML-5 | CML: Elbow | 3 | 2019-05-12 | 2018-11-23 | 2014-05-01 09:30 | 2.5 | 0.77498 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 6 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.8 | 6.4 | 6.9 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-5 | 150-WC-40003-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22261 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 6.675 | CML-5 | CML: Elbow | 3 | 2019-05-12 | 2018-11-23 | 2014-05-01 09:30 | 2.5 | 0.77498 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 6 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.8 | 6.4 | 6.9 | 0.22174
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-11 | 200-PL-20034-03C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21608 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.925 | CML-11 | CML: Pipe Length | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 8.8 | 12 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.19 |  | 8.8 | 8.9 | 8.9 | 9.1 | 0.12583
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-4 | 50-CG-38487-09C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23573 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | Check Corrosion Rate of 0.369mm/ yr |  | John Wilson | 2017-03-24 11:20 | [32 empty] | 8.35 | CML-4 | CML: Pipe Length | 3 | 2030-04-28 | 2025-12-07 | 2015-09-10 07:00 | 2.5 | 0.36882 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 7.9 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 0.53207 | 7.9 | 8.4 | 8.5 | 8.6 | 0.31091
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-3 | 50-CG-38487-09C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23572 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | Check Corrosion Rate of 0.369mm/ yr |  | John Wilson | 2017-03-24 11:19 | [32 empty] | 8.35 | CML-3 | CML: Pipe Length | 3 | 2030-04-28 | 2025-12-07 | 2015-09-10 07:00 | 2.5 | 0.36882 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 7.9 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 0.53207 | 7.9 | 8.5 | 8.4 | 8.6 | 0.31091
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-32 | 400-FH-43508-01C02 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6581 | Rope Access. No access to CML''s 33 - 55 due to Flare | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 8.85 | CML-32 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 8.4 | 6 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.1 | 8.9 | 8.4 | 9 | 0.31091
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-21 | 150-PG-20507-01C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 2865 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 12.25 | CML-21 | CML: type TBC | 6 | 2098-02-09 | 2085-10-05 | 2014-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.8 | 6 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.5 | 12.4 | 11.8 | 12.3 | 0.31091
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23744 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 14.75 | CML-4 | CML: Reducer | 3 | 2075-10-24 | 2059-08-12 | 2015-10-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 14.5 | 6 O'Clock | 100 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12 |  | 14.6 | 14.7 | 14.5 | 15.2 | 0.31091
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23049-25C02-P | CML-4 | 100-PG-23049-25C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2754 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 17.675 | CML-4 | CML: Pipe Length | 3 | 2090-08-11 | 2067-01-05 | 2014-03-13 09:00 | 9.4 | 0 | A3: Inside Quadrant |  | 14.12 | 9.4 | 11.76 | 17.4 | 6 O'Clock | 100 | 17.12 | 100-PG-23049-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 18.1 | 17.7 | 17.4 | 17.5 | 0.30957
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-9 | 250-PG-20036-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21367 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.625 | CML-9 | CML: Elbow | 6 | 2020-06-27 | 2020-02-01 | 2014-07-14 07:30 | 2.5 | 0.9565 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.2 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.9 | 8.6 | 8.2 | 8.8 | 0.30957
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-7 | 50-DH-56137-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21145 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.625 | CML-7 | CML: Elbow | 6 | 2016-01-09 | 2015-05-21 | 2014-07-16 07:30 | 2.5 | 4.5101 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 9.2 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.9 | 9.8 | 9.6 | 9.2 | 0.30957
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57003-01C02 | CML-3 | 80-DC-57003-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12505 |  | 2014-02-04 16:00 | 2014-02-04 17:00 | [36 empty] | 6.225 | CML-3 | CML: Elbow | 3 | 2062-11-29 | 2056-08-05 | 2014-02-04 16:00 | 0.54 | 0 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.9 | 6 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.36 |  | 6.1 | 6.4 | 5.9 | 6.5 | 0.27538
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-3 | 80-PW-20024-01C03-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23047 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 7.95 | CML-3 | CML: Elbow | 6 | 2018-04-08 | 2017-07-12 | 2015-05-06 07:00 | 2.5 | 1.7776 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 7.7 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8 | 8.3 | 7.8 | 7.7 | 0.26458
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-28 | 50-DH-56137-01C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 21648 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.025 | CML-28 | CML: Pipe Length | 6 | 2031-12-02 | 2028-08-04 | 2014-09-27 07:00 | 4.9 | 0.50601 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14.3 | 14 | 13.6 | 14.2 | 0.30957
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45044-03C02 | CML-1 | 50-FG-45044-03C02 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24398 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.775 | CML-1 | CML: Elbow | 3 | 2022-03-31 | 2022-03-09 | 2016-06-08 07:00 | 2.5 | 0.34406 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45044-03C02-E | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.6 | 5.2 | 4.8 | 0.30957
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-12 | 50-PW-44013-01X01 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10326 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.75 | CML-12 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2013-11-10 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.7 | 5.7 | 5.8 | 0.057735
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-12 | 100-PW-20021-01C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22830 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.95 | CML-12 | CML: Pipe Length | 3 | 2044-01-02 | 2045-01-05 | 2015-04-30 07:00 | 2.5 | 0.11499 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.36318 | 6 | 5.9 | 5.8 | 6.1 | 0.1291
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-3 | 200-PG-23008-15S01-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3469 | Rope Access | 2014-05-13 10:30 | 2014-05-13 12:00 | [36 empty] | 5.525 | CML-3 | CML: type TBC | 3 | 2020-09-08 | 2021-07-14 | 2014-05-13 10:30 | 2.5 | 0.4109 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-DH-56012-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.5 | 5.1 | 5.8 | 0.30957
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-7 | 200-PW-44019-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23035 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 6.975 | CML-7 | CML: Elbow | 3 | 2026-11-30 | 2026-10-25 | 2015-05-06 07:00 | 2.5 | 0.28504 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 1.4787 | 7.8 | 7.2 | 5.8 | 7.1 | 0.84212
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-13 | 200-PL-20008-01C02-H CML-13 | yes | FPSO 2015 | Pipe Wall Thickness | 8810 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 7.2 | CML-13 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.4 | 7.5 | 7 | 6.9 | 0.29439
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-4 | 50-PW-44013-01X01 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10318 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 6.7333 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2013-11-10 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  |  | 7.2 | 5.8 | 7.2 | 0.80829
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-12 | 50-DH-56070-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 3228 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.225 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 6.4 | 5.8 | 6.5 | 0.30957
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-18 | 150-FH-43026-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23517 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 7.275 | CML-18 | CML: Fitting | 3 | 2132-07-22 | 2111-02-02 | 2015-07-28 07:00 | 1.03 | 0.051 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 | 0 | 7.1 | 7.7 | 7 | 7.3 | 0.30957
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-9 | 50-FH-43016-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12608 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.375 | CML-9 | CML: Pipe Length | 3 | 2017-11-21 | 2018-05-15 | 2014-01-23 13:00 | 2.5 | 0.67895 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.2 | 5.8 | 5.1 | 0.30957
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-10 | 250-PW-44004-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22754 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 5.9 | CML-10 | CML: Reducing Tee | 3 | 2026-10-12 | 2026-09-06 | 2015-04-29 07:00 | 2.5 | 0.2879 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.58353 | 5.8 | 6 | 5.8 | 6 | 0.11547
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-9 | 200-PL-20020-01C02-P CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 21313 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 9.2 | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 6 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 10 | 10.9 | 7.7 | 8.2 | 1.5033
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-11 | 50-CG-38454-01C02-H CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 23675 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 6.925 | CML-11 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.9 | 7.1 | 6.5 | 7.2 | 0.30957
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56052-01C02 | CML-1 | 50-DH-56052-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3176 | Rope Access | 2014-05-07 13:00 | 2014-05-07 14:00 | [36 empty] | 6.925 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-DH-56052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.9 | 6.5 | 7.1 | 7.2 | 0.30957
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-1 | 50-DH-56056-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20128 | Rope Access | 2014-05-07 13:00 | 2014-05-07 14:00 | [36 empty] | 6.925 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | -4505.1429 | 6.9 | 6.5 | 7.1 | 7.2 | 0.30957
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56141-01C02 | CML-28 | 50-DH-56141-01C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 21166 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 17.875 | CML-28 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 17.6 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.7 |  | 18.3 | 17.9 | 17.7 | 17.6 | 0.30957
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-8 | 50-CH-98806-1CG CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10890 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.825 | CML-8 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 0.23548 | A3: Inside Quadrant |  | 2.54 |  |  | 5.4 | 6 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.6 | 5.6 | 5.4 | 5.7 | 0.53151
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-7 | 50-CH-98806-1CG CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10889 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5 | CML-7 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 3.0949 | A4: Left Quadrant |  | 2.54 |  |  | 3.7 | 9 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 5.3 | 5.7 | 5.3 | 3.7 | 0.88694
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-3 | 50-DH-56137-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5481 | Rope Access | 2014-05-28 11:30 | 2014-05-28 14:00 | [36 empty] | 17.625 | CML-3 | CML: Straight | 3 | 2066-05-13 |  | 2014-05-28 11:30 |  | 0.28273 | A1: Outside Quadrant |  |  | 2.5 |  | 17.2 | 12 O'Clock | 300 | 17.48 | 300-WC-40513-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.7 |  | 17.2 | 17.6 | 17.8 | 17.9 | 0.30957
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-12 | 50-CG-38500-01C02 CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 23299 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.525 | CML-12 | CML: Elbow | 3 | 2016-01-08 | 2016-04-19 | 2015-07-04 09:30 | 2.5 | 1.1666 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.1 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 | 0.64051 | 3.5 | 3.7 | 3.1 | 3.8 | 0.30957
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-7 | 200-PW-44021-01X01 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10712 | Deck Level. Line is FFS. High CR. Line rechecked (refer to Jan. 15 values) | 2013-11-10 | 2013-11-10 |  |  | Administrator | 2015-09-13 11:06 | [32 empty] | 6.725 | CML-7 | CML: Elbow | 3 | 2016-07-09 | 2016-06-30 | 2013-11-10 | 2.5 | 1.2392 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.7 | 6.8 | 7.6 | 0.73655
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56556-01C02 | CML-4 | 50-DH-56556-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21130 | Reviewed on 20/11/14. FFS. Recheck in Oct. 18. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-20 17:40 | [32 empty] | 5.175 | CML-4 | CML: Elbow | 3 | 2019-11-04 | 2020-07-13 | 2014-10-08 07:00 | 2.5 | 0.4726 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-DH-56556-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5 | 5.6 | 4.9 | 0.30957
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45048-03C02 | CML-4 | 50-FG-45048-03C02 CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 2279 |  | 2014-03-16 14:00 | 2014-03-16 14:30 | [36 empty] | 5.325 | CML-4 | CML: type TBC | 3 |  |  | 2014-03-16 14:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 4.9 | 3 O'Clock | 50 |  | 50-PG-45048-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 4.9 | 5.3 | 5.5 | 0.30957
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-8 | 50-CG-38458-01C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23736 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.325 | CML-8 | CML: Reducing Tee | 3 | 2024-11-16 | 2026-02-08 | 2015-10-30 07:00 | 2.5 | 0.26507 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 5.6 | 4.9 | 5.5 | 0.30957
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-1 | 25-FG-45455-01C02-E CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24346 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.325 | CML-1 | CML: Reducer | 3 | 2039-03-19 | 2039-01-09 | 2016-06-06 07:00 | 2.5 | 0.14914 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 50 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.6 | 6.5 | 6.3 | 0.30957
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-16 | 200-PL-20020-01C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21320 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 8.45 | CML-16 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 6 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9.6 | 8.7 | 7.7 | 7.8 | 0.88882
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-16 | 50-PL-23020-01C03 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10130 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 7.675 | CML-16 | CML: type TBC | 6 | 2015-06-16 | 2015-06-01 | 2013-11-08 | 2.5 | 3.0569 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.4 | 3 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.5 | 7.4 | 7.7 | 8.1 | 0.30957
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-7 | 50-PL-23040-03C03 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10192 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 7.925 | CML-7 | CML: type TBC | 6 | 2015-08-15 | 2015-07-30 | 2013-11-08 | 2.5 | 2.8287 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.5 | 12 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8.1 | 7.9 | 8.2 | 0.30957
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-2 | 50-CG-38470-01C02-P CML-2 | Yes | FPSO 2015 | Pipe Wall Thickness | 23608 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 7.925 | CML-2 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 9 O'Clock | 80 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.2 | 8.1 | 7.9 | 7.5 | 0.30957
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-26 | 250-PW-44006-01X01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 8018 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.3 | CML-26 | CML: Pipe Length | 3 | 2024-11-18 | 2024-10-18 | 2015-01-20 08:30 | 2.5 | 0.3355 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0 | 7.3 | 5.8 | 5.9 | 6.2 | 0.68799
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-6 | 250-PW-20022-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2049 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 12.05 | CML-6 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 10.8 | 12 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 12.3 | 12.7 | 12.4 | 0.85049
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-6 | 50-CH-98806-1CG CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10888 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.5333 | CML-6 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 0.06728 | A1: Outside Quadrant |  | 2.54 |  |  | 5.5 | 3 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 5.5 | 5.5 |  | 5.6 | 0.057735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5578 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 6.3 | CML-1 | CML: Fitting | 3 | 2020-10-06 | 2020-09-16 | 2014-06-19 10:30 | 2.5 | 0.52355 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 7.1 | 5.8 | 6 | 6.3 | 0.57155
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20053-01C03-P | CML-1 | 80-PG-20053-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21508 | Protective mesh removed | 2014-06-29 08:00 | 2014-06-29 09:00 | [36 empty] | 11.425 | CML-1 | CML: Elbow | 6 | 2084-11-26 | 2074-01-04 | 2014-06-29 08:00 | 2.5 | 0.12064 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 11 | 3 O'Clock | 80 | 11.13 | 80-PG-20053-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11.7 | 11 | 11.4 | 11.6 | 0.30957
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-7 | 0200-DH-56L9003-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5092 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.425 | CML-7 | CML: type TBC | 3 | 2029-01-25 | 2026-04-22 | 2015-03-06 07:00 | 2.5 | 0.38845 | A2: Right Quadrant |  | 5.74 | 2.5 | 3.5737 | 7.9 | 3 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.4 | 7.9 | 8.6 | 8.8 | 0.38622
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-1 | 250-PG-23005-06C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10047 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 16.975 | CML-1 | CML: Pipe Length | 6 | 2016-02-04 | 2015-08-03 | 2013-11-06 | 8.6 | 3.6038 | A2: Right Quadrant |  | 12.26 | 8.6 | 10.43 | 16.7 | 3 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 17.4 | 16.7 | 17 | 16.8 | 0.30957
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40049-01C02 | CML-1 | 50-WC-40049-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1230 |  | 2014-03-22 08:30 | 2014-03-22 09:00 | [36 empty] | 6.625 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 08:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-WC-40049-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.7 | 6.4 | 6.7 | 0.15
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-2 | 50-PL-23020-01C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10116 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 14.0667 | CML-2 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 13.8 | 9 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 14 |  | 14.4 | 13.8 | 0.30551
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-2 | 80-CG-38459-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5881 |  | 2014-06-25 14:00 | 2014-06-25 15:00 | [36 empty] | 15.0667 | CML-2 | CML: Equal Tee | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 14:00 | 3.3 | 0 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 14.8 | 12 O'Clock | 200 | 12.7 | 200-PG-20301-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 14.8 | 15.4 |  | 15 | 0.30551
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-5 | 200-PG-23008-15S01-A CML-5 | Yes | FPSO 2013 | Pipe Wall Thickness | 10091 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 20.55 | CML-5 | CML: Elbow | 1 | 2014-11-28 | 2014-03-31 | 2013-11-07 | 14.06 | 5.9915 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 21 | 20.4 | 0.3
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-25 | 50-DH-56137-01C02 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 23453 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 17.85 | CML-25 | CML: Cap End | 3 | 2023-06-16 | 2019-03-26 | 2015-07-23 07:00 | 2.5 | 1.885 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.4 | 6 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.9 | -2.7602 | 18 | 18 | 17.4 | 18 | 0.3
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PL-57403-01C03 |  | 50-PL-57403-01C03 |  | FPSO 2015 | Pipe Wall Thickness | 8373 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | Check Corrosion Rate of 0.505mm/ yr | [35 empty] | 9.325 | 50-PL-57403-01C03 | Piping | 6 | 2025-10-07 |  | 2015-01-29 07:30 |  | 0.50485 | A1: Outside Quadrant |  |  | 2.5 |  | 7.9 | 12 O'Clock | 50 | 8.74 | Pipework | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 9.7 | 10.6 | 9.1 | 1.1325
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-5 | 50-CH-98806-1CG CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10887 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.3 | CML-5 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 0 | A2: Right Quadrant |  | 2.54 |  |  | 7.4 | 3 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 8.6 | 7.4 | 8.8 | 8.4 | 0.62183
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-4 | 50-CH-98806-1CG CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10886 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 6.275 | CML-4 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 0 | A4: Left Quadrant |  | 2.54 |  |  | 5.6 | 9 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.8 | 6.6 | 6.1 | 5.6 | 0.53774
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-3 | 50-CH-98806-1CG CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10885 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 7.4 | CML-3 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 0 | A1: Outside Quadrant |  | 2.54 |  |  | 6.7 | 12 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.7 | 7.7 | 7.3 | 7.9 | 0.52915
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-3 | 150-PG-20009-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2697 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 10.55 | CML-3 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-12 09:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 10.2 | 3 O'Clock | 100 | 8.56 | 100-PG-20009-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.8 | 10.2 | 10.4 | 10.8 | 0.3
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-3 | 150-PG-20009-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 668 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 10.55 | CML-3 | CML: Pipe Length | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 09:00 | 2.03 | 0 | A2: Right Quadrant |  | 1.11 | 2.03 | 1.57 | 10.2 | 3 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.17 | 0 | 10.8 | 10.2 | 10.4 | 10.8 | 0.3
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-3 | 150-PG-20009-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 386 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 10.55 | CML-3 | CML: Pipe Length | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 | 2.03 | 0 | A2: Right Quadrant |  | 1.11 | 2.03 | 1.57 | 10.2 | 3 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.17 |  | 10.8 | 10.2 | 10.4 | 10.8 | 0.3
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-16 | 300-PG-20005-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 6172 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.45 | CML-16 | CML: Reducing Tee | 6 | 2161-12-15 | 2135-03-31 | 2014-07-11 07:30 | 4.9 | 0.06304 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.2 | 14.8 | 14.2 | 14.6 | 0.3
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-10 | 50-FG-45018-03C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10509 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.05 | CML-10 | CML: type TBC | 3 | 2015-04-18 | 2015-04-13 | 2013-11-15 | 2.5 | 1.6174 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.4 | 4.8 | 5.2 | 0.3
PG06 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PG-23008-15S01-A | CML-1 | 200-PG-23008-15S01-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21924 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 5.45 | CML-1 | CML: Fitting | 3 | 2023-10-24 | 2025-01-08 | 2014-10-09 07:00 | 2.5 | 0.28741 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.7 | 5.1 | 5.3 | 0.3
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-8 | 80-DC-57002-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20237 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 8.075 | CML-8 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.9 | 9 O'Clock | 20 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.2 | 8 | 8.2 | 7.9 | 0.15
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-9 | 80-DC-57002-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20238 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 8.15 | CML-9 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.9 | 6 O'Clock | 20 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.5 | 8.2 | 7.9 | 8 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-9 | 50-FH-43011-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7959 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 5.85 | CML-9 | CML: Elbow | 3 | 2017-03-25 | 2016-09-22 | 2015-01-18 08:00 | 2.5 | 1.42 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 5.6 | 6 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.2 | 5.6 | 6 | 0.3
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23409-01C03 | CML-5 | 100-PG-23409-01C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20770 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.025 | CML-5 | CML: Elbow | 6 | 2017-02-07 | 2016-07-25 | 2014-10-02 07:00 | 2.5 | 2.2948 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 7.9 | 3 O'Clock | 150 | 10.97 | 100-PG-23409-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9.4 | 7.9 | 9.4 | 9.4 | 0.75
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45503-01C02 | CML-5 | 50-FG-45503-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 7740 | Line is FFS despite the High CR on CML-1 to 6. Current RBI frequency is 48m. Action: Inspect in 24m. RBI to be updated. | 2015-01-10 08:00 | 2015-01-10 10:00 |  |  | Administrator | 2015-09-21 14:30 | [32 empty] | 5.05 | CML-5 | CML: Elbow | 3 | 2018-08-16 | 2019-03-08 | 2015-01-10 08:00 | 2.5 | 0.58317 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45503-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.2 | 5.2 | 5.2 | 4.6 | 0.3
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-2 | 50-CH-98806-1CG CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10884 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 7.2 | CML-2 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 0 | A3: Inside Quadrant |  | 2.54 |  |  | 7 | 6 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 7.3 | 7.4 | 7 | 7.1 | 0.18257
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-16 | 50-FG-45019-03C02 CML-16 | yes | FPSO 2013 | Pipe Wall Thickness | 10498 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.05 | CML-16 | CML: type TBC | 3 | 2014-11-23 | 2014-11-19 | 2013-11-15 | 2.5 | 2.0545 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.2 | 5.2 | 5.2 | 0.3
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-5 | 250-PG-23003-06C02-PA CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7684 | Re-check.Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:57 | [32 empty] | 4.95 | CML-5 | CML: Elbow | 3 | 2018-08-10 | 2019-03-02 | 2015-01-08 13:00 | 2.5 | 0.58495 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0.5245 | 5.2 | 4.8 | 5.2 | 4.6 | 0.3
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21887 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 6.3 | CML-1 | CML: Fitting | 3 | 2020-10-06 | 2020-09-16 | 2014-06-19 10:30 | 2.5 | 0.52355 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 7.1 | 5.8 | 6 | 6.3 | 0.57155
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-9 | 250-PW-44004-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22753 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 5.875 | CML-9 | CML: Reducing Tee | 3 | 2026-10-12 | 2026-09-06 | 2015-04-29 07:00 | 2.5 | 0.2879 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.93365 | 5.9 | 5.8 | 5.8 | 6 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-2 | 250-PW-44007-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1959 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 6.55 | CML-2 | CML: Elbow | 3 | 2019-02-19 | 2019-02-04 | 2014-03-26 11:30 | 2.5 | 0.67258 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 7 | 6.9 | 6.5 | 0.54467
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-3 | 50-FG-45020-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2602 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.55 | CML-3 | CML: type TBC | 3 | 2024-11-02 | 2024-10-05 | 2014-04-26 09:30 | 2.5 | 0.26594 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | -1.1378 | 5.3 | 5.9 | 5.7 | 5.3 | 0.3
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20016-01C02-P | CML-4 | 200-PL-20016-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21235 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.8 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 9 O'Clock | 200 | 6.35 | 200-PL-20016-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9.7 | 9 | 8.8 | 7.7 | 0.82865
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-6 | 150-WC-40003-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2983 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 6.45 | CML-6 | CML: Elbow | 3 | 2019-05-12 | 2018-11-23 | 2014-05-01 09:30 | 2.5 | 0.77498 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 9 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 6.6 | 6.4 | 0.1
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-6 | 150-WC-40003-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22262 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 6.45 | CML-6 | CML: Elbow | 3 | 2019-05-12 | 2018-11-23 | 2014-05-01 09:30 | 2.5 | 0.77498 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 9 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 6.6 | 6.4 | 0.1
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-16 | 300-FL-43070-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12709 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.55 | CML-16 | CML: type TBC | 3 | 2023-10-05 | 2023-09-08 | 2014-02-01 09:00 | 2.5 | 0.37188 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.7 | 6.1 | 6.7 | 6.7 | 0.3
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43121-01C02 | CML-5 | 150-FH-43121-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1768 | Rope access | 2014-04-27 09:30 | 2014-04-27 11:00 | [36 empty] | 6.55 | CML-5 | CML: Elbow | 3 | 2018-07-25 | 2018-02-28 | 2014-04-27 09:30 | 2.5 | 0.89484 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.3 | 3 O'Clock | 150 | 7.11 | 150-FH-43121-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.3 | 6.7 | 6.9 | 0.3
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-3 | 150-FH-43027-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10565 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 6.75 | CML-3 | CML: type TBC | 3 | 2016-05-26 | 2016-03-02 | 2013-11-16 | 2.5 | 1.5426 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 3 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7 | 6.4 | 7 | 6.6 | 0.3
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-1 | 150-FH-43026-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12641 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 6.75 | CML-1 | CML: Pipe Length | 3 | 2018-12-06 | 2017-12-08 | 2014-01-22 07:00 | 1.03 | 1.1014 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 |  | 6.6 | 7 | 6.4 | 7 | 0.3
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20027-03C03-P | CML-3 | 80-PG-20027-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21326 | Protective mesh removed | 2014-06-27 09:30 | 2014-06-27 10:30 | [36 empty] | 11.85 | CML-3 | CML: Fitting | 6 | 2099-09-17 | 2086-07-24 | 2014-06-27 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.5 | 6 O'Clock | 80 | 11.13 | 80-PG-20027-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 12.1 | 11.7 | 11.5 | 12.1 | 0.3
VA01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-VA-23054-01C02 | CML-19 | 25-VA-23054-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 22010 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 13.25 | CML-19 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 12.9 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 13.5 | 13.5 | 12.9 | 13.1 | 0.3
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-15 | 50-CG-38001-09C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 10929 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.65 | CML-15 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0.56154 | A1: Outside Quadrant |  | 5.74 |  |  | 8.4 | 3 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.4 | 8.4 | 8.4 | 8.8 | 9 | 0.3
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-40 | 50-DH-56070-01C02 CML-40 |  | FPSO 2014 | Pipe Wall Thickness | 3256 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.35 | CML-40 | CML: type TBC | 3 | 2017-11-12 | 2018-05-06 | 2014-05-09 07:00 | 2.5 | 0.68246 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.5 | 5.5 | 5.5 | 0.3
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7674 | New Isometric drawing | 2015-01-08 09:30 | 2015-01-08 12:00 |  |  | Administrator | 2015-09-08 12:40 | [32 empty] | 6.15 | CML-5 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.6 | 6 | 6 | 6 | 0.3
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20016-01C02-P | CML-3 | 200-PL-20016-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21234 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.5 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 9 O'Clock | 200 | 6.35 | 200-PL-20016-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.9 | 9.2 | 9.2 | 7.7 | 0.8124
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-19 | 50-FG-45301-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 5805 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 7.85 | CML-19 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 3 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8 | 7.4 | 8 | 8 | 0.3
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-8 | 50-PL-23020-01C03 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10122 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.05 | CML-8 | CML: type TBC | 6 | 2015-10-24 | 2015-10-07 | 2013-11-08 | 2.5 | 2.6006 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.6 | 3 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.2 | 7.6 | 8.2 | 8.2 | 0.3
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-14 | 50-FL-43454-01C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1870 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.25 | CML-14 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 9 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.7 | 9.1 | 9.1 | 9.1 | 0.3
FL02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FL-43454-01C02-P | CML-19 | 50-FL-43454-01C02-P CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10459 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.05 | CML-19 | CML: type TBC | 6 | 2016-06-26 | 2016-02-21 | 2013-11-13 | 0.99 | 2.5218 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.6 | 12 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.61 |  | 7.6 | 8.2 | 8.2 | 8.2 | 0.3
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23044-03C03 | CML-2 | 50-PG-23044-03C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13104 |  | 2014-02-07 07:00 | 2014-02-07 08:00 | [36 empty] | 8.75 | CML-2 | CML: type TBC | 6 | 2051-08-07 | 2047-04-02 | 2014-02-07 07:00 | 0.97 | 0.20335 | A2: Right Quadrant |  | 2.74 | 0.97 | 1.855 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PG-23044-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.63 |  | 9.2 | 8.6 | 8.6 | 8.6 | 0.3
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-9 | 50-CG-38488-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20827 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 11.95 | CML-9 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 11.5 | 12 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 11.5 | 12.1 | 12.1 | 12.1 | 0.3
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-7 | 50-DN-56101-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 847 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 8.0667 | CML-7 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-02 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 3 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8 | 7.9 | 8.3 |  | 0.20817
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98806-1CG | CML-1 | 50-CH-98806-1CG CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10883 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 6.525 | CML-1 | CML: type TBC | 3 |  |  | 2014-01-04 |  | 0 | A1: Outside Quadrant |  | 2.54 |  |  | 6 | 12 O'Clock | 50 | 5.54 | 50-CH-98806-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6 | 6.8 | 6.3 | 7 | 0.45735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-12 | 50-PW-44014-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2014 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 6.175 | CML-12 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-27 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 5.8 | 5.8 | 6.9 | 0.51881
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38463-01C02 | CML-5 | 50-CG-38463-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3116 | Rope Access | 2014-05-04 08:00 | 2014-05-04 09:00 | [36 empty] | 5.05 | CML-5 | CML: Elbow | 3 | 2016-10-03 | 2017-02-11 | 2014-05-04 08:00 | 2.5 | 0.90889 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-CG-38463-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 5.3 | 4.7 | 5.3 | 0.3
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-12 | 50-FG-45021-03C02 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10540 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 4.95 | CML-12 | CML: type TBC | 3 | 2015-01-30 | 2015-01-26 | 2013-11-16 | 2.5 | 1.825 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 5.3 | 4.7 | 4.7 | 0.3
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-4 | 50-FH-43137-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22678 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.05 | CML-4 | CML: Elbow | 3 | 2020-04-21 | 2021-01-16 | 2015-04-27 07:00 | 2.5 | 0.44097 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | -0.23858 | 4.9 | 5.3 | 4.7 | 5.3 | 0.3
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38472-01C02 | CML-6 | 50-CG-38472-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23661 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.95 | CML-6 | CML: Elbow | 3 | 2022-02-23 | 2023-01-31 | 2015-10-30 07:00 | 2.5 | 0.3479 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38472-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 4.7 | 5.1 | 4.7 | 0.3
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-4 | 25-PW-44028-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10310 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.55 | CML-4 | CML: Reducer | 3 | 2014-11-25 | 2014-11-21 | 2013-11-10 | 2.5 | 2.5911 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 3 O'Clock | 50 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.8 | 5.8 | 0.3
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20013-01C02-P | CML-1 | 200-PL-20013-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21211 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.3 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 9 O'Clock | 200 | 6.35 | 200-PL-20013-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.5 | 8.7 | 8.3 | 7.7 | 0.43205
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-13 | 50-DC-57020-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2455 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 7.95 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 9 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8 | 8 | 7.9 | 0.057735
FG02 | Montara_Topside | Yes | Potable Water (53) | Pipework | 25-FG-45455-01C02-E | CML-17 | 25-FG-45455-01C02-E CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8156 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.35 | CML-17 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.2 | 6.6 | 6.6 | 0.3
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43306-01C02 | CML-1 | 80-FH-43306-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5760 | Rope access | 2014-06-23 09:30 | 2014-06-23 11:00 | [36 empty] | 5.05 | CML-1 | CML: Elbow | 3 | 2020-01-23 | 2019-03-19 | 2014-06-23 09:30 | 0.54 | 0.74433 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 4.7 | 12 O'Clock | 80 | 5.49 | 80-FH-43306-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.16 |  | 4.7 | 4.9 | 5.3 | 5.3 | 0.3
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-7 | 50-CG-38452-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20346 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.55 | CML-7 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 12 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.8 | 7.4 | 7.8 | 0.3
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-18 | 80-CG-38459-09C02-P CML-18 | Yes | FPSO 2014 | Pipe Wall Thickness | 23851 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 66.425 | CML-18 | CML: Elbow | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 20.9 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.6 |  | 20.9 | 20.3 | 20.9 | 20.9 | 0.3
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-10 | 250-PG-23004-06C03-A CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23377 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | Check Corrosion Rate of 0.309mm/ yr |  | John Wilson | 2017-03-23 15:11 | Loss within CA no further action required. | [31 empty] | 17.95 | CML-10 | CML: Elbow | 6 | 2044-11-04 | 2038-11-03 | 2015-07-21 07:00 | 8.55 | 0.30873 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 17.6 | 3 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.05 | 0.13137 | 18.2 | 17.6 | 17.8 | 18.2 | 0.3
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-8 | 80-CG-38459-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10958 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 17.45 | CML-8 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 17.1 | 12 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.88 |  | 17.1 | 17.7 | 17.7 | 17.3 | 0.3
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-16 | 50-DH-56137-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23444 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 17.85 | CML-16 | CML: Pipe Length | 3 | 2023-12-24 | 2019-07-14 | 2015-07-23 07:00 | 2.5 | 1.7917 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 17.6 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.1 | 0.36803 | 18.2 | 17.6 | 18 | 17.6 | 0.3
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40016-01C02 | CML-2 | 250-WC-40016-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20364 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-24 10:37 | [32 empty] | 6.5 | CML-2 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-10-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 6 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.5 | 6.4 | 6.5 | 0.08165
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-36 | 250-PW-44006-01X01 CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 1933 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.325 | CML-36 | CML: Pipe Length | 3 | 2019-02-18 | 2019-02-02 | 2014-03-26 07:00 | 2.5 | 0.673 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 5.8 | 7 | 6.3 | 0.49917
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-2 | 50-CG-38488-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20820 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 8.975 | CML-2 | CML: Fitting | 3 | 2189-07-31 | 2143-11-05 | 2014-07-18 11:00 | 2.5 | 0.0354 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.9 | 9.4 | 8.9 | 8.7 | 0.29861
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-22 | 300-PF-20001-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21160 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.125 | CML-22 | CML: Elbow | 6 | 2015-10-16 | 2015-03-17 | 2014-07-16 07:30 | 2.5 | 4.9549 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.7 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.4 | 9.2 | 9.2 | 8.7 | 0.29861
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-6 | 200-FH-43003-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12529 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 8.475 | CML-6 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 11:30 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 8.2 | 9 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.86 |  | 8.9 | 8.4 | 8.4 | 8.2 | 0.29861
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-22 | 80-PW-44001-01C02-P CML-22 | yes | FPSO 2015 | Pipe Wall Thickness | 23231 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 7.45 | CML-22 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 4.366 | 5.9 | 8.5 | 7.9 | 7.5 | 1.1121
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-1 | 100-FG-45001-09C02 CML-1 | Yes | FPSO 2015 | Pipe Wall Thickness | 23306 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 14.475 | CML-1 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A4: Left Quadrant |  | 8.13 | 4.7 | 6.415 | 14.1 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 | -1.0251 | 14.6 | 14.8 | 14.4 | 14.1 | 0.29861
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PG-20030-01C03-P | CML-4 | 50-PG-20030-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21672 | Protective mesh removed | 2014-06-26 09:30 | 2014-06-26 11:00 | [36 empty] | 12.525 | CML-4 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-06-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 12.2 | 6 O'Clock | 80 | 11.13 | 80-PG-20030-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 12.6 | 12.9 | 12.2 | 12.4 | 0.29861
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40014-01C02 | CML-6 | 50-WC-40014-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1553 | Rope Access | 2014-04-09 08:00 | 2014-04-09 09:00 | [36 empty] | 7.325 | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-WC-40014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 8.7 | 6.9 | 7.2 | 6.5 | 0.96047
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56084-01C02 | CML-8 | 100-DH-56084-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3350 | Rope Access | 2014-05-08 13:00 | 2014-05-08 14:00 | [36 empty] | 4.925 | CML-8 | CML: type TBC | 3 | 2015-09-25 | 2015-10-23 | 2014-05-08 13:00 | 2.5 | 1.5175 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.6 | 6 O'Clock | 100 | 6.02 | 100-DH-56084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.3 | 4.8 | 4.6 | 5 | 0.29861
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40014-01C02 | CML-5 | 50-WC-40014-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1552 | Rope Access | 2014-04-09 08:00 | 2014-04-09 09:00 | [36 empty] | 7.075 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-WC-40014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.8 | 6.5 | 6.5 | 7.5 | 0.67515
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-5 | 50-CG-38476-01C02-H CML-5 | Yes | FPSO 2015 | Pipe Wall Thickness | 23637 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.075 | CML-5 | CML: Elbow | 3 | 2022-02-16 | 2023-01-23 | 2015-10-28 07:00 | 2.5 | 0.34869 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.4 | 5 | 5.2 | 4.7 | 0.29861
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57024-01C02 | CML-4 | 50-DC-57024-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2876 | Rope Access | 2014-04-24 13:00 | 2014-04-24 14:00 | [36 empty] | 6.225 | CML-4 | CML: type TBC | 3 | 2065-02-10 | 2057-09-22 | 2014-04-24 13:00 | 0.37 | 0 | A4: Left Quadrant |  | 2.54 | 0.37 | 1.1087 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DC-57024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.43 |  | 6.4 | 6.4 | 6.3 | 5.8 | 0.28723
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57017-01C02 | CML-4 | 20-DC-57017-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2899 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 6.025 | CML-4 | CML: type TBC | 3 | 2067-05-31 | 2058-11-20 | 2014-04-25 08:00 | 0.16 | 0 | A3: Inside Quadrant |  | 2.56 | 0.16 | 1.0125 | 5.6 | 6 O'Clock | 20 | 5.56 | 20-DC-57017-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.44 |  | 6.4 | 6.3 | 5.6 | 5.8 | 0.38622
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40036-01C02 | CML-2 | 200-WC-40036-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7706 |  | 2015-01-09 07:00 | 2015-01-09 10:00 | [36 empty] | 6.925 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 9 O'Clock | 200 | 6.35 | 200-WC-40036-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.5 | 6.7 | 7 | 6.5 | 0.43493
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-5 | 100-WC-40035-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1738 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 6.775 | CML-5 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.5 | 6 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.5 | 6.5 | 7.4 | 0.4272
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1755 | Rope access | 2014-04-27 07:00 | 2014-04-27 08:00 | [36 empty] | 5.075 | CML-6 | CML: Elbow | 3 | 2016-09-08 | 2017-01-14 | 2014-04-27 07:00 | 2.5 | 0.92827 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 5.4 | 4.7 | 5 | 0.29861
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-19 | 25-FG-45455-01C02-E CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 12638 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.075 | CML-19 | CML: type TBC | 3 | 2015-10-04 | 2016-01-04 | 2014-01-23 10:00 | 2.5 | 1.2969 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 5.4 | 4.7 | 5.2 | 0.29861
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-26 | 250-PW-44006-01X01 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 1923 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.15 | CML-26 | CML: Pipe Length | 3 | 2019-02-18 | 2019-02-02 | 2014-03-26 07:00 | 2.5 | 0.673 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6.8 | 6.2 | 0.47258
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38463-01C02 | CML-3 | 50-CG-38463-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3114 | Rope Access | 2014-05-04 08:00 | 2014-05-04 09:00 | [36 empty] | 5.125 | CML-3 | CML: Elbow | 3 | 2017-03-17 | 2017-08-13 | 2014-05-04 08:00 | 2.5 | 0.80069 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-CG-38463-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 5.5 | 4.8 | 5.2 | 0.29861
PG06 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 200-PG-23008-15S01-A | CML-3 | 200-PG-23008-15S01-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20837 | Reviewed on 20/11/14. FFS. This line has not been RBI assessed. CML to be rechecked Oct. 18 based on other line on this circuit which are a 48m interval | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 16:18 | [32 empty] | 5.425 | CML-3 | CML: Elbow | 3 | 2022-09-09 | 2023-09-08 | 2014-10-04 07:00 | 2.5 | 0.32756 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-CG-38464-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.5 | 5.1 | 5.3 | 5.8 | 0.29861
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38489-01C02-P | CML-4 | 50-CG-38489-01C02-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 20861 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 5.675 | CML-4 | CML: Fitting | 3 | 2030-05-08 | 2032-03-01 | 2014-10-02 07:00 | 2.5 | 0.1794 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-CG-38489-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6 | 5.6 | 5.3 | 5.8 | 0.29861
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-15 | 50-CH-98808-1CG CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 10878 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.35 | CML-15 | CML: type TBC | 3 | 2014-08-03 | 2014-07-31 | 2014-01-04 | 2.5 | 2.5903 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4 | 3 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 6.9 | 4 | 5.5 | 5 | 1.2069
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-11 | 50-CH-98808-1CG CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10874 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.55 | CML-11 | CML: type TBC | 3 | 2015-07-26 | 2015-07-21 | 2014-01-04 | 2.5 | 1.4129 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.7 | 5.9 | 4.7 | 5.9 | 0.57446
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-8 | 50-CH-98808-1CG CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10871 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.575 | CML-8 | CML: type TBC | 3 | 2016-03-27 | 2016-03-20 | 2014-01-04 | 2.5 | 1.0765 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5.9 | 4.9 | 6.3 | 0.63966
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-3 | 250-PW-44006-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7995 | Leak | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.3 | CML-3 | CML: Elbow | 3 | 2024-11-18 | 2024-10-18 | 2015-01-20 08:30 | 2.5 | 0.3355 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.85149 | 6.9 | 6.3 | 5.8 | 6.2 | 0.45461
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 | yes | FPSO 2016 | Pipe Wall Thickness | 24321 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.075 | CML-3 | CML: Fitting | 3 | 2022-08-27 | 2021-03-24 | 2016-06-01 07:00 | 2.77 | 0.46945 | A1: Outside Quadrant |  | 4.11 | 2.77 | 3.44 | 5.7 | 12 O'Clock | 150 | 7.11 | 150-FG-45005-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.93 |  | 5.7 | 6.4 | 6 | 6.2 | 0.29861
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-4 | 200-PW-44019-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21895 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 6.325 | CML-4 | CML: Fitting | 3 | 2020-10-05 | 2020-09-16 | 2014-06-19 09:30 | 2.5 | 0.52361 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 6.2 | 6.8 | 5.8 | 0.4272
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-50 | 50-DH-56070-01C02 CML-50 |  | FPSO 2014 | Pipe Wall Thickness | 3266 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.125 | CML-50 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.2 | 6.4 | 5.7 | 6.2 | 0.29861
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-1 | 50-CH-98808-1CG CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10864 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.625 | CML-1 | CML: type TBC | 3 | 2016-03-27 | 2016-03-20 | 2014-01-04 | 2.5 | 1.0765 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.8 | 5.8 | 6 | 0.49244
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67300-01E01 | CML-9 | 25-GN-67300-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22493 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 8.175 | CML-9 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-04-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 3 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8 | 8.2 | 8.2 | 0.12583
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20280 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 6.325 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-DC-57030-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.7 | 6.4 | 6.2 | 0.29861
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-12 | 50-CH-98808-1CG CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10875 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.2 | CML-12 | CML: type TBC | 3 | 2016-10-04 | 2016-09-26 | 2014-01-04 | 2.5 | 0.90829 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 12 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.1 | 5.5 | 0.21602
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-12 | 0200-DH-56L9003-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5097 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.5 | CML-12 | CML: type TBC | 3 | 2031-03-28 | 2028-02-07 | 2015-03-06 07:00 | 2.5 | 0.34221 | A4: Left Quadrant |  | 5.74 | 2.5 | 3.5737 | 8 | 9 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.8 | 8.7 | 8.5 | 8 | 0.3559
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-14 | 50-FG-45023-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1162 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.425 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.5 | 6.1 | 6.3 | 6.8 | 0.29861
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-17 | 150-FL-43453-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2261 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.575 | CML-17 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.2 | 6 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 6.5 | 6.2 | 6.9 | 0.29861
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-15 | 50-FG-45301-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 5801 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.575 | CML-15 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 7 | 6.3 | 6.5 | 0.29861
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21252 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.625 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.9 | 7.2 | 7.7 | 7.7 | 0.29861
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20059-01C02 | CML-4 | 200-PL-20059-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2869 | Rope Access | 2014-03-25 11:00 | 2014-03-25 12:00 | [36 empty] | 8 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-25 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 12 O'Clock | 200 | 6.35 | 200-PL-20059-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 8.1 | 8.3 | 7.9 | 0.2582
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45009-01C02-E | CML-1 | 150-FG-45009-01C02-E CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24295 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.625 | CML-1 | CML: Equal Tee | 3 | 2074-03-18 | 2063-04-04 | 2016-05-27 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.3 | 12 O'Clock | 150 | 7.11 | 150-FG-45009-01C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.27 |  | 7.3 | 7.7 | 8 | 7.5 | 0.29861
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 | yes | FPSO 2013 | Pipe Wall Thickness | 10671 | Deck Level.High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.2738 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 16:08 | [32 empty] | 4.925 | CML-4 | CML: Pipe Length | 3 | 2014-10-08 | 2014-11-30 | 2013-11-17 | 2.5 | 2.2462 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5 | 5 | 5.2 | 0.29861
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-4 | 200-PW-44019-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5570 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 6.325 | CML-4 | CML: Fitting | 3 | 2020-10-05 | 2020-09-16 | 2014-06-19 09:30 | 2.5 | 0.52361 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 6.2 | 6.8 | 5.8 | 0.4272
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-10 | 50-CH-98808-1CG CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10873 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.4 | CML-10 | CML: type TBC | 3 | 2016-10-04 | 2016-09-26 | 2014-01-04 | 2.5 | 0.90829 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5.7 | 5.1 | 5 | 0.40825
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-24 | 50-FG-45021-03C02 CML-24 |  | FPSO 2013 | Pipe Wall Thickness | 10552 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.125 | CML-24 | CML: type TBC | 3 | 2015-01-30 | 2015-01-26 | 2013-11-16 | 2.5 | 1.825 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.2 | 5.2 | 5.4 | 0.29861
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43142-01C02 | CML-4 | 100-FH-43142-01C02 CML-4 | Yes | FPSO 2013 | Pipe Wall Thickness | 10522 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.975 | CML-4 | CML: type TBC | 3 | 2014-08-20 | 2014-09-04 | 2013-11-15 | 2.5 | 2.885 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.7 | 12 O'Clock | 100 | 6.02 | 100-FH-43142-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 4.9 | 4.9 | 5.4 | 0.29861
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44036-01C02-P | CML-6 | 80-PW-44036-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22964 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 6.45 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 3 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 0.35437 | 6.1 | 5.9 | 7.3 | 6.5 | 0.61914
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45036-03C02 | CML-5 | 50-FG-45036-03C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2577 |  | 2014-04-26 13:00 | 2014-04-26 14:00 | [36 empty] | 5.275 | CML-5 | CML: type TBC | 3 | 2018-06-30 | 2018-06-17 | 2014-04-26 13:00 | 2.5 | 0.5981 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45036-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.7 | 5.2 | 5.2 | 0.29861
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5581 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 6.075 | CML-4 | CML: Fitting | 3 | 2020-10-06 | 2020-09-16 | 2014-06-19 10:30 | 2.5 | 0.52355 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0 | 6.1 | 6.6 | 5.8 | 5.8 | 0.37749
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-18 | 100-DH-56082-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 3386 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.075 | CML-18 | CML: type TBC | 3 | 2028-06-16 | 2028-12-14 | 2014-05-10 09:30 | 2.5 | 0.23384 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 3 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.8 | 6 | 6.5 | 0.29861
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-2 | 50-CH-98808-1CG CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10865 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.2 | CML-2 | CML: type TBC | 3 | 2016-10-04 | 2016-09-26 | 2014-01-04 | 2.5 | 0.90829 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5.4 | 5.1 | 5 | 0.18257
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-9 | 200-FH-43038-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12690 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 6.425 | CML-9 | CML: type TBC | 3 | 2020-12-15 | 2020-11-25 | 2014-02-06 09:00 | 2.5 | 0.51023 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6.5 | 6 | 6.7 | 0.29861
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-13 | 50-CH-98808-1CG CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10876 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 5.9 | CML-13 | CML: type TBC | 3 | 2026-04-26 | 2026-03-26 | 2014-01-04 | 2.5 | 0.23548 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.4 | 5.5 | 6.7 | 0.59442
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-15 | 50-FG-45302-01C02 CML-15 | Yes | FPSO 2014 | Pipe Wall Thickness | 5783 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 6.625 | CML-15 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 25 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.7 | 6.7 | 6.9 | 0.29861
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-6 | 25-VA-23054-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1475 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 4.975 | CML-6 | CML: type TBC | 3 | 2016-05-11 | 2016-09-03 | 2014-04-29 10:00 | 2.5 | 1.0321 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 5.1 | 4.6 | 5.3 | 0.29861
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-10 | 50-PL-23514-01C03 CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 8643 | This CML is on a straight piping section. It appears that CML-10 together with CML-8 & 9 below are located in the same spool. This spool was confirmed to have being wrongly fabricated with Sched. Extra strong (NWT: 5.54 mm) instead of sched. 160 (NWT: 8.74). | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:22 | [32 empty] | 5.025 | CML-10 | CML: Pipe Length | 6 | 2016-01-13 | 2015-12-26 | 2015-02-10 11:30 | 2.5 | 2.3804 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 4.7 | 3 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 4.7 | 5.1 | 5.4 | 0.29861
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38477-01C02-P | CML-1 | 50-CG-38477-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20893 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.475 | CML-1 | CML: type TBC | 3 | 2017-07-20 | 2017-07-09 | 2014-10-04 07:00 | 2.5 | 0.93057 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.1 | 6 O'Clock | 25 | 6.35 | 25-CG-38477-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.4 | 5.1 | 5.8 | 0.29861
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21890 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 6.075 | CML-4 | CML: Fitting | 3 | 2020-10-06 | 2020-09-16 | 2014-06-19 10:30 | 2.5 | 0.52355 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 6.6 | 5.8 | 5.8 | 0.37749
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20948 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 7.475 | CML-3 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-05-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.1 | 6 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.8 | 7.6 | 7.1 | 7.4 | 0.29861
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38008-01C02 | CML-3 | 50-CG-38008-01C02 CML-3 | Yes | FPSO 2015 | Pipe Wall Thickness | 8431 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 8.075 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.7 | 9 O'Clock | 15 | 5.54 | 50-CG-38008-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.4 | 8.2 | 8 | 7.7 | 0.29861
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-26 | 150-PG-23506-25C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 2800 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.475 | CML-26 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.1 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.22 |  | 22.1 | 22.4 | 22.8 | 22.6 | 0.29861
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-14 | 50-CG-38500-01C02 CML-14 | High Priority | FPSO 2016 | Pipe Wall Thickness | 24499 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.475 | CML-14 | CML: Pipe Length | 3 | 2017-04-14 | 2017-09-12 | 2016-07-09 07:00 | 2.5 | 0.78516 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.1 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 | 0.59046 | 3.4 | 3.1 | 3.8 | 3.6 | 0.29861
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-5 | 50-CH-98808-1CG CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10868 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 7.35 | CML-5 | CML: type TBC | 3 | 2058-07-27 | 2058-04-09 | 2014-01-04 | 2.5 | 0.06728 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 8.1 | 5.5 | 7.8 | 8 | 1.2396
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56029-01C02 | CML-3 | 80-DH-56029-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20909 | Rope Access | 2014-05-22 09:30 | 2014-05-22 11:00 | [36 empty] | 5.325 | CML-3 | CML: Elbow | 3 | 2018-05-07 | 2018-12-02 | 2014-05-22 09:30 | 2.5 | 0.60594 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 9 O'Clock | 80 | 5.49 | 80-DH-56029-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 5.4 | 5.6 | 4.9 | 0.29861
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56121-01C02 | CML-2 | 50-DH-56121-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21040 | Rope Access | 2014-05-19 07:00 | 2014-05-19 08:00 | [36 empty] | 5.325 | CML-2 | CML: type TBC | 3 | 2017-12-30 | 2018-06-27 | 2014-05-19 07:00 | 2.5 | 0.66309 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56121-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 4.9 | 5.4 | 5.4 | 0.29861
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-7 | 50-CH-98808-1CG CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10870 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 6.1333 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-01-04 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.8 |  | 6.6 | 0.41633
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-4 | 50-CH-98808-1CG CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10867 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 6.175 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-01-04 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.7 | 6.2 | 5.8 | 6 | 0.38622
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-9 | 50-CH-98808-1CG CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10872 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 6.5 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-01-04 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 6 | 12 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.6 | 7 | 6.4 | 0.41633
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-6 | 50-CG-38474-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23630 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.825 | CML-6 | CML: Equal Tee | 3 | 2065-09-09 | 2071-04-20 | 2015-10-28 07:00 | 2.5 | 0.05811 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.1 | 5.9 | 5.9 | 0.29861
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-13 | 100-PG-23028-25C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 452 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 15.675 | CML-13 | CML: Pipe Length | 3 | 2016-09-19 | 2015-09-16 | 2014-03-12 09:00 | 9.4 | 2.336 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 15.3 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 15.6 | 15.3 | 16 | 15.8 | 0.29861
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-6 | 300-PF-20001-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21144 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.275 | CML-6 | CML: Elbow | 6 | 2015-11-17 | 2015-04-10 | 2014-07-16 07:30 | 2.5 | 4.777 | A1: Outside Quadrant |  | 8.27 | 2.5 | 5.385 | 8.9 | 12 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9.4 | 9.2 | 9.6 | 0.29861
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43107-01C02 | CML-1 | 300-FH-43107-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20424 | Protective mesh removed | 2014-07-02 13:00 | 2014-07-02 14:00 | [36 empty] | 9.725 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-07-02 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 3 O'Clock | 300 | 6.35 | 300-FH-43107-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.8 | 9.4 | 9.6 | 10.1 | 0.29861
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-6 | 80-PG-23025-06C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13077 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 11.175 | CML-6 | CML: Pipe Length | 6 | 2038-05-08 | 2034-11-11 | 2014-02-07 11:00 | 2.8 | 0.33385 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 10.9 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.9 | 11.1 | 11.1 | 11.6 | 0.29861
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-10 | 50-DH-56116-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5220 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.275 | CML-10 | CML: Elbow | 3 | 2018-01-04 | 2018-07-03 | 2014-05-20 09:30 | 2.5 | 0.66102 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5.4 | 5.6 | 4.9 | 0.29861
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-18 | 50-FH-43450-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 7697 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-13 13:52 | [32 empty] | 5.275 | CML-18 | CML: Pipe Length | 3 | 2021-01-16 | 2021-11-11 | 2015-01-08 13:00 | 2.5 | 0.39827 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.087416 | 5.6 | 5.4 | 5.2 | 4.9 | 0.29861
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40402-01C02 | CML-5 | 100-WC-40402-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20378 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.9 | CML-5 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.5 | 9 O'Clock | 100 | 6.02 | 100-WC-40402-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.2 | 6.8 | 7.1 | 6.5 | 0.31623
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-6 | 50-FG-45302-01C02 CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 5774 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 6.325 | CML-6 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.4 | 6.6 | 6.4 | 0.29861
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56107-01C02 | CML-2 | 80-DH-56107-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2041 |  | 2014-03-27 14:00 | 2014-03-27 14:30 | [36 empty] | 6.275 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-27 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 12 O'Clock | 80 | 5.49 | 80-DH-56107-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.4 | 6.2 | 6.6 | 0.29861
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-10 | 150-FH-43157-01C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10666 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.775 | CML-10 | CML: type TBC | 3 | 2016-06-08 | 2016-03-14 | 2013-11-18 | 2.5 | 1.5244 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 9 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.9 | 6.7 | 7.1 | 6.4 | 0.29861
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-24 | 400-FH-43508-01C02 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6573 | Rope Access.Line is FFS. Action: to recheck in a year (Mar. 2016) to confirm CR. | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 8.925 | CML-24 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 8.5 | 12 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 9 | 9.2 | 9 | 0.29861
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-6 | 50-DN-56101-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 846 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 8.6 | CML-6 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-02 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8 | 3 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 9.5 | 8 | 8.3 |  | 0.79373
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-3 | 50-WC-40032-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1237 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 6.625 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7 | 6.5 | 6.5 | 0.25
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-14 | 50-CG-24002-09C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2560 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 9.925 | CML-14 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.5 | 6 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.2 | 10 | 9.5 | 10 | 0.29861
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-1 | 200-FH-43131-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2822 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 8.825 | CML-1 | CML: Reducer | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 8.4 | 6 O'Clock | 150 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.06 |  | 8.9 | 9.1 | 8.4 | 8.9 | 0.29861
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-4 | 150-PG-20507-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2848 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.075 | CML-4 | CML: type TBC | 6 | 2019-02-17 | 2018-04-18 | 2014-03-16 07:00 | 2.5 | 1.4813 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 9.8 | 6 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.5 | 10 | 9.8 | 10 | 0.29861
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23018-09C03-A | CML-8 | 200-PG-23018-09C03-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13069 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 20.225 | CML-8 | CML: type TBC | 6 | 2021-03-16 | 2019-07-19 | 2014-01-10 07:00 | 10.17 | 1.3404 | A1: Outside Quadrant |  | 14.62 | 10.17 | 12.395 | 19.8 | 12 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.63 |  | 19.8 | 20.3 | 20.3 | 20.5 | 0.29861
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20301-03C03-P | CML-3 | 200-PG-20301-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5882 |  | 2014-06-25 14:00 | 2014-06-25 15:00 | [36 empty] | 14.275 | CML-3 | CML: Cap End | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 14:00 | 3.3 | 0 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 14 | 12 O'Clock | 200 | 12.7 | 200-PG-20301-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 14 | 14.2 | 14.7 | 14.2 | 0.29861
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56069-01C02 | CML-4 | 50-DH-56069-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3399 | Rope Access | 2014-05-10 13:00 | 2014-05-10 14:00 | [36 empty] | 8.375 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-10 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8 | 12 O'Clock | 50 | 5.54 | 50-DH-56069-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.7 | 8.5 | 8.3 | 0.29861
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-13 | 250-PW-20040-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21397 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.775 | CML-13 | CML: Reducer | 6 | 2045-04-21 | 2040-06-25 | 2014-07-12 07:30 | 4.1 | 0.2695 | A3: Inside Quadrant |  | 6.7 | 4.1 | 5.4 | 12.4 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 12.9 | 13.4 | 12.4 | 12.4 | 0.47871
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20062-01C03-P | CML-3 | 250-PG-20062-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21540 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 13.125 | CML-3 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2014-07-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 12.8 | 12 O'Clock | 150 | 9.27 | 250-PG-20062-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.3 |  | 12.8 | 13 | 13.2 | 13.5 | 0.29861
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-11 | 50-FL-43454-01C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22876 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.5 | CML-11 | CML: Elbow | 6 | 2026-11-20 | 2025-04-29 | 2015-05-01 07:00 | 2.5 | 0.57937 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 0 | 9.9 | 9.2 | 9.5 | 9.4 | 0.29439
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-10 | 300-PL-20011-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 23795 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 26.675 | CML-10 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 12 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 8 | 8.3 | 8 | 0.24495
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20014-01C02-P | CML-6 | 200-PL-20014-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21225 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.875 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20014-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 9 | 9.3 | 9.4 | 7.8 | 0.73655
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-14 | 50-CH-98808-1CG CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 10877 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 6.5333 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-01-04 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  |  | 6.7 | 6.4 | 6.5 | 0.15275
FG04 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-FG-45003-03C02 | CML-16 | 150-FG-45003-03C02 CML-16 | yes | FPSO 2015 | Pipe Wall Thickness | 23251 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.9 | CML-16 | CML: Elbow | 3 | 2019-09-11 | 2020-05-15 | 2015-05-11 07:00 | 2.5 | 0.48372 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0.26707 | 4.9 | 5.3 | 4.8 | 4.6 | 0.29439
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56064-01C02 | CML-4 | 50-DH-56064-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3274 | Rope Access | 2014-05-09 13:00 | 2014-05-09 14:00 | [36 empty] | 5.1 | CML-4 | CML: type TBC | 3 | 2017-04-08 | 2017-09-06 | 2014-05-09 13:00 | 2.5 | 0.78852 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56064-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.4 | 4.9 | 5.3 | 0.29439
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1752 | Rope access | 2014-04-27 07:00 | 2014-04-27 08:00 | [36 empty] | 5.1 | CML-3 | CML: Elbow | 3 | 2017-02-16 | 2017-07-12 | 2014-04-27 07:00 | 2.5 | 0.81776 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FH-43117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.3 | 4.9 | 5.4 | 0.29439
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43081-01C02 | CML-2 | 80-FH-43081-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20419 | CML Reviewed 19-11-14. Line is FFS. Repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-19 17:20 | [32 empty] | 5.4 | CML-2 | CML: Elbow | 3 | 2021-08-21 | 2022-08-06 | 2014-10-06 07:00 | 2.5 | 0.3633 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-FH-43081-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 1.1589 | 5.4 | 5.5 | 5.7 | 5 | 0.29439
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-4 | 100-DH-56561-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7936 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 5.4 | CML-4 | CML: Elbow | 3 | 2019-01-16 | 2019-03-25 | 2015-01-17 13:00 | 2.5 | 0.62515 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.5 | 5.4 | 5.7 | 0.29439
PG06 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20865 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.4 | CML-2 | CML: Elbow | 3 | 2022-09-09 | 2023-09-08 | 2014-10-04 07:00 | 2.5 | 0.32756 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.1 | 5.7 | 5.2 | 0.29439
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-19 | 200-PG-23008-15S01-A CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 3387 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 5.5 | CML-19 | CML: type TBC | 3 | 2017-01-04 | 2017-02-17 | 2014-05-10 09:30 | 2.5 | 0.97788 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.5 | 5.8 | 5.6 | 0.29439
PG06 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-PG-23008-15S01-A | CML-18 | 200-PG-23008-15S01-A CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 3080 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 0.477mm/ yr | [35 empty] | 5.5 | CML-18 | CML: Pipe Length | 3 | 2019-10-11 | 2020-06-17 | 2014-05-03 08:00 | 2.5 | 0.4775 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | -0.41635 | 5.8 | 5.5 | 5.1 | 5.6 | 0.29439
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-10 | 250-PW-44007-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23143 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 6.125 | CML-10 | CML: Pipe Length | 3 | 2026-12-28 | 2026-11-21 | 2015-05-10 07:00 | 2.5 | 0.28343 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.35626 | 6.1 | 6.6 | 6 | 5.8 | 0.34034
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-15 | 250-PW-44006-01X01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8007 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.225 | CML-15 | CML: Pipe Length | 3 | 2024-11-18 | 2024-10-18 | 2015-01-20 08:30 | 2.5 | 0.3355 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | -0.48657 | 6.2 | 5.8 | 6.3 | 6.6 | 0.3304
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43079-01C02 | CML-10 | 50-FL-43079-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 3053 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 5.6 | CML-10 | CML: type TBC | 3 | 2025-01-28 | 2026-04-30 | 2014-05-03 07:00 | 2.5 | 0.26049 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.4 | 5.3 | 5.8 | 0.29439
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-1 | 250-PW-44006-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23172 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.175 | CML-1 | CML: Pipe Length | 3 | 2027-01-04 | 2026-11-28 | 2015-05-11 07:00 | 2.5 | 0.28303 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 150 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.32901 | 6.4 | 6.4 | 6.1 | 5.8 | 0.28723
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-42 | 50-FG-45501-01C02 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 6604 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.9 | CML-42 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 5.6 | 5.7 | 6.1 | 0.29439
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-3 | 100-FH-43507-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7982 |  | 2015-01-18 14:00 | 2015-01-18 15:00 | [36 empty] | 6.1 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-18 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43507-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | -45.3103 | 6.2 | 6.1 | 5.7 | 6.4 | 0.29439
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20012-01C02-P | CML-8 | 200-PL-20012-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21210 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.525 | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20012-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.6 | 9.3 | 8.4 | 7.8 | 0.61847
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-31 | 200-PL-20010-01C02-P CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 23831 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.5 | CML-31 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.2 | 9.1 | 8.9 | 7.8 | 0.60553
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43101-01C02 | CML-2 | 100-FH-43101-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12741 |  | 2014-01-24 07:00 | 2014-01-24 08:00 | [36 empty] | 6.1 | CML-2 | CML: Pipe Length | 3 | 2023-10-23 | 2024-02-26 | 2014-01-24 07:00 | 2.5 | 0.3384 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 6 O'Clock | 100 | 6.02 | 100-FH-43101-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 6 | 5.8 | 6.1 | 0.29439
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43170-01C02 | CML-5 | 250-FL-43170-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23072 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.3 | CML-5 | CML: Elbow | 3 | 2034-08-28 | 2034-07-02 | 2015-05-07 07:00 | 2.5 | 0.18113 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 0.19363 | 6.7 | 6.2 | 6.3 | 6 | 0.29439
FG02 | Montara_Topside | Yes | Potable Water (53) | Pipework | 25-FG-45455-01C02-E | CML-1 | 25-FG-45455-01C02-E CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8244 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.4 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6 | 6.7 | 6.4 | 0.29439
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43017-01C02 | CML-3 | 150-FH-43017-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10649 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.7 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-18 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.3 | 12 O'Clock | 100 | 6.02 | 100-FH-43017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.8 | 7 | 6.7 | 0.29439
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43107-01C02 | CML-2 | 300-FH-43107-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20425 | Protective mesh removed | 2014-07-02 13:00 | 2014-07-02 14:00 | [36 empty] | 7.5 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-02 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 9 O'Clock | 300 | 6.35 | 300-FH-43107-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.5 | 7.8 | 7.6 | 7.1 | 0.29439
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-7 | 150-FG-45505-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22347 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 8.1 | CML-7 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.8 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.1 | 8 | 7.8 | 8.5 | 0.29439
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38009-01C02 | CML-2 | 50-CG-38009-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7860 |  | 2015-01-14 08:00 | 2015-01-14 09:00 |  |  | Administrator | 2016-03-02 11:37 | [32 empty] | 5.2 | CML-2 | CML: Pipe Length | 3 | 2021-02-12 | 2021-12-11 | 2015-01-14 08:00 | 2.5 | 0.39437 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 15 | 5.54 | 50-CG-38009-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 5.5 | 4.9 | 5 | 0.29439
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-8 | 250-PW-44006-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1905 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.2 | CML-8 | CML: Pipe Length | 3 | 2019-02-18 | 2019-02-02 | 2014-03-26 07:00 | 2.5 | 0.673 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.4 | 6.2 | 5.8 | 0.28284
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-26 | 200-PL-20010-01C02-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 23826 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.35 | CML-26 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 12 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.7 | 9 | 7.9 | 0.59161
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56028-01C02 | CML-5 | 80-DH-56028-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20902 | Rope Access | 2014-05-22 07:00 | 2014-05-22 08:00 | [36 empty] | 6 | CML-5 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-22 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 9 O'Clock | 80 | 5.49 | 80-DH-56028-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.2 | 5.8 | 6.3 | 5.7 | 0.29439
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57024-01C02 | CML-5 | 50-DC-57024-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2877 | Rope Access | 2014-04-24 13:00 | 2014-04-24 14:00 | [36 empty] | 6.075 | CML-5 | CML: type TBC | 3 | 2065-02-10 | 2057-09-22 | 2014-04-24 13:00 | 0.37 | 0 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-DC-57024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.53 |  | 5.9 | 6.1 | 6.2 | 6.1 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57017-01C02 | CML-5 | 20-DC-57017-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2900 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 6.275 | CML-5 | CML: type TBC | 3 | 2067-05-31 | 2058-11-20 | 2014-04-25 08:00 | 0.16 | 0 | A1: Outside Quadrant |  | 2.56 | 0.16 | 1.0125 | 5.7 | 12 O'Clock | 20 | 5.56 | 20-DC-57017-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.54 |  | 5.7 | 6 | 7.3 | 6.1 | 0.70415
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-12 | 250-PW-44007-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23145 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.925 | CML-12 | CML: Pipe Length | 3 | 2026-12-28 | 2026-11-21 | 2015-05-10 07:00 | 2.5 | 0.28343 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.35626 | 6 | 5.9 | 5.8 | 6 | 0.095743
FG02 | Montara_Topside | Yes | Potable Water (53) | Pipework | 25-FG-45455-01C02-E | CML-10 | 25-FG-45455-01C02-E CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8149 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.3 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.6 | 6 | 6.1 | 6.5 | 0.29439
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20015-01C02-P | CML-1 | 200-PL-20015-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21226 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.475 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20015-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.6 | 9.1 | 8.4 | 7.8 | 0.53774
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-14 | 200-PL-20008-01C02-H CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8811 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 7.05 | CML-14 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 12 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.2 | 7 | 7.1 | 0.1291
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-6 | 50-CH-98808-1CG CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10869 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 7.575 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-01-04 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 7.2 | 9 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.5 | 7.5 | 8.1 | 7.2 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43155-01C02 | CML-1 | 80-FH-43155-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10714 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 8.1 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2013-11-18 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.7 | 12 O'Clock | 80 | 5.49 | 80-FH-43155-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 8.1 | 8.4 | 8.2 | 0.29439
Marine | Montara_Topside | No | Prevention System (98) | Pipework | 50-CH-98808-1CG | CML-3 | 50-CH-98808-1CG CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10866 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 7.825 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-01-04 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 7.4 | 6 O'Clock | 50 | 5.54 | 50-CH-98808-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.5 | 8.3 | 7.4 | 8.1 | 0.44253
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57016-01C02 | CML-1 | 50-DC-57016-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1355 | Rope access | 2014-04-04 10:45 | 2014-04-04 12:00 | [36 empty] | 5.1 | CML-1 | CML: type TBC | 3 |  |  | 2014-04-04 10:45 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 4.8 | 12 O'Clock | 50 |  | 50-DC-57016-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.2 | 5.1 | 5.3 | 0.21602
DC01 | Montara_Topside | No | Separation (20) | Pipework | 50-DC-57016-01C02 | CML-16 | 50-DC-57016-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23354 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 8.375 | CML-16 | CML: Pipe Length | 6 | 2019-09-17 | 2018-10-17 | 2015-07-20 07:00 | 2.5 | 1.3442 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 8.1 | 9 O'Clock | 100 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | -0.28167 | 8.3 | 8.8 | 8.3 | 8.1 | 0.29861
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57016-01C02 | CML-4 | 50-DC-57016-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1358 | Rope access | 2014-04-04 10:45 | 2014-04-04 12:00 | [36 empty] | 5.2 | CML-4 | CML: type TBC | 3 |  |  | 2014-04-04 10:45 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 4.9 | 12 O'Clock | 50 |  | 50-DC-57016-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5.2 | 5.3 | 0.21602
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57016-01C02 | CML-7 | 50-DC-57016-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1361 | Rope access | 2014-04-04 10:45 | 2014-04-04 12:00 | [36 empty] | 5.325 | CML-7 | CML: type TBC | 3 |  |  | 2014-04-04 10:45 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5 | 12 O'Clock | 50 |  | 50-DC-57016-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.9 | 5.3 | 5.1 | 0.40311
DC01 | Montara_Topside | No | Separation (20) | Pipework | 50-DC-57016-01C02 | CML-10 | 50-DC-57016-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23108 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 8.725 | CML-10 | CML: Pipe Length | 6 | 2024-08-20 | 2023-12-31 | 2015-05-10 07:00 | 2.5 | 0.60293 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 8.1 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | 1.4314 | 8.8 | 8.1 | 8.8 | 9.2 | 0.45735
DC01 | Montara_Topside | No | Separation (20) | Pipework | 50-DC-57016-01C02 | CML-9 | 50-DC-57016-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23107 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.675 | CML-9 | CML: Equal Tee | 6 | 2024-08-20 | 2023-12-31 | 2015-05-10 07:00 | 2.5 | 0.60293 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.1 | 12 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | 3.7574 | 8.1 | 10.3 | 9.3 | 11 | 1.2606
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-DC-57016-01C02 | CML-2 | 50-DC-57016-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23024 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 9.425 | CML-2 | CML: Equal Tee | 6 | 2024-07-28 | 2023-12-09 | 2015-05-06 07:00 | 2.5 | 0.60635 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.1 | 6 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | 0.46218 | 8.1 | 10.9 | 8.1 | 10.6 | 1.5349
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-DC-57016-01C02 | CML-15 | 50-DC-57016-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23000 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.075 | CML-15 | CML: Pipe Length | 6 | 2024-07-22 | 2023-12-04 | 2015-05-05 07:00 | 2.5 | 0.60722 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.1 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | 2.0381 | 9.1 | 9.5 | 8.1 | 9.6 | 0.68496
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-DC-57016-01C02 | CML-1 | 50-DC-57016-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22976 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 8.925 | CML-1 | CML: Elbow | 6 | 2032-02-29 | 2031-10-20 | 2015-05-04 07:00 | 2.5 | 0.33263 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | 0.81629 | 8.2 | 8.1 | 10 | 9.4 | 0.92871
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57016-01C02 | CML-3 | 50-DC-57016-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1357 | Rope access | 2014-04-04 10:45 | 2014-04-04 12:00 | [36 empty] | 5.2 | CML-3 | CML: type TBC | 3 |  |  | 2014-04-04 10:45 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5 | 9 O'Clock | 50 |  | 50-DC-57016-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 5.5 | 5 | 0.24495
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-DC-57016-01C02 | CML-6 | 50-DC-57016-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22813 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 8.65 | CML-6 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.1 | 12 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | 0 | 8.1 | 9.1 | 9 | 8.4 | 0.47958
DC01 | Montara_Topside | No | Flare (43) | Pipework | 50-DC-57016-01C02 | CML-11 | 50-DC-57016-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 350 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.25 | CML-11 | CML: Elbow | 3 | 2018-06-10 | 2017-08-03 | 2014-03-12 | 1.23 | 1.1695 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.2 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.97 |  | 6.2 | 7.7 | 7.6 | 7.5 | 0.70475
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DC-57016-01C02 | CML-5 | 50-DC-57016-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5090 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.275 | CML-5 | CML: type TBC | 3 | 2034-01-31 | 2030-06-17 | 2015-03-06 07:00 | 2.5 | 0.29596 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 8.1 | 6 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.5 | 8.1 | 8.4 | 0.20616
DC01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-DC-57016-01C02 | CML-19 | 50-DC-57016-01C02 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8692 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:57 | [32 empty] | 8.525 | CML-19 | CML: Pipe Length | 3 | 2035-11-11 | 2030-03-12 | 2015-02-13 07:00 | 2.5 | 0.26981 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.1 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.8 | 8.4 | 8.1 | 8.8 | 0.34034
DC01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-DC-57016-01C02 | CML-13 | 50-DC-57016-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8686 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:56 | [32 empty] | 8.5 | CML-13 | CML: Pipe Length | 3 | 2035-11-11 | 2030-03-12 | 2015-02-13 07:00 | 2.5 | 0.26981 | A4: Left Quadrant |  | 5.56 | 2.5 | 4.03 | 8.1 | 9 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.8 | 8.4 | 8.7 | 8.1 | 0.31623
DC01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-DC-57016-01C02 | CML-1 | 50-DC-57016-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8674 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:53 | [32 empty] | 8.35 | CML-1 | CML: Elbow | 3 | 2035-11-11 | 2030-03-12 | 2015-02-13 07:00 | 2.5 | 0.26981 | A2: Right Quadrant |  | 5.56 | 2.5 | 4.03 | 8.1 | 3 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.6 | 8.1 | 8.5 | 8.2 | 0.23805
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-DC-57016-01C02 | CML-2 | 50-DC-57016-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8651 |  | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:49 | [32 empty] | 8.35 | CML-2 | CML: Elbow | 6 | 2029-12-31 | 2029-09-06 | 2015-02-12 07:00 | 2.5 | 0.37599 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.2 | 9 | 0.43589
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-DC-57016-01C02 | CML-4 | 50-DC-57016-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8637 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:19 | [32 empty] | 8.5 | CML-4 | CML: Elbow | 6 | 2029-12-13 | 2029-08-19 | 2015-02-10 11:30 | 2.5 | 0.37709 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 12 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.4 | 9.2 | 8.3 | 0.48305
DC01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-DC-57016-01C02 | CML-1 | 50-DC-57016-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8582 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-07 14:00 | 2015-02-07 16:00 | [36 empty] | 8.65 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-07 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.1 | 12 O'Clock | 50 | 5.54 | 50-AI-63035-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.8 | 8.9 | 8.8 | 0.36968
DC01 | Montara_Topside | No | Separation (20) | Pipework | 50-DC-57016-01C02 | CML-51 | 50-DC-57016-01C02 CML-51 |  | FPSO 2014 | Pipe Wall Thickness | 21189 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 12.3 | CML-51 | CML: Elbow | 6 | 2016-10-21 | 2016-02-10 | 2014-07-16 07:30 | 4.1 | 2.9978 | A4: Left Quadrant |  | 8.27 | 4.1 | 6.185 | 10.9 | 9 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 13.2 | 12.4 | 12.7 | 10.9 | 0.98995
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-DC-57016-01C02 | CML-3 | 50-DC-57016-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22038 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.175 | CML-3 | CML: Elbow | 6 | 2021-06-08 | 2020-12-23 | 2014-10-20 07:00 | 2.5 | 0.84349 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.1 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 9.9 | 9.6 | 8.1 | 9.1 | 0.78899
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-DC-57016-01C02 | CML-4 | 50-DC-57016-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21956 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 8.425 | CML-4 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.1 | 3 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.9 | 8.1 | 8.5 | 8.2 | 0.3594
DC01 | Montara_Topside | No | Flare (43) | Pipework | 50-DC-57016-01C02 |  | 50-DC-57016-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21797 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.225 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 8.1 | 12 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.7 | 8.3 | 11.8 | 1.7347
DC01 | Montara_Topside | No | Separation (20) | Pipework | 50-DC-57016-01C02 | CML-15 | 50-DC-57016-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21266 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 8.675 | CML-15 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.7 | 9.2 | 8.7 | 0.45
DC01 | Montara_Topside | No | Separation (20) | Pipework | 50-DC-57016-01C02 | CML-42 | 50-DC-57016-01C02 CML-42 |  | FPSO 2014 | Pipe Wall Thickness | 21293 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 8.475 | CML-42 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.6 | 8.7 | 8.5 | 0.263
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57016-01C02 | CML-5 | 50-DC-57016-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1359 | Rope access | 2014-04-04 10:45 | 2014-04-04 12:00 | [36 empty] | 5.425 | CML-5 | CML: type TBC | 3 |  |  | 2014-04-04 10:45 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.2 | 9 O'Clock | 50 |  | 50-DC-57016-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.7 | 5.5 | 5.2 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57016-01C02 | CML-6 | 50-DC-57016-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1360 | Rope access | 2014-04-04 10:45 | 2014-04-04 12:00 | [36 empty] | 5.6 | CML-6 | CML: type TBC | 3 |  |  | 2014-04-04 10:45 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5.4 | 3 O'Clock | 50 |  | 50-DC-57016-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 5.8 | 5.5 | 0.18257
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-DC-57016-01C02 | CML-6 | 50-DC-57016-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20603 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 8.1 | CML-6 | CML: Elbow | 6 | 2017-06-21 | 2017-01-01 | 2014-07-25 07:30 | 2.5 | 1.9237 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 8.1 | 9 O'Clock | 20 | 10.31 | 300-PG-23070-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.1 | 8.1 | 0
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57016-01C02 | CML-2 | 50-DC-57016-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1356 | Rope access | 2014-04-04 10:45 | 2014-04-04 12:00 | [36 empty] | 5.675 | CML-2 | CML: type TBC | 3 |  |  | 2014-04-04 10:45 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.5 | 9 O'Clock | 50 |  | 50-DC-57016-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 5.7 | 5.6 | 5.5 | 0.17078
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45044-03C02 | CML-9 | 50-FG-45044-03C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23578 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 8.9 | CML-9 | CML: Elbow | 3 | 2114-11-10 | 2088-07-09 | 2015-09-10 07:00 | 2.5 | 0.06147 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 0.21283 | 9.1 | 8.6 | 8.7 | 9.2 | 0.29439
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45048-03C02 | CML-1 | 50-FG-45048-03C02 CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 2276 |  | 2014-03-16 14:00 | 2014-03-16 14:30 | [36 empty] | 8.9 | CML-1 | CML: type TBC | 3 |  |  | 2014-03-16 14:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 8.6 | 9 O'Clock | 50 |  | 50-PG-45048-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.1 | 9.2 | 8.7 | 8.6 | 0.29439
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43108-01C02 | CML-2 | 200-FH-43108-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12777 |  | 2014-01-18 15:30 | 2014-01-18 16:30 | [36 empty] | 8.6 | CML-2 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 15:30 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 8.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43108-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.96 |  | 8.4 | 8.8 | 8.9 | 8.3 | 0.29439
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-18 | 250-PW-20041-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21427 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.6 | CML-18 | CML: Fitting | 6 | 2045-04-21 | 2040-06-25 | 2014-07-12 07:30 | 4.1 | 0.2695 | A1: Outside Quadrant |  | 6.7 | 4.1 | 5.4 | 12.4 | 3 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 12.4 | 12.4 | 12.5 | 13.1 | 0.33665
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-12 | 50-PL-23040-03C03 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10197 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.7 | CML-12 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 10.4 | 3 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.9 | 10.4 | 10.5 | 11 | 0.29439
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-6 | 50-DC-57031-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2185 | Rope Access | 2014-03-30 14:00 | 2014-03-30 15:00 | [36 empty] | 6 | CML-6 | CML: type TBC | 3 | 2023-11-28 | 2025-01-13 | 2014-03-30 14:00 | 2.5 | 0.28951 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57031A-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.5 | 6.7 | 5.3 | 5.5 | 0.70238
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-3 | 50-DC-57031-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2182 | Rope Access | 2014-03-30 14:00 | 2014-03-30 15:00 | [36 empty] | 5.65 | CML-3 | CML: type TBC | 3 | 2023-11-28 | 2025-01-13 | 2014-03-30 14:00 | 2.5 | 0.28951 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57031A-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.4 | 5.3 | 6.2 | 0.40415
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-2 | 80-PW-44001-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21993 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.35 | CML-2 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 3 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 5.9 | 6.2 | 6.7 | 0.36968
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-2 | 100-FL-43455-01C02-P CML-2 | High Priority | FPSO 2014 | Pipe Wall Thickness | 20485 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 5.3 | CML-2 | CML: Elbow | 3 | 2017-08-16 | 2017-10-06 | 2014-10-03 07:00 | 2.5 | 0.83549 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 3 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 4.9 | 5.3 | 5.6 | 0.29439
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43303-01C02 | CML-6 | 50-FL-43303-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20462 | Reviewed 24/11/14. FFS. Repeat on Oct.18. | 2014-10-05 07:00 | 2014-10-05 15:00 |  |  | Nestor | 2014-11-26 15:03 | [32 empty] | 5.2 | CML-6 | CML: Elbow | 3 | 2019-10-21 | 2020-06-28 | 2014-10-05 07:00 | 2.5 | 0.47548 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FL-43303-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 5.6 | 5.2 | 4.9 | 0.29439
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56118-01C02 | CML-4 | 50-DH-56118-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21023 | Rope Access | 2014-05-19 11:00 | 2014-05-19 12:00 | [36 empty] | 5.3 | CML-4 | CML: type TBC | 3 | 2017-12-31 | 2018-06-28 | 2014-05-19 11:00 | 2.5 | 0.66277 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DH-56118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 5.4 | 4.9 | 5.3 | 0.29439
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-6 | 50-WC-40452-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10603 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 6.6667 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2013-11-17 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  |  | 6.8 | 6.7 | 6.5 | 0.15275
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-4 | 50-DC-57031-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2183 | Rope Access | 2014-03-30 14:00 | 2014-03-30 15:00 | [36 empty] | 5.475 | CML-4 | CML: type TBC | 3 | 2031-05-28 | 2033-05-02 | 2014-03-30 14:00 | 2.5 | 0.16888 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57031A-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.5 | 5.4 | 5.5 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-2 | 50-DC-57031-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2181 | Rope Access | 2014-03-30 14:00 | 2014-03-30 15:00 | [36 empty] | 5.6 | CML-2 | CML: type TBC | 3 | 2076-05-17 | 2083-02-18 | 2014-03-30 14:00 | 2.5 | 0.04825 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57031A-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.8 | 5.5 | 5.5 | 0.14142
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57014-01C02 | CML-4 | 50-DC-57014-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1365 | Rope access | 2014-04-04 13:00 | 2014-04-04 15:00 | [36 empty] | 8.525 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-04 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.9 | 8.4 | 8.7 | 8.1 | 0.35
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-37 | 250-PG-23003-06C02-PA CML-37 |  | FPSO 2014 | Pipe Wall Thickness | 3253 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.7 | CML-37 | CML: type TBC | 3 | 2033-10-06 | 2035-12-13 | 2014-05-09 07:00 | 2.5 | 0.14929 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 5.4 | 5.7 | 5.6 | 0.29439
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-5 | 50-DH-56137-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21089 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.3 | CML-5 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.9 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 6.3 | 6.4 | 5.9 | 0.29439
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-14 | 250-FH-43303-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12952 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.7 | CML-14 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.1 | 6.7 | 6.6 | 0.29439
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-9 | 50-FG-45024-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1213 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.7 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.4 | 6.6 | 7.1 | 0.29439
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45005-03C02-E | CML-2 | 150-FG-45005-03C02-E CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24320 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.3 | CML-2 | CML: Elbow | 3 | 2075-06-12 | 2065-11-14 | 2016-06-01 07:00 | 2.77 | 0.06992 | A1: Outside Quadrant |  | 4.11 | 2.77 | 3.44 | 6.9 | 12 O'Clock | 150 | 7.11 | 150-FG-45005-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.13 |  | 6.9 | 7.3 | 7.4 | 7.6 | 0.29439
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-10 | 200-PL-20020-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21314 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 8.45 | CML-10 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.9 | 8.3 | 8.8 | 7.8 | 0.50662
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-19 | 250-WC-40017-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2082 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 6.525 | CML-19 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.5 | 6.5 | 6.5 | 0.05
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43074-01C02 | CML-1 | 50-FL-43074-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1786 | Rope access | 2014-04-28 09:30 | 2014-04-28 10:30 | [36 empty] | 9.3 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-28 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9 | 6 O'Clock | 50 | 5.54 | 50-FL-43074-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.2 | 9.3 | 9 | 9.7 | 0.29439
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-20 | 50-PL-23052-09C03 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10184 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.4 | CML-20 | CML: type TBC | 6 | 2016-10-25 | 2016-05-08 | 2013-11-09 | 2.81 | 2.4258 | A4: Left Quadrant |  | 5.07 | 2.81 | 3.94 | 10 | 9 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.19 |  | 10.5 | 10.4 | 10.7 | 10 | 0.29439
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40014-01C02 | CML-4 | 50-WC-40014-01C02 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 1551 | Rope Access | 2014-04-09 08:00 | 2014-04-09 09:00 | [36 empty] | 7.625 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-WC-40014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 9.7 | 7.2 | 7 | 6.6 | 1.4056
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-30 | 300-PF-20501-03C03-P CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 23533 | Re-check | 2015-07-29 07:00 | 2015-07-29 12:00 | [36 empty] | 13.7 | CML-30 | CML: type TBC | 6 | 2036-08-28 | 2032-06-24 | 2015-07-29 07:00 | 4.9 | 0.40283 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 | -10.5658 | 13.7 | 14.1 | 13.6 | 13.4 | 0.29439
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-4 | 250-PG-23004-06C03-A CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23372 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.1 | CML-4 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2015-07-21 07:00 | 8.55 | 0 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.8 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.25 |  | 19.3 | 19.4 | 18.8 | 18.9 | 0.29439
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40502-1CG | CML-1 | 250-WC-40502-1CG CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5617 | Material typre 1CG (no option in drop down box) | 2014-06-20 11:00 | 2014-06-20 12:00 | Check Corrosion Rate of 1.794mm/ yr | [35 empty] | 13.825 | CML-1 | CML: Fitting | 3 | 2020-06-05 | 2017-10-03 | 2014-06-20 11:00 | 2.5 | 1.7943 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 13.2 | 6 O'Clock | 250 | 15.09 | 250-WC-40502-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 14.7 | 13.8 | 13.2 | 13.6 | 0.63443
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-8 | 150-WC-40003-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2985 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.557mm/ yr | [35 empty] | 7.375 | CML-8 | CML: Elbow | 3 | 2021-09-09 | 2021-01-16 | 2014-05-01 09:30 | 2.5 | 0.55668 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 3 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 6.6 | 8 | 7.9 | 0.68496
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-9 | 300-PG-20005-03C03-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22771 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.45 | CML-9 | CML: Pipe Length | 6 | 2118-08-23 | 2099-09-19 | 2015-04-29 07:00 | 4.9 | 0.08899 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 | -0.87506 | 14.8 | 14.1 | 14.5 | 14.4 | 0.28868
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-8 | 150-WC-40003-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 22264 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.557mm/ yr | [35 empty] | 7.375 | CML-8 | CML: Elbow | 3 | 2021-09-09 | 2021-01-16 | 2014-05-01 09:30 | 2.5 | 0.55668 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 3 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 6.6 | 8 | 7.9 | 0.68496
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-1 | 50-DC-57031-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2180 | Rope Access | 2014-03-30 14:00 | 2014-03-30 15:00 | [36 empty] | 6.2 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-30 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57031A-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.1 | 6.3 | 6.7 | 0.41633
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-5 | 50-DC-57031-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2184 | Rope Access | 2014-03-30 14:00 | 2014-03-30 15:00 | [36 empty] | 6.375 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-30 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-DC-57031A-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.7 | 6.2 | 6.4 | 0.23629
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-9 | 50-FH-43450-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7688 | Re-check. FFS | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:11 | [32 empty] | 5.35 | CML-9 | CML: Pipe Length | 3 | 2022-06-16 | 2023-06-05 | 2015-01-08 13:00 | 2.5 | 0.33604 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -1.049 | 5.4 | 5 | 5.7 | 5.3 | 0.28868
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-3 | 25-VA-23054-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1472 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 5.35 | CML-3 | CML: type TBC | 3 | 2018-07-16 | 2019-02-02 | 2014-04-29 10:00 | 2.5 | 0.59293 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5.4 | 5 | 5.7 | 0.28868
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56556-01C02 | CML-3 | 50-DH-56556-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21129 | Reviewed on 20/11/14. FFS. Recheck in Oct. 19. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-20 17:40 | [32 empty] | 5.65 | CML-3 | CML: Elbow | 3 | 2030-07-23 | 2032-05-24 | 2014-10-08 07:00 | 2.5 | 0.17722 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56556-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6 | 5.6 | 5.7 | 5.3 | 0.28868
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-1 | 50-PG-23074-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20623 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.65 | CML-1 | CML: Elbow | 3 | 2027-12-28 | 2029-07-22 | 2014-07-26 07:00 | 2.5 | 0.20843 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.3 | 5.6 | 6 | 0.28868
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-6 | 100-WC-40035-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1739 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 6.95 | CML-6 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 9 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.9 | 6.7 | 6.6 | 6.6 | 0.63509
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43101-01C02 | CML-3 | 100-FH-43101-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12742 |  | 2014-01-24 07:00 | 2014-01-24 08:00 | [36 empty] | 6.15 | CML-3 | CML: Pipe Length | 3 | 2023-10-23 | 2024-02-26 | 2014-01-24 07:00 | 2.5 | 0.3384 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 12 O'Clock | 100 | 6.02 | 100-FH-43101-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.1 | 6.5 | 6.2 | 0.28868
FG02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8384 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 6.35 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-29 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-PG-23408-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 6.3 | 6.7 | 6 | 0.28868
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43460-01C02 | CML-5 | 80-FL-43460-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2970 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.65 | CML-5 | CML: Fitting | 3 | 2037-04-12 | 2034-03-27 | 2014-05-01 14:00 | 0.54 | 0.20727 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 3 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 | 0 | 5.7 | 5.3 | 5.6 | 6 | 0.28868
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57058-06C02 | CML-4 | 50-DC-57058-06C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10345 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 1.433mm/ yr | [35 empty] | 8.325 | CML-4 | CML: Pipe Length | 3 | 2017-10-07 | 2017-01-06 | 2013-11-11 | 2.5 | 1.4331 | A2: Right Quadrant |  | 5.74 | 2.5 | 3.5737 | 8.1 | 9 O'Clock | 50 | 8.74 | 50-DC-57058-06C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 9 | 8.1 | 8.1 | 8.1 | 0.45
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-5 | 50-DC-57031-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2136 | Rope Access | 2014-03-29 09:30 | 2014-03-29 10:30 | Check Corrosion Rate of 0.654mm/ yr | [35 empty] | 5.35 | CML-5 | CML: type TBC | 3 | 2018-01-22 | 2018-07-23 | 2014-03-29 09:30 | 2.5 | 0.65396 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57031B-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.4 | 5.6 | 0.25166
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43460-01C02 | CML-5 | 80-FL-43460-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22249 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.65 | CML-5 | CML: Fitting | 3 | 2037-04-12 | 2034-03-27 | 2014-05-01 14:00 | 0.54 | 0.20727 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 3 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.7 | 5.3 | 5.6 | 6 | 0.28868
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-2 | 50-DH-56109-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20991 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.05 | CML-2 | CML: Elbow | 3 | 2016-12-15 | 2017-05-03 | 2014-05-24 10:30 | 2.5 | 0.85777 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.1 | 5 | 5.4 | 0.28868
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43116-01C02 | CML-1 | 150-FH-43116-01C02 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 7865 | Line is FFS. It has been check twice. The higher values reported here are from the data collected in Apr. 2014. The rechecked CR’s from data from Jan. 2015 are lower. Current RBI frequency is 48m. Action: to recheck line in a 24m (Jan. 2017) to confirm CR. | 2015-01-14 09:30 | 2015-01-14 10:30 |  |  | Administrator | 2015-09-07 17:06 | [32 empty] | 5.05 | CML-1 | CML: Elbow | 3 | 2016-07-08 | 2016-04-10 | 2015-01-14 09:30 | 2.5 | 1.4849 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 4.7 | 12 O'Clock | 80 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.13939 | 4.7 | 5.1 | 5 | 5.4 | 0.28868
PG06 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PG-23008-15S01-A | CML-15 | 200-PG-23008-15S01-A CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21947 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.45 | CML-15 | CML: Reducing Tee | 3 | 2023-10-31 | 2025-01-16 | 2014-10-10 07:00 | 2.5 | 0.28683 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.5 | 5.1 | 5.8 | 0.28868
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-10 | 80-PW-44001-01C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23219 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.325 | CML-10 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 2.0957 | 5.9 | 6.5 | 6.7 | 6.2 | 0.35
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-3 | 250-PW-44007-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23136 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.875 | CML-3 | CML: Pipe Length | 3 | 2026-12-28 | 2026-11-21 | 2015-05-10 07:00 | 2.5 | 0.28343 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.35626 | 5.9 | 5.9 | 5.8 | 5.9 | 0.05
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56130-01C02 | CML-4 | 50-DH-56130-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21056 | Rope Access | 2014-05-15 13:00 | 2014-05-15 14:00 | [36 empty] | 6.05 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-15 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-DH-56130-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6 | 6.4 | 6.1 | 0.28868
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-11 | 100-FG-45043-03C02-E CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22657 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 6.55 | CML-11 | CML: Elbow | 3 | 2054-10-24 | 2049-02-10 | 2015-04-27 07:00 | 1.88 | 0 | A3: Inside Quadrant |  | 3.02 | 1.88 | 2.45 | 6.2 | 6 O'Clock | 50 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.32 |  | 6.6 | 6.9 | 6.2 | 6.5 | 0.28868
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-4 | 150-FH-43157-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10660 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 7.2333 | CML-4 | CML: type TBC | 3 | 2023-08-19 | 2022-10-31 | 2013-11-18 | 2.5 | 0.45088 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.9 | 3 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  |  | 6.9 | 7.4 | 7.4 | 0.28868
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-12 | 50-CG-38452-09C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1814 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 7.45 | CML-12 | CML: Reducer | 3 | 2433-01-13 | 2400-03-18 | 2014-04-29 11:00 | 2.5 | 0.01098 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.1 | 3 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.4 | 7.1 | 7.8 | 7.5 | 0.28868
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-2 | 50-FG-45018-03C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10501 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.15 | CML-2 | CML: type TBC | 3 | 2015-08-03 | 2015-07-29 | 2013-11-15 | 2.5 | 1.3988 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 4.9 | 5.4 | 5.4 | 0.28868
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38477-01C02-P | CML-6 | 50-CG-38477-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2618 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.25 | CML-6 | CML: type TBC | 3 | 2018-06-29 | 2018-06-17 | 2014-04-26 10:45 | 2.5 | 0.59827 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0 | 5 | 5.5 | 5 | 5.5 | 0.28868
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-34 | 250-PW-44006-01X01 CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 1931 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.65 | CML-34 | CML: Pipe Length | 3 | 2020-05-27 | 2020-05-08 | 2014-03-26 07:00 | 2.5 | 0.55064 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 7.2 | 6.4 | 7.1 | 0.61373
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-11 | 250-PW-44004-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5630 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 6.275 | CML-11 | CML: Elbow | 3 | 2022-06-03 | 2022-05-10 | 2014-06-20 13:00 | 2.5 | 0.42713 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.5 | 6.6 | 6.1 | 5.9 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-2 | 150-WC-40002-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20341 | Reviewed on 18/11/14. Line is FFS. Repeat on Oct.19 | 2014-10-09 07:00 | 2014-10-09 15:00 | Check Corrosion Rate of 0.376mm/ yr |  | Nestor | 2014-11-24 10:28 | [32 empty] | 7.35 | CML-2 | CML: Elbow | 3 | 2025-09-03 | 2024-09-17 | 2014-10-09 07:00 | 2.5 | 0.37584 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 3 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.7 | 6.6 | 7.2 | 7.9 | 0.58023
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80002-01C02 | CML-1 | 100-VA-80002-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2161 | Rope Access | 2014-03-30 09:30 | 2014-03-30 11:00 | [36 empty] | 5.75 | CML-1 | CML: type TBC | 3 | 2019-01-07 | 2019-03-16 | 2014-03-30 09:30 | 2.5 | 0.62765 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 3 O'Clock | 100 | 6.02 | 100-VA-80002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.5 | 6 | 6 | 0.28868
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56106-01C02 | CML-9 | 80-DH-56106-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2035 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 6.15 | CML-9 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-27 14:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 6 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.4 | 5.9 | 6.4 | 0.28868
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43119-01C02 | CML-2 | 80-FH-43119-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12829 |  | 2014-01-18 10:00 | 2014-01-18 11:30 | [36 empty] | 5.3667 | CML-2 | CML: Fitting | 3 | 2024-03-25 | 2022-11-06 | 2014-01-18 10:00 | 0.54 | 0.4574 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-FH-43119-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 5.2 | 5.2 | 5.7 |  | 0.28868
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-12 | 80-FH-43007-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12573 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 6.05 | CML-12 | CML: Elbow | 3 | 2062-11-29 | 2056-08-05 | 2014-01-18 07:00 | 0.54 | 0 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.8 | 6 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.26 |  | 6.3 | 5.8 | 5.8 | 6.3 | 0.28868
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-5 | 200-PW-44020-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23012 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 6.425 | CML-5 | CML: Reducer | 3 | 2029-11-21 | 2029-10-08 | 2015-05-05 07:00 | 2.5 | 0.23354 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 2.1692 | 7.1 | 6.1 | 6.6 | 5.9 | 0.53774
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-28 | 200-PL-20010-01C02-P CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 23828 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 27.125 | CML-28 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.4 | 7.9 | 8.8 | 7.8 | 0.46458
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-9 | 100-FG-45001-09C02 CML-9 | Yes | FPSO 2015 | Pipe Wall Thickness | 23314 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 10.85 | CML-9 | CML: type TBC | 3 | 2034-12-09 | 2029-03-13 | 2015-07-11 07:00 | 4.7 | 0.29852 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.5 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | -0.42211 | 11.2 | 10.5 | 10.9 | 10.8 | 0.28868
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-11 | 300-PL-20011-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 23796 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.175 | CML-11 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.4 | 8.7 | 7.8 | 7.8 | 0.45
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-1 | 250-PG-23015-06C03-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13033 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 14.125 | CML-1 | CML: Reducer | 6 | 2014-09-22 | 2014-06-22 | 2014-01-11 13:00 | 8.55 | 7.4124 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 13.7 | 12 O'Clock | 100 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.15 |  | 13.7 | 14.3 | 14.2 | 14.3 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-10 | 400-FH-43500-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5646 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 8.375 | CML-10 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 8.2 | 9 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.8 | 8.3 | 8.2 | 0.28723
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-7 | 300-PG-20037-03C03-PA CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21382 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | Check Corrosion Rate of 0.529mm/ yr | [35 empty] | 14.125 | CML-7 | CML: Fitting | 6 | 2030-04-25 | 2027-07-15 | 2014-06-29 13:00 | 5.33 | 0.52866 | A1: Outside Quadrant |  | 8.27 | 5.33 | 6.8 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.37 |  | 13.7 | 14.2 | 14.3 | 14.3 | 0.28723
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-3 | 100-PG-23028-25C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 442 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 15.975 | CML-3 | CML: Pipe Length | 3 | 2017-05-15 | 2016-02-28 | 2014-03-12 09:00 | 9.4 | 1.9509 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 15.6 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 16 | 15.6 | 16 | 16.3 | 0.28723
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-1 | 50-DC-57031-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2132 | Rope Access | 2014-03-29 09:30 | 2014-03-29 10:30 | Check Corrosion Rate of 0.533mm/ yr | [35 empty] | 5.45 | CML-1 | CML: type TBC | 3 | 2019-02-12 | 2019-09-23 | 2014-03-29 09:30 | 2.5 | 0.53285 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-DC-57031B-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.7 | 5.6 | 5.4 | 0.26458
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-8 | 250-PW-44006-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23179 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.6 | CML-8 | CML: Pipe Length | 3 | 2030-01-11 | 2029-11-28 | 2015-05-11 07:00 | 2.5 | 0.23157 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 1.6451 | 7 | 6.7 | 6.8 | 5.9 | 0.48305
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-7 | 50-FG-45021-03C02 CML-7 | yes | FPSO 2013 | Pipe Wall Thickness | 10535 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 4.825 | CML-7 | CML: type TBC | 3 | 2014-11-26 | 2014-11-22 | 2013-11-16 | 2.5 | 2.0423 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.2 | 4.6 | 4.9 | 4.6 | 0.28723
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-8 | 50-FG-45501-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6591 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.675 | CML-8 | CML: Elbow | 3 | 2036-07-22 | 2039-01-15 | 2015-03-30 07:00 | 2.5 | 0.13128 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.3 | 5.9 | 5.6 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-1 | 250-PW-44006-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7993 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.35 | CML-1 | CML: Pipe Length | 3 | 2027-06-07 | 2027-04-30 | 2015-01-20 08:30 | 2.5 | 0.2745 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 3 O'Clock | 150 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 1.4597 | 6.8 | 5.9 | 6.4 | 6.3 | 0.36968
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-2 | 50-DC-57031-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2133 | Rope Access | 2014-03-29 09:30 | 2014-03-29 10:30 | Check Corrosion Rate of 0.412mm/ yr | [35 empty] | 5.35 | CML-2 | CML: type TBC | 3 | 2020-10-16 | 2021-08-02 | 2014-03-29 09:30 | 2.5 | 0.41175 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-DC-57031B-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.2 | 5.4 | 5.3 | 0.1291
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-18 | 250-PW-44006-01X01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23189 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.25 | CML-18 | CML: Pipe Length | 3 | 2030-01-11 | 2029-11-28 | 2015-05-11 07:00 | 2.5 | 0.23157 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 6 O'Clock | 150 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 1.6451 | 6.2 | 6.4 | 5.9 | 6.5 | 0.26458
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-12 | 50-PW-44012-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2026 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 6.15 | CML-12 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-27 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.1 | 6.3 | 6.3 | 0.19149
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-36 | 250-PW-44006-01X01 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 23207 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.025 | CML-36 | CML: Pipe Length | 3 | 2030-01-11 | 2029-11-28 | 2015-05-11 07:00 | 2.5 | 0.23157 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 1.6451 | 5.9 | 6.3 | 5.9 | 6 | 0.1893
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-16 | 250-PW-44004-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 5635 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 6.3 | CML-16 | CML: Reducing Tee | 3 | 2022-06-03 | 2022-05-10 | 2014-06-20 13:00 | 2.5 | 0.42713 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.4 | 6.6 | 6.3 | 0.29439
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56111-01C02 | CML-1 | 50-DH-56111-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21010 | Rope Access | 2014-05-24 14:00 | 2014-05-24 15:00 | [36 empty] | 4.975 | CML-1 | CML: Elbow | 3 | 2017-06-08 | 2017-11-13 | 2014-05-24 14:00 | 2.5 | 0.75535 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56111-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 5.4 | 4.8 | 4.8 | 0.28723
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-2 | 0200-DH-56L9003-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5087 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.925 | CML-2 | CML: type TBC | 3 | 2037-12-26 | 2033-09-09 | 2015-03-06 07:00 | 2.5 | 0.24972 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 8.2 | 12 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.8 | 8.7 | 10 | 0.76322
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-1 | 0200-DH-56L9003-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5086 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.3 | CML-1 | CML: type TBC | 3 | 2037-12-26 | 2033-09-09 | 2015-03-06 07:00 | 2.5 | 0.24972 | A2: Right Quadrant |  | 5.74 | 2.5 | 3.5737 | 8.2 | 3 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.3 | 8.2 | 8.4 | 8.3 | 0.08165
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56121-01C02 | CML-1 | 50-DH-56121-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21039 | Rope Access | 2014-05-19 07:00 | 2014-05-19 08:00 | [36 empty] | 5.475 | CML-1 | CML: type TBC | 3 | 2025-08-19 | 2026-12-11 | 2014-05-19 07:00 | 2.5 | 0.24866 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56121-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.3 | 5.4 | 5.3 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-6 | 80-FH-43158-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12887 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.775 | CML-6 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-22 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 9 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 6.2 | 5.6 | 0.28723
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-11 | 80-DH-56074-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20956 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 5.975 | CML-11 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 3 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 5.6 | 6.2 | 5.9 | 0.28723
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-47 | 200-PL-20019-01C02 CML-47 |  | FPSO 2014 | Pipe Wall Thickness | 21298 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 8.1 | CML-47 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.9 | 7.8 | 8.3 | 8.4 | 0.29439
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-4 | 50-DC-57031-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2135 | Rope Access | 2014-03-29 09:30 | 2014-03-29 10:30 | [36 empty] | 5.5 | CML-4 | CML: type TBC | 3 | 2023-11-13 | 2024-12-27 | 2014-03-29 09:30 | 2.5 | 0.29065 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-DC-57031B-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.7 | 5.5 | 5.5 | 0.1633
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20059-01C02 | CML-7 | 200-PL-20059-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2872 | Rope Access | 2014-03-25 11:00 | 2014-03-25 12:00 | [36 empty] | 8.1 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-25 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 12 O'Clock | 200 | 6.35 | 200-PL-20059-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.9 | 8.4 | 8.3 | 0.29439
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-3 | 300-PL-20011-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 23788 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8 | 7.9 | 8.3 | 7.8 | 0.21602
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-16 | 80-DC-57002-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20245 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 9.575 | CML-16 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.2 | 3 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 9 | 8.2 | 11.6 | 9.5 | 1.4523
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-12 | 300-PL-20011-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 23797 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 7.975 | CML-12 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 12 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.9 | 8 | 8.2 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-9 | 250-FH-43303-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12947 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 7.025 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.2 | 7.2 | 7.1 | 6.6 | 0.28723
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-6 | 50-DC-57031-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2137 | Rope Access | 2014-03-29 09:30 | 2014-03-29 10:30 | [36 empty] | 6.1 | CML-6 | CML: type TBC | 3 | 2076-02-17 | 2082-11-10 | 2014-03-29 09:30 | 2.5 | 0.04844 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57031B-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.3 | 6.3 | 6.3 | 0.4
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-10 | 50-CG-38452-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1724 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.475 | CML-10 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.7 | 7.7 | 7.1 | 7.4 | 0.28723
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-7 | 50-DC-57031-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2138 | Rope Access | 2014-03-29 09:30 | 2014-03-29 10:30 | [36 empty] | 5.625 | CML-7 | CML: type TBC | 3 | 2076-02-17 | 2082-11-10 | 2014-03-29 09:30 | 2.5 | 0.04844 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57031B-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 5.8 | 5.6 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57031-01C02 | CML-3 | 50-DC-57031-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2134 | Rope Access | 2014-03-29 09:30 | 2014-03-29 10:30 | [36 empty] | 7.5667 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-29 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 12 O'Clock | 50 | 5.54 | 50-DC-57031B-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.7 | 7.7 |  | 0.23094
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-21 | 150-WC-40002-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 20360 | Reviewed on 18/11/14. Line is FFS. Repeat on Oct.19 | 2014-10-09 07:00 | 2014-10-09 15:00 | Check Corrosion Rate of 0.376mm/ yr |  | Nestor | 2014-11-24 10:29 | [32 empty] | 7.325 | CML-21 | CML: Pipe Length | 3 | 2025-09-03 | 2024-09-17 | 2014-10-09 07:00 | 2.5 | 0.37584 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 12 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.6 | 7.3 | 7.8 | 0.5252
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-1 | 50-FG-45302-01C02 CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 5769 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 5.325 | CML-1 | CML: Elbow | 3 | 2019-05-22 | 2020-01-11 | 2014-06-23 11:00 | 2.5 | 0.5087 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.7 | 5.3 | 5.3 | 0.28723
PG06 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PG-23008-15S01-A | CML-12 | 200-PG-23008-15S01-A CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20258 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | Check Corrosion Rate of 0.388mm/ yr | [35 empty] | 5.475 | CML-12 | CML: type TBC | 3 | 2021-02-09 | 2022-01-02 | 2014-06-02 13:00 | 2.5 | 0.38836 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.8 | 5.5 | 5.1 | 5.5 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-5 | 250-PW-44007-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23138 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 6.075 | CML-5 | CML: Fitting | 3 | 2030-01-02 | 2029-11-19 | 2015-05-10 07:00 | 2.5 | 0.2319 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 0.2672 | 5.9 | 6.3 | 6 | 6.1 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56065-01C02 | CML-1 | 50-DH-56065-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3409 | Rope Access | 2014-05-11 09:30 | 2014-05-11 11:00 | [36 empty] | 5.975 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-11 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56065-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 5.6 | 6 | 6.3 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-35 | 250-PW-44006-01X01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 23206 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.025 | CML-35 | CML: Pipe Length | 3 | 2030-01-11 | 2029-11-28 | 2015-05-11 07:00 | 2.5 | 0.23157 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 1.3161 | 5.9 | 6.1 | 6.1 | 6 | 0.095743
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57046-01C02 | CML-2 | 50-DC-57046-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1448 | Rope access | 2014-04-08 13:30 | 2014-04-08 14:00 | Check Corrosion Rate of 0.398mm/ yr | [35 empty] | 5.45 | CML-2 | CML: type TBC | 3 | 2021-01-15 | 2021-11-10 | 2014-04-08 13:30 | 2.5 | 0.39831 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DC-57046-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.5 | 5.2 | 5.6 | 0.17321
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-22 | 200-PL-20034-03C02-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21619 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 9.45 | CML-22 | CML: Elbow | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 9 | 9 O'Clock | 250 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.39 |  | 9.6 | 9.7 | 9.5 | 9 | 0.31091
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-11 | 50-PL-24003-09C02 CML-11 | yes | FPSO 2014 | Pipe Wall Thickness | 13150 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 9.05 | CML-11 | CML: type TBC | 3 | 2018-02-15 | 2016-11-25 | 2014-01-18 13:00 | 2.5 | 1.3242 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 7.9 | 6 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 10.5 | 8.3 | 7.9 | 9.5 | 1.1818
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-15 | 25-FG-45455-01C02-E CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2457 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 6.375 | CML-15 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 6.4 | 6 | 6.7 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43306-01C02 | CML-5 | 80-FH-43306-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5764 | Rope access | 2014-06-23 09:30 | 2014-06-23 11:00 | [36 empty] | 5.175 | CML-5 | CML: Elbow | 3 | 2021-01-09 | 2020-01-20 | 2014-06-23 09:30 | 0.54 | 0.65011 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 4.8 | 12 O'Clock | 80 | 5.49 | 80-FH-43306-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.26 |  | 4.8 | 5.2 | 5.2 | 5.5 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43135-01C02 | CML-2 | 200-FH-43135-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7850 | Line is FFS. Current RBI frequency is 48m. Action: CML’s to Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-08 13:39 | [32 empty] | 7.325 | CML-2 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 6 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.3 | 7.3 | 7 | 7.7 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43110-01C02 | CML-7 | 200-FH-43110-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12798 |  | 2014-01-18 13:30 | 2014-01-18 14:30 | [36 empty] | 8.125 | CML-7 | CML: type TBC | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 13:30 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.8 | 6 O'Clock | 200 | 6.35 | 200-FH-43110-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.46 |  | 8.5 | 8.1 | 7.8 | 8.1 | 0.28723
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57046-01C02 | CML-3 | 50-DC-57046-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1449 | Rope access | 2014-04-08 13:30 | 2014-04-08 14:00 | [36 empty] | 5.775 | CML-3 | CML: type TBC | 3 | 2031-12-09 | 2033-12-04 | 2014-04-08 13:30 | 2.5 | 0.16401 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DC-57046-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.4 | 5.9 | 5.9 | 0.25
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20012-01C02-P | CML-3 | 200-PL-20012-01C02-P CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 21205 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 9.05 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20012-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9.5 | 8.6 | 10.2 | 7.9 | 1.0083
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-11 | 50-DN-56101-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 851 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 8.5333 | CML-11 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-02 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.2 | 12 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 9.1 | 8.3 |  | 0.49329
FH01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FH-43141-01C02 | CML-5 | 150-FH-43141-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23292 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.825 | CML-5 | CML: Pipe Length | 3 | 2016-05-20 | 2016-09-13 | 2015-07-04 09:30 | 2.5 | 1.0232 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 | 0.427 | 4 | 3.9 | 4 | 3.4 | 0.28723
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-44 | 150-FH-43141-01C02 CML-44 | yes | FPSO 2015 | Pipe Wall Thickness | 6030 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.575 | CML-44 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 4 | 3.4 | 3.5 | 0.28723
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57046-01C02 | CML-1 | 50-DC-57046-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1447 | Rope access | 2014-04-08 13:30 | 2014-04-08 14:00 | [36 empty] | 5.9 | CML-1 | CML: type TBC | 3 | 2031-12-09 | 2033-12-04 | 2014-04-08 13:30 | 2.5 | 0.16401 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DC-57046-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.4 | 5.9 | 6.3 | 0.37417
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43072-01C02 | CML-3 | 50-FL-43072-01C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 22255 | Deck Level | 2014-05-01 13:00 | 2014-05-01 14:00 | [36 empty] | 5.075 | CML-3 | CML: Elbow | 3 | 2016-10-01 | 2017-02-04 | 2014-05-01 13:00 | 2.48 | 0.91648 | A2: Right Quadrant |  | 2.54 | 2.48 | 2.1637 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FL-43072-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.22 |  | 5.1 | 4.7 | 5.4 | 5.1 | 0.28723
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43072-01C02 | CML-3 | 50-FL-43072-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2976 | Deck Level | 2014-05-01 13:00 | 2014-05-01 14:00 | [36 empty] | 5.075 | CML-3 | CML: Elbow | 3 | 2016-10-01 | 2017-02-04 | 2014-05-01 13:00 | 2.48 | 0.91648 | A2: Right Quadrant |  | 2.54 | 2.48 | 2.1637 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FL-43072-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.22 |  | 5.1 | 4.7 | 5.4 | 5.1 | 0.28723
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-2 | 250-PW-44004-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22746 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 6.15 | CML-2 | CML: Pipe Length | 3 | 2029-09-30 | 2029-08-18 | 2015-04-29 07:00 | 2.5 | 0.23555 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 0.11671 | 6.5 | 6 | 6.2 | 5.9 | 0.26458
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-5 | 200-PW-44021-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23020 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 7.7 | CML-5 | CML: Elbow | 3 | 2034-08-06 | 2034-06-10 | 2015-05-05 07:00 | 2.5 | 0.18165 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 3.442 | 6 | 7.8 | 8.7 | 8.3 | 1.1916
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-25 | 250-PW-44006-01X01 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 1922 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.475 | CML-25 | CML: Elbow | 3 | 2022-05-26 | 2022-05-02 | 2014-03-26 07:00 | 2.5 | 0.42827 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6.9 | 6.9 | 0.49244
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57052-01C02 | CML-1 | 50-DC-57052-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1444 | Rope access | 2014-04-08 13:00 | 2014-04-08 13:30 | [36 empty] | 6.975 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-08 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-DC-57052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.3 | 6.3 | 6.8 | 7.5 | 0.53774
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-8 | 300-PF-20501-03C03-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23529 | Re-check | 2015-07-29 07:00 | 2015-07-29 12:00 | [36 empty] | 14.225 | CML-8 | CML: Pipe Length | 6 | 2088-04-24 | 2074-11-05 | 2015-07-29 07:00 | 4.9 | 0.12502 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 | -0.96053 | 14.6 | 14.3 | 14 | 14 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-3 | 200-PW-44021-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7700 | Re-check. CR reported in 2013 was 4.37. It appears that it was an error. Point need to be rechecked | 2015-01-08 15:30 | 2015-01-08 16:30 |  |  | Administrator | 2015-09-04 14:22 | [32 empty] | 6.625 | CML-3 | CML: Elbow | 3 | 2031-01-31 | 2030-12-14 | 2015-01-08 15:30 | 2.5 | 0.21776 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | -0.68763 | 6 | 7 | 6.5 | 7 | 0.47871
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-21 | 25-FG-45455-01C02-E CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 12640 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.325 | CML-21 | CML: type TBC | 3 | 2016-06-27 | 2016-10-26 | 2014-01-23 10:00 | 2.5 | 0.98809 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 5.5 | 5.5 | 4.9 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-10 | 250-PW-44006-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1907 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.325 | CML-10 | CML: Pipe Length | 3 | 2022-05-26 | 2022-05-02 | 2014-03-26 07:00 | 2.5 | 0.42827 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.8 | 6.4 | 6 | 6.1 | 0.3594
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-1 | 50-WC-40028-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1681 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 7.1 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 12 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.4 | 6.8 | 7.6 | 0.4761
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57052-01C02 | CML-3 | 50-DC-57052-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1446 | Rope access | 2014-04-08 13:00 | 2014-04-08 13:30 | [36 empty] | 6.9 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-08 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-DC-57052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 6.5 | 6.9 | 7.2 | 0.29439
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45038-03C02 | CML-2 | 150-FG-45038-03C02 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24343 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.125 | CML-2 | CML: Fitting | 3 | 2047-04-26 | 2041-05-25 | 2016-06-06 07:00 | 2.5 | 0.13589 | A3: Inside Quadrant |  | 4.11 | 2.5 | 3.305 | 6.7 | 6 O'Clock | 150 | 7.11 | 150-FG-45038-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.3 | 7.3 | 6.7 | 7.2 | 0.28723
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML5 | 150-FL-43174-01C02 CML5 |  | FPSO 2015 | Pipe Wall Thickness | 7344 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 3.875 | CML5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4.1 | 4.1 | 3.8 | 3.5 | 0.28723
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-27 | 50-DH-56137-01C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 21111 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 4.775 | CML-27 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 4.4 | 6 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5 | 4.7 | 4.4 | 5 | 0.28723
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57058-06C02 | CML-3 | 50-DC-57058-06C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10344 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 1.209mm/ yr | [35 empty] | 8.325 | CML-3 | CML: Reducer | 3 | 2018-07-28 | 2017-09-07 | 2013-11-11 | 2.5 | 1.2092 | A4: Left Quadrant |  | 5.74 | 2.5 | 3.5737 | 8.2 | 9 O'Clock | 50 | 8.74 | 50-DC-57058-06C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.4 | 8.4 | 8.3 | 8.2 | 0.095743
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-21 | 50-FG-45021-03C02 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10549 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.125 | CML-21 | CML: type TBC | 3 | 2015-01-30 | 2015-01-26 | 2013-11-16 | 2.5 | 1.825 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.2 | 5.3 | 5.3 | 0.28723
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56120-01C02 | CML-2 | 50-DH-56120-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21034 | Rope Access | 2014-05-19 08:00 | 2014-05-19 09:00 | [36 empty] | 5.325 | CML-2 | CML: type TBC | 3 | 2017-12-30 | 2018-06-28 | 2014-05-19 08:00 | 2.5 | 0.66301 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56120-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.5 | 4.9 | 5.4 | 5.5 | 0.28723
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-18 | 50-FG-45302-01C02 CML-18 | Yes | FPSO 2014 | Pipe Wall Thickness | 5786 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 5.375 | CML-18 | CML: Reducer | 3 | 2019-05-22 | 2020-01-11 | 2014-06-23 11:00 | 2.5 | 0.5087 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.3 | 5.6 | 5.6 | 0.28723
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-3 | 50-FG-45023-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12989 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 5.425 | CML-3 | CML: type TBC | 3 | 2017-01-04 | 2017-05-25 | 2014-01-20 07:00 | 2.5 | 0.84487 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.6 | 5.5 | 5.6 | 0.28723
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1971 |  | 2014-03-26 13:00 | 2014-03-26 14:00 | [36 empty] | 5.825 | CML-2 | CML: type TBC | 3 | 2031-03-01 | 2033-01-25 | 2014-03-26 13:00 | 2.5 | 0.17117 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56105-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6 | 6 | 5.9 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-5 | 250-PW-44006-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1902 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.3 | CML-5 | CML: Fitting | 3 | 2022-05-26 | 2022-05-02 | 2014-03-26 07:00 | 2.5 | 0.42827 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6.6 | 6.5 | 0.29439
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-16 | 250-PW-44004-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 22760 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 19.55 | CML-16 | CML: Reducing Tee | 3 | 2029-09-30 | 2029-08-18 | 2015-04-29 07:00 | 2.5 | 0.23555 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 3 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 0 | 6 | 5.9 | 6 | 6.3 | 0.17321
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-5 | 50-DH-56013-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1854 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 5.925 | CML-5 | CML: type TBC | 3 | 2084-01-09 | 2091-08-08 | 2014-05-06 08:00 | 2.5 | 0.04303 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.1 | 6.1 | 6 | 0.28723
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-5 | 50-DH-56013-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22334 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 5.925 | CML-5 | CML: type TBC | 3 | 2084-01-09 | 2091-08-08 | 2014-05-06 08:00 | 2.5 | 0.04303 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.1 | 6.1 | 6 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43123-01C02 | CML-1 | 50-FH-43123-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1777 |  | 2014-04-28 14:30 | 2014-04-28 15:00 | [36 empty] | 5.675 | CML-1 | CML: Fitting | 3 | 2082-05-31 | 2089-10-26 | 2014-04-28 14:30 | 2.5 | 0.04403 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-FH-43123-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 6.1 | 5.5 | 5.5 | 0.28723
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-16 | 25-FG-45455-01C02-E CML-16 |  | FPSO 2016 | Pipe Wall Thickness | 24361 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.875 | CML-16 | CML: Elbow | 3 | 2027-01-27 | 2026-12-21 | 2016-06-06 07:00 | 2.5 | 0.28171 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 3 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.1 | 5.5 | 6.1 | 5.8 | 0.28723
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-5 | 200-PL-20010-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 23805 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.65 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9.1 | 8.4 | 9.2 | 7.9 | 0.61373
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38455-01C02-H | CML-5 | 50-CG-38455-01C02-H CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23689 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 6.275 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 80 | 5.54 | 50-CG-38455-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.5 | 6.5 | 5.9 | 0.28723
FG02 | Montara_Topside | Yes | Potable Water (53) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8142 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.425 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.6 | 6 | 6.6 | 6.5 | 0.28723
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H |  | 50-CG-38454-01C02-H |  | FPSO 2015 | Pipe Wall Thickness | 23680 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 6.375 | 50-CG-38454-01C02-H | Piping | 3 | 2043-10-24 |  | 2015-10-30 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.2 | 9 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.8 | 6.2 | 6.3 | 6.2 | 0.28723
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57052-01C02 | CML-2 | 50-DC-57052-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1445 | Rope access | 2014-04-08 13:00 | 2014-04-08 13:30 | [36 empty] | 7.1 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-08 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.9 | 9 O'Clock | 50 | 5.54 | 50-DC-57052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7 | 7.4 | 7.1 | 6.9 | 0.21602
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-27 | 50-CG-38452-09C02-P CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 1303 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.375 | CML-27 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 9 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.3 | 7.8 | 7.2 | 7.2 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43156-01C02 | CML-1 | 80-FH-43156-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10719 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 7.775 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2013-11-19 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.4 | 12 O'Clock | 80 | 5.49 | 80-FH-43156-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 8 | 8 | 7.7 | 0.28723
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43300-01C02-E | CML-1 | 200-PL-43300-01C02-E CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 8587 | Line is FFS. Current RBI frequency is 36m. Action: CML’s to Inspect in 48m. RBI to be updated | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-08 14:53 | [32 empty] | 6.85 | CML-1 | CML: Elbow | 3 | 2069-11-17 | 2063-01-09 | 2015-02-08 11:00 | 1.34 | 0.08867 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.2 | 12 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 6.2 | 7.4 | 6.6 | 7.2 | 0.55076
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-3 | 200-PL-20010-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 23803 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.625 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 12 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.4 | 9.3 | 8.9 | 0.60759
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20017-01C02-P | CML-5 | 200-PL-20017-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21244 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.45 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20017-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9 | 8.7 | 8.2 | 7.9 | 0.49329
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-15 | 80-FH-43007-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12576 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 6.075 | CML-15 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-01-18 07:00 | 0.54 | 0 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.9 | 9 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.36 |  | 6 | 6.5 | 5.9 | 5.9 | 0.28723
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-6 | 100-FG-45001-09C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10421 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.275 | CML-6 | CML: type TBC | 3 | 2016-03-27 | 2015-06-26 | 2013-11-13 | 4.7 | 2.2785 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.1 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 10.7 | 10.1 | 10.1 | 10.2 | 0.28723
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-19 | 200-PL-20010-01C02-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 23819 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.525 | CML-19 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.4 | 9 | 8.8 | 7.9 | 0.48563
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-6 | 400-FH-43508-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6555 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.575 | CML-6 | CML: Pipe Length | 3 | 2062-08-12 | 2057-12-18 | 2015-03-30 07:00 | 3 | 0 | A2: Right Quadrant |  | 4.92 | 3 | 3.465 | 9.4 | 6 O'Clock | 500 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.5 | 9.4 | 9.4 | 10 | 0.28723
FL02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FL-43454-01C02-P | CML-10 | 50-FL-43454-01C02-P CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10450 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.025 | CML-10 | CML: type TBC | 6 | 2016-06-26 | 2016-02-21 | 2013-11-13 | 0.99 | 2.5218 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.6 | 12 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.61 |  | 7.6 | 8.2 | 8.1 | 8.2 | 0.28723
PL03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PL-57066-01C03 | CML-4 | 50-PL-57066-01C03 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22748 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 9.725 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-04-29 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | 0.35012 | 9.9 | 9.9 | 9.8 | 9.3 | 0.28723
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-14 | 50-PL-23041-06C03 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10227 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.525 | CML-14 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 2.2128 | A4: Left Quadrant |  | 5.07 |  |  | 10.1 | 9 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.7 | 10.7 | 10.6 | 10.1 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43127-01C02 | CML-4 | 150-FH-43127-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1797 | Rope access | 2014-04-28 10:30 | 2014-04-28 12:00 | [36 empty] | 7.875 | CML-4 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-28 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 12 O'Clock | 150 | 7.11 | 150-FH-43127-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8.2 | 7.9 | 7.9 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-9 | 250-PW-44006-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23180 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.35 | CML-9 | CML: Elbow | 3 | 2034-10-11 | 2034-08-15 | 2015-05-11 07:00 | 2.5 | 0.18011 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 1.3161 | 6 | 6.5 | 6.5 | 6.4 | 0.23805
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-5 | 350-FL-43511-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2286 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 7.975 | CML-5 | CML: type TBC | 3 | 2026-10-31 | 2025-01-23 | 2014-03-17 08:00 | 2.5 | 0.40369 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.6 | 12 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 7.9 | 8.2 | 8.2 | 0.28723
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-9 | 250-PG-20036-01C03-P CML-9 | Yes | FPSO 2016 | Pipe Wall Thickness | 24414 | Re-check as requested by N.Sequera | 2016-07-06 07:00 | 2016-07-06 15:00 | Check Corrosion Rate of 0.442mm/ yr | 41 | Kirstie Albone | 2017-03-23 15:13 | [32 empty] | 8.275 | CML-9 | CML: Elbow | 6 | 2028-09-20 | 2027-11-07 | 2016-07-06 07:00 | 2.5 | 0.44202 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.9 | 12 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 0.10399 | 7.9 | 8.6 | 8.3 | 8.3 | 0.28723
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-6 | 50-CG-38454-01C02-H CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 23670 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.625 | CML-6 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 9 O'Clock | 100 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.7 | 9 | 8.4 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5583 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 6.175 | CML-6 | CML: Elbow | 3 | 2024-12-17 | 2024-11-17 | 2014-06-19 10:30 | 2.5 | 0.33317 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.4 | 6 | 6.1 | 0.17078
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-12 | 50-FL-43454-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1884 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.475 | CML-12 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.4 | 9.1 | 9.7 | 9.7 | 0.28723
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40038-01C02 | CML-4 | 200-WC-40038-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7712 |  | 2015-01-09 10:00 | 2015-01-09 12:00 | [36 empty] | 6.925 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-09 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 12 O'Clock | 200 | 6.35 | 200-WC-40038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.5 | 6.7 | 6.9 | 0.40311
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-2 | 300-PG-23001-03C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10952 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.475 | CML-2 | CML: Elbow | 6 | 2045-10-09 | 2040-04-26 | 2014-01-09 | 5.22 | 0.2795 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 14.1 | 6 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.88 |  | 14.7 | 14.4 | 14.1 | 14.7 | 0.28723
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-1 | 50-DC-57069-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1344 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.3 | CML-1 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 4.8 | 12 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.4 | 5.3 | 5.7 | 0.37417
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-9 | 50-DC-57069-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1352 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.3 | CML-9 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 4.9 | 9 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.3 | 6 | 4.9 | 0.49666
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-14 | 150-PG-20054-01C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21525 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 11.775 | CML-14 | CML: Reducer | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 11.4 | 3 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.8 | 11.4 | 12.1 | 11.8 | 0.28723
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-18 | 200-PL-20019-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21269 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 8.5 | CML-18 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.9 | 8.5 | 8.7 | 0.43205
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43155-01C02 | CML-3 | 80-FH-43155-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10716 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.275 | CML-3 | CML: type TBC | 3 | 2015-10-10 | 2016-01-18 | 2013-11-18 | 2.5 | 1.2668 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-FH-43155-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 5.3 | 5.6 | 0.28723
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56106-01C02 | CML-5 | 80-DH-56106-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2031 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 5.225 | CML-5 | CML: type TBC | 3 | 2017-07-28 | 2018-01-21 | 2014-03-27 14:30 | 2.5 | 0.71878 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 9 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 5.2 | 5.2 | 4.9 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43118-01C02 | CML-2 | 50-FH-43118-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1757 | Rope access | 2014-04-27 08:00 | 2014-04-27 08:30 | [36 empty] | 5.225 | CML-2 | CML: Elbow | 3 | 2017-09-17 | 2018-03-04 | 2014-04-27 08:00 | 2.5 | 0.70716 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FH-43118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.2 | 5.2 | 5.6 | 0.28723
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-11 | 50-DC-57069-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1354 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.475 | CML-11 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5 | 6 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6 | 5.5 | 5 | 5.4 | 0.4113
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-6 | 50-DC-57069-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1349 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.45 | CML-6 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5 | 9 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 6.7 | 5 | 5 | 0.83467
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-10 | 50-DC-57069-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1353 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.45 | CML-10 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5.3 | 9 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.3 | 5.6 | 5.3 | 0.17321
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-7 | 50-DC-57069-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1350 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.5 | CML-7 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.3 | 6 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.5 | 5.3 | 5.4 | 0.21602
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12967 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.725 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 3 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.1 | 6.4 | 6.7 | 6.7 | 0.28723
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-4 | 50-FG-45024-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1208 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.725 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 7.1 | 6.4 | 6.7 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-20 | 200-FH-43025-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 2493 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 7.225 | CML-20 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 3 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.2 | 6.9 | 7.6 | 7.2 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43407-01C02 | CML-2 | 150-FH-43407-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7948 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-18 07:00 | 2015-01-18 08:00 |  |  | Administrator | 2015-09-08 13:27 | [32 empty] | 7.225 | CML-2 | CML: Elbow | 3 | 2049-04-03 | 2046-06-14 | 2015-01-18 07:00 | 2.5 | 0.12854 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.9 | 3 O'Clock | 150 | 7.11 | 150-FH-43407-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.2 | 6.9 | 7.2 | 7.6 | 0.28723
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-4 | 200-PL-20020-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21308 | Reading on larger diameter | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 8.2 | CML-4 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 6 O'Clock | 150 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.6 | 7.9 | 7.9 | 8.4 | 0.3559
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DN-56L9004-AC21M-00 | CML-1 | 0200-DN-56L9004-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5068 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.95 | CML-1 | CML: type TBC | 3 | 2043-08-30 | 2038-05-22 | 2015-03-06 07:00 | 2.5 | 0.20347 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 8.3 | 12 O'Clock | 50 | 8.74 | 0200-DN-56L9004-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.8 | 9.5 | 9.2 | 0.51962
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-19 | 50-AI-63005-01E01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8895 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 9.1 | CML-19 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.3 | 6 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.2 | 9.2 | 8.3 | 9.7 | 0.5831
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-20 | 50-AI-63005-01E01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 8896 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 8.5 | CML-20 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.3 | 3 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.5 | 8.3 | 8.6 | 8.6 | 0.14142
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-16 | 150-PG-23506-25C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2790 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.275 | CML-16 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.1 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.22 |  | 22.1 | 22.2 | 22.7 | 22.1 | 0.28723
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-14 | 50-DH-56137-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 6170 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 20.475 | CML-14 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 20.3 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 |  | 20.9 | 20.3 | 20.4 | 20.3 | 0.28723
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-25 | 200-PG-23065-09C02-A CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 439 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.675 | CML-25 | CML: Pipe Length | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 19.2 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.03 |  | 19.5 | 19.2 | 20 | 20 | 0.39476
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45024-01C02 | CML-3 | 50-FG-45024-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5835 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 9.6 | CML-3 | CML: Pipe Length | 6 | 2116-04-19 | 2110-06-13 | 2014-06-24 13:00 | 2.5 | 0.06576 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.2 | 6 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.8 | 9.8 | 9.2 | 9.6 | 0.28284
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-24 | 100-PW-20021-01C02-P CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 22842 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 6.25 | CML-24 | CML: Reducing Tee | 3 | 2349-11-26 | 2361-01-06 | 2015-04-30 07:00 | 2.5 | 0.01045 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 0 | 6.1 | 6 | 6.7 | 6.2 | 0.31091
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44029-01C02 | CML-4 | 250-PW-44029-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22901 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 6.225 | CML-4 | CML: Reducing Tee | 3 | 2034-06-23 | 2034-04-28 | 2015-05-01 07:00 | 2.5 | 0.18268 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 3.9752 | 6.4 | 6.5 | 6 | 6 | 0.263
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57404-01C03 | CML-1 | 50-DC-57404-01C03 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8374 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9 | CML-1 | CML: type TBC | 6 | 2036-12-29 | 2036-07-17 | 2015-01-29 07:30 | 2.5 | 0.26444 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 3 O'Clock | 50 | 8.74 | 50-DC-57404-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.1 | 8.3 | 8.7 | 9.9 | 0.68313
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PL-57403-01C03 |  | 50-PL-57403-01C03 |  | FPSO 2015 | Pipe Wall Thickness | 8368 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.65 | 50-PL-57403-01C03 | Piping | 6 | 2036-12-29 |  | 2015-01-29 07:30 |  | 0.26444 | A1: Outside Quadrant |  |  | 2.5 |  | 8.3 | 12 O'Clock | 50 | 8.74 | Pipework | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.5 | 10.6 | 10.2 | 1.0083
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57400-01C03 | CML-5 | 50-DC-57400-01C03 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8355 |  | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 8.475 | CML-5 | CML: type TBC | 6 | 2036-12-15 | 2036-07-03 | 2015-01-28 07:30 | 2.5 | 0.26488 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 6 O'Clock | 50 | 8.74 | 50-DC-57400-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.7 | 8.5 | 8.3 | 8.4 | 0.17078
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57400-01C03 | CML-3 | 50-DC-57400-01C03 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8353 |  | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 8.475 | CML-3 | CML: type TBC | 6 | 2036-12-15 | 2036-07-03 | 2015-01-28 07:30 | 2.5 | 0.26488 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-DC-57400-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.5 | 8.6 | 8.5 | 8.3 | 0.12583
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57303-03C03 | CML-7 | 20-DC-57303-03C03 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7932 |  | 2015-01-17 10:30 | 2015-01-17 12:00 | [36 empty] | 9.05 | CML-7 | CML: type TBC | 6 | 2044-01-06 | 2058-09-17 | 2015-01-17 10:30 | 2.5 | 0 | A4: Left Quadrant |  | -0.44 | 2.5 | 1.03 | 8.3 | 9 O'Clock | 20 | 5.56 | 20-DC-57303-03C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9 | 9.5 | 9.4 | 8.3 | 0.54467
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-22 | 150-WC-40002-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 20361 | Reviewed on 18/11/14. Line is FFS. Repeat on Oct.19 | 2014-10-09 07:00 | 2014-10-09 15:00 | Check Corrosion Rate of 0.376mm/ yr |  | Nestor | 2014-11-24 10:29 | [32 empty] | 7.15 | CML-22 | CML: Pipe Length | 3 | 2025-09-03 | 2024-09-17 | 2014-10-09 07:00 | 2.5 | 0.37584 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 12 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.3 | 7.4 | 7.3 | 0.36968
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45052-03C02 | CML-2 | 150-FG-45052-03C02 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24332 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.2 | CML-2 | CML: Elbow | 3 | 2024-01-10 | 2022-03-04 | 2016-06-06 07:00 | 2.5 | 0.43417 | A3: Inside Quadrant |  | 4.11 | 2.5 | 3.305 | 5.8 | 6 O'Clock | 150 | 7.11 | 150-FG-45052-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.2 | 5.8 | 6.4 | 0.28284
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-2 | 200-PW-44020-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5592 |  | 2014-06-19 14:00 | 2014-06-19 15:00 | [36 empty] | 6.2 | CML-2 | CML: Reducing Tee | 3 | 2024-12-19 | 2024-11-18 | 2014-06-19 14:00 | 2.5 | 0.33304 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.4 | 6.2 | 6.2 | 0.1633
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-22 | 250-FH-43303-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 12960 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.5 | CML-22 | CML: type TBC | 3 | 2023-07-21 | 2023-06-24 | 2014-01-27 10:00 | 2.5 | 0.37955 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.5 | 6.7 | 6.7 | 0.28284
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57048-03C02 | CML-4 | 50-DC-57048-03C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7616 |  | 2015-01-07 07:00 | 2015-01-07 08:00 | [36 empty] | 8.9 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2015-01-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 8.3 | 12 O'Clock | 50 | 5.54 | 50-DC-57048-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.1 | 8.9 | 9.3 | 0.43205
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-3 | 50-DC-57069-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1346 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.65 | CML-3 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.3 | 12 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.6 | 5.6 | 6.1 | 0.33166
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-2 | 50-DC-57069-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1345 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.6 | CML-2 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.3 | 12 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.5 | 5.8 | 5.8 | 0.24495
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-13 | 150-WC-40004-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1815 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | Check Corrosion Rate of 0.56mm/ yr | [35 empty] | 7.075 | CML-13 | CML: Reducer | 3 | 2021-08-23 | 2020-12-31 | 2014-04-29 11:00 | 2.5 | 0.55992 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.2 | 7.1 | 6.6 | 7.4 | 0.34034
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43513-01C02 | CML-4 | 50-FL-43513-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 7986 | Line is FFS. Current RBI frequency is 48m Action: to recheck line in 24m (Jan. 2017) to confirm CR. RBI frequency to be updated | 2015-01-18 16:00 | 2015-01-18 17:00 |  |  | Administrator | 2015-09-07 14:59 | [32 empty] | 5.1 | CML-4 | CML: Elbow | 3 | 2021-03-05 | 2022-01-03 | 2015-01-18 16:00 | 2.5 | 0.39151 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-FL-43513-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 4.9 | 5.5 | 5.1 | 0.28284
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-4 | 100-FH-43507-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7753 |  | 2015-01-11 08:00 | 2015-01-11 09:00 | [36 empty] | 5.1 | CML-4 | CML: type TBC | 3 | 2021-01-29 | 2021-11-25 | 2015-01-11 08:00 | 2.5 | 0.39638 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-FH-43507-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 4.9 | 5.5 | 5.1 | 0.28284
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23415-01C03 | CML-3 | 100-PG-23415-01C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20783 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.75 | CML-3 | CML: type TBC | 6 | 2017-08-28 | 2017-01-14 | 2014-10-02 07:00 | 2.5 | 1.9958 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 8.3 | 3 O'Clock | 150 | 10.97 | 150-PG-23415-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.8 | 8.3 | 9 | 8.9 | 0.31091
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43146-01C02 | CML-4 | 80-FH-43146-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10557 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.2 | CML-4 | CML: type TBC | 3 | 2016-03-22 | 2016-07-19 | 2013-11-16 | 2.5 | 1.0646 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-FH-43146-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.6 | 5 | 5 | 0.28284
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-11 | 200-FH-43038-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12692 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 6.4 | CML-11 | CML: type TBC | 3 | 2031-01-04 | 2030-11-18 | 2014-02-06 09:00 | 2.5 | 0.21867 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.4 | 6.2 | 6.8 | 0.28284
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-4 | 50-DC-57069-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1347 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.45 | CML-4 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.4 | 9 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.6 | 5.4 | 0.1
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-8 | 50-DC-57069-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1351 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.775 | CML-8 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.5 | 12 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.8 | 5.8 | 6 | 0.20616
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-5 | 50-DC-57069-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1348 | Rope access | 2014-04-04 09:30 | 2014-04-04 10:45 | [36 empty] | 5.575 | CML-5 | CML: type TBC | 3 |  |  | 2014-04-04 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.5 | 12 O'Clock | 50 |  | 50-DC-57069-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 5.6 | 5.6 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57069-01C02 | CML-1 | 50-DC-57069-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7992 |  | 2015-01-19 13:00 | 2015-01-19 14:00 | Check Corrosion Rate of 0.898mm/ yr | [35 empty] | 10.325 | CML-1 | CML: type TBC | 6 | 2022-08-10 | 2021-05-08 | 2015-01-19 13:00 | 2.81 | 0.89793 | A4: Left Quadrant |  | 5.07 | 2.81 | 3.94 | 9.6 | 9 O'Clock | 50 | 11.07 | 50-DC-57306-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.79 |  | 10.8 | 10 | 10.9 | 9.6 | 0.62915
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 24270 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 9.8 | CML-1 | CML: Elbow | 3 | 2018-09-01 | 2017-11-14 | 2014-09-24 07:00 | 4.7 | 1.1931 | A1: Outside Quadrant |  | 7.97 | 4.7 | 5.6494 | 9.4 | 12 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 9.4 | 9.8 | 10 | 10 | 0.28284
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-5 | 50-PL-23515-01C03 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8654 | Line is FFS despite the High CR. They are all in the same spool. Current RBI frequency is 48m. RBI frequency to stay at 48m. Action: to recheck CML-1 to 6 in a year to confirm CR. RBI frequency to stay at 48m | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:50 | [32 empty] | 8.4 | CML-5 | CML: Pipe Length | 6 | 2027-10-05 | 2027-06-26 | 2015-02-12 07:00 | 2.5 | 0.43474 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.4 | 8.6 | 8.6 | 8 | 0.28284
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40402-01C02 | CML-3 | 100-WC-40402-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20376 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.925 | CML-3 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 6 O'Clock | 100 | 6.02 | 100-WC-40402-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.3 | 6.7 | 6.6 | 7.1 | 0.3304
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-13 | 25-DO-62007-15S01 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2638 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [35 empty] | Low alarm breach | 6.775 | CML-13 | CML: Reducer | 1 | 2014-12-19 | 2014-05-15 | 2014-04-29 09:30 | 4.41 | 2.7891 | A2: Right Quadrant |  | 7.74 | 4.41 | 6.075 | 6.2 | 3 O'Clock | 25 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.79 |  | 7 | 6.2 | 6.9 | 7 | 0.38622
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML 6 | 200-PW-44021-01X01 CML 6 |  | FPSO 2014 | Pipe Wall Thickness | 22370 |  | 2014-06-19 13:00 | 2014-06-19 14:00 | [36 empty] | 6.325 | CML 6 | CML: Fitting | 3 | 2029-08-02 | 2029-06-20 | 2014-06-19 13:00 | 2.5 | 0.23791 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 9 O'Clock | 200 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.5 | 6.6 | 6.1 | 6.1 | 0.263
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-13 | 50-FG-45023-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12999 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 9 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-01-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9 | 9.4 | 8.8 | 0.28284
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43124-01C02 | CML-1 | 80-FH-43124-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12843 |  | 2014-02-05 11:00 | 2014-02-05 13:00 | [36 empty] | 7.8 | CML-1 | CML: Reducer | 3 | 2062-11-29 | 2056-08-05 | 2014-02-05 11:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 7.6 | 6 O'Clock | 50 | 5.49 | 80-FH-43124-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.06 |  | 7.6 | 7.8 | 7.6 | 8.2 | 0.28284
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-4 | 80-PW-20024-01C03-P CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 23048 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [35 empty] | Low alarm breach | 5.85 | CML-4 | CML: Reducing Tee | 6 | 2016-01-17 | 2015-08-23 | 2015-05-06 07:00 | 2.5 | 3.2805 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 4.8 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6 | 6.1 | 4.8 | 6.5 | 0.73258
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-12 | 25-DO-62007-15S01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 6543 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [35 empty] | Low alarm breach | 9.7 | CML-12 | CML: Elbow | 1 | 2017-02-11 | 2015-09-10 | 2014-07-24 07:30 | 4.41 | 1.1692 | A4: Left Quadrant |  | 7.74 | 4.41 | 6.075 | 7.4 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.99 | 16.5684 | 9.5 | 10.1 | 11.8 | 7.4 | 1.8166
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-10 | 150-PG-20507-01C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2854 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.1 | CML-10 | CML: type TBC | 6 | 2019-08-31 | 2018-10-02 | 2014-03-16 07:00 | 2.5 | 1.3547 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 9.9 | 9 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 10.1 | 10.5 | 9.9 | 0.28284
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-7 | 300-PG-20004-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 6130 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 12.5 | CML-7 | CML: Pipe Length | 6 | 2019-08-05 | 2018-03-12 | 2014-07-11 07:30 | 3.3 | 1.7741 | A3: Inside Quadrant |  | 8.27 | 3.3 | 5.785 | 12.3 | 9 O'Clock | 200 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 12.9 | 12.5 | 12.3 | 12.3 | 0.28284
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-20 | 300-PF-20500-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21640 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.6 | CML-20 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.4 | 3 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 14.4 | 14.4 | 15 | 14.6 | 0.28284
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-8 | 250-PW-20040-03C03-P CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 23465 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 10.925 | CML-8 | CML: Elbow | 6 | 2024-12-05 | 2022-07-23 | 2015-07-24 07:00 | 2.5 | 0.88537 | A2: Right Quadrant |  | 6.7 | 2.5 | 4.6 | 10.8 | 3 O'Clock | 40 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 | -3.1951 | 11 | 10.8 | 11 | 10.9 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-13 | 50-DH-56109-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21002 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 9.025 | CML-13 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-24 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.7 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 9.2 | 8.9 | 9.3 | 0.27538
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-10 | 50-CG-38001-09C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10923 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.975 | CML-10 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0.06606 | A1: Outside Quadrant |  | 5.74 |  |  | 8.7 | 12 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.7 | 8.7 | 8.8 | 9.1 | 9.3 | 0.27538
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23032-01C03 | CML-4 | 50-PL-23032-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20788 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 8.975 | CML-4 | CML: Pipe Length | 6 | 2225-05-22 | 2221-04-24 | 2014-10-10 07:00 | 2.5 | 0.02942 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.7 | 12 O'Clock | 50 | 8.74 | 50-PL-23032-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 9.3 | 8.8 | 9.1 | 0.27538
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-8 | 150-PG-20054-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21519 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 11.025 | CML-8 | CML: Fitting | 6 | 2046-12-16 | 2042-01-25 | 2014-06-26 13:00 | 2.5 | 0.25234 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 10.7 | 9 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.9 | 11.2 | 11.3 | 10.7 | 0.27538
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-11 | 25-DO-62007-15S01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 6542 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [35 empty] | Low alarm breach | 9.675 | CML-11 | CML: Elbow | 1 | 2018-03-08 | 2016-05-07 | 2014-07-24 07:30 | 4.41 | 0.90746 | A4: Left Quadrant |  | 7.74 | 4.41 | 6.075 | 7.7 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.29 | 6.7973 | 9.2 | 9.6 | 12.2 | 7.7 | 1.8715
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-1 | 25-DO-62007-15S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6532 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:15 | [31 empty] | Low alarm breach | 7.7 | CML-1 | CML: Elbow | 1 | 2018-03-08 | 2016-05-07 | 2014-07-24 07:30 | 4.41 | 0.90746 | A1: Outside Quadrant |  | 7.74 | 4.41 | 6.075 | 7.7 | 9 O'Clock | 25 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.29 | 15.7187 | 7.7 | 7.7 | 7.7 | 7.7 | 0
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-3 | 25-DO-62007-15S01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2627 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 9.2 | CML-3 | CML: Elbow | 1 | 2018-02-08 | 2016-04-20 | 2014-04-29 09:30 | 4.41 | 0.92239 | A4: Left Quadrant |  | 7.74 | 4.41 | 6.075 | 7.9 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.49 |  | 8.8 | 10.4 | 9.7 | 7.9 | 1.0863
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-34 | 250-PW-44006-01X01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 23205 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.225 | CML-34 | CML: Pipe Length | 3 | 2043-04-28 | 2043-02-07 | 2015-05-11 07:00 | 2.5 | 0.12865 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 | 0.65803 | 6.1 | 6.2 | 6.1 | 6.5 | 0.1893
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-6 | 200-PW-44020-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5596 |  | 2014-06-19 14:00 | 2014-06-19 15:00 | [36 empty] | 6.3 | CML-6 | CML: Elbow | 3 | 2029-08-03 | 2029-06-21 | 2014-06-19 14:00 | 2.5 | 0.23789 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.1 | 6.4 | 6.5 | 0.18257
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56119-01C02 | CML-6 | 50-DH-56119-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21032 | Rope Access | 2014-05-19 09:30 | 2014-05-19 11:00 | [36 empty] | 5.075 | CML-6 | CML: type TBC | 3 | 2017-05-18 | 2017-10-21 | 2014-05-19 09:30 | 2.5 | 0.76647 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56119-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.9 | 5.2 | 5.4 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43140-01C02 | CML-2 | 50-FH-43140-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22691 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.125 | CML-2 | CML: Elbow | 3 | 2021-03-27 | 2022-01-27 | 2015-04-27 07:00 | 2.5 | 0.38847 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FH-43140-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.15839 | 4.8 | 5.3 | 5 | 5.4 | 0.27538
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-4 | 250-PW-44006-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1901 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.25 | CML-4 | CML: Pipe Length | 3 | 2025-12-28 | 2025-11-25 | 2014-03-26 07:00 | 2.5 | 0.30591 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.1 | 6.2 | 6.3 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-9 | 50-FH-43137-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12861 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 5.625 | CML-9 | CML: Elbow | 3 | 2021-08-11 | 2022-06-28 | 2014-01-23 08:00 | 2.5 | 0.37066 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.8 | 5.3 | 5.5 | 0.27538
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-8 | 250-PG-23003-06C02-PA CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 22654 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.075 | CML-8 | CML: Reducer | 3 | 2019-11-16 | 2018-12-26 | 2015-04-27 07:00 | 1.88 | 0.64045 | A4: Left Quadrant |  | 3.02 | 1.88 | 2.45 | 4.8 | 9 O'Clock | 100 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.92 |  | 5.4 | 4.9 | 5.2 | 4.8 | 0.27538
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-3 | 200-PL-20008-01C02-H CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8800 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.25 | CML-3 | CML: Fitting | 3 | 2039-04-20 | 2035-09-17 | 2015-02-21 07:00 | 1.1 | 0.20268 | A2: Right Quadrant |  | 3.35 | 1.1 | 1.8281 | 6 | 3 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 6.2 | 6 | 6.1 | 6.7 | 0.31091
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-12 | 80-PL-44008-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5749 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 7.975 | CML-12 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.9 | 9 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8 | 8 | 8 | 7.9 | 0.05
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43014-01C02 | CML-2 | 250-FL-43014-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2892 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 6.425 | CML-2 | CML: Fitting | 3 | 2027-04-05 | 2027-02-27 | 2014-04-25 08:00 | 2.5 | 0.27792 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.6 | 6.7 | 6.3 | 0.27538
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-22 | 300-FL-43070-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 12715 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.375 | CML-22 | CML: type TBC | 3 | 2023-10-05 | 2023-09-08 | 2014-02-01 09:00 | 2.5 | 0.37188 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.5 | 6.7 | 6.2 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-9 | 200-FH-43004-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12549 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 6.575 | CML-9 | CML: type TBC | 3 | 2065-02-15 | 2064-09-30 | 2014-02-01 07:00 | 2.5 | 0.0744 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.4 | 6.9 | 6.3 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43108-01C02 | CML-8 | 200-FH-43108-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12783 |  | 2014-01-18 15:30 | 2014-01-18 16:30 | [36 empty] | 6.375 | CML-8 | CML: Pipe Length | 3 | 2026-02-15 | 2024-07-31 | 2014-01-18 15:30 | 1.34 | 0.39392 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.1 | 12 O'Clock | 200 | 6.35 | 200-FH-43108-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 6.1 | 6.2 | 6.5 | 6.7 | 0.27538
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57001-01C02 | CML-2 | 80-DC-57001-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12502 |  | 2014-02-04 15:00 | 2014-02-04 16:00 | [36 empty] | 6.65 | CML-2 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-02-04 15:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 6.4 | 12 O'Clock | 80 | 5.49 | 80-DC-57001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.86 |  | 6.4 | 6.8 | 6.6 | 6.8 | 0.19149
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40069-01C02 | CML-1 | 100-WC-40069-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1710 | Rope access | 2014-04-21 07:00 | 2014-04-21 08:00 | [36 empty] | 6.775 | CML-1 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 9 O'Clock | 100 | 6.02 | 100-WC-40069-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.9 | 6.6 | 7 | 6.6 | 0.20616
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-5 | 300-PW-44003-01C03 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22870 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 12 | CML-5 | CML: Equal Tee | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.9 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | -1.8814 | 12.9 | 13.2 | 10.9 | 11 | 1.2193
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-8 | 80-PW-44034-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21990 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.75 | CML-8 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 12 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 6.9 | 7.8 | 0.78528
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-11 | 50-FG-45020-03C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2610 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.225 | CML-11 | CML: type TBC | 3 | 2017-09-12 | 2017-09-02 | 2014-04-26 09:30 | 2.5 | 0.70918 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.22756 | 5.1 | 5.5 | 4.9 | 5.4 | 0.27538
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44036-01C02-P | CML-6 | 80-PW-44036-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21958 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 6.575 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 9 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.7 | 7.4 | 6.1 | 0.61847
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40038-01C02 | CML-3 | 200-WC-40038-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7711 |  | 2015-01-09 10:00 | 2015-01-09 12:00 | [36 empty] | 6.875 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-09 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 6 O'Clock | 200 | 6.35 | 200-WC-40038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 7 | 6.6 | 6.9 | 0.1893
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3344 | Rope Access | 2014-05-08 13:00 | 2014-05-08 14:00 | [36 empty] | 5.725 | CML-2 | CML: type TBC | 3 | 2018-09-22 | 2018-11-25 | 2014-05-08 13:00 | 2.5 | 0.66258 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 3 O'Clock | 100 | 6.02 | 100-DH-56084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.4 | 6 | 5.6 | 0.27538
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-1 | 250-PW-44004-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5620 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 6.6 | CML-1 | CML: Pipe Length | 3 | 2029-08-17 | 2029-07-05 | 2014-06-20 13:00 | 2.5 | 0.2373 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7.1 | 7 | 6.1 | 6.2 | 0.52281
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-17 | 200-PL-20035-03C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21349 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 9.725 | CML-17 | CML: Equal Tee | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 9.1 | 6 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.49 |  | 9.9 | 10 | 9.1 | 9.9 | 0.41932
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-50 | 350-FL-43512-01C02 CML-50 |  | FPSO 2015 | Pipe Wall Thickness | 23561 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.725 | CML-50 | CML: Pipe Length | 3 | 2036-04-02 | 2033-03-29 | 2015-08-10 07:30 | 2.5 | 0.23716 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 3 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.9 | 7.4 | 7.6 | 8 | 0.27538
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40402-01C02 | CML-6 | 100-WC-40402-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20379 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.75 | CML-6 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 3 O'Clock | 100 | 6.02 | 100-WC-40402-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.6 | 6.9 | 6.7 | 0.1291
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-17 | 150-PG-20054-01C03-P CML-17 | Yes | FPSO 2016 | Pipe Wall Thickness | 24464 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | [36 empty] | 8.225 | CML-17 | CML: Pipe Length | 6 | 2021-12-14 | 2020-09-15 | 2016-07-05 07:00 | 2.5 | 0.99138 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 7.9 | 6 O'Clock | 100 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 0.31197 | 8.4 | 8.1 | 7.9 | 8.5 | 0.27538
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-5 | 25-DO-62007-15S01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2629 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 8.95 | CML-5 | CML: Elbow | 1 | 2018-09-27 | 2016-09-10 | 2014-04-29 09:30 | 4.41 | 0.81259 | A3: Inside Quadrant |  | 7.74 | 4.41 | 6.075 | 8 | 6 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.59 |  | 10.1 | 8.3 | 8 | 9.4 | 0.97468
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-9 | 25-DO-62007-15S01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 6540 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 9.65 | CML-9 | CML: Elbow | 1 | 2022-08-07 | 2019-01-25 | 2014-07-24 07:30 | 4.41 | 0.47118 | A4: Left Quadrant |  | 7.74 | 4.41 | 6.075 | 8.2 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.79 | 2.549 | 12 | 8.4 | 10 | 8.2 | 1.7616
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-2 | 25-DO-62007-15S01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2626 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 8.825 | CML-2 | CML: Reducer | 1 | 2022-05-16 | 2018-12-05 | 2014-04-29 09:30 | 4.41 | 0.48316 | A3: Inside Quadrant |  | 7.74 | 4.41 | 6.075 | 8.3 | 6 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.89 |  | 8.6 | 8.7 | 8.3 | 9.7 | 0.60759
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-8 | 25-DO-62007-15S01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 6539 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 10.625 | CML-8 | CML: Elbow | 1 | 2034-01-29 | 2026-02-18 | 2014-07-24 07:30 | 4.41 | 0.20941 | A4: Left Quadrant |  | 7.74 | 4.41 | 6.075 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.09 | 1.2745 | 10.5 | 12.5 | 11 | 8.5 | 1.652
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40049-01C02 | CML-4 | 50-WC-40049-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1233 |  | 2014-03-22 08:30 | 2014-03-22 09:00 | [36 empty] | 6.65 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-WC-40049-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.7 | 6.7 | 6.6 | 0.057735
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43084-01C02 | CML-2 | 150-FL-43084-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2567 | Rope Access | 2014-04-08 07:30 | 2014-04-08 08:30 | [36 empty] | 8.675 | CML-2 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-04-08 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.4 | 9 O'Clock | 150 | 7.11 | 150-FL-43084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9 | 8.8 | 8.5 | 8.4 | 0.27538
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-13 | 150-WC-40006-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1654 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 7.4 | CML-13 | CML: Elbow | 3 | 2023-02-14 | 2022-05-13 | 2014-04-12 07:30 | 2.5 | 0.47461 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 9 O'Clock | 100 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.8 | 7.7 | 8.4 | 6.7 | 0.80416
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-2 | 200-FH-43025-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2475 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 9.775 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 3 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.9 | 9.5 | 9.6 | 10.1 | 0.27538
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-6 | 300-PG-20502-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 23893 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.325 | CML-6 | CML: Pipe Length | 6 | 2046-09-06 | 2042-10-29 | 2014-09-26 07:00 | 2.5 | 0.23461 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10 | 6 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.6 | 10.5 | 10 | 10.2 | 0.27538
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-6 | 300-PG-20502-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20753 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.325 | CML-6 | CML: type TBC | 6 | 2046-09-06 | 2042-10-29 | 2014-09-26 07:00 | 2.5 | 0.23461 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10 | 6 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.6 | 10.5 | 10 | 10.2 | 0.27538
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-2 | 250-PW-20041-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21411 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.575 | CML-2 | CML: Elbow | 6 | 2061-04-01 | 2054-01-07 | 2014-07-12 07:30 | 4.1 | 0.17966 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.5 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 14.1 | 14.4 | 13.3 | 12.5 | 0.85391
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-11 | 300-PG-20049-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21497 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | [36 empty] | 12.875 | CML-11 | CML: Pipe Length | 6 | 2020-06-21 | 2018-11-15 | 2014-06-28 10:45 | 3.3 | 1.5532 | A3: Inside Quadrant |  | 8.27 | 3.3 | 5.785 | 12.6 | 6 O'Clock | 200 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 13 | 13.2 | 12.6 | 12.7 | 0.27538
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43302-01C02 | CML-3 | 50-FL-43302-01C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 20456 | Reviewed on 24/1/14. FFS. Repeat on Oct.17 | 2014-10-05 07:00 | 2014-10-05 15:00 |  |  | Nestor | 2014-11-24 11:40 | [32 empty] | 5.025 | CML-3 | CML: Elbow | 3 | 2018-04-14 | 2018-10-21 | 2014-10-05 07:00 | 2.5 | 0.62407 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FL-43302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 4.7 | 5.2 | 4.9 | 0.27538
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-15 | 50-FG-45018-03C02 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10514 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.025 | CML-15 | CML: type TBC | 3 | 2015-01-26 | 2015-01-22 | 2013-11-15 | 2.5 | 1.8359 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 4.7 | 4.9 | 5.2 | 0.27538
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-23 | 250-PW-44006-01X01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 8015 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 9.225 | CML-23 | CML: Elbow | 3 | 2055-06-18 | 2055-02-26 | 2015-01-20 08:30 | 2.5 | 0.0915 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | 4.1358 | 6.2 | 11 | 9.7 | 10 | 2.0918
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-2 | 50-FG-45501-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6585 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.175 | CML-2 | CML: Elbow | 3 | 2022-02-03 | 2023-01-09 | 2015-03-30 07:00 | 2.5 | 0.35007 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.5 | 4.9 | 5.3 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43122-01C02 | CML-5 | 50-FH-43122-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1763 | Rope access | 2014-04-27 08:30 | 2014-04-27 09:00 | [36 empty] | 5.175 | CML-5 | CML: Elbow | 3 | 2017-09-17 | 2018-03-04 | 2014-04-27 08:30 | 2.5 | 0.70712 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FH-43122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.5 | 4.9 | 5.3 | 0.27538
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-6 | 50-FG-45501-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6589 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.325 | CML-6 | CML: Pipe Length | 3 | 2023-09-13 | 2024-10-20 | 2015-03-30 07:00 | 2.5 | 0.29537 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.6 | 5 | 5.2 | 0.27538
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56114-01C02 | CML-5 | 50-DH-56114-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5230 | Rope Access | 2014-05-20 11:00 | 2014-05-20 12:00 | [36 empty] | 5.325 | CML-5 | CML: Elbow | 3 | 2018-11-11 | 2019-06-13 | 2014-05-20 11:00 | 2.5 | 0.55763 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-DH-56114-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.6 | 5 | 5.2 | 0.27538
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-6 | 25-DO-62007-15S01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 6537 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 10.1 | CML-6 | CML: Elbow | 1 | 2034-01-29 | 2026-02-18 | 2014-07-24 07:30 | 4.41 | 0.20941 | A4: Left Quadrant |  | 7.74 | 4.41 | 6.075 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.09 | 1.6993 | 10.3 | 10.2 | 11.4 | 8.5 | 1.1972
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-26 | 50-DH-56137-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 21110 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 5.325 | CML-26 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5 | 3 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5.6 | 5.5 | 0.27538
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-16 | 250-PW-44006-01X01 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1913 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.625 | CML-16 | CML: Pipe Length | 3 | 2034-05-18 | 2034-03-23 | 2014-03-26 07:00 | 2.5 | 0.18355 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 7.4 | 6.7 | 6.2 | 0.56789
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-4 | 150-WC-40003-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2981 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.448mm/ yr | [35 empty] | 7.55 | CML-4 | CML: Elbow | 3 | 2023-09-16 | 2022-11-26 | 2014-05-01 09:30 | 2.5 | 0.44752 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 12 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.3 | 8.1 | 8.1 | 0.68069
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43154-01C02 | CML-1 | 100-FL-43154-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12871 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 5.975 | CML-1 | CML: type TBC | 3 | 2020-11-11 | 2021-02-09 | 2014-02-03 08:00 | 2.5 | 0.47224 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 3 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.1 | 5.7 | 6.3 | 5.8 | 0.27538
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45004-03C02 | CML-7 | 150-FG-45004-03C02 CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24339 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.175 | CML-7 | CML: Equal Tee | 3 | 2024-11-25 | 2022-11-24 | 2016-06-06 07:00 | 2.5 | 0.40103 | A4: Left Quadrant |  | 4.11 | 2.5 | 3.305 | 5.9 | 9 O'Clock | 150 | 7.11 | 150-FG-45004-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6.5 | 6.3 | 5.9 | 0.27538
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20012-01C02-P | CML-2 | 200-PL-20012-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21204 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.675 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 9 O'Clock | 200 | 6.35 | 200-PL-20012-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.5 | 8.7 | 9.5 | 8 | 0.62383
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-4 | 150-WC-40003-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22260 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.448mm/ yr | [35 empty] | 7.55 | CML-4 | CML: Elbow | 3 | 2023-09-16 | 2022-11-26 | 2014-05-01 09:30 | 2.5 | 0.44752 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 12 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.3 | 8.1 | 8.1 | 0.68069
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-8 | 200-FH-43038-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12689 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 6.525 | CML-8 | CML: type TBC | 3 | 2031-01-04 | 2030-11-18 | 2014-02-06 09:00 | 2.5 | 0.21867 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.8 | 6.2 | 6.7 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-3 | 150-FH-43157-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10659 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.825 | CML-3 | CML: type TBC | 3 | 2016-12-06 | 2016-08-28 | 2013-11-18 | 2.5 | 1.3097 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.5 | 6 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 7.1 | 6.5 | 7 | 0.27538
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40038-01C02 | CML-5 | 200-WC-40038-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7713 |  | 2015-01-09 10:00 | 2015-01-09 12:00 | [36 empty] | 7.275 | CML-5 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-01-09 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 200 | 6.35 | 200-WC-40038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 6.8 | 7.6 | 8 | 0.62915
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-10 | 0200-DH-56L9003-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5095 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 8.75 | CML-10 | CML: type TBC | 3 | 2052-09-03 | 2045-11-07 | 2015-03-06 07:00 | 2.5 | 0.15723 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 8.4 | 12 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.7 | 8.9 | 9 | 0.26458
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63019-01E01 | CML-1 | 50-AU-63019-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8869 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 08:00 | 2015-02-25 09:00 | [36 empty] | 8.625 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 3 O'Clock | 50 | 5.54 | 50-AU-63019-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.5 | 8.4 | 8.8 | 8.8 | 0.20616
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-13 | 200-FH-43003-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12536 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.975 | CML-13 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 11:30 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.7 | 9 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.36 |  | 6.8 | 7.3 | 7.1 | 6.7 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43108-01C02 | CML-4 | 200-FH-43108-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12779 |  | 2014-01-18 15:30 | 2014-01-18 16:30 | [36 empty] | 8.425 | CML-4 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 15:30 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 8.1 | 6 O'Clock | 200 | 6.35 | 200-FH-43108-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.76 |  | 8.3 | 8.6 | 8.1 | 8.7 | 0.27538
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-4 | 200-PG-23051-09C02-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13109 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 18.925 | CML-4 | CML: type TBC | 3 | 2103-01-05 | 2073-03-18 | 2014-02-07 11:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 18.6 | 12 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 18.6 | 19 | 19.2 | 18.9 | 0.25
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-10 | 250-PW-44007-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1967 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 6.6 | CML-10 | CML: Pipe Length | 3 | 2034-05-22 | 2034-03-28 | 2014-03-26 11:30 | 2.5 | 0.18343 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.7 | 7.2 | 6.3 | 0.45461
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-7 | 250-PW-44007-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1964 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 6.575 | CML-7 | CML: Pipe Length | 3 | 2034-05-22 | 2034-03-28 | 2014-03-26 11:30 | 2.5 | 0.18343 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.6 | 6.2 | 7.2 | 0.45
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56130-01C02 | CML-6 | 50-DH-56130-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21058 | Rope Access | 2014-05-15 13:00 | 2014-05-15 14:00 | [36 empty] | 5 | CML-6 | CML: type TBC | 3 | 2016-07-02 | 2016-10-31 | 2014-05-15 13:00 | 2.5 | 0.98439 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56130-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.1 | 4.6 | 5.2 | 5.1 | 0.2708
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-2 | 50-CG-38476-01C02-H CML-2 | Yes | FPSO 2015 | Pipe Wall Thickness | 23634 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5 | CML-2 | CML: Elbow | 3 | 2023-04-22 | 2024-05-13 | 2015-10-28 07:00 | 2.5 | 0.30718 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 4.9 | 4.9 | 4.8 | 0.2708
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-4 | 25-DO-62007-15S01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2628 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 8.65 | CML-4 | CML: Elbow | 1 | 2029-10-31 | 2023-07-09 | 2014-04-29 09:30 | 4.41 | 0.26354 | A1: Outside Quadrant |  | 7.74 | 4.41 | 6.075 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.09 |  | 8.5 | 8.6 | 8.8 | 8.7 | 0.1291
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PL-57403-01C03 |  | 50-PL-57403-01C03 |  | FPSO 2015 | Pipe Wall Thickness | 8366 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.2 | 50-PL-57403-01C03 | Piping | 6 | 2043-12-06 |  | 2015-01-29 07:30 |  | 0.20434 | A1: Outside Quadrant |  |  | 2.5 |  | 8.4 | 12 O'Clock | 50 | 8.74 | Pipework | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.4 | 9.5 | 9.5 | 0.53541
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57402-01C03 | CML-1 | 50-DC-57402-01C03 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8358 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.325 | CML-1 | CML: type TBC | 6 | 2043-12-06 | 2043-05-06 | 2015-01-29 07:30 | 2.5 | 0.20434 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-DC-57402-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.5 | 10 | 9.4 | 0.6702
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57401-01C03 | CML-2 | 50-DC-57401-01C03 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8357 |  | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 9.15 | CML-2 | CML: type TBC | 6 | 2043-11-18 | 2043-04-18 | 2015-01-28 07:30 | 2.5 | 0.20468 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-DC-57401-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.5 | 8.4 | 9.7 | 9 | 0.58023
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53012-01E01 | CML-5 | 50-WD-53012-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8213 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 8.825 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 9 O'Clock | 50 | 5.54 | 50-WD-53012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.8 | 9.3 | 8.8 | 8.4 | 0.36856
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-5 | 25-DO-62007-15S01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6536 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 10.4 | CML-5 | CML: Elbow | 1 | 2048-11-01 | 2035-03-20 | 2014-07-24 07:30 | 4.41 | 0.12216 | A4: Left Quadrant |  | 7.74 | 4.41 | 6.075 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 | -2.549 | 10.7 | 10.7 | 11.6 | 8.6 | 1.2728
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-5 | 50-FG-45501-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6588 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.3 | CML-5 | CML: Pipe Length | 3 | 2026-01-14 | 2027-05-24 | 2015-03-30 07:00 | 2.5 | 0.24067 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.2 | 5.2 | 5.1 | 0.2708
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-4 | 200-PG-23008-15S01-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3464 | Rope Access | 2014-05-13 09:30 | 2014-05-13 10:30 | [36 empty] | 5.3 | CML-4 | CML: type TBC | 3 | 2020-09-07 | 2021-07-13 | 2014-05-13 09:30 | 2.5 | 0.41095 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 3 O'Clock | 80 | 5.49 | 80-DH-56019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.1 | 5.2 | 5.7 | 0.2708
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-11 | 250-PW-44007-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1968 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 6.55 | CML-11 | CML: Pipe Length | 3 | 2034-05-22 | 2034-03-28 | 2014-03-26 11:30 | 2.5 | 0.18343 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 7.1 | 6.2 | 6.2 | 0.43589
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-12 | 250-PW-44007-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1969 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 6.575 | CML-12 | CML: Pipe Length | 3 | 2034-05-22 | 2034-03-28 | 2014-03-26 11:30 | 2.5 | 0.18343 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.2 | 6.9 | 7 | 0.43493
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-4 | 150-WC-40002-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20343 | Reviewed on 18/11/14. Line is FFS. Repeat on Oct.19 | 2014-10-09 07:00 | 2014-10-09 15:00 | Check Corrosion Rate of 0.302mm/ yr |  | Nestor | 2014-11-24 10:28 | [32 empty] | 7.425 | CML-4 | CML: Elbow | 3 | 2028-08-30 | 2027-06-21 | 2014-10-09 07:00 | 2.5 | 0.30215 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 12 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.4 | 8.1 | 7.5 | 0.57373
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-3 | 25-DO-62007-15S01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6534 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:15 | [32 empty] | 10.425 | CML-3 | CML: Elbow | 1 | 2048-11-01 | 2035-03-20 | 2014-07-24 07:30 | 4.41 | 0.12216 | A4: Left Quadrant |  | 7.74 | 4.41 | 6.075 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 | -2.9738 | 10.6 | 10.4 | 12.1 | 8.6 | 1.4338
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-7 | 25-DO-62007-15S01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2631 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 9.65 | CML-7 | CML: Fitting | 1 | 2041-07-24 | 2030-09-27 | 2014-04-29 09:30 | 4.41 | 0.15373 | A2: Right Quadrant |  | 7.74 | 4.41 | 6.075 | 8.6 | 3 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 |  | 9.7 | 8.6 | 9.5 | 10.8 | 0.9037
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-7 | 50-CG-38452-09C02-P CML-7 | Yes | FPSO 2015 | Pipe Wall Thickness | 7855 | Line is FFS. Action: to recheck in two years CML-7 &8 (Jan. 2017) to confirm CR. | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-07 16:50 | [32 empty] | 5.7 | CML-7 | CML: Elbow | 3 | 2019-05-12 | 2019-04-26 | 2015-01-14 07:00 | 2.5 | 0.64706 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 6 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.9 | 5.3 | 5.8 | 0.2708
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-8 | 50-PW-44013-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22727 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 6.775 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-04-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | 1.0605 | 7.2 | 6.2 | 6.8 | 6.9 | 0.41932
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43179-01C02 | CML-3 | 80-FH-43179-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2347 | Rope Access | 2014-03-17 11:30 | 2014-03-17 12:00 | [36 empty] | 6.3 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-17 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 12 O'Clock | 80 | 5.49 | 80-FH-43179-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.7 | 6.2 | 6.2 | 0.2708
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40043-01C02 | CML-5 | 300-WC-40043-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1046 |  | 2014-03-20 13:00 | 2014-03-20 14:00 | [36 empty] | 7.15 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-20 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 300 | 6.35 | 300-WC-40043-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 6.8 | 7.2 | 7.9 | 0.54467
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-1 | 100-WC-40035-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1734 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.075 | CML-1 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.7 | 6 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7 | 6.9 | 6.7 | 7.7 | 0.43493
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-4 | 25-DO-62007-15S01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6535 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 10.475 | CML-4 | CML: Elbow | 1 | 2137-05-24 | 2089-09-20 | 2014-07-24 07:30 | 4.41 | 0.0349 | A4: Left Quadrant |  | 7.74 | 4.41 | 6.075 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.29 | -0.84966 | 10.1 | 10.3 | 12.8 | 8.7 | 1.7056
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-15 | 150-DC-57308-01C03 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20312 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.725 | CML-15 | CML: Elbow | 6 | 2017-10-27 | 2017-03-06 | 2014-10-02 07:00 | 2.5 | 1.9211 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 8.4 | 6 O'Clock | 100 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.3 | 8.4 | 8.4 | 8.8 | 0.4272
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-4 | 150-DC-57308-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20301 | Reviewed 24/11/14. FFS. CML to be checked in Oct.16 | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 1.921mm/ yr |  | Nestor | 2014-11-24 08:45 | [32 empty] | 9.025 | CML-4 | CML: Elbow | 6 | 2017-10-27 | 2017-03-06 | 2014-10-02 07:00 | 2.5 | 1.9211 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 8.4 | 9 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9 | 9.8 | 8.9 | 8.4 | 0.57951
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-6 | 250-PW-44004-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5625 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 6.35 | CML-6 | CML: Elbow | 3 | 2029-08-17 | 2029-07-05 | 2014-06-20 13:00 | 2.5 | 0.2373 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.3 | 6.6 | 6.4 | 0.20817
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-10 | 50-FG-45021-03C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2622 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.2 | CML-10 | CML: type TBC | 3 | 2018-06-29 | 2018-06-17 | 2014-04-26 10:45 | 2.5 | 0.59827 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.22608 | 5.1 | 5.6 | 5 | 5.1 | 0.2708
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45017-03C02 | CML-11 | 100-FG-45017-03C02 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10635 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.6 | CML-11 | CML: type TBC | 3 | 2015-05-31 | 2015-04-07 | 2013-11-18 | 2.5 | 1.7606 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.76 | 5.2 | 9 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.8 | 5.7 | 5.2 | 0.2708
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43020-01C02 | CML-2 | 80-FH-43020-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12614 |  | 2014-01-23 07:00 | 2014-01-23 08:00 | [36 empty] | 5.6 | CML-2 | CML: type TBC | 3 | 2020-02-01 | 2020-11-10 | 2014-01-23 07:00 | 2.5 | 0.44796 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-FH-43020-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.7 | 5.8 | 5.7 | 0.2708
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-7 | 25-DO-62007-15S01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 6538 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:15 | [32 empty] | 8.9 | CML-7 | CML: Fitting | 1 | 2056-09-17 | 2040-01-24 | 2014-07-24 07:30 | 4.41 | 0 | A3: Inside Quadrant |  | 7.74 | 4.41 | 6.075 | 8.8 | 9 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 | -0.84966 | 9 | 9 | 8.8 | 8.8 | 0.11547
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-9 | 25-DO-62007-15S01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2633 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 9.825 | CML-9 | CML: Elbow | 1 | 2056-09-17 | 2040-01-24 | 2014-04-29 09:30 | 4.41 | 0 | A3: Inside Quadrant |  | 7.74 | 4.41 | 6.075 | 8.8 | 6 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 |  | 10.4 | 9.6 | 8.8 | 10.5 | 0.7932
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-8 | 25-DO-62007-15S01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2632 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 9.725 | CML-8 | CML: Elbow | 1 | 2056-09-17 | 2040-01-24 | 2014-04-29 09:30 | 4.41 | 0 | A1: Outside Quadrant |  | 7.74 | 4.41 | 6.075 | 8.8 | 12 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 |  | 8.8 | 9.8 | 11 | 9.3 | 0.94296
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-3 | 250-PW-44007-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1960 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 6.65 | CML-3 | CML: Pipe Length | 3 | 2034-05-22 | 2034-03-28 | 2014-03-26 11:30 | 2.5 | 0.18343 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.9 | 6.8 | 6.2 | 6.7 | 0.31091
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-33 | 250-PW-44006-01X01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 8025 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.5 | CML-33 | CML: Elbow | 3 | 2055-06-18 | 2055-02-26 | 2015-01-20 08:30 | 2.5 | 0.0915 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | 0.12164 | 6.7 | 6.7 | 6.2 | 6.4 | 0.24495
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-6 | 250-WC-40026-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1282 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.15 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 6 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.5 | 7.4 | 6.7 | 7 | 0.36968
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-8 | 80-PW-44001-01C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23217 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.325 | CML-8 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 | 1.2225 | 6.1 | 6.4 | 6.5 | 6.3 | 0.17078
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-13 | 100-PW-20021-01C02-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22831 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 19.625 | CML-13 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2015-04-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 | -0.18159 | 6.2 | 6.2 | 6.1 | 6 | 0.095743
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-3 | 50-FG-45300-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 7826 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:44 | [32 empty] | 6.1 | CML-3 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-01-13 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 25 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.5 | 6 | 6 | 5.9 | 0.2708
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 23878 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.4 | CML-6 | CML: Pipe Length | 3 | 2027-12-10 | 2027-11-01 | 2014-09-26 07:00 | 2.5 | 0.26488 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6.6 | 6 | 6.5 | 0.2708
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-2 | 50-FG-45024-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1206 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.2 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.1 | 6.6 | 0.2708
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-10 | 50-FG-45024-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1214 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.7 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 12 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.6 | 6.6 | 7.1 | 0.2708
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45004-03C02 | CML-1 | 150-FG-45004-03C02 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24333 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.4 | CML-1 | CML: Fitting | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 3.305 | 7.2 | 3 O'Clock | 150 | 7.11 | 150-FG-45004-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.3 | 7.2 | 7.3 | 7.8 | 0.2708
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20392 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 7.4 | CML-2 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-10-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-WC-40404-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.8 | 7.3 | 7.3 | 7.2 | 0.2708
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-10 | 25-DO-62007-15S01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 6541 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:14 | [32 empty] | 9.025 | CML-10 | CML: Fitting | 1 | 2056-09-17 | 2040-01-24 | 2014-07-24 07:30 | 4.41 | 0 | A1: Outside Quadrant |  | 7.74 | 4.41 | 6.075 | 8.9 | 12 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.49 |  | 8.9 | 9 | 9 | 9.2 | 0.12583
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-48 | 50-CG-38452-09C02-P CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 9135 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 7.6 | CML-48 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 12 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.7 | 7.8 | 7.7 | 0.2708
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-6 | 25-DO-62007-15S01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2630 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 9.7 | CML-6 | CML: Elbow | 1 | 2056-09-17 | 2040-01-24 | 2014-04-29 09:30 | 4.41 | 0 | A1: Outside Quadrant |  | 7.74 | 4.41 | 6.075 | 8.9 | 12 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.49 |  | 8.9 | 9.8 | 10.8 | 9.3 | 0.82057
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-15 | 150-FH-43518-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2715 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.2 | CML-15 | CML: Pipe Length | 3 | 2055-01-13 | 2047-12-27 | 2014-03-12 09:00 | 1.23 | 0.14119 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 | 0 | 7 | 7.6 | 7.1 | 7.1 | 0.2708
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-15 | 150-FH-43518-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 354 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.2 | CML-15 | CML: Pipe Length | 3 | 2054-12-24 | 2047-12-10 | 2014-03-12 | 1.23 | 0.14137 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 |  | 7 | 7.6 | 7.1 | 7.1 | 0.2708
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-7 | 150-FH-43136-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2768 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.3 | CML-7 | CML: Pipe Length | 3 | 2036-01-14 | 2031-12-17 | 2014-03-13 09:00 | 1.03 | 0.26859 | A4: Left Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.9 | 9 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.87 |  | 7.5 | 7.4 | 7.4 | 6.9 | 0.2708
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-11 | 250-PW-20040-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21395 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.3 | CML-11 | CML: Elbow | 6 | 2061-04-01 | 2054-01-07 | 2014-07-12 07:30 | 4.1 | 0.17966 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 12.5 | 3 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 14.2 | 12.5 | 13.6 | 12.9 | 0.75277
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-2 | 50-FL-43454-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5845 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 9.5 | CML-2 | CML: Reducing Tee | 6 | 2075-10-24 | 2074-08-12 | 2014-06-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.7 | 9.6 | 9.1 | 9.6 | 0.2708
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-9 | 100-PG-23071-01C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2407 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 10.6 | CML-9 | CML: type TBC | 6 | 2025-04-11 | 2023-07-19 | 2014-03-19 13:00 | 2.5 | 0.71362 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 10.4 | 9 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 11 | 10.5 | 10.5 | 10.4 | 0.2708
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-5 | 250-PW-20040-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21389 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.825 | CML-5 | CML: Fitting | 6 | 2061-04-01 | 2054-01-07 | 2014-07-12 07:30 | 4.1 | 0.17966 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.5 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 13.4 | 12.7 | 12.7 | 12.5 | 0.39476
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-1 | 80-CG-38459-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21669 | Protective mesh removed | 2014-06-26 09:30 | 2014-06-26 11:00 | [36 empty] | 14.4 | CML-1 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-06-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 14 | 6 O'Clock | 80 | 11.13 | 80-PG-20030-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 14.5 | 14.6 | 14 | 14.5 | 0.2708
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20016-01C02-P | CML-8 | 200-PL-20016-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21239 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.725 | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 9 O'Clock | 200 | 6.35 | 200-PL-20016-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.5 | 9.2 | 9.2 | 8 | 0.58523
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-3 | 200-FH-43012-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2833 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 8.15 | CML-3 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.8 | 6 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.46 |  | 8.1 | 8.3 | 7.8 | 8.4 | 0.26458
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-5 | 250-PW-44007-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1962 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 6.425 | CML-5 | CML: Fitting | 3 | 2034-05-22 | 2034-03-28 | 2014-03-26 11:30 | 2.5 | 0.18343 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.4 | 6.2 | 6.7 | 0.20616
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-20 | 250-PW-20041-03C03-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23492 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 12.65 | CML-20 | CML: Fitting | 6 | 2105-12-26 | 2091-12-28 | 2015-07-27 07:00 | 4.1 | 0.09284 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.5 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | -0.96058 | 12.6 | 12.6 | 12.9 | 12.5 | 0.17321
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56142-01C02 | CML-8 | 25-DH-56142-01C02 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 7529 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 4.65 | CML-8 | CML: Elbow | 3 | 2016-12-01 | 2016-11-22 | 2015-04-13 07:00 | 2.5 | 1.0983 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.3 | 6 O'Clock | 25 | 6.35 | 25-DH-56142-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.8 | 4.9 | 4.3 | 4.6 | 0.26458
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-14 | 50-FG-45018-03C02 CML-14 | yes | FPSO 2013 | Pipe Wall Thickness | 10513 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.85 | CML-14 | CML: type TBC | 3 | 2014-11-23 | 2014-11-19 | 2013-11-15 | 2.5 | 2.0545 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.2 | 4.7 | 4.6 | 4.9 | 0.26458
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-5 | 50-FG-45024-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2582 |  | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 5.15 | CML-5 | CML: type TBC | 3 | 2017-02-12 | 2017-02-03 | 2014-04-26 07:00 | 2.5 | 0.82025 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FG-45035-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.1 | 5.3 | 5.4 | 0.26458
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-3 | 50-WC-40048-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 880 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 7.225 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 12 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.4 | 7.3 | 7.5 | 0.3594
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-2 | 25-PW-44026-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22734 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 6.15 | CML-2 | CML: Elbow | 3 | 2026-10-05 | 2026-08-30 | 2015-04-28 07:00 | 2.5 | 0.28831 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 25 | 6.35 | 25-PW-44026-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 6.4 | 5.8 | 6.3 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-7 | 80-FH-43151-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2241 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 6.35 | CML-7 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 3 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.1 | 6.4 | 6.7 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-10 | 200-FH-43025-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2483 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 7.65 | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 6 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.8 | 7.9 | 7.3 | 7.6 | 0.26458
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-6 | 50-CG-38458-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23734 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.05 | CML-6 | CML: Elbow | 3 | 2023-04-30 | 2024-05-22 | 2015-10-30 07:00 | 2.5 | 0.30648 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 4.8 | 4.9 | 5.1 | 0.26458
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-20 | 50-DH-56070-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 3236 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.95 | CML-20 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.1 | 6.2 | 5.9 | 5.6 | 0.26458
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-8 | 100-DH-56082-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3376 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 7.55 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.3 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.6 | 7.9 | 7.4 | 0.26458
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-9 | 50-CG-38466-01C02 CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 2523 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.7 | CML-9 | CML: type TBC | 3 | 2076-12-28 | 2083-10-25 | 2014-04-02 13:00 | 2.5 | 0.04778 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 5.5 |  | 5.5 | 6 | 5.6 | 0.26458
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-11 | 25-DO-62007-15S01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2636 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 9.925 | CML-11 | CML: Elbow | 1 | 2056-09-17 | 2040-01-24 | 2014-04-29 09:30 | 4.41 | 0 | A3: Inside Quadrant |  | 7.74 | 4.41 | 6.075 | 9.3 | 6 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.89 |  | 10.7 | 9.8 | 9.3 | 9.9 | 0.57951
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-13 | 25-DO-62007-15S01 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 6544 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 10.525 | CML-13 | CML: Reducer | 1 | 2056-09-17 | 2040-01-24 | 2014-07-24 07:30 | 4.41 | 0 | A2: Right Quadrant |  | 7.74 | 4.41 | 6.075 | 10 | 3 O'Clock | 25 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.59 | -16.1435 | 10.7 | 10 | 10.3 | 11.1 | 0.47871
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-12 | 25-DO-62007-15S01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2637 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 11.5 | CML-12 | CML: Elbow | 1 | 2056-09-17 | 2040-01-24 | 2014-04-29 09:30 | 4.41 | 0 | A1: Outside Quadrant |  | 7.74 | 4.41 | 6.075 | 11.3 | 12 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.89 |  | 11.3 | 11.7 | 11.4 | 11.6 | 0.18257
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-1 | 25-DO-62007-15S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2625 | Rope Access | 2014-04-29 09:30 | 2014-04-29 10:00 | [36 empty] | 11.475 | CML-1 | CML: Elbow | 1 | 2056-09-17 | 2040-01-24 | 2014-04-29 09:30 | 4.41 | 0 | A1: Outside Quadrant |  | 7.74 | 4.41 | 6.075 | 11.4 | 12 O'Clock | 25 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.99 |  | 11.4 | 11.5 | 11.5 | 11.5 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-2 | 200-FH-43038-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12683 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 6.4 | CML-2 | CML: type TBC | 3 | 2023-12-21 | 2023-11-23 | 2014-02-06 09:00 | 2.5 | 0.36445 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.6 | 6.1 |  | 6.5 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-2 | 200-FH-43037-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12671 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 6.6 | CML-2 | CML: type TBC | 3 | 2066-03-20 | 2065-10-30 | 2014-02-06 11:00 | 2.5 | 0.07287 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.8 |  | 6.7 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-9 | 150-FH-43027-01C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10571 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 6.9 | CML-9 | CML: type TBC | 3 | 2017-07-28 | 2017-03-31 | 2013-11-16 | 2.5 | 1.108 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  |  | 7.1 | 6.6 | 7 | 0.26458
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-13 | 50-CG-38452-09C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12976 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 8.4 | CML-13 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 3 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  |  | 8.1 | 8.6 | 8.5 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-15 | 200-FH-43003-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12538 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 10 | CML-15 | CML: Tee | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 11:30 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 9.8 | 3 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.46 |  | 10.3 | 9.8 | 9.9 |  | 0.26458
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-15 | 50-PL-23300-09C03 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 13131 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 12.2 | CML-15 | CML: type TBC | 6 | 2096-01-05 | 2084-09-16 | 2014-02-04 07:00 | 2.81 | 0 | A4: Left Quadrant |  | 5.07 | 2.81 | 3.94 | 12 | 9 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.19 |  |  | 12.5 | 12.1 | 12 | 0.26458
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-4 | 200-PL-20008-01C02-H CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8801 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.425 | CML-4 | CML: Elbow | 3 | 2039-04-20 | 2035-09-17 | 2015-02-21 07:00 | 1.1 | 0.20268 | A3: Inside Quadrant |  | 3.35 | 1.1 | 1.8281 | 6 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 6.6 | 6.5 | 6 | 6.6 | 0.28723
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-3 | 300-PG-20506-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13217 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.25 | CML-3 | CML: type TBC | 6 | 2037-01-14 | 2032-10-15 | 2014-02-04 15:00 | 4.9 | 0.39638 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 12 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 14 | 14.1 | 14.3 | 14.6 | 0.26458
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-30 | 50-PF-20301-03C03-P CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 3028 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 13.35 | CML-30 | CML: Reducer | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 13.1 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.49 | 0 | 13.4 | 13.2 | 13.7 | 13.1 | 0.26458
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-30 | 50-PF-20301-03C03-P CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 22307 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 13.35 | CML-30 | CML: Reducer | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 13.1 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.49 |  | 13.4 | 13.2 | 13.7 | 13.1 | 0.26458
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23043 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 7.2 | CML-6 | CML: Elbow | 3 | 2161-11-22 | 2160-10-22 | 2015-05-06 07:00 | 2.5 | 0.02591 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | -0.34128 | 6.3 | 7.8 | 6.8 | 7.9 | 0.77889
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56054-01C02 | CML-3 | 80-DH-56054-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20945 | Rope Access | 2014-05-17 08:00 | 2014-05-17 09:00 | [36 empty] | 5.25 | CML-3 | CML: type TBC | 3 | 2018-04-11 | 2018-11-04 | 2014-05-17 08:00 | 2.5 | 0.6147 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 9 O'Clock | 80 | 5.49 | 80-DH-56054-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.5 | 5.2 | 5.4 | 4.9 | 0.26458
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-3 | 50-WC-40048-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1544 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 7.225 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 12 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.4 | 7.3 | 7.5 | 0.3594
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-3 | 200-PW-44021-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23018 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 7.05 | CML-3 | CML: Elbow | 3 | 2161-09-06 | 2160-08-06 | 2015-05-05 07:00 | 2.5 | 0.02595 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | -0.93874 | 6.3 | 7.1 | 7.5 | 7.3 | 0.52599
PG05 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21552 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 5.75 | CML-4 | CML: Elbow | 3 | 2019-10-23 | 2020-01-08 | 2014-07-17 07:30 | 2.5 | 0.55019 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 9 O'Clock | 100 | 6.02 | 100-PL-20068-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.9 | 5.7 | 5.4 | 0.26458
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 | no | FPSO 2014 | Pipe Wall Thickness | 22082 | Rope Access | 2014-05-25 09:30 | 2014-05-25 10:30 | [36 empty] | 5.75 | CML-6 | CML: type TBC | 3 | 2018-12-26 | 2018-07-29 | 2014-05-25 09:30 | 2.5 | 0.63142 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.4 | 12 O'Clock | 100 | 6.02 | 100-FG-45305-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.7 | 5.9 | 6 | 0.26458
PG05 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-PG-23003-06C02-PA | CML-15 | 250-PG-23003-06C02-PA CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 3077 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | [36 empty] | 5.65 | CML-15 | CML: Fitting | 3 | 2033-05-30 | 2035-07-23 | 2014-05-03 08:00 | 2.5 | 0.15193 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 5.2044 | 5.7 | 5.5 | 5.4 | 6 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43101-01C02 | CML-4 | 100-FH-43101-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12743 |  | 2014-01-24 07:00 | 2014-01-24 08:00 | [36 empty] | 5.95 | CML-4 | CML: Elbow | 3 | 2020-07-24 | 2020-10-18 | 2014-01-24 07:00 | 2.5 | 0.49222 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-FH-43101-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6 | 5.8 | 6.3 | 0.26458
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38477-01C02-P | CML-3 | 50-CG-38477-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22649 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.45 | CML-3 | CML: Elbow | 3 | 2023-01-10 | 2021-09-14 | 2015-04-27 07:00 | 1.88 | 0.43047 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.32 |  | 5.5 | 5.2 | 5.3 | 5.8 | 0.26458
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-30 | 25-FG-45455-01C02-E CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 21281 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.25 | CML-30 | CML: Fitting | 3 | 2028-01-23 | 2027-12-15 | 2014-09-30 07:00 | 2.5 | 0.2627 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6 | 6.1 | 6.6 | 0.26458
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56115-01C02 | CML-8 | 50-DH-56115-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5239 | Rope Access | 2014-05-20 13:00 | 2014-05-20 14:00 | [36 empty] | 6.75 | CML-8 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-20 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56115-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 7 | 6.9 | 6.4 | 0.26458
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-20 | 250-WC-40026-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 1296 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.2 | CML-20 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.4 | 7.4 | 7.3 | 0.33665
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62007-15S01 | CML-2 | 25-DO-62007-15S01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6533 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:44 | [32 empty] | 12.425 | CML-2 | CML: Reducer | 1 | 2056-09-17 | 2040-01-24 | 2014-07-24 07:30 | 4.41 | 0 | A3: Inside Quadrant |  | 7.74 | 4.41 | 6.075 | 12.1 | 6 O'Clock | 50 | 8.74 | 50-DO-62007-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.69 | -16.1435 | 13 | 12.3 | 12.1 | 12.3 | 0.39476
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-1 | 150-WC-40003-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2978 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.448mm/ yr | [35 empty] | 7.05 | CML-1 | CML: Fitting | 3 | 2023-09-16 | 2022-11-26 | 2014-05-01 09:30 | 2.5 | 0.44752 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 9 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 | 0 | 7 | 7.3 | 7.2 | 6.7 | 0.26458
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40505-1CG | CML-3 | 250-WC-40505-1CG CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8629 | Rope Access / Material Class Not Selectable. Line is FFS. Only one CM-3 is showing high CR. Current RBI frequency is 48m Action: NIL. RBI to stay at 48m | 2015-02-10 08:00 | 2015-02-10 09:00 | Check Corrosion Rate of 1.114mm/ yr |  | Administrator | 2015-09-08 10:30 | [32 empty] | 13.925 | CML-3 | CML: Elbow | 3 | 2024-09-16 | 2020-05-29 | 2015-02-10 08:00 | 2.5 | 1.1139 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 13.2 | 6 O'Clock | 250 | 15.09 | 250-WC-40505-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 14 | 14.7 | 13.2 | 13.8 | 0.61847
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-33 | 250-PW-44006-01X01 CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 1930 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.625 | CML-33 | CML: Elbow | 3 | 2076-04-19 | 2075-11-03 | 2014-03-26 07:00 | 2.5 | 0.06118 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.9 | 6.3 | 6.4 | 6.9 | 0.32016
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-34 | 250-PW-44006-01X01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 8026 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.475 | CML-34 | CML: Pipe Length | 3 | 2139-07-24 | 2138-08-21 | 2015-01-20 08:30 | 2.5 | 0.0305 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | -0.48657 | 6.3 | 6.5 | 6.8 | 6.3 | 0.23629
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-4 | 80-DH-56004-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 8538 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 3.45 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-02-04 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 9 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.5 | 3.3 | 3.8 | 3.2 | 0.26458
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80005-01C02 | CML-2 | 50-VA-80005-01C02 CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 3128 | Rope Access | 2014-05-02 10:30 | 2014-05-02 11:30 | [36 empty] | 4.95 | CML-2 | CML: type TBC | 3 | 2016-09-26 | 2017-02-04 | 2014-05-02 10:30 | 2.5 | 0.91403 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-VA-80005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 4.8 | 5 | 4.7 | 0.26458
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-5 | 50-FG-45020-03C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2604 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.05 | CML-5 | CML: type TBC | 3 | 2016-09-05 | 2016-08-28 | 2014-04-26 09:30 | 2.5 | 0.9308 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.68269 | 5 | 5.2 | 4.7 | 5.3 | 0.26458
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20014-01C02-P | CML-1 | 200-PL-20014-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21220 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.425 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 9 O'Clock | 200 | 6.35 | 200-PL-20014-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.4 | 9.1 | 8 | 0.47871
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56004-01C02 | CML-1 | 80-DH-56004-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3404 | Rope Access | 2014-05-11 07:00 | 2014-05-11 09:00 | [36 empty] | 5.35 | CML-1 | CML: type TBC | 3 |  |  | 2014-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5 | 6 O'Clock | 100 |  | 100-DH-56004-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.6 | 5 | 5.3 | 0.26458
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-35 | 250-PW-44006-01X01 CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 1932 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.5 | CML-35 | CML: Pipe Length | 3 | 2076-04-19 | 2075-11-03 | 2014-03-26 07:00 | 2.5 | 0.06118 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.7 | 6.5 | 6.5 | 0.1633
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-35 | 250-PW-44006-01X01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 8027 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.375 | CML-35 | CML: Pipe Length | 3 | 2139-07-24 | 2138-08-21 | 2015-01-20 08:30 | 2.5 | 0.0305 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | 0 | 6.4 | 6.4 | 6.4 | 6.3 | 0.05
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-8 | 250-PW-44006-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8000 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 7.125 | CML-8 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 | -0.72985 | 7.4 | 6.4 | 8.2 | 6.5 | 0.84607
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40003-01C02 | CML-1 | 150-WC-40003-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22257 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | Check Corrosion Rate of 0.448mm/ yr | [35 empty] | 7.05 | CML-1 | CML: Fitting | 3 | 2023-09-16 | 2022-11-26 | 2014-05-01 09:30 | 2.5 | 0.44752 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 9 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7 | 7.3 | 7.2 | 6.7 | 0.26458
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-5 | 25-VA-23054-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1474 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 5.65 | CML-5 | CML: type TBC | 3 | 2033-03-06 | 2035-04-19 | 2014-04-29 10:00 | 2.5 | 0.15372 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 6 | 5.7 | 0.26458
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63010-01E01 | CML-1 | 50-AI-63010-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8771 |  | 2015-02-15 13:00 | 2015-02-15 14:00 | [36 empty] | 8.825 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.5 | 9 O'Clock | 50 | 5.54 | 50-AI-63010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.2 | 8.8 | 8.8 | 8.5 | 0.28723
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40044-01C02 | CML-5 | 300-WC-40044-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1120 |  | 2014-03-21 11:30 | 2014-03-21 12:00 | [36 empty] | 7.05 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-21 11:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 300 | 6.35 | 300-WC-40044-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.1 | 7.2 | 7.2 | 6.7 | 0.23805
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-8 | 50-FH-43011-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7958 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.05 | CML-8 | CML: Elbow | 3 | 2017-05-26 | 2016-11-15 | 2015-01-18 08:00 | 2.5 | 1.3588 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 5.7 | 12 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 6.2 | 6 | 0.26458
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57400-01C03 | CML-4 | 50-DC-57400-01C03 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8354 |  | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 9.275 | CML-4 | CML: type TBC | 6 | 2056-07-29 | 2055-09-29 | 2015-01-28 07:30 | 2.5 | 0.14448 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-DC-57400-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.9 | 10.1 | 9.6 | 0.71356
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57400-01C03 | CML-2 | 50-DC-57400-01C03 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8352 |  | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 9.25 | CML-2 | CML: type TBC | 6 | 2056-07-29 | 2055-09-29 | 2015-01-28 07:30 | 2.5 | 0.14448 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-DC-57400-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 9.2 | 10.2 | 9.1 | 0.70475
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML 3 | 200-PW-44021-01X01 CML 3 |  | FPSO 2014 | Pipe Wall Thickness | 22367 |  | 2014-06-19 13:00 | 2014-06-19 14:00 | [36 empty] | 6.925 | CML 3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 40 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7 | 7.3 | 7 | 0.37749
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-9 | 80-PW-44001-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 22000 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.15 | CML-9 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.2 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 8.2 | 6.7 | 6.2 | 7.5 | 0.88129
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-15 | 200-PL-20020-01C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21319 | Reading on larger diameter | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 8.3 | CML-15 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 9 O'Clock | 150 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8.9 | 8 | 8 | 0.42426
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-4 | 25-DO-62008-15S01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6523 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:45 | [32 empty] | 9.45 | CML-4 | CML: Elbow | 1 | 2019-07-22 | 2017-02-03 | 2014-07-24 07:30 | 3.7 | 0.8202 | A4: Left Quadrant |  | 7.74 | 3.7 | 5.72 | 7.8 | 9 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 9.3 | 9.3 | 11.4 | 7.8 | 1.4799
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-3 | 25-DO-62008-15S01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6522 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:14 | [32 empty] | 9.875 | CML-3 | CML: Elbow | 1 | 2019-07-22 | 2017-02-03 | 2014-07-24 07:30 | 3.7 | 0.8202 | A4: Left Quadrant |  | 7.74 | 3.7 | 5.72 | 7.8 | 9 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 9.6 | 9.8 | 12.3 | 7.8 | 1.85
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-1 | 100-FH-43507-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7980 |  | 2015-01-18 14:00 | 2015-01-18 15:00 | [36 empty] | 6.45 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-18 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-FH-43507-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | -70.4827 | 6.3 | 6.5 | 6.8 | 6.2 | 0.26458
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-3 | 50-FG-45024-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1207 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.75 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.8 | 7.1 | 6.5 | 6.6 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43124-01C02 | CML-6 | 80-FH-43124-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12848 |  | 2014-02-05 11:00 | 2014-02-05 13:00 | [36 empty] | 5.75 | CML-6 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-02-05 11:00 | 0.54 | 0 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.5 | 9 O'Clock | 80 | 5.49 | 80-FH-43124-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 6.1 | 5.6 | 5.8 | 5.5 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-3 | 150-FH-43026-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23502 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 7.05 | CML-3 | CML: Pipe Length | 3 | 2045-05-18 | 2039-08-15 | 2015-07-28 07:00 | 1.03 | 0.19008 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.7 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.67 | 0.19837 | 7.2 | 7 | 6.7 | 7.3 | 0.26458
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-12 | 200-PL-20018-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 23884 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 8.6 | CML-12 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 12 O'Clock | 40 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 | 0 | 8 | 8.9 | 8.7 | 8.8 | 0.40825
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40038-01C02 | CML-1 | 200-WC-40038-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7709 |  | 2015-01-09 10:00 | 2015-01-09 12:00 | [36 empty] | 6.975 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-09 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 200 | 6.35 | 200-WC-40038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 6.9 | 7.2 | 7.1 | 0.22174
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-17 | 150-DC-57308-01C03 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20314 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 1.846mm/ yr | [35 empty] | 9.4 | CML-17 | CML: type TBC | 6 | 2017-12-31 | 2017-05-01 | 2014-10-02 07:00 | 2.5 | 1.8463 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 8.5 | 3 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.7 | 8.5 | 10.1 | 9.3 | 0.68313
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-13 | 150-DC-57308-01C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20310 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.25 | CML-13 | CML: Elbow | 6 | 2017-12-31 | 2017-05-01 | 2014-10-02 07:00 | 2.5 | 1.8463 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 8.5 | 3 O'Clock | 100 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.2 | 8.5 | 9.3 | 10 | 0.61373
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-2 | 25-DO-62008-15S01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6521 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:14 | [32 empty] | 9.85 | CML-2 | CML: Elbow | 1 | 2019-07-22 | 2017-02-03 | 2014-07-24 07:30 | 3.7 | 0.8202 | A4: Left Quadrant |  | 7.74 | 3.7 | 5.72 | 7.8 | 9 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 9.4 | 10 | 12.2 | 7.8 | 1.8212
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-12 | 25-DO-62008-15S01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 6531 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [35 empty] | Low alarm breach | 7.3 | CML-12 | CML: Elbow | 1 | 2017-02-05 | 2015-07-21 | 2014-07-24 07:30 | 2.5 | 1.6927 | A2: Right Quadrant |  | 7.74 | 2.5 | 5.12 | 6.8 | 3 O'Clock | 25 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.6 | 6.8 | 7.4 | 7.4 | 0.34641
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-10 | 25-DO-62008-15S01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 6529 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 10.625 | CML-10 | CML: Elbow | 1 | 2030-05-23 | 2023-08-03 | 2014-07-24 07:30 | 3.7 | 0.29667 | A4: Left Quadrant |  | 7.74 | 3.7 | 5.72 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 10.2 | 11.1 | 12.8 | 8.4 | 1.8337
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23405-03C02-P | CML-7 | 100-PG-23405-03C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 23859 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 9.425 | CML-7 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A1: Outside Quadrant |  |  | 2.7 |  | 8.7 | 12 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.7 | 9.7 | 10 | 9.3 | 0.56199
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-18 | 50-DH-56137-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21102 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 7.85 | CML-18 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 7.6 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.7 | 8.2 | 7.9 | 7.6 | 0.26458
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-7 | 25-DO-62008-15S01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 6526 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 10.475 | CML-7 | CML: Elbow | 1 | 2157-09-21 | 2099-11-19 | 2014-07-24 07:30 | 3.7 | 0.0349 | A4: Left Quadrant |  | 7.74 | 3.7 | 5.72 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 10.2 | 10.5 | 12.5 | 8.7 | 1.5628
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-12 | 200-PL-20018-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21248 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 8.6 | CML-12 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 12 O'Clock | 40 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.9 | 8.7 | 8.8 | 0.40825
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-3 | 300-FL-43080-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2382 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 8.35 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 3 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.6 | 8 | 8.3 | 8.5 | 0.26458
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56071-01C02 | CML-4 | 50-DH-56071-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3419 | Rope Access | 2014-05-11 13:00 | 2014-05-11 14:00 | [36 empty] | 8.45 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-11 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.1 | 12 O'Clock | 50 | 5.54 | 50-DH-56071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.4 | 8.7 | 8.6 | 0.26458
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-3 | 250-PW-20041-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21412 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.675 | CML-3 | CML: Elbow | 6 | 2109-01-31 | 2094-08-15 | 2014-07-12 07:30 | 4.1 | 0.08983 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.6 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 14.1 | 13.4 | 14.6 | 12.6 | 0.86939
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-1 | 50-FL-43454-01C02-P CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 20504 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 9.05 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.8 | 6 O'Clock | 80 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.1 | 9.4 | 8.8 | 8.9 | 0.26458
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-3 | 50-FL-43454-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22988 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.45 | CML-3 | CML: Elbow | 6 | 2090-02-04 | 2085-09-25 | 2015-05-05 07:00 | 2.5 | 0.08823 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.1 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | -1.8528 | 9.6 | 9.7 | 9.1 | 9.4 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-3 | 200-FH-43025-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2476 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 9.85 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 3 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.1 | 9.5 | 10 | 9.8 | 0.26458
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-3 | 150-WC-40002-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20342 | Reviewed on 18/11/14. Line is FFS. Repeat on Oct.19 | 2014-10-09 07:00 | 2014-10-09 15:00 | Check Corrosion Rate of 0.302mm/ yr |  | Nestor | 2014-11-24 10:28 | [32 empty] | 6.95 | CML-3 | CML: Fitting | 3 | 2028-08-30 | 2027-06-21 | 2014-10-09 07:00 | 2.5 | 0.30215 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 3 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.1 | 6.7 | 7 | 7 | 0.17321
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-18 | 50-PL-45016-03C03 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10458 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.95 | CML-18 | CML: type TBC | 6 | 2038-06-03 | 2035-08-07 | 2013-11-13 | 0.99 | 0.3097 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.61 |  | 8.6 | 8.9 | 9.1 | 9.2 | 0.26458
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40505-1CG | CML-2 | 250-WC-40505-1CG CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8628 | Rope Access / Material Class Not Selectable. Line is FFS. Only one CM-3 is showing high CR. Current RBI frequency is 48m Action: NIL. RBI to stay at 48m | 2015-02-10 08:00 | 2015-02-10 09:00 |  |  | Administrator | 2015-09-08 10:30 | [32 empty] | 15.625 | CML-2 | CML: Elbow | 3 | 2139-04-24 | 2091-05-12 | 2015-02-10 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 15.2 | 12 O'Clock | 250 | 15.09 | 250-WC-40505-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.7 |  | 15.2 | 15.7 | 16.3 | 15.3 | 0.49917
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-12 | 200-PG-23007-09C03-PA CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23403 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 19.85 | CML-12 | CML: Fitting | 6 | 2035-03-24 | 2030-08-11 | 2015-07-22 07:00 | 10.22 | 0.47652 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 19.6 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.38 | 0.28313 | 19.9 | 20.2 | 19.7 | 19.6 | 0.26458
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20017-01C02-P | CML-6 | 200-PL-20017-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21245 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.375 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 12 O'Clock | 200 | 6.35 | 200-PL-20017-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.2 | 8.4 | 8.9 | 0.38622
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20062-01C03-P | CML-4 | 250-PG-20062-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21541 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 10.425 | CML-4 | CML: Fitting | 6 | 2081-02-10 | 2077-04-05 | 2014-07-13 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 10.2 | 6 O'Clock | 300 | 9.27 | 250-PG-20062-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.3 | 10.8 | 10.2 | 10.4 | 0.263
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-11 | 150-PG-20054-01C03-P CML-11 |  | FPSO 2016 | Pipe Wall Thickness | 24461 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | [36 empty] | 12.425 | CML-11 | CML: Fitting | 6 | 2098-02-09 | 2085-10-05 | 2016-07-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 12.2 | 9 O'Clock | 200 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 | 0.31197 | 12.8 | 12.4 | 12.3 | 12.2 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-26 | 50-DH-56062-01C02 CML-26 | yes | FPSO 2015 | Pipe Wall Thickness | 9113 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.675 | CML-26 | CML: type TBC | 3 | 2017-09-15 | 2018-03-02 | 2015-03-02 07:00 | 2.5 | 0.70797 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.8 | 4.9 | 4.7 | 4.3 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-2 | 50-WC-40032-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1236 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 6.9 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 12 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7 | 6.9 | 7 | 0.14142
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-9 | 250-PW-44006-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8001 | Leak | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.7 | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 | 0.24328 | 6.8 | 6.7 | 6.9 | 6.4 | 0.21602
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-1 | 50-CG-38476-01C02-H CML-1 | Yes | FPSO 2015 | Pipe Wall Thickness | 23633 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.175 | CML-1 | CML: Pipe Length | 3 | 2023-04-22 | 2024-05-13 | 2015-10-28 07:00 | 2.5 | 0.30718 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 4.8 | 5.3 | 5.4 | 0.263
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62004-01S01 | CML-11 | 50-DO-62004-01S01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1460 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [36 empty] | 9.2 | CML-11 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2014-04-25 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 8.5 | 6 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10 | 9.1 | 8.5 | 9.2 | 0.61644
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-9 | 80-PW-44034-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21991 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.85 | CML-9 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.2 | 12 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 7.1 | 7.4 | 6.7 | 0.51962
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43513-01C02 | CML-1 | 50-FL-43513-01C02 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 7983 | Line is FFS. Current RBI frequency is 48m Action: to recheck line in 24m (Jan. 2017) to confirm CR. RBI frequency to be updated | 2015-01-18 16:00 | 2015-01-18 17:00 |  |  | Administrator | 2015-09-07 14:59 | [32 empty] | 5.025 | CML-1 | CML: Elbow | 3 | 2020-02-16 | 2020-11-05 | 2015-01-18 16:00 | 2.5 | 0.45268 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FL-43513-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 4.9 | 5.4 | 4.8 | 0.263
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38463-01C02 | CML-2 | 50-CG-38463-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3113 | Rope Access | 2014-05-04 08:00 | 2014-05-04 09:00 | [36 empty] | 5.175 | CML-2 | CML: Elbow | 3 | 2017-03-17 | 2017-08-13 | 2014-05-04 08:00 | 2.5 | 0.80069 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-CG-38463-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 4.8 | 5.3 | 5.2 | 0.263
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-4 | 50-FG-45018-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2586 | Rope Access | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 5.025 | CML-4 | CML: type TBC | 3 | 2017-02-12 | 2017-02-03 | 2014-04-26 07:00 | 2.5 | 0.82025 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | -0.2249 | 4.9 | 5 | 4.8 | 5.4 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40016-01C02 | CML-6 | 250-WC-40016-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20368 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-24 10:38 | [32 empty] | 6.825 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 3 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.9 | 6.7 | 6.8 | 6.9 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-1 | 100-FH-43507-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7750 |  | 2015-01-11 08:00 | 2015-01-11 09:00 | [36 empty] | 5.025 | CML-1 | CML: type TBC | 3 | 2020-01-17 | 2020-10-02 | 2015-01-11 08:00 | 2.5 | 0.45831 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FH-43507-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 4.9 | 5.4 | 4.8 | 0.263
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56133-01C02 | CML-1 | 50-DN-56133-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1318 |  | 2014-03-31 10:15 | 2014-03-31 10:30 | [36 empty] | 8.7 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-31 10:15 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.5 | 6 O'Clock | 50 | 5.54 | 50-DN-56133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.7 | 8.8 | 8.5 | 8.8 | 0.14142
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-17 | 80-PW-44001-01C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 22008 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.5 | CML-17 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.2 | 3 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 6.2 | 6.4 | 6.7 | 0.24495
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20927 | Rope Access | 2014-05-18 08:00 | 2014-05-18 09:00 | [36 empty] | 5.475 | CML-2 | CML: type TBC | 3 | 2020-10-15 | 2021-08-25 | 2014-05-18 08:00 | 2.5 | 0.40517 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 12 O'Clock | 80 | 5.49 | 80-DH-56042-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.6 | 5.7 | 5.5 | 0.263
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-5 | 25-DO-62008-15S01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6524 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:16 | [32 empty] | 10.5 | CML-5 | CML: Elbow | 1 | 2063-10-24 | 2043-08-12 | 2014-07-24 07:30 | 3.7 | 0 | A4: Left Quadrant |  | 7.74 | 3.7 | 5.72 | 8.8 | 9 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 11.1 | 10.4 | 11.7 | 8.8 | 1.2517
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43118-01C02 | CML-3 | 50-FH-43118-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1758 | Rope access | 2014-04-27 08:00 | 2014-04-27 08:30 | [36 empty] | 5.525 | CML-3 | CML: Pipe Length | 3 | 2024-11-14 | 2026-02-06 | 2014-04-27 08:00 | 2.5 | 0.26519 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FH-43118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.9 | 5.5 | 5.4 | 0.263
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45004-03C02 | CML-5 | 150-FG-45004-03C02 CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24337 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. No internal damage in RBI | [31 empty] | 5.975 | CML-5 | CML: Fitting | 3 | 2022-08-15 | 2021-01-05 | 2016-06-06 07:00 | 2.5 | 0.50046 | A2: Right Quadrant |  | 4.11 | 2.5 | 3.305 | 5.6 | 3 O'Clock | 150 | 7.11 | 150-FG-45004-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 5.6 | 6 | 6.1 | 0.263
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-9 | 50-CG-38476-01C02-H CML-9 | Yes | FPSO 2015 | Pipe Wall Thickness | 23641 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.825 | CML-9 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.7 | 6.2 | 5.6 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56043-01C02 | CML-1 | 80-DH-56043-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20929 | Rope Access | 2014-05-16 07:00 | 2014-05-16 08:00 | [36 empty] | 5.825 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-DH-56043-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.2 | 5.8 | 5.7 | 0.263
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38495-01C02 | CML-3 | 25-CG-38495-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10400 | Deck Level | 2013-11-12 | 2013-11-12 | Dissimilar metals in contact. | [35 empty] | 5.825 | CML-3 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 25 | 6.35 | 25-CG-38495-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 6.2 | 5.8 | 5.6 | 5.7 | 0.263
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-29 | 200-PL-20010-01C02-P CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 23829 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.425 | CML-29 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 3 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.4 | 8 | 8.9 | 8.4 | 0.36856
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-12 | 50-FG-45023-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1160 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.475 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 | -5.3761 | 6.6 | 6.1 | 6.7 | 6.5 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-10 | 250-FH-43303-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12948 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.525 | CML-10 | CML: type TBC | 3 | 2064-02-06 | 2063-09-23 | 2014-01-27 10:00 | 2.5 | 0.07591 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 9 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.4 | 6.5 | 6.9 | 6.3 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 150-DH-56080-01C02 | CML-6 | 150-DH-56080-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3329 | Rope Access | 2014-05-08 07:00 | 2014-05-08 09:00 | [36 empty] | 6.975 | CML-6 | CML: type TBC | 3 | 2021-11-11 | 2021-03-14 | 2014-05-08 07:00 | 2.5 | 0.54543 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 3 O'Clock | 150 | 7.11 | 150-DH-56080-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 6.6 | 7.1 | 7.2 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-16 | 150-WC-40004-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1818 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | Check Corrosion Rate of 0.34mm/ yr | [35 empty] | 7.325 | CML-16 | CML: Elbow | 3 | 2026-12-13 | 2025-11-22 | 2014-04-29 11:00 | 2.5 | 0.34034 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 6 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.5 | 6.8 | 8.2 | 0.6702
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-18 | 250-PW-44006-01X01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8010 | Leak | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.525 | CML-18 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 6 O'Clock | 150 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 | 0.12164 | 6.7 | 6.4 | 6.4 | 6.6 | 0.15
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3484 | Rope Access | 2014-05-14 09:30 | 2014-05-14 11:00 | [36 empty] | 7.325 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-14 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.1 | 3 O'Clock | 80 | 5.49 | 80-DH-56022-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.7 | 7.1 | 7.2 | 7.3 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43517-01C02 | CML-3 | 150-FH-43517-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20471 | Rope Access | 2014-05-27 14:00 | 2014-05-27 15:00 | [36 empty] | 7.475 | CML-3 | CML: type TBC | 3 |  |  | 2014-05-27 14:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 7.1 | 6 O'Clock | 150 |  | 150-FH-43517-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.7 | 7.6 | 7.1 | 7.5 | 0.263
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-9 | 25-DO-62008-15S01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 6528 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 10.325 | CML-9 | CML: Elbow | 1 | 2063-10-24 | 2043-08-12 | 2014-07-24 07:30 | 3.7 | 0 | A4: Left Quadrant |  | 7.74 | 3.7 | 5.72 | 8.9 | 9 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 10.4 | 10.3 | 11.7 | 8.9 | 1.1442
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-8 | 25-DO-62008-15S01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 6527 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 10.825 | CML-8 | CML: Elbow | 1 | 2063-10-24 | 2043-08-12 | 2014-07-24 07:30 | 3.7 | 0 | A4: Left Quadrant |  | 7.74 | 3.7 | 5.72 | 9.3 | 9 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 10.3 | 10.9 | 12.8 | 9.3 | 1.4728
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-6 | 25-DO-62008-15S01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 6525 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:45 | [32 empty] | 9.65 | CML-6 | CML: Fitting | 1 | 2063-10-24 | 2043-08-12 | 2014-07-24 07:30 | 3.7 | 0 | A1: Outside Quadrant |  | 7.74 | 3.7 | 5.72 | 9.6 | 3 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.6 | 9.6 | 9.7 | 9.7 | 0.057735
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40005-01C02 | CML-4 | 150-WC-40005-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3157 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | Check Corrosion Rate of 0.337mm/ yr | [35 empty] | 7.7 | CML-4 | CML: Elbow | 3 | 2027-01-25 | 2025-12-31 | 2014-05-02 07:00 | 2.5 | 0.33747 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 12 O'Clock | 150 | 7.11 | 150-WC-40005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.8 | 7.9 | 8.3 | 0.6377
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-11 | 25-DO-62008-15S01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 6530 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 11.5 | CML-11 | CML: Reducer | 1 | 2063-10-24 | 2043-08-12 | 2014-07-24 07:30 | 3.7 | 0 | A2: Right Quadrant |  | 7.74 | 3.7 | 5.72 | 11.2 | 3 O'Clock | 50 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 11.6 | 11.2 | 11.7 | 11.5 | 0.21602
FG04 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-FG-45003-03C02 | CML-9 | 150-FG-45003-03C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23244 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.825 | CML-9 | CML: Elbow | 3 | 2019-09-11 | 2020-05-15 | 2015-05-11 07:00 | 2.5 | 0.48372 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0 | 4.6 | 5.1 | 4.6 | 5 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-11 | 250-WC-40017-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2074 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 7.2 | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 8 | 7.2 | 6.8 | 6.8 | 0.56569
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-12 | 100-DH-56082-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 3380 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.475 | CML-12 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 6.7 | 6.7 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56084-01C02 | CML-6 | 100-DH-56084-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3348 | Rope Access | 2014-05-08 13:00 | 2014-05-08 14:00 | [36 empty] | 7.525 | CML-6 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.3 | 9 O'Clock | 100 | 6.02 | 100-DH-56084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.8 | 7.3 | 7.7 | 7.3 | 0.263
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-25 | 250-PW-44006-01X01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 8017 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.6 | CML-25 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 | -0.48657 | 6.7 | 6.6 | 6.4 | 6.7 | 0.14142
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57001-01C02 | CML-1 | 80-DC-57001-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12501 |  | 2014-02-04 15:00 | 2014-02-04 16:00 | [36 empty] | 6.8 | CML-1 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-02-04 15:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 6.6 | 12 O'Clock | 80 | 5.49 | 80-DC-57001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.06 |  | 6.6 | 7 | 6.8 | 6.8 | 0.1633
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43170-01C02 | CML-1 | 250-FL-43170-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2886 | Rope Access | 2014-04-25 07:00 | 2014-04-25 08:00 | [36 empty] | 9.075 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-04-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.8 | 6 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.3 | 9.3 | 8.8 | 8.9 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-16 | 400-FH-43500-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 5652 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 9.575 | CML-16 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 9.3 | 3 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.8 | 9.3 | 9.4 | 9.8 | 0.263
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-30 | 200-PL-20008-01C02-H CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 8827 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.1 | CML-30 | CML: Elbow | 3 | 2039-04-20 | 2035-09-17 | 2015-02-21 07:00 | 1.1 | 0.20268 | A1: Outside Quadrant |  | 3.35 | 1.1 | 1.8281 | 6 | 3 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 6 | 6 | 6.2 | 6.2 | 0.11547
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-1 | 100-DH-56561-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7933 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 10.275 | CML-1 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-17 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10 | 6 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.5 | 10.5 | 10 | 10.1 | 0.263
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23072-03C03 | CML-3 | 100-PG-23072-03C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20607 | Rope Access. Line is FFS | 2014-05-25 10:30 | 2014-05-25 11:30 |  |  | Administrator | 2015-09-08 08:12 | [32 empty] | 11.175 | CML-3 | CML: type TBC | 6 | 2050-03-28 | 2044-08-16 | 2014-05-25 10:30 | 2.5 | 0.23421 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 6 O'Clock | 100 | 11.13 | 100-PG-23072-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.4 | 11 | 10.9 | 11.4 | 0.263
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43079-01C02 | CML-9 | 50-FL-43079-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 3052 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 5.175 | CML-9 | CML: type TBC | 3 | 2017-10-15 | 2018-04-04 | 2014-05-03 07:00 | 2.5 | 0.69464 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5 | 5.4 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-13 | 100-DH-56009-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 3436 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.275 | CML-13 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5 | 6 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.5 | 5 | 5.5 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56061-01C02 | CML-3 | 50-DH-56061-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3367 | Rope Access | 2014-05-10 08:00 | 2014-05-10 09:00 | [36 empty] | 5.275 | CML-3 | CML: type TBC | 3 | 2018-09-15 | 2019-04-11 | 2014-05-10 08:00 | 2.5 | 0.57408 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DH-56061-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.5 | 5.5 | 5 | 0.263
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23301-01C02 | CML-1 | 80-VA-23301-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22508 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.225 | CML-1 | CML: Reducer | 3 | 2024-11-29 | 2026-04-02 | 2015-04-20 07:00 | 2.5 | 0.25985 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 50 | 5.49 | 80-VA-23301-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.5 | 5 | 0.263
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45007-03C02-E | CML-1 | 100-FG-45007-03C02-E CML-1 | yes | FPSO 2016 | Pipe Wall Thickness | 24308 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 | Wet CO2 Gas Corrosion, downstream of super heaters and approaching dew point temperature (36 Deg C) |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.825 | CML-1 | CML: Elbow | 3 | 2022-02-15 | 2020-12-04 | 2016-05-27 07:00 | 1.88 | 0.47494 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 4.6 | 9 O'Clock | 100 | 6.02 | 100-FG-45007-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.72 |  | 5.1 | 4.6 | 5 | 4.6 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-24 | 250-WC-40026-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 1300 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.1 | CML-24 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 9 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.7 |  | 6.8 | 0.51962
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44029-01C02 | CML-5 | 250-PW-44029-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22902 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 6.3 | CML-5 | CML: Pipe Length | 3 | 2062-07-22 | 2062-03-13 | 2015-05-01 07:00 | 2.5 | 0.07829 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | 6.3243 | 6.3 | 6.4 | 6.3 | 6.2 | 0.08165
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-36 | 250-PW-44006-01X01 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 8028 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.45 | CML-36 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 | -0.72985 | 6.4 | 6.5 | 6.5 | 6.4 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-15 | 50-FH-43011-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 7965 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 7.325 | CML-15 | CML: type TBC | 3 | 2024-03-16 | 2022-10-13 | 2015-01-18 08:00 | 2.5 | 0.5019 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.1 | 9 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.5 | 7.6 | 7.1 | 0.263
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-19 | 150-FG-45505-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 22359 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.725 | CML-19 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.9 | 7.5 | 8 | 0.263
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 25-DO-62008-15S01 | CML-1 | 25-DO-62008-15S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6520 | Rope Access | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:11 | [32 empty] | 11.475 | CML-1 | CML: Reducer | 1 | 2075-10-24 | 2049-08-12 | 2014-07-24 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 7.74 | 2.5 | 5.12 | 11.2 | 9 O'Clock | 25 | 8.74 | 50-DO-62008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.4 | 12 | 11.3 | 11.2 | 0.3594
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40046-01C02 | CML-7 | 300-WC-40046-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1257 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7.1 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 9 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7 | 7.6 | 7 | 6.8 | 0.34641
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40405-01C02 | CML-6 | 150-WC-40405-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20400 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 7.125 | CML-6 | CML: type TBC | 3 | 2033-11-27 | 2032-04-20 | 2014-10-17 07:00 | 2.5 | 0.22482 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 6 O'Clock | 150 | 7.11 | 150-WC-40405-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7 | 7.1 | 6.8 | 7.6 | 0.34034
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-8 | 0200-DH-56L9003-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5093 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 9 | CML-8 | CML: type TBC | 3 | 2109-05-02 | 2092-10-04 | 2015-03-06 07:00 | 2.5 | 0.06474 | A2: Right Quadrant |  | 5.74 | 2.5 | 3.5737 | 8.6 | 3 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.9 | 8.6 | 8.8 | 9.7 | 0.48305
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML17 | 150-FH-43141-01C02 CML17 | yes | FPSO 2015 | Pipe Wall Thickness | 7262 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 16:44 | [32 empty] | 3.625 | CML17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.8 | 3.9 | 3.4 | 0.263
DH01 | Montara_Topside | Yes | Potable Water (53) | Pipework | 80-DH-56004-01C02 | CML-4 | 80-DH-56004-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 5108 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 3.575 | CML-4 | CML: type TBC | 0 | 2023-07-31 | 2020-10-31 | 2015-03-06 07:00 | 2.5 | 0.08324 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.2 | 3 O'Clock | 25 | 3.38 | 0100-WZ-53L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.6 | 3.2 | 3.8 | 3.7 | 0.263
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67007-01E01 | CML-8 | 50-GN-67007-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8479 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 8.75 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.6 | 3 O'Clock | 50 | 5.54 | 50-GN-67007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.8 | 8.6 | 8.7 | 8.9 | 0.1291
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57402-01C03 | CML-8 | 50-DC-57402-01C03 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8365 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.2 | CML-8 | CML: type TBC | 6 | 2087-07-11 | 2086-02-06 | 2015-01-29 07:30 | 2.5 | 0.08414 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-DC-57402-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.1 | 9.8 | 9.3 | 0.49666
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57401-01C03 | CML-1 | 50-DC-57401-01C03 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8356 |  | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 8.7 | CML-1 | CML: type TBC | 6 | 2087-05-28 | 2085-12-24 | 2015-01-28 07:30 | 2.5 | 0.08428 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-DC-57401-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.7 | 8.8 | 8.7 | 0.08165
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23301-01C02 | CML-5 | 80-VA-23301-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22512 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.875 | CML-5 | CML: Pipe Length | 3 | 2016-03-31 | 2016-07-29 | 2015-04-20 07:00 | 2.5 | 1.0553 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.5 | 12 O'Clock | 50 | 5.49 | 80-VA-23301-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.5 | 3.9 | 4.1 | 4 | 0.263
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-18 | 250-PW-44006-01X01 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1915 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 7.225 | CML-18 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 150 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.8 | 6.9 | 6.5 | 7.7 | 0.62915
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-3 | 250-PW-44006-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1900 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 7.25 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.4 | 6.5 | 7.4 | 7.7 | 0.51962
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-10 | 50-CG-38457-01C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23728 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.075 | CML-10 | CML: Elbow | 3 | 2022-02-23 | 2023-01-31 | 2015-10-30 07:00 | 2.5 | 0.3479 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 4.7 | 5.1 | 5.2 | 0.263
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38472-01C02 | CML-7 | 50-CG-38472-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23662 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.925 | CML-7 | CML: Elbow | 3 | 2022-02-23 | 2023-01-31 | 2015-10-30 07:00 | 2.5 | 0.3479 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38472-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 4.8 | 5.3 | 4.7 | 0.263
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24036-09C02 | CML-1 | 50-PL-24036-09C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13160 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 8.35 | CML-1 | CML: type TBC | 3 | 2018-10-06 | 2017-05-17 | 2014-01-18 15:00 | 2.5 | 1.1661 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8 | 12 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.6 | 8.7 | 8.1 | 0.35119
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-9 | 25-VA-23054-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1478 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 5.275 | CML-9 | CML: type TBC | 3 | 2017-09-26 | 2018-03-15 | 2014-04-29 10:00 | 2.5 | 0.70273 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 5.5 | 4.9 | 5.4 | 0.263
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80005-01C02 | CML-7 | 50-VA-80005-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3133 | Rope Access | 2014-05-02 10:30 | 2014-05-02 11:30 | [36 empty] | 5.225 | CML-7 | CML: type TBC | 3 | 2018-08-02 | 2019-02-21 | 2014-05-02 10:30 | 2.5 | 0.58759 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-VA-80005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.6 | 5.1 | 5.2 | 0.263
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44036-01C02-P | CML-1 | 80-PW-44036-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21953 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 6.825 | CML-1 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.3 | 6 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.3 | 6.8 | 6.3 | 6.9 | 0.4113
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-5 | 50-FG-45023-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12991 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 5.225 | CML-5 | CML: type TBC | 3 | 2017-01-04 | 2017-05-25 | 2014-01-20 07:00 | 2.5 | 0.84487 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.1 | 5.6 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43121-01C02 | CML-1 | 150-FH-43121-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 1764 | Rope access | 2014-04-27 09:30 | 2014-04-27 11:00 | [36 empty] | 5.375 | CML-1 | CML: Elbow | 3 | 2015-06-28 | 2015-04-30 | 2014-04-27 09:30 | 2.5 | 2.2205 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.1 | 12 O'Clock | 150 | 7.11 | 150-FH-43121-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.6 | 5.2 | 5.6 | 0.263
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-3 | 200-PW-44020-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23010 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 6.725 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-05 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | 0.57083 | 7.2 | 6.6 | 6.5 | 6.6 | 0.32016
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80001-01C02 | CML-3 | 50-VA-80001-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3136 | Rope Access | 2014-05-02 09:30 | 2014-05-02 10:30 | [36 empty] | 5.425 | CML-3 | CML: type TBC | 3 | 2021-08-16 | 2022-07-04 | 2014-05-02 09:30 | 2.5 | 0.37001 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-VA-80001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.2 | 5.7 | 5.2 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43142-01C02 | CML-5 | 100-FH-43142-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10523 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.575 | CML-5 | CML: type TBC | 3 | 2015-05-18 | 2015-06-11 | 2013-11-15 | 2.5 | 1.7922 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 9 O'Clock | 100 | 6.02 | 100-FH-43142-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.6 | 5.8 | 5.2 | 0.263
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-7 | 200-PW-44020-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23014 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 6.65 | CML-7 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 9 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | 1.7125 | 6.6 | 6.8 | 6.7 | 6.5 | 0.1291
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-9 | 250-PW-44006-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1906 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 7.125 | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.6 | 7.7 | 7.4 | 0.51235
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56021-01C02 | CML-2 | 80-DH-56021-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3479 | Rope Access | 2014-05-14 07:00 | 2014-05-14 08:00 | [36 empty] | 5.575 | CML-2 | CML: type TBC | 3 | 2028-05-18 | 2030-02-13 | 2014-05-14 07:00 | 2.5 | 0.19969 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-DH-56021-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.8 | 5.4 | 5.3 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-3 | 100-WC-40035-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1736 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.175 | CML-3 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.8 | 9 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7 | 7.5 | 7.4 | 6.8 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40046-01C02 | CML-6 | 300-WC-40046-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1256 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7.025 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 6 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7 | 6.8 | 7.5 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40405-01C02 | CML-4 | 150-WC-40405-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20398 | Reviewed 24/11/14. FFS. Repeat on Oct. 19 | 2014-10-17 07:00 | 2014-10-17 15:00 |  |  | Nestor | 2014-11-24 10:32 | [32 empty] | 7.175 | CML-4 | CML: Elbow | 3 | 2033-11-27 | 2032-04-20 | 2014-10-17 07:00 | 2.5 | 0.22482 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 6 O'Clock | 150 | 7.11 | 150-WC-40405-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.4 | 7.2 | 6.8 | 7.3 | 0.263
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-10 | 250-PW-44004-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5629 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 6.825 | CML-10 | CML: Reducing Tee | 3 | 2094-06-25 | 2093-11-21 | 2014-06-20 13:00 | 2.5 | 0.04746 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7 | 6.8 | 6.3 | 7.2 | 0.38622
PG05 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1937 | Rope Access. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Mar. 2020). RBI to be updated | 2014-03-26 09:30 | 2014-03-26 10:30 |  |  | Administrator | 2015-09-08 12:55 | [32 empty] | 5.625 | CML-2 | CML: Pipe Length | 3 | 2031-02-26 | 2033-01-21 | 2014-03-26 09:30 | 2.5 | 0.17125 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.6 | 5.5 | 5.4 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43126-01C02 | CML-4 | 100-FH-43126-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2513 | Rope Access | 2014-03-24 14:30 | 2014-03-24 15:00 | [36 empty] | 6.075 | CML-4 | CML: type TBC | 3 | 2022-05-07 | 2022-08-23 | 2014-03-24 14:30 | 2.5 | 0.39379 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 6 O'Clock | 100 | 6.02 | 100-FH-43126-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.1 | 6.3 | 5.7 | 6.2 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-10 | 50-FH-43011-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7960 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.075 | CML-10 | CML: Fitting | 3 | 2017-08-03 | 2017-01-14 | 2015-01-18 08:00 | 2.5 | 1.2976 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 5.8 | 12 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.3 | 5.9 | 6.3 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-28 | 50-DH-56137-01C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 21112 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.125 | CML-28 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5.9 | 3 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.5 | 5.9 | 6 | 6.1 | 0.263
FG02 | Montara_Topside | Yes | Potable Water (53) | Pipework | 25-FG-45455-01C02-E | CML-14 | 25-FG-45455-01C02-E CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8257 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.375 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.6 | 6.4 | 6.5 | 6 | 0.263
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-13 | 25-FG-45455-01C02-E CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21816 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6.225 | CML-13 | CML: Pipe Length | 3 | 2253-01-17 | 2260-12-16 | 2014-10-11 07:00 | 2.5 | 0.01468 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.6 | 6.1 | 6.2 | 6 | 0.263
FG02 | Montara_Topside | Yes | Main Power (80) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2165 | Rope Access | 2014-03-30 09:30 | 2014-03-30 11:00 | [36 empty] | 6.225 | CML-5 | CML: type TBC | 3 | 2159-02-17 | 2163-12-11 | 2014-03-30 09:30 | 2.5 | 0.02414 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 6 O'Clock | 100 | 6.02 | 100-VA-80002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.6 | 6 | 6.1 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-7 | 300-FH-43001-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12519 |  | 2014-01-24 13:00 | 2014-01-24 15:00 | [36 empty] | 6.425 | CML-7 | CML: type TBC | 3 | 2030-02-08 | 2029-12-26 | 2014-01-24 13:00 | 2.5 | 0.23049 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.6 | 6.7 | 6.2 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-5 | 200-FH-43038-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12686 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 6.425 | CML-5 | CML: type TBC | 3 | 2031-01-04 | 2030-11-18 | 2014-02-06 09:00 | 2.5 | 0.21867 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.8 | 6.3 | 6.4 | 6.2 | 0.263
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-6 | 200-PL-20020-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21310 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 8.375 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 12 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.2 | 8.6 | 8.7 | 0.3304
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40046-01C02 | CML-5 | 300-WC-40046-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1255 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7.1 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 9 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.4 | 7.2 | 7 | 6.8 | 0.2582
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-21 | 50-FG-45024-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 1204 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.625 | CML-21 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.8 | 6.9 | 6.4 | 6.4 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-1 | 200-FH-43037-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12670 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 6.625 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7 | 6.5 | 6.6 | 0.263
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-19 | 50-PL-24003-09C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 13158 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.725 | CML-19 | CML: type TBC | 3 | 2019-08-06 | 2017-12-28 | 2014-01-18 13:00 | 2.5 | 1.0089 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 9 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.9 | 9.5 | 8.4 | 8.1 | 0.61305
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-15 | 150-PG-20054-01C03-P CML-15 | yes | FPSO 2016 | Pipe Wall Thickness | 24462 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | [36 empty] | 6.875 | CML-15 | CML: Elbow | 6 | 2019-04-12 | 2018-06-04 | 2016-07-05 07:00 | 2.5 | 1.4435 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 6.5 | 6 O'Clock | 100 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | 0.41595 | 6.9 | 7.1 | 6.5 | 7 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-4 | 250-FH-43303-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12942 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.875 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.6 | 7.1 | 7.1 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43306-01C02 | CML-9 | 80-FH-43306-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5768 | Rope access | 2014-06-23 09:30 | 2014-06-23 11:00 | [36 empty] | 5.075 | CML-9 | CML: Elbow | 3 | 2020-01-23 | 2019-03-19 | 2014-06-23 09:30 | 0.54 | 0.74433 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 4.7 | 3 O'Clock | 80 | 5.49 | 80-FH-43306-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.16 |  | 5.1 | 4.7 | 5.3 | 5.2 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-4 | 80-FH-43009-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12582 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.425 | CML-4 | CML: Elbow | 3 | 2025-01-24 | 2023-07-31 | 2014-02-05 08:00 | 0.54 | 0.42453 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 5.2 | 5.8 | 5.3 | 5.4 | 0.263
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 7827 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:44 | [32 empty] | 7.425 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-13 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 6 O'Clock | 25 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.6 | 7.2 | 7.2 | 7.7 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-16 | 200-FH-43003-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12539 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.775 | CML-16 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 11:30 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.06 |  | 6.8 | 7 | 6.9 | 6.4 | 0.263
FH02 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43313-01S01-P | CML-2 | 150-FH-43313-01S01-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20476 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.875 | CML-2 | CML: Elbow | 1 | 2059-07-07 | 2045-11-27 | 2014-10-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 6.11 | 2.5 | 3.8606 | 7.6 | 3 O'Clock | 150 | 7.11 | 150-FH-43313-01S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.1 | 7.6 | 7.7 | 8.1 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56084-01C02 | CML-1 | 100-DH-56084-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3343 | Rope Access | 2014-05-08 13:00 | 2014-05-08 14:00 | [36 empty] | 8.125 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.9 | 3 O'Clock | 100 | 6.02 | 100-DH-56084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.1 | 7.9 | 8.5 | 8 | 0.263
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-23 | 350-FL-43511-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 2304 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 8.225 | CML-23 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 8 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.1 | 8.2 | 8.6 | 8 | 0.263
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-4 | 200-PW-44021-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23019 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 6.675 | CML-4 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 | -3.442 | 6.6 | 6.8 | 6.7 | 6.6 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-7 | 200-FH-43131-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2828 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.425 | CML-7 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.2 | 6 O'Clock | 200 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.86 |  | 7.3 | 7.8 | 7.2 | 7.4 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40046-01C02 | CML-1 | 300-WC-40046-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1251 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7.125 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 6 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.4 | 7.2 | 6.8 | 7.1 | 0.25
PL03 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-57066-01C03 | CML-3 | 50-PL-57066-01C03 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22967 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.525 | CML-3 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2015-05-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.3 | 3 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | -0.11633 | 9.4 | 9.3 | 9.9 | 9.5 | 0.263
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-5 | 50-PW-44013-01X01 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10319 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 7.5 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2013-11-10 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 9 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 8.4 | 7.4 |  | 6.7 | 0.8544
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-6 | 50-PL-23052-09C03 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10170 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.225 | CML-6 | CML: type TBC | 6 | 2016-10-25 | 2016-05-08 | 2013-11-09 | 2.81 | 2.4258 | A4: Left Quadrant |  | 5.07 | 2.81 | 3.94 | 10 | 9 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.19 |  | 10.2 | 10.6 | 10.1 | 10 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-5 | 400-FH-43508-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6554 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 11.625 | CML-5 | CML: Reducer | 3 | 2062-08-12 | 2057-12-18 | 2015-03-30 07:00 | 3 | 0 | A2: Right Quadrant |  | 4.92 | 3 | 3.465 | 11.4 | 3 O'Clock | 500 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 12 | 11.4 | 11.5 | 11.6 | 0.263
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20508-03C03-P | CML-2 | 300-PF-20508-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6511 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 14.525 | CML-2 | CML: Fitting | 6 | 2107-02-11 | 2090-04-05 | 2014-07-24 07:30 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.3 | 9 O'Clock | 300 | 14.27 | 300-PF-20508-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 14.4 | 14.9 | 14.5 | 14.3 | 0.263
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-19 | 100-PG-23503-03C03-A CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2735 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 11.175 | CML-19 | CML: Elbow | 6 | 2026-05-14 | 2026-12-29 | 2014-03-13 09:00 | 5.66 | 0.42208 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.8 | 12 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.14 |  | 10.8 | 11.3 | 11.4 | 11.2 | 0.263
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-2 | 200-PW-44019-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23030 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 7.8 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 | 1.4787 | 6.7 | 8.7 | 7.9 | 7.9 | 0.82462
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-8 | 200-PW-44020-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23015 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 7.4 | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.6 | 7.9 | 7.4 | 0.5099
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56134-01C02 | CML-1 | 50-DN-56134-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1313 |  | 2014-03-31 10:00 | 2014-03-31 10:15 | [36 empty] | 8.675 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-31 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.6 | 6 O'Clock | 50 | 5.54 | 50-DN-56134-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.6 | 8.6 | 8.8 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML 4 | 200-PW-44021-01X01 CML 4 |  | FPSO 2014 | Pipe Wall Thickness | 22368 |  | 2014-06-19 13:00 | 2014-06-19 14:00 | [36 empty] | 6.8 | CML 4 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 40 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 6.8 | 6.9 | 6.8 | 0.08165
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-28 | 150-PG-23506-25C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 2802 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.525 | CML-28 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 22.3 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.42 |  | 22.8 | 22.3 | 22.7 | 22.3 | 0.263
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24036-09C02 | CML-10 | 50-PL-24036-09C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 13169 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 8.65 | CML-10 | CML: type TBC | 3 | 2019-08-07 | 2017-12-29 | 2014-01-18 15:00 | 2.5 | 1.0085 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 6 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 9.4 | 8.5 | 8.1 | 8.6 | 0.54467
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-8 | 250-PW-44004-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5627 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 7.325 | CML-8 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-06-20 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.4 | 8.1 | 7.4 | 0.6994
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-9 | 100-PG-23028-25C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 448 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 16 | CML-9 | CML: Pipe Length | 3 | 2017-08-25 | 2016-05-09 | 2014-03-12 09:00 | 9.4 | 1.8226 | A1: Outside Quadrant |  | 14.12 | 9.4 | 11.76 | 15.7 | 12 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 15.7 | 16.3 | 15.9 | 16.1 | 0.2582
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20013-01C02-P | CML-6 | 200-PL-20013-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21216 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.575 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 12 O'Clock | 200 | 6.35 | 200-PL-20013-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 9.2 | 8.5 | 8.5 | 0.45735
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-16 | 100-DC-57075-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2435 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | [36 empty] | 9.7 | CML-16 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.6 | 12 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.6 | 10.2 | 10.4 | 0.80829
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-5 | 100-DC-57075-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2424 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | [36 empty] | 9.45 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.6 | 12 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.5 | 9.5 | 10.2 | 0.65574
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23048-09C02 | CML-10 | 50-PG-23048-09C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20592 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9 | CML-10 | CML: Reducer | 3 | 2189-07-31 | 2143-11-05 | 2014-07-18 11:00 | 2.5 | 0.0354 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 3 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.9 | 8.7 | 9.3 | 9.1 | 0.2582
FG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-FG-45024-01C02 | CML-4 | 50-FG-45024-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13143 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 9.5 | CML-4 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-01-18 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 9 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.4 | 9.6 | 9.8 | 9.2 | 0.2582
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-12 | 300-PG-20005-03C03-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22774 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 12.5 | CML-12 | CML: Pipe Length | 6 | 2022-01-21 | 2020-07-02 | 2015-04-29 07:00 | 4.9 | 1.0836 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.2 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 | 0.25002 | 12.8 | 12.4 | 12.2 | 12.6 | 0.2582
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-11 | 50-CG-38466-01C02 CML-11 | yes | FPSO 2014 | Pipe Wall Thickness | 2525 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.4 | CML-11 | CML: type TBC | 3 | 2019-03-13 | 2019-10-25 | 2014-04-02 13:00 | 2.5 | 0.52562 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 5.1 | 5.7 | 5.5 | 5.1 | 5.3 | 0.2582
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40029-01C02 | CML-1 | 50-WC-40029-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1539 |  | 2014-04-06 16:30 | 2014-04-06 17:00 | [36 empty] | 7.1 | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 50 | 5.54 | 50-WC-40029-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.2 | 7.2 | 7.2 | 6.8 | 0.2
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56119-01C02 | CML-5 | 50-DH-56119-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21031 | Rope Access | 2014-05-19 09:30 | 2014-05-19 11:00 | [36 empty] | 5.1 | CML-5 | CML: type TBC | 3 | 2017-05-18 | 2017-10-21 | 2014-05-19 09:30 | 2.5 | 0.76647 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56119-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.2 | 5 | 5.4 | 0.2582
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-10 | 50-FH-43016-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22671 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.1 | CML-10 | CML: Elbow | 3 | 2021-03-27 | 2022-01-27 | 2015-04-27 07:00 | 2.5 | 0.38847 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | -0.079564 | 4.8 | 5.2 | 5 | 5.4 | 0.2582
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-19 | 50-FG-45501-01C02 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6602 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.4 | CML-19 | CML: Pipe Length | 3 | 2026-01-14 | 2027-05-24 | 2015-03-30 07:00 | 2.5 | 0.24067 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.5 | 5.3 | 5.1 | 5.7 | 0.2582
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43100-01C02 | CML-1 | 100-FH-43100-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12728 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 5.6 | CML-1 | CML: Elbow | 3 | 2016-08-04 | 2016-09-11 | 2014-01-24 09:00 | 2.5 | 1.1071 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 9 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.9 | 5.5 | 5.3 | 0.2582
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40029-01C02 | CML-1 | 50-WC-40029-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 875 |  | 2014-04-06 16:30 | 2014-04-06 17:00 | [36 empty] | 7.1 | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 50 | 5.54 | 50-WC-40029-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.2 | 7.2 | 7.2 | 6.8 | 0.2
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40046-01C02 | CML-10 | 300-WC-40046-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1260 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7 | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 3 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.1 | 6.8 | 7.1 | 7 | 0.14142
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20016-01C02-P | CML-2 | 200-PL-20016-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21233 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.425 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 9 O'Clock | 200 | 6.35 | 200-PL-20016-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.5 | 9 | 8.1 | 0.4272
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-15 | 200-PG-23013-09C03-A CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 10999 | Rope Access | 2014-01-10 | 2014-01-10 | [35 empty] | Low alarm breach | 14.8 | CML-15 | CML: type TBC | 6 | 2014-06-14 | 2014-03-26 | 2014-01-10 | 10.22 | 10.017 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 14.5 | 9 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.28 |  | 14.9 | 14.7 | 15.1 | 14.5 | 0.2582
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20014-01C02-P | CML-3 | 200-PL-20014-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21222 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.5 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 12 O'Clock | 200 | 6.35 | 200-PL-20014-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.4 | 9.1 | 8.4 | 0.42426
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40511-1CG | CML-3 | 300-WC-40511-1CG CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5656 | Material class 1CG | 2014-06-21 10:00 | 2014-06-21 11:00 | [36 empty] | 18.1 | CML-3 | CML: type TBC | 3 | 2211-01-04 | 2131-12-31 | 2014-06-21 10:00 | 2.5 | 0.07576 | A1: Outside Quadrant |  | 14.48 | 2.5 | 8.49 | 17.4 | 12 O'Clock | 300 | 17.48 | 300-WC-40511-1CG-S1 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.9 |  | 17.4 | 19.2 | 17.6 | 18.2 | 0.80829
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-18 | 150-WC-40002-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 20357 | Reviewed on 18/11/14. Line is FFS. Repeat on Oct.19 | 2014-10-09 07:00 | 2014-10-09 15:00 |  |  | Nestor | 2014-11-24 10:29 | [32 empty] | 7.6 | CML-18 | CML: Elbow | 3 | 2043-03-08 | 2040-11-08 | 2014-10-09 07:00 | 2.5 | 0.15476 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.9 | 3 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.2 | 6.9 | 8.4 | 7.9 | 0.67823
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38006-01C02 | CML-1 | 50-CG-38006-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8432 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 8.8 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.5 | 9 O'Clock | 15 | 5.54 | 50-CG-38006-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.1 | 8.9 | 8.7 | 8.5 | 0.2582
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-2 | 250-PW-20040-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21386 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.375 | CML-2 | CML: Elbow | 6 | 2109-01-31 | 2094-08-15 | 2014-07-12 07:30 | 4.1 | 0.08983 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.6 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 12.8 | 13.7 | 14.4 | 12.6 | 0.83417
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-14 | 150-PG-20507-01C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2858 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.8 | CML-14 | CML: type TBC | 6 | 2027-08-22 | 2025-07-25 | 2014-03-16 07:00 | 2.5 | 0.59506 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 10.5 | 9 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11.1 | 10.7 | 10.9 | 10.5 | 0.2582
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-2 | 50-FH-43450-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7681 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: Re-check point to confirm values in Jan. 2016 | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:10 | [32 empty] | 5.2 | CML-2 | CML: Pipe Length | 3 | 2021-01-16 | 2021-11-11 | 2015-01-08 13:00 | 2.5 | 0.39827 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.61191 | 5.3 | 4.9 | 5.1 | 5.5 | 0.2582
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-4 | 200-PW-44020-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5594 |  | 2014-06-19 14:00 | 2014-06-19 15:00 | [36 empty] | 7.55 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 12 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.3 | 8.4 | 7.7 | 0.67577
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-12 | 50-FG-45018-03C02 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10511 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.3 | CML-12 | CML: type TBC | 3 | 2015-12-28 | 2015-12-21 | 2013-11-15 | 2.5 | 1.1802 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 3 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5.4 | 5.6 | 0.2582
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20057-01C02-P | CML-5 | 100-PW-20057-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21842 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.95 | CML-5 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.4 | 3 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.8 | 6.4 | 6.7 | 7.9 | 0.65574
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-11 | 80-PW-44001-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 22002 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7 | CML-11 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.4 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.7 | 7 | 6.9 | 6.4 | 0.53541
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40001-01C02 | CML-8 | 150-WC-40001-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20337 | Reviewed 24/11/14. FFS. Repeat on Oct. 19. | 2014-10-09 07:00 | 2014-10-09 15:00 |  |  | Nestor | 2014-11-24 10:18 | [32 empty] | 7.3 | CML-8 | CML: Elbow | 3 | 2043-03-08 | 2040-11-08 | 2014-10-09 07:00 | 2.5 | 0.15476 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.9 | 12 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.7 | 7.2 | 7.4 | 0.33665
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-13 | 150-WC-40002-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20352 | Reviewed on 18/11/14. Line is FFS. Repeat on Oct.19 | 2014-10-09 07:00 | 2014-10-09 15:00 |  |  | Nestor | 2014-11-24 10:29 | [32 empty] | 7 | CML-13 | CML: Fitting | 3 | 2043-03-08 | 2040-11-08 | 2014-10-09 07:00 | 2.5 | 0.15476 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.9 | 9 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.1 | 7.1 | 6.9 | 0.11547
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1662 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.225 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.9 | 7 | 8.2 | 8.8 | 0.87321
CG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20269 | Rope Access | 2014-05-26 08:00 | 2014-05-26 09:00 | Check Corrosion Rate of 0.549mm/ yr | [35 empty] | 5.3 | CML-2 | CML: type TBC | 3 | 2022-11-01 | 2021-06-27 | 2014-05-26 08:00 | 0.37 | 0.54852 | A4: Left Quadrant |  | 2.54 | 0.37 | 1.1087 | 5 | 9 O'Clock | 50 | 5.54 | 50-DC-57028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.63 |  | 5.2 | 5.6 | 5.4 | 5 | 0.2582
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-14 | 150-FH-43026-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23513 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 7.2 | CML-14 | CML: Elbow | 3 | 2075-10-27 | 2064-07-29 | 2015-07-28 07:00 | 1.03 | 0.09736 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.9 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.87 | 0 | 7.1 | 7.5 | 6.9 | 7.3 | 0.2582
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56117-01C02 | CML-6 | 50-DH-56117-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21019 | Rope Access | 2014-05-19 13:00 | 2014-05-19 14:00 | [36 empty] | 5 | CML-6 | CML: type TBC | 3 | 2016-11-27 | 2017-04-13 | 2014-05-19 13:00 | 2.5 | 0.86968 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-DH-56117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 4.7 | 5.3 | 5.1 | 0.2582
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38463-01C02 | CML-4 | 50-CG-38463-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3115 | Rope Access | 2014-05-04 08:00 | 2014-05-04 09:00 | [36 empty] | 5 | CML-4 | CML: Elbow | 3 | 2016-10-03 | 2017-02-11 | 2014-05-04 08:00 | 2.5 | 0.90889 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-CG-38463-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 5.3 | 4.7 | 4.9 | 0.2582
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-9 | 100-WC-40035-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1742 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.9 | CML-9 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.3 | 6 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.6 | 7.9 | 7.3 | 7.8 | 0.53541
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43021-01C02 | CML-1 | 80-FH-43021-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20412 |  | 2014-10-06 07:00 | 2014-10-06 15:00 | [36 empty] | 5.5 | CML-1 | CML: Pipe Length | 3 | 2027-04-24 | 2028-12-05 | 2014-10-06 07:00 | 2.5 | 0.21501 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-FH-43021-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.28968 | 5.4 | 5.6 | 5.2 | 5.8 | 0.2582
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-13 | 200-PL-20034-03C02-P CML-13 | yes | FPSO 2014 | Pipe Wall Thickness | 21610 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 10.325 | CML-13 | CML: Equal Tee | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 9.3 | 6 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.69 |  | 11.6 | 9.7 | 9.3 | 10.7 | 1.034
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-2 | 100-FG-45043-03C02-E CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22648 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 6.5 | CML-2 | CML: Elbow | 3 | 2054-10-24 | 2049-02-10 | 2015-04-27 07:00 | 1.88 | 0 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 6.2 | 12 O'Clock | 100 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.32 |  | 6.2 | 6.6 | 6.8 | 6.4 | 0.2582
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1717 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.5 | CML-3 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 9 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.4 | 7.6 | 7.8 | 7.2 | 0.2582
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43109-01C02 | CML-3 | 200-FH-43109-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12787 |  | 2014-01-18 14:30 | 2014-01-18 15:30 | [36 empty] | 6.5 | CML-3 | CML: Pipe Length | 3 | 2034-08-05 | 2032-01-09 | 2014-01-18 14:30 | 1.34 | 0.23639 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-FH-43109-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 6.6 | 6.4 | 6.2 | 6.8 | 0.2582
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20047-03C03-P | CML-2 | 80-PG-20047-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21469 | Protective mesh removed | 2014-06-28 07:00 | 2014-06-28 08:00 | [36 empty] | 11.1 | CML-2 | CML: Fitting | 6 | 2041-07-03 | 2037-03-22 | 2014-06-28 07:00 | 2.5 | 0.30704 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.8 | 6 O'Clock | 80 | 11.13 | 80-PG-20047-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.4 | 11.2 | 10.8 | 11 | 0.2582
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-8 | 50-PW-44015-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5718 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 7.6 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-06-22 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.9 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 | 2.4397 | 8.7 | 7.6 | 7.2 | 6.9 | 0.7874
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12565 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.575 | CML-4 | CML: Elbow | 3 | 2019-10-24 | 2018-12-30 | 2014-01-18 07:00 | 0.54 | 0.77327 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5 | 12 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.46 |  | 5 | 5.7 | 5.9 | 5.7 | 0.39476
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40014-01C02 | CML-8 | 50-WC-40014-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1555 | Rope Access | 2014-04-09 08:00 | 2014-04-09 09:00 | [36 empty] | 7.675 | CML-8 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.9 | 8.2 | 7.3 | 7.3 | 0.45
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40009-01C02 | CML-7 | 200-WC-40009-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3126 | Rope Access | 2014-05-04 07:00 | 2014-05-04 08:00 | [36 empty] | 7.75 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-05-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 3 O'Clock | 200 | 6.35 | 200-WC-40009-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.7 | 7.3 | 8.2 | 7.8 | 0.36968
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-4 | 25-PW-44028-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22953 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 9.45 | CML-4 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 3 O'Clock | 50 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 0.11624 | 9.4 | 9.2 | 9.4 | 9.8 | 0.25166
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-49 | 50-FL-43306-01C02 CML-49 |  | FPSO 2015 | Pipe Wall Thickness | 7665 | Line is FFS. Action: to recheck in a year (Jan. 2016) to confirm CR. | 2015-01-08 07:00 | 2015-01-08 09:00 |  |  | Administrator | 2015-09-07 15:25 | [32 empty] | 4.3 | CML-49 | CML: Elbow | 3 | 2016-01-25 | 2016-05-08 | 2015-01-08 07:00 | 2.5 | 1.1455 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 12 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 4.6 | 4.7 | 4.2 | 0.45461
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-16 | 50-FG-45018-03C02 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10515 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.15 | CML-16 | CML: type TBC | 3 | 2015-04-18 | 2015-04-13 | 2013-11-15 | 2.5 | 1.6174 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 5.2 | 4.8 | 5.2 | 0.25166
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67009-01E01 | CML-5 | 50-GN-67009-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8783 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 9 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.7 | 3 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.9 | 8.7 | 9.6 | 8.8 | 0.40825
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-5 | 100-DH-56086-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20964 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 5.05 | CML-5 | CML: type TBC | 3 | 2016-03-05 | 2016-04-07 | 2014-05-16 13:00 | 2.5 | 1.2739 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 5.4 | 5 | 4.8 | 0.25166
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-4 | 50-FG-45020-03C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10576 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.15 | CML-4 | CML: type TBC | 3 | 2015-04-26 | 2015-04-21 | 2013-11-17 | 2.5 | 1.5982 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 5.2 | 4.8 | 5.2 | 0.25166
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63022-01E01 | CML-2 | 50-AU-63022-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8440 |  | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 9.325 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.7 | 6 O'Clock | 50 | 5.54 | 50-AU-63022-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.9 | 9 | 8.7 | 9.7 | 0.56789
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PL-57403-01C03 |  | 50-PL-57403-01C03 |  | FPSO 2015 | Pipe Wall Thickness | 8367 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 8.95 | 50-PL-57403-01C03 | Piping | 6 | 2272-10-21 |  | 2015-01-29 07:30 |  | 0.02404 | A3: Inside Quadrant |  |  | 2.5 |  | 8.7 | 6 O'Clock | 50 | 8.74 | Pipework | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.8 | 9.3 | 8.7 | 9 | 0.26458
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-14 | 250-PG-23003-06C02-PA CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10681 | Deck Level | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-13 13:52 | [32 empty] | 5.05 | CML-14 | CML: Pipe Length | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 5 | 5 | 4.8 | 0.25166
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-6 | 250-DC-57064-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20286 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 9.675 | CML-6 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 9 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 10.1 | 8.7 | 11.2 | 8.7 | 1.2121
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43302-01C02-E | CML-1 | 200-PL-43302-01C02-E CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8602 |  | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6.625 | CML-1 | CML: type TBC | 3 | 2183-01-15 | 2162-06-14 | 2015-02-09 07:30 | 1.34 | 0.02952 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.3 | 3 O'Clock | 200 | 6.35 | 200-PL-43302-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 6.4 | 6.3 | 7.1 | 6.7 | 0.3594
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23410-01C03 | CML-1 | 100-PG-23410-01C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20771 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.025 | CML-1 | CML: Pipe Length | 6 | 2074-02-03 | 2073-10-17 | 2014-10-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 8.7 | 9 O'Clock | 100 | 8.56 | 100-PG-23410-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.2 | 8.9 | 9.3 | 8.7 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-9 | 150-FH-43518-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5524 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 6.95 | CML-9 | CML: Elbow | 3 | 2024-12-11 | 2022-12-29 | 2014-06-01 07:00 | 1.23 | 0.50959 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 | -0.45108 | 7 | 7 | 6.6 | 7.2 | 0.25166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43110-01C02 | CML-6 | 200-FH-43110-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12797 |  | 2014-01-18 13:30 | 2014-01-18 14:30 | [36 empty] | 7.95 | CML-6 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 13:30 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.7 | 3 O'Clock | 200 | 6.35 | 200-FH-43110-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.36 |  | 7.9 | 7.7 | 7.9 | 8.3 | 0.25166
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-13 | 50-PL-24003-09C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 13152 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.675 | CML-13 | CML: type TBC | 3 | 2020-09-27 | 2018-11-02 | 2014-01-18 13:00 | 2.5 | 0.85125 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.2 | 3 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.4 | 8.2 | 9.3 | 8.8 | 0.48563
PG05 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 2518 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.6333 | CML-4 | CML: type TBC | 3 | 2031-07-31 | 2033-07-12 | 2014-04-02 13:00 | 2.5 | 0.16724 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 5.4 |  | 5.9 | 5.4 | 5.6 | 0.25166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-2 | 80-FH-43007-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12563 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.8667 | CML-2 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-01-18 07:00 | 0.54 | 0 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.6 | 3 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.06 |  | 6.1 | 5.6 | 5.9 |  | 0.25166
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-22 | 50-CG-38452-09C02-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 12985 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 9.0333 | CML-22 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.8 | 6 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  |  | 9.3 | 8.8 | 9 | 0.25166
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-2 | 50-PL-24003-09C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13141 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.675 | CML-2 | CML: type TBC | 3 | 2020-09-27 | 2018-11-02 | 2014-01-18 13:00 | 2.5 | 0.85125 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.2 | 12 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.4 | 8.9 | 9.2 | 0.45735
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-8 | 50-FG-45020-03C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2607 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.15 | CML-8 | CML: type TBC | 3 | 2017-09-12 | 2017-09-02 | 2014-04-26 09:30 | 2.5 | 0.70918 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.68269 | 5.1 | 5.1 | 5.5 | 4.9 | 0.25166
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-46 | 50-FL-43306-01C02 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 7662 |  | 2015-01-08 07:00 | 2015-01-08 09:00 | [36 empty] | 4.2 | CML-46 | CML: Elbow | 3 | 2016-05-22 | 2016-09-16 | 2015-01-08 07:00 | 2.5 | 1.021 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.9 | 12 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.5 | 4 | 4.4 | 0.29439
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-1 | 50-FH-43137-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12853 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 5.65 | CML-1 | CML: Pipe Length | 3 | 2027-06-19 | 2028-12-21 | 2014-01-23 08:00 | 2.5 | 0.21622 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.6 | 5.6 | 6 | 0.25166
FG02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-FG-45455-01C02-E | CML-1 | 25-FG-45455-01C02-E CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21983 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.35 | CML-1 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 6 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 6.6 | 6 | 6.4 | 0.25166
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40001-01C02 | CML-5 | 150-WC-40001-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20334 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 25.525 | CML-5 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.3 | 6 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.1 | 7.7 | 7.3 | 7.9 | 0.34157
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-2 | 50-WC-40028-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1682 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 7.55 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.5 | 7.4 | 8 | 7.3 | 0.31091
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-18 | 25-FG-45455-01C02-E CML-18 |  | FPSO 2016 | Pipe Wall Thickness | 24363 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 8.25 | CML-18 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 9 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.6 | 8.2 | 8 | 0.25166
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40511-1CG | CML-2 | 300-WC-40511-1CG CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 5655 | Material class 1CG | 2014-06-21 10:00 | 2014-06-21 11:00 | [36 empty] | 19.725 | CML-2 | CML: type TBC | 3 | 2163-03-18 | 2103-04-25 | 2014-06-21 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 14.48 | 2.5 | 8.49 | 18 | 9 O'Clock | 300 | 17.48 | 300-WC-40511-1CG-S1 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.5 |  | 20.3 | 19.6 | 21 | 18 | 1.2842
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-14 | 100-WC-40035-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1747 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.7 | CML-14 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.3 | 6 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.9 | 7.7 | 7.3 | 7.9 | 0.28284
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-24 | 250-PW-20041-03C03-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21433 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.175 | CML-24 | CML: Elbow | 6 | 2109-01-31 | 2094-08-15 | 2014-07-12 07:30 | 4.1 | 0.08983 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.6 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 12.9 | 13.4 | 13.8 | 12.6 | 0.53151
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43125-01C02 | CML-4 | 200-FH-43125-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2758 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.85 | CML-4 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-03-13 09:00 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.5 | 9 O'Clock | 200 | 6.35 | 200-FH-43125-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.16 |  | 7.9 | 8.1 | 7.9 | 7.5 | 0.25166
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-12 | 80-CG-38459-09C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23709 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.35 | CML-12 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 9 | 12 O'Clock | 40 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.4 | 9.6 | 9.4 | 0.25166
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-30 | 300-PF-20500-03C03-P CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 21650 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 13.95 | CML-30 | CML: Pipe Length | 6 | 2031-12-02 | 2028-08-04 | 2014-09-27 07:00 | 4.9 | 0.50601 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 3 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14 | 13.6 | 14.2 | 14 | 0.25166
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-10 | 300-PG-23002-03C03-A CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10106 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 14.35 | CML-10 | CML: Elbow | 6 | 2028-01-03 | 2025-07-19 | 2013-11-07 | 5.22 | 0.61981 | A4: Left Quadrant |  | 8.27 | 5.22 | 6.745 | 14 | 9 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.78 |  | 14.4 | 14.6 | 14.4 | 14 | 0.25166
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-8 | 50-CG-38454-01C02-H CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 23672 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.15 | CML-8 | CML: Elbow | 3 | 2024-11-16 | 2026-02-08 | 2015-10-30 07:00 | 2.5 | 0.26507 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 25 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.5 | 4.9 | 5.1 | 5.1 | 0.25166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43017-01C02 | CML-4 | 150-FH-43017-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10650 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.85 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-18 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.5 | 12 O'Clock | 100 | 6.02 | 100-FH-43017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7.1 | 6.9 | 6.9 | 0.25166
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-13 | 50-FG-45018-03C02 CML-13 | yes | FPSO 2013 | Pipe Wall Thickness | 10512 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.55 | CML-13 | CML: type TBC | 3 | 2014-06-14 | 2014-06-12 | 2013-11-15 | 2.5 | 2.9287 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.2 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.6 | 4.6 | 4.2 | 4.8 | 0.25166
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-9 | 150-WC-40002-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20348 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.525 | CML-9 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.3 | 6 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.5 | 7.9 | 7.3 | 7.4 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-16 | 250-WC-40026-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1292 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.6 | CML-16 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 6 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.7 | 7.5 | 7.3 | 7.9 | 0.2582
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-25 | 50-FG-45301-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 5811 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.75 | CML-25 | CML: Reducer | 3 | 2094-01-20 | 2102-09-17 | 2014-06-23 13:00 | 2.5 | 0.03767 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.7 | 5.7 | 6.1 | 0.25166
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38007-01C02 | CML-3 | 50-CG-38007-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3110 | Rope Access | 2014-05-04 09:30 | 2014-05-04 10:00 | [36 empty] | 5.95 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-04 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 15 | 5.54 | 50-CG-38007-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.3 | 5.7 | 5.9 | 5.9 | 0.25166
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-21 | 50-FG-45301-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 5807 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.25 | CML-21 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.5 | 6.3 | 6.3 | 5.9 | 0.25166
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-7 | 25-FG-45455-01C02-E CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22083 | Rope Access | 2014-05-25 09:30 | 2014-05-25 10:30 | [36 empty] | 6.25 | CML-7 | CML: type TBC | 3 | 2186-02-11 | 2173-05-11 | 2014-05-25 09:30 | 2.5 | 0.02037 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.76 | 6 | 9 O'Clock | 100 | 6.02 | 100-FG-45305-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.2 | 6.6 | 6 | 0.25166
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-1 | 25-PW-44028-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22950 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 6.45 | CML-1 | CML: Elbow | 3 | 2062-08-17 | 2062-04-07 | 2015-05-02 07:00 | 2.5 | 0.07818 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 25 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | 0 | 6.2 | 6.8 | 6.4 | 6.4 | 0.25166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-25 | 250-FH-43303-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 12963 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 7.25 | CML-25 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 9 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.3 | 7.3 | 7.5 | 6.9 | 0.25166
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-3 | 50-CG-38500-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7875 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:41 | [32 empty] | 3.75 | CML-3 | CML: Fitting | 3 | 2015-10-31 | 2016-02-03 | 2015-01-14 10:30 | 2.5 | 1.2568 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.5 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.7 | 4.1 | 3.5 | 3.7 | 0.25166
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-8 | 100-PW-20021-01C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22826 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 7.15 | CML-8 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.4 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 | 1.9975 | 6.4 | 7.4 | 7.5 | 7.3 | 0.50662
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-45 | 50-FL-43306-01C02 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 7661 |  | 2015-01-08 07:00 | 2015-01-08 09:00 | [36 empty] | 4.6 | CML-45 | CML: Elbow | 3 | 2016-10-20 | 2017-03-02 | 2015-01-08 07:00 | 2.5 | 0.89648 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.1 | 6 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.7 | 4.8 | 4.1 | 4.8 | 0.33665
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-7 | 100-PW-20021-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21810 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 7.1 | CML-7 | CML: Reducer | 3 | 2048-08-12 | 2049-10-10 | 2014-10-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.4 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.4 | 7.2 | 7.4 | 0.4761
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-12 | 50-FG-45301-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5798 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.75 | CML-12 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 12 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7.1 | 6.7 | 6.7 | 0.25166
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-7 | 50-CG-38488-09C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23596 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 12.15 | CML-7 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-15 15:30 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 11.8 | 9 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 | -1.1186 | 12.2 | 12.4 | 12.2 | 11.8 | 0.25166
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-3 | 150-PG-20054-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21514 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 11.15 | CML-3 | CML: Pipe Length | 6 | 2066-09-09 | 2058-12-02 | 2014-06-26 13:00 | 2.5 | 0.15888 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 10.8 | 3 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.2 | 10.8 | 11.4 | 11.2 | 0.25166
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-13 | 100-PG-23028-25C02-P CML-13 | Yes | FPSO 2014 | Pipe Wall Thickness | 20557 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 15.775 | CML-13 | CML: Pipe Length | 3 | 2018-02-26 | 2016-09-15 | 2014-05-30 09:30 | 9.4 | 1.6272 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 15.5 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | -0.92381 | 15.7 | 15.5 | 16.1 | 15.8 | 0.25
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-8 | 100-DC-57075-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2427 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | [36 empty] | 9.125 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.7 | 12 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 9.2 | 9.4 | 9.2 | 0.29861
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-24 | 250-PG-23004-06C03-A CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 13024 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 17.775 | CML-24 | CML: Pipe Length | 6 | 2021-04-09 | 2019-10-09 | 2014-01-11 15:00 | 8.55 | 1.2349 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 17.5 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.95 |  | 18.1 | 17.7 | 17.8 | 17.5 | 0.25
FH01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 100-FH-43507-01C02 | CML-15 | 100-FH-43507-01C02 CML-15 | yes | FPSO 2015 | Pipe Wall Thickness | 23679 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.025 | CML-15 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.3 | 8.7 | 9 | 9.1 | 0.25
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-9 | 50-WC-40028-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1689 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 7.55 | CML-9 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 3 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.7 | 7.3 | 7.8 | 7.4 | 0.23805
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-4 | 250-PW-20041-03C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23490 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 13.2 | CML-4 | CML: Elbow | 6 | 2198-07-22 | 2170-07-27 | 2015-07-27 07:00 | 4.1 | 0.04642 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.6 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 | -1.0566 | 13.5 | 13.7 | 13 | 12.6 | 0.49666
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-4 | 200-PG-20300-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5869 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | Check Corrosion Rate of 0.469mm/ yr |  | Kirstie Albone | 2017-03-23 10:14 | This review was conducted in 2017. Loss within CA no further action required, include in next inspec | [31 empty] | 12.525 | CML-4 | CML: Pipe Length | 6 | 2033-06-16 | 2029-10-31 | 2014-06-25 09:30 | 3.3 | 0.46867 | A3: Inside Quadrant |  | 6.7 | 3.3 | 5 | 12.2 | 6 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 12.5 | 12.6 | 12.2 | 12.8 | 0.25
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-15 | 50-FG-45020-03C02 CML-15 | yes | FPSO 2013 | Pipe Wall Thickness | 10587 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.925 | CML-15 | CML: type TBC | 3 | 2014-11-29 | 2014-11-25 | 2013-11-17 | 2.5 | 2.0302 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 4.6 | 5.2 | 5 | 0.25
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56558-01C02 | CML-2 | 50-DH-56558-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21133 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-21 08:54 | [32 empty] | 5.075 | CML-2 | CML: Elbow | 3 | 2018-12-22 | 2019-07-28 | 2014-10-08 07:00 | 2.5 | 0.54644 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56558-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 5 | 5.4 | 4.8 | 0.25
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43079-01C02 | CML-6 | 50-FL-43079-01C02 CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 3049 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 5.075 | CML-6 | CML: type TBC | 3 | 2017-03-13 | 2017-08-08 | 2014-05-03 07:00 | 2.5 | 0.80317 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5 | 5.1 | 5.4 | 0.25
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57058-06C02 | CML-5 | 50-DC-57058-06C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10346 | Deck Level | 2013-11-11 | 2013-11-11 | [36 empty] | 8.75 | CML-5 | CML: Pipe Length | 3 | 2083-01-13 | 2071-01-20 | 2013-11-11 | 2.5 | 0.08957 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-DC-57058-06C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 8.7 | 8.9 | 8.7 | 0.1
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-42 | 50-FL-43306-01C02 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 7658 |  | 2015-01-08 07:00 | 2015-01-08 09:00 | [36 empty] | 4.275 | CML-42 | CML: Elbow | 3 | 2016-10-20 | 2017-03-02 | 2015-01-08 07:00 | 2.5 | 0.89648 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.1 | 12 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.2 | 4.5 | 4.3 | 0.17078
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-41 | 50-FL-43306-01C02 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 7657 |  | 2015-01-08 07:00 | 2015-01-08 09:00 | [36 empty] | 4.5 | CML-41 | CML: Elbow | 3 | 2017-01-21 | 2017-06-12 | 2015-01-08 07:00 | 2.5 | 0.83423 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.8 | 4.3 | 4.7 | 0.29439
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23039 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 7.95 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 | 0.34128 | 8.5 | 7.6 | 7 | 8.7 | 0.79373
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-6 | 80-PW-44034-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21988 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.75 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.4 | 12 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.7 | 7.4 | 6.5 | 0.45092
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-20 | 200-PL-20010-01C02-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 23820 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.625 | CML-20 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 3 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 9.1 | 8.2 | 8.9 | 8.3 | 0.44253
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-12 | 200-PL-20020-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21316 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 8.425 | CML-12 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 9 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 9 | 8.3 | 8.2 | 8.2 | 0.38622
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-3 | 200-PW-44020-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5593 |  | 2014-06-19 14:00 | 2014-06-19 15:00 | [36 empty] | 7.35 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 8.3 | 7 | 7 | 0.63509
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-40 | 50-FL-43306-01C02 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 7656 |  | 2015-01-08 07:00 | 2015-01-08 09:00 | [36 empty] | 4.45 | CML-40 | CML: Elbow | 3 | 2017-01-21 | 2017-06-12 | 2015-01-08 07:00 | 2.5 | 0.83423 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 6 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.4 | 4.7 | 4.2 | 4.5 | 0.20817
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-48 | 50-FL-43306-01C02 CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 7664 |  | 2015-01-08 07:00 | 2015-01-08 09:00 | [36 empty] | 4.575 | CML-48 | CML: Elbow | 3 | 2017-05-08 | 2017-10-09 | 2015-01-08 07:00 | 2.5 | 0.77197 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.6 | 4.6 | 4.8 | 4.3 | 0.20616
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56558-01C02 | CML-1 | 50-DH-56558-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21132 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-21 09:08 | [32 empty] | 5.625 | CML-1 | CML: Cap End | 3 | 2030-07-23 | 2032-05-24 | 2014-10-08 07:00 | 2.5 | 0.17722 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56558-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.7 | 5.6 | 5.3 | 0.25
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56010-01C02 | CML-5 | 50-DH-56010-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22322 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 5.575 | CML-5 | CML: type TBC | 3 | 2025-03-09 | 2026-06-13 | 2014-05-06 10:30 | 2.5 | 0.25807 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0 | 5.6 | 5.3 | 5.5 | 5.9 | 0.25
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56010-01C02 | CML-5 | 50-DH-56010-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1842 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 5.575 | CML-5 | CML: type TBC | 3 | 2025-03-09 | 2026-06-13 | 2014-05-06 10:30 | 2.5 | 0.25807 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.3 | 5.5 | 5.9 | 0.25
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40053-01C02 | CML-2 | 50-WC-40053-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 873 |  | 2014-04-06 16:00 | 2014-04-06 16:30 | [36 empty] | 7.475 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40053-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.6 | 7.3 | 7.7 | 7.3 | 0.20616
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-11 | 100-FH-43104-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12762 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 5.875 | CML-11 | CML: type TBC | 3 | 2018-11-19 | 2019-01-24 | 2014-01-25 07:00 | 2.5 | 0.64333 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 6.2 | 5.9 | 5.6 | 0.25
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-13 | 50-FG-45024-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1196 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.075 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 6.4 | 5.8 | 6.1 | 0.25
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24036-09C02 | CML-5 | 50-PL-24036-09C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13164 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 8.55 | CML-5 | CML: type TBC | 3 | 2020-09-28 | 2018-11-03 | 2014-01-18 15:00 | 2.5 | 0.85094 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.2 | 9 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.7 | 8.8 | 8.5 | 8.2 | 0.26458
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40053-01C02 | CML-2 | 50-WC-40053-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1537 |  | 2014-04-06 16:00 | 2014-04-06 16:30 | [36 empty] | 7.475 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40053-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.6 | 7.3 | 7.7 | 7.3 | 0.20616
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-8 | 100-DH-56009-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3431 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 7.975 | CML-8 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.7 | 12 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 8 | 8.3 | 7.9 | 0.25
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-44 | 50-FL-43306-01C02 CML-44 |  | FPSO 2015 | Pipe Wall Thickness | 7660 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-08 07:00 | 2015-01-08 09:00 |  |  | Administrator | 2015-09-08 15:53 | [32 empty] | 5.325 | CML-44 | CML: Pipe Length | 3 | 2024-07-03 | 2025-09-11 | 2015-01-08 07:00 | 2.5 | 0.27393 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.5 | 5.4 | 5.3 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-12 | 50-FG-45020-03C02 CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 2611 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 4.975 | CML-12 | CML: type TBC | 3 | 2016-05-01 | 2016-04-24 | 2014-04-26 09:30 | 2.5 | 1.0416 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | -0.22756 | 4.6 | 5.1 | 5.1 | 5.1 | 0.25
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-12 | 50-FG-45019-03C02 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10494 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.025 | CML-12 | CML: type TBC | 3 | 2015-08-03 | 2015-07-29 | 2013-11-15 | 2.5 | 1.3988 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 4.9 | 4.9 | 4.9 | 0.25
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-6 | 50-CG-38467-01C02 CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 22277 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.275 | CML-6 | CML: Elbow | 3 | 2017-10-06 | 2018-03-26 | 2014-05-01 11:00 | 2.5 | 0.69844 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0 | 5.4 | 5.4 | 4.9 | 5.4 | 0.25
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-39 | 50-FL-43306-01C02 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 7655 | Blanked off/Frame 56. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-08 07:00 | 2015-01-08 09:00 |  |  | Administrator | 2015-09-08 15:53 | [32 empty] | 5.225 | CML-39 | CML: Pipe Length | 3 | 2024-07-03 | 2025-09-11 | 2015-01-08 07:00 | 2.5 | 0.27393 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.1 | 5.4 | 5.2 | 0.12583
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-47 | 50-FL-43306-01C02 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 7663 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-08 07:00 | 2015-01-08 09:00 |  |  | Administrator | 2015-09-08 15:53 | [32 empty] | 5.4 | CML-47 | CML: Fitting | 3 | 2027-10-08 | 2029-04-22 | 2015-01-08 07:00 | 2.5 | 0.21167 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.3 | 5.5 | 5.2 | 0.18257
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-43 | 50-FL-43306-01C02 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 7659 |  | 2015-01-08 07:00 | 2015-01-08 09:00 | [36 empty] | 5.4 | CML-43 | CML: Pipe Length | 3 | 2033-09-30 | 2035-12-06 | 2015-01-08 07:00 | 2.5 | 0.14941 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 5.5 | 5.4 | 0.08165
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-6 | 50-CG-38467-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2998 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.275 | CML-6 | CML: Elbow | 3 | 2017-10-06 | 2018-03-26 | 2014-05-01 11:00 | 2.5 | 0.69844 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 5.4 | 4.9 | 5.4 | 0.25
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43156-01C02 | CML-4 | 80-FH-43156-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10722 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 5.125 | CML-4 | CML: type TBC | 3 | 2016-04-09 | 2016-08-08 | 2013-11-19 | 2.5 | 1.0459 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-FH-43156-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5 | 5 | 5 | 0.25
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67010-01E01 | CML-5 | 50-GN-67010-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8708 |  | 2015-02-14 07:00 | 2015-02-14 09:00 | [36 empty] | 9.275 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.8 | 6 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.5 | 9.6 | 8.8 | 9.2 | 0.3594
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-3 | 80-PW-44001-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21994 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.75 | CML-3 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.4 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7 | 6.8 | 6.8 | 0.25166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43128-01C02 | CML-3 | 50-FH-43128-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1802 |  | 2014-04-28 14:00 | 2014-04-28 14:30 | [36 empty] | 5.575 | CML-3 | CML: Pipe Length | 3 | 2021-07-13 | 2022-05-27 | 2014-04-28 14:00 | 2.5 | 0.37426 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FH-43128-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.7 | 5.2 | 5.7 | 0.25
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PL-57403-01C03 |  | 50-PL-57403-01C03 |  | FPSO 2015 | Pipe Wall Thickness | 8370 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.525 | 50-PL-57403-01C03 | Piping | 6 | 2075-10-24 |  | 2015-01-29 07:30 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 8.8 | 12 O'Clock | 50 | 8.74 | Pipework | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9.1 | 10.6 | 9.6 | 0.78899
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57402-01C03 | CML-5 | 50-DC-57402-01C03 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8362 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.375 | CML-5 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.8 | 12 O'Clock | 50 | 8.74 | 50-DC-57402-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9.7 | 9.7 | 9.3 | 0.4272
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57400-01C03 | CML-1 | 50-DC-57400-01C03 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8351 |  | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 9.325 | CML-1 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2015-01-28 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.8 | 12 O'Clock | 50 | 8.74 | 50-DC-57400-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9.4 | 9.6 | 9.5 | 0.3594
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45007-03C02-E | CML-3 | 100-FG-45007-03C02-E CML-3 | yes | FPSO 2016 | Pipe Wall Thickness | 24310 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 | Wet CO2 Gas Corrosion, downstream of super heaters and approaching dew point temperature (36 Deg C) |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.975 | CML-3 | CML: Elbow | 3 | 2022-02-15 | 2020-12-04 | 2016-05-27 07:00 | 1.88 | 0.47494 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 4.6 | 3 O'Clock | 100 | 6.02 | 100-FG-45007-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.72 |  | 5.1 | 4.6 | 5.1 | 5.1 | 0.25
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-38 | 50-FL-43306-01C02 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 7654 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-38 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-37 | 50-FL-43306-01C02 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 7653 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-37 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-4 | 200-PW-44021-01X01 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10709 | Deck Level. Line is FFS. High CR. Line rechecked (refer to Jan. 15 values) | 2013-11-10 | 2013-11-10 |  |  | Administrator | 2015-09-13 11:05 | [32 empty] | 7.525 | CML-4 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2013-11-10 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 12 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.4 | 7.8 | 7.9 | 0.4113
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-22 | 250-PW-20041-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21431 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13 | CML-22 | CML: Reducer | 6 | 2109-01-31 | 2094-08-15 | 2014-07-12 07:30 | 4.1 | 0.08983 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.6 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 13.4 | 13.2 | 12.8 | 12.6 | 0.36515
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-8 | 50-WC-40451-01C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10148 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 7.5 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2013-11-09 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 3 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.6 | 7.3 | 7.4 | 7.7 | 0.18257
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-36 | 50-FL-43306-01C02 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 7652 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-36 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-35 | 50-FL-43306-01C02 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 7651 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-35 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38477-01C02-P | CML-2 | 50-CG-38477-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23416 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | Check Corrosion Rate of 0.799mm/ yr |  | John Wilson | 2017-03-24 08:54 | Anomaly raised to re inspect 7/5/2018 | [31 empty] | 8.975 | CML-2 | CML: Equal Tee | 6 | 2019-10-13 | 2020-05-08 | 2015-07-22 07:00 | 5.22 | 0.79887 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 8.6 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.38 | -0.34845 | 8.6 | 9.1 | 9.1 | 9.1 | 0.25
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-24 | 50-DH-56137-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21108 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.125 | CML-24 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6 | 6 | 6 | 0.25
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-2 | 50-WC-40048-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 879 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 7.45 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.4 | 7.7 | 7.4 | 7.3 | 0.17321
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-9 | 80-PG-23025-06C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20548 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 8.675 | CML-9 | CML: Elbow | 6 | 2016-04-26 | 2015-11-30 | 2014-05-27 08:00 | 2.8 | 2.8666 | A2: Right Quadrant |  | 5.13 | 2.8 | 3.965 | 8.3 | 3 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 | 35.2009 | 8.8 | 8.3 | 8.8 | 8.8 | 0.25
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-10 | 150-FH-43518-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2710 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.325 | CML-10 | CML: Pipe Length | 3 | 2072-03-18 | 2062-04-04 | 2014-03-12 09:00 | 1.23 | 0 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 | 0 | 7.2 | 7.7 | 7.2 | 7.2 | 0.25
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-10 | 150-FH-43518-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 349 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.325 | CML-10 | CML: Pipe Length | 3 | 2072-03-18 | 2062-04-04 | 2014-03-12 | 1.23 | 0 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 |  | 7.2 | 7.7 | 7.2 | 7.2 | 0.25
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-2 | 50-WC-40048-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1543 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 7.45 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.4 | 7.7 | 7.4 | 7.3 | 0.17321
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-13 | 50-PL-23023-03C03 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10213 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.675 | CML-13 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 10.3 | 3 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.8 | 10.3 | 10.8 | 10.8 | 0.25
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-14 | 200-PG-24001-09C02 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10270 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 17.675 | CML-14 | CML: Elbow | 3 | 2017-07-29 | 2016-03-08 | 2013-11-09 | 9.2 | 2.1764 | A4: Left Quadrant |  | 15.26 | 9.2 | 12.23 | 17.3 | 9 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 17.8 | 17.8 | 17.8 | 17.3 | 0.25
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-17 | 250-PG-23004-06C03-A CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20531 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 17.875 | CML-17 | CML: Pipe Length | 6 | 2026-02-15 | 2023-09-12 | 2014-05-30 09:30 | 8.55 | 0.76335 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.5 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.95 | 0 | 17.5 | 18 | 18 | 18 | 0.25
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-8 | 50-CG-38457-01C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23726 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.175 | CML-8 | CML: Elbow | 3 | 2024-11-16 | 2026-02-08 | 2015-10-30 07:00 | 2.5 | 0.26507 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.5 | 4.9 | 5.2 | 5.1 | 0.25
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20023-01C03-P | CML-4 | 250-PW-20023-01C03-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 5601 |  | 2014-06-20 07:00 | 2014-06-20 08:00 | [36 empty] | 11.425 | CML-4 | CML: Equal Tee | 6 | 2081-02-10 | 2077-04-05 | 2014-06-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 11.1 | 9 O'Clock | 250 | 9.27 | 250-PW-20023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.9 | 11.2 | 11.5 | 11.1 | 0.3594
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-8 | 50-CG-38487-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20808 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 10.725 | CML-8 | CML: Reducer | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.4 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 10.7 | 10.8 | 11 | 0.25
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-2 | 150-FL-43174-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5919 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.825 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.9 | 3.8 | 4.1 | 3.5 | 0.25
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62006-01S01 | CML-9 | 50-DO-62006-01S01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1469 | Rope access | 2014-04-25 11:00 | 2014-04-25 12:00 | [36 empty] | 8.975 | CML-9 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2014-04-25 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 8.8 | 12 O'Clock | 50 | 5.54 | 50-DO-62006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9 | 8.9 | 9.2 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-20 | 250-PW-44006-01X01 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 1917 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 7.175 | CML-20 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7.1 | 7.4 | 7 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40014-01C02 | CML-2 | 50-WC-40014-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1549 | Rope Access | 2014-04-09 08:00 | 2014-04-09 09:00 | [36 empty] | 7.45 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 12 O'Clock | 50 | 5.54 | 50-WC-40014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.4 | 7.7 | 7.4 | 0.17321
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1974 |  | 2014-03-26 14:00 | 2014-03-26 15:00 | [36 empty] | 5.675 | CML-2 | CML: type TBC | 3 | 2031-03-02 | 2033-01-26 | 2014-03-26 14:00 | 2.5 | 0.17114 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DH-56104-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.4 | 5.6 | 5.7 | 0.25
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-9 | 200-PW-44018-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12570 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.475 | CML-9 | CML: Elbow | 3 | 2021-06-14 | 2020-06-04 | 2014-01-18 07:00 | 0.54 | 0.61546 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.1 | 3 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.56 |  | 5.6 | 5.1 | 5.7 | 5.5 | 0.263
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-28 | 100-DC-57036-01C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 1434 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 9.4333 | CML-28 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.8 | 6 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 10.6 | 8.9 | 8.8 |  | 1.0116
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-46 | 200-PL-20019-01C02 CML-46 |  | FPSO 2014 | Pipe Wall Thickness | 21297 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 8.425 | CML-46 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.4 | 8.2 | 8.3 | 8.8 | 0.263
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-34 | 50-FL-43306-01C02 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 7650 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-34 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-8 | 50-PW-44013-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5732 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 7.65 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-06-22 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 | 2.4383 | 7.1 | 7.3 | 8.6 | 7.6 | 0.66583
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-35 | 50-DH-56062-01C02 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 9122 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 7.675 | CML-35 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.6 | 8 | 7.7 | 7.4 | 0.25
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20015-01C02-P | CML-6 | 200-PL-20015-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21231 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.5 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 12 O'Clock | 200 | 6.35 | 200-PL-20015-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.6 | 8.8 | 8.4 | 0.2582
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-4 | 50-PF-20301-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3002 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.325 | CML-4 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 9 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.39 | 0 | 9 | 9.4 | 9.6 | 9.3 | 0.25
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-4 | 50-PF-20301-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22281 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.325 | CML-4 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 9 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.39 |  | 9 | 9.4 | 9.6 | 9.3 | 0.25
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-18 | 100-FG-45001-09C02 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10433 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.425 | CML-18 | CML: type TBC | 3 | 2016-03-27 | 2015-06-26 | 2013-11-13 | 4.7 | 2.2785 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.1 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 10.5 | 10.1 | 10.7 | 10.4 | 0.25
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-11 | 200-PL-20020-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21315 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 8.4 | CML-11 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 3 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.4 | 8.2 | 8.4 | 8.6 | 0.1633
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-56 | 400-FH-43508-01C02 CML-56 |  | FPSO 2015 | Pipe Wall Thickness | 6582 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.175 | CML-56 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 8.9 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.2 | 8.9 | 9.1 | 9.5 | 0.25
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-15 | 200-PL-20035-03C02-P CML-15 | yes | FPSO 2014 | Pipe Wall Thickness | 21347 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 10.475 | CML-15 | CML: Equal Tee | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 9.4 | 6 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.79 |  | 12.2 | 10.4 | 9.4 | 9.9 | 1.2203
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-6 | 80-PW-20024-01C03-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23050 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 7.2 | CML-6 | CML: Reducer | 6 | 2016-11-10 | 2016-05-02 | 2015-05-06 07:00 | 2.5 | 2.5032 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 6.3 | 12 O'Clock | 40 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7.8 | 6.8 | 7.9 | 0.77889
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-17 | 150-WC-40002-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20356 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.475 | CML-17 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.3 | 9 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.5 | 7.7 | 7.4 | 7.3 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-3 | 50-FG-45018-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2585 | Rope Access | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 4.975 | CML-3 | CML: type TBC | 3 | 2016-09-04 | 2016-08-27 | 2014-04-26 07:00 | 2.5 | 0.93109 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 1.1245 | 5 | 4.7 | 5.3 | 4.9 | 0.25
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57017-01C02 | CML-1 | 20-DC-57017-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2896 | Rope Access | 2014-04-25 13:00 | 2014-04-25 14:00 | [36 empty] | 7.375 | CML-1 | CML: type TBC | 3 | 2067-05-31 | 2058-11-20 | 2014-04-25 13:00 | 0.16 | 0 | A1: Outside Quadrant |  | 2.56 | 0.16 | 1.0125 | 6.5 | 12 O'Clock | 20 | 5.56 | 20-DC-57017-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 6.5 | 7.4 | 8 | 7.6 | 0.63443
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 200-PG-23066-15S01 | CML-4 | 200-PG-23066-15S01 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10283 | Deck Level | 2013-11-09 | 2013-11-09 | [35 empty] | Low alarm breach | 20.4 | CML-4 | CML: type TBC | 1 | 2014-12-05 | 2014-04-03 | 2013-11-09 | 14.06 | 5.9171 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23066-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 20.4 | 20.4 | 0
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 200-PG-23066-15S01 | CML-3 | 200-PG-23066-15S01 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10282 | Deck Level | 2013-11-09 | 2013-11-09 | [35 empty] | Low alarm breach | 20.4 | CML-3 | CML: type TBC | 1 | 2014-12-05 | 2014-04-03 | 2013-11-09 | 14.06 | 5.9171 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23066-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 20.4 | 20.4 | 0
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 200-PG-23066-15S01 | CML-2 | 200-PG-23066-15S01 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10281 | Deck Level | 2013-11-09 | 2013-11-09 | [35 empty] | Low alarm breach | 20.4 | CML-2 | CML: type TBC | 1 | 2014-12-05 | 2014-04-03 | 2013-11-09 | 14.06 | 5.9171 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23066-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 20.4 | 20.4 | 0
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 200-PG-23066-15S01 | CML-1 | 200-PG-23066-15S01 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10280 | Deck Level | 2013-11-09 | 2013-11-09 | [35 empty] | Low alarm breach | 20.4 | CML-1 | CML: type TBC | 1 | 2014-12-05 | 2014-04-03 | 2013-11-09 | 14.06 | 5.9171 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23066-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 20.4 | 20.4 | 0
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-33 | 50-FL-43306-01C02 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 7649 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-33 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-32 | 50-FL-43306-01C02 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 7648 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-32 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-31 | 50-FL-43306-01C02 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 7647 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-31 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-30 | 50-FL-43306-01C02 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 7646 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-30 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-29 | 50-FL-43306-01C02 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 7645 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-29 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-28 | 50-FL-43306-01C02 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 7644 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-28 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-27 | 50-FL-43306-01C02 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 7643 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-27 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-10 | 50-CG-38500-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7882 |  | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:43 | [32 empty] | 5.225 | CML-10 | CML: Pipe Length | 3 | 2021-02-13 | 2021-12-12 | 2015-01-14 10:30 | 2.5 | 0.3943 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5.3 | 5.5 | 4.9 | 0.25
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45046-03C02-E | CML-3 | 80-FG-45046-03C02-E CML-3 | yes | FPSO 2016 | Pipe Wall Thickness | 24409 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.275 | CML-3 | CML: Elbow | 3 | 2031-11-06 | 2031-11-17 | 2016-06-08 07:00 | 2.5 | 0.16211 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.495 | 5 | 12 O'Clock | 80 | 5.49 | 80-FG-45046-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.3 | 5.6 | 0.25
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56105-01C02 | CML-1 | 50-DH-56105-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1970 |  | 2014-03-26 13:00 | 2014-03-26 14:00 | [36 empty] | 5.525 | CML-1 | CML: type TBC | 3 | 2020-09-21 | 2021-07-04 | 2014-03-26 13:00 | 2.5 | 0.41569 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DH-56105-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.8 | 5.6 | 5.5 | 0.25
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-6 | 250-PW-44004-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22750 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 6.575 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-04-29 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 | -0.35012 | 6.6 | 6.6 | 6.7 | 6.4 | 0.12583
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-21 | 80-PW-44001-01C02-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 22012 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.5 | CML-21 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.5 | 3 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.2 | 6.5 | 7.6 | 8.7 | 0.92014
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40046-01C02 | CML-4 | 300-WC-40046-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1254 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7.375 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 9 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.6 | 7.3 | 7.3 | 7.3 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-4 | 50-WC-40048-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 881 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 7.475 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.6 | 7.4 | 7.6 | 7.3 | 0.15
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45035-03C02 | CML-4 | 50-FG-45035-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2581 |  | 2014-04-26 14:00 | 2014-04-26 15:00 | [36 empty] | 5.725 | CML-4 | CML: type TBC | 3 | 2033-01-03 | 2032-11-17 | 2014-04-26 14:00 | 2.5 | 0.15504 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-FG-45035-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.4 | 5.7 | 6 | 0.25
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-17 | 200-PL-20008-01C02-H CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8814 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 8.125 | CML-17 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.5 | 8.3 | 8.2 | 7.5 | 0.43493
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-2 | 200-FH-43004-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12542 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 6.275 | CML-2 | CML: type TBC | 3 | 2020-10-20 | 2020-09-30 | 2014-02-01 07:00 | 2.5 | 0.52081 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.2 | 6.3 | 6.6 | 0.25
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43170-01C02 | CML-5 | 250-FL-43170-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2890 | Rope Access | 2014-04-25 07:00 | 2014-04-25 08:00 | [36 empty] | 6.475 | CML-5 | CML: Elbow | 3 | 2036-06-26 | 2036-04-25 | 2014-04-25 07:00 | 2.5 | 0.16677 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.4 | 6.8 | 6.2 | 0.25
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-4 | 50-WC-40048-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1545 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 7.475 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.6 | 7.4 | 7.6 | 7.3 | 0.15
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-5 | 80-PW-44034-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21987 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7 | CML-5 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.5 | 9 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 7.5 | 7 | 6.5 | 0.40825
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-26 | 50-FL-43306-01C02 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 7642 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-26 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-25 | 50-FL-43306-01C02 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 7641 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-25 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-9 | 50-CG-38452-09C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7857 | Line is FFS. Current RBI frequency is 48m. Action: CML’s to Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-08 13:38 | [32 empty] | 6.975 | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 3 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.3 | 6.7 | 7 | 6.9 | 0.25
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-24 | 50-FL-43306-01C02 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 7640 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-24 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-9 | 200-FH-43025-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2482 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 6.975 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 6 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.9 | 7.3 | 6.7 | 7 | 0.25
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1804 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 7.525 | CML-2 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-29 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 3 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.8 | 7.2 | 7.6 | 7.5 | 0.25
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-49 | 400-FH-43508-01C02 CML-49 |  | FPSO 2015 | Pipe Wall Thickness | 23568 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.875 | CML-49 | CML: Pipe Length | 3 | 2050-07-12 | 2045-08-19 | 2015-08-10 07:30 | 2.5 | 0.14594 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.6 | 12 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 7.8 | 8.2 | 7.9 | 0.25
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-7 | 50-CG-24002-09C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2553 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 8.625 | CML-7 | CML: type TBC | 3 | 2025-04-26 | 2022-03-24 | 2014-04-03 13:00 | 2.5 | 0.52391 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.7 | 8.9 | 8.6 | 8.3 | 0.25
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43014-01C02 | CML-1 | 250-FL-43014-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2891 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 9.125 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-04-25 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.8 | 6 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.4 | 9.2 | 8.8 | 9.1 | 0.25
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-34 | 50-FG-45023-01C02 CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 1182 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 9.875 | CML-34 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.6 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.6 | 9.8 | 10.2 | 9.9 | 0.25
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-23 | 50-FL-43306-01C02 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 7639 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-23 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-22 | 50-FL-43306-01C02 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 7638 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-22 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42045-01S01 | CML-6 | 50-CI-42045-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7489 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 9.2 | CML-6 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 8.9 | 12 O'Clock | 50 | 5.54 | 50-CI-42045-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9 | 9.4 | 9.5 | 0.29439
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42043-01S01 | CML-9 | 50-CI-42043-01S01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7482 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 9.2 | CML-9 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 8.9 | 6 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.5 | 8.9 | 8.9 | 9.5 | 0.34641
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-13 | 300-PG-20048-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21483 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 14.375 | CML-13 | CML: Fitting | 6 | 2072-08-17 | 2061-12-24 | 2014-06-28 09:30 | 4.9 | 0.15813 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 6 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 14.3 | 14.7 | 14.1 | 14.4 | 0.25
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-1 | 150-FL-43174-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12899 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.825 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.7 | 9 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.2 | 7.7 | 7.7 | 7.7 | 0.25
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-11 | 200-PG-23051-09C02-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 13116 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.225 | CML-11 | CML: type TBC | 3 | 2103-01-05 | 2073-03-18 | 2014-02-07 11:00 | 9.3 | 0 | A2: Right Quadrant |  | 15.26 | 9.3 | 12.28 | 18.7 | 6 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 20.4 | 18.7 | 18.7 | 19.1 | 0.80571
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63023-01E01 | CML-3 | 50-AU-63023-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8864 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 07:00 | 2015-02-25 08:00 | [36 empty] | 9.125 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.9 | 6 O'Clock | 50 | 5.54 | 50-AU-63023-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.2 | 9.1 | 8.9 | 9.3 | 0.17078
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-10 | 200-PG-24001-09C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10266 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 17.875 | CML-10 | CML: Pipe Length | 3 | 2019-06-20 | 2017-06-10 | 2013-11-09 | 9.2 | 1.4963 | A4: Left Quadrant |  | 15.26 | 9.2 | 12.23 | 17.6 | 9 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 18.2 | 17.9 | 17.8 | 17.6 | 0.25
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57402-01C03 | CML-2 | 50-DC-57402-01C03 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8359 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.175 | CML-2 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 12 O'Clock | 50 | 8.74 | 50-DC-57402-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9.2 | 9.1 | 9.5 | 0.25
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63040-01E01 | CML-1 | 50-AI-63040-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8317 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 9.125 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.9 | 12 O'Clock | 50 | 5.54 | 50-AI-63040-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9.2 | 9.3 | 9.1 | 0.17078
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-21 | 50-FL-43306-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 7637 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-21 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-1 | 150-WC-40002-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20340 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.45 | CML-1 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.3 | 12 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.6 | 7.4 | 7.5 | 0.1291
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-29 | 50-PF-20301-03C03-P CML-29 | no | FPSO 2014 | Pipe Wall Thickness | 3027 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.1 | CML-29 | CML: type TBC | 6 | 2024-06-03 | 2026-02-22 | 2014-05-01 07:00 | 3.61 | 0.41491 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 7.8 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 | 0 | 8.3 | 8.3 | 8 | 7.8 | 0.24495
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-29 | 50-PF-20301-03C03-P CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 22306 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.1 | CML-29 | CML: type TBC | 6 | 2024-06-03 | 2026-02-22 | 2014-05-01 07:00 | 3.61 | 0.41491 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 7.8 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 |  | 8.3 | 8.3 | 8 | 7.8 | 0.24495
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-1 | 200-PL-20035-03C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21336 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 9.85 | CML-1 | CML: Reducer | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 9.4 | 9 O'Clock | 300 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.79 |  | 9.4 | 10.2 | 10.4 | 9.4 | 0.52599
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-12 | 250-PG-23003-06C02-PA CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10679 | Deck Level. High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.9583 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-13 13:12 | [32 empty] | 4.9 | CML-12 | CML: Elbow | 3 | 2014-11-29 | 2015-01-27 | 2013-11-17 | 2.5 | 2.0302 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.9 | 5.2 | 4.9 | 0.24495
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-2 | 50-FL-43454-01C02-P CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 20505 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.9 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 5.6 | 5.9 | 6.2 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-20 | 50-FL-43306-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 7636 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-20 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 927 |  | 2014-04-10 11:00 | 2014-04-10 12:00 | [36 empty] | 7.4 | CML-3 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-04-10 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.1 | 6 O'Clock | 80 | 5.49 | 80-WC-40068-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.4 | 7.4 | 7.1 | 7.7 | 0.24495
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1591 |  | 2014-04-10 11:00 | 2014-04-10 12:00 | [36 empty] | 7.4 | CML-3 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-04-10 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.1 | 6 O'Clock | 80 | 5.49 | 80-WC-40068-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.4 | 7.4 | 7.1 | 7.7 | 0.24495
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-8 | 150-FL-43514-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20501 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.6 | CML-8 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 7.3 | 3 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.9 | 7.3 | 7.6 | 7.6 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-19 | 50-FL-43306-01C02 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 7635 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-19 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-18 | 50-FL-43306-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 7634 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-18 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-17 | 50-FL-43306-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 7633 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-17 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-16 | 50-FL-43306-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 7632 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-16 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-15 | 50-DH-56116-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 5225 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.2 | CML-15 | CML: Elbow | 3 | 2018-01-04 | 2018-07-03 | 2014-05-20 09:30 | 2.5 | 0.66102 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5.4 | 5.1 | 0.24495
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-7 | 80-PW-44034-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21989 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.775 | CML-7 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.5 | 9 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 7 | 6.9 | 6.5 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-2 | 80-FH-43111-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12800 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 6.2 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-02-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 6 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 6.4 | 5.9 | 6.1 | 0.24495
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-14 | 50-FG-45024-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 13000 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 6.3 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-01-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.6 | 6.4 | 6.1 | 0.24495
PG02 | Montara_Topside | No | Separation (20) | Pipework | 150-PG-20043-01D01-P | CML-1 | 150-PG-20043-01D01-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21446 | Protective mesh removed | 2014-06-29 07:00 | 2014-06-29 08:00 | [36 empty] | 8.2 | CML-1 | CML: Elbow | 1 | 293525 | 2412-05-14 | 2014-06-29 07:00 | 0.7 | 0.00928 | A1: Outside Quadrant |  | 6.11 | 0.7 | 3.405 | 7.1 | 12 O'Clock | 150 | 7.11 | 150-PG-20043-01D01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 7.1 | 8.5 | 8.4 | 8.8 | 0.75277
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43121-01C02 | CML-7 | 150-FH-43121-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1770 | Rope access | 2014-04-27 09:30 | 2014-04-27 11:00 | [36 empty] | 6.3 | CML-7 | CML: Elbow | 3 | 2017-07-18 | 2017-03-22 | 2014-04-27 09:30 | 2.5 | 1.1158 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.1 | 3 O'Clock | 150 | 7.11 | 150-FH-43121-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.1 | 6.6 | 6.4 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-15 | 50-FL-43306-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 7631 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-15 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-5 | 150-FH-43027-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10567 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 6.7 | CML-5 | CML: type TBC | 3 | 2016-05-26 | 2016-03-02 | 2013-11-16 | 2.5 | 1.5426 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 12 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.9 | 6.9 | 6.6 | 0.24495
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40053-01C02 | CML-1 | 50-WC-40053-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 872 |  | 2014-04-06 16:00 | 2014-04-06 16:30 | [36 empty] | 7.45 | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 3 O'Clock | 50 | 5.54 | 50-WC-40053-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.6 | 7.3 | 7.4 | 7.5 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43119-01C02 | CML-7 | 80-FH-43119-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12834 |  | 2014-01-18 10:00 | 2014-01-18 11:30 | [36 empty] | 5.8 | CML-7 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-01-18 10:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.6 | 9 O'Clock | 80 | 5.49 | 80-FH-43119-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.06 |  | 5.6 | 6.1 | 5.9 | 5.6 | 0.24495
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40053-01C02 | CML-1 | 50-WC-40053-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1536 |  | 2014-04-06 16:00 | 2014-04-06 16:30 | [36 empty] | 7.45 | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 3 O'Clock | 50 | 5.54 | 50-WC-40053-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.6 | 7.3 | 7.4 | 7.5 | 0.1291
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-10 | 250-PW-20040-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21394 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.6 | CML-10 | CML: Elbow | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 12.8 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 13.4 | 13.2 | 15 | 12.8 | 0.96609
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-14 | 100-DC-57036-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1420 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 9.9 | CML-14 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.9 | 3 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  |  | 8.9 | 10 | 10.8 | 0.95394
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57014-01C02 | CML-3 | 50-DC-57014-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1364 | Rope access | 2014-04-04 13:00 | 2014-04-04 15:00 | [36 empty] | 9.525 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-04 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.9 | 6 O'Clock | 50 | 5.54 | 50-DC-57014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10.4 | 9.4 | 8.9 | 9.4 | 0.62915
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-10 | 100-FG-45043-03C02-E CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22656 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 8.7 | CML-10 | CML: Elbow | 3 | 2054-10-24 | 2049-02-10 | 2015-04-27 07:00 | 1.88 | 0 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 8.4 | 3 O'Clock | 50 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.52 |  | 8.6 | 8.4 | 8.9 | 8.9 | 0.24495
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-2 | 200-FH-43131-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2823 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 9.4 | CML-2 | CML: Reducer | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 9.2 | 3 O'Clock | 150 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.86 |  | 9.2 | 9.2 | 9.7 | 9.5 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-14 | 50-FL-43306-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7630 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-14 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-7 | 300-PG-20005-03C03-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22769 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 13.3 | CML-7 | CML: Pipe Length | 6 | 2028-09-14 | 2025-12-15 | 2015-04-29 07:00 | 4.9 | 0.61244 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.1 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 | -0.75005 | 13.1 | 13.6 | 13.1 | 13.4 | 0.24495
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-19 | 150-PG-20507-01C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2863 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 11.1 | CML-19 | CML: type TBC | 6 | 2052-09-27 | 2047-01-03 | 2014-03-16 07:00 | 2.5 | 0.21523 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.8 | 6 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.3 | 11 | 10.8 | 11.3 | 0.24495
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-17 | 250-PG-23004-06C03-A CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 13017 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 17.8 | CML-17 | CML: Pipe Length | 6 | 2021-04-09 | 2019-10-09 | 2014-01-11 15:00 | 8.55 | 1.2349 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.5 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.95 |  | 17.5 | 18 | 18 | 17.7 | 0.24495
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-23 | 80-PW-44001-01C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 22014 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.45 | CML-23 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.6 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.2 | 8.6 | 7.4 | 0.83865
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-19 | 300-PG-20004-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 6142 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 16.2 | CML-19 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 16 | 3 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 16 | 16 | 16.3 | 16.5 | 0.24495
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-5 | 50-CG-38452-09C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23745 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 20.2 | CML-5 | CML: Fitting | 3 | 2075-10-24 | 2059-08-12 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 20 | 9 O'Clock | 100 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.5 |  | 20 | 20.3 | 20.5 | 20 | 0.24495
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80001-01C02 | CML-4 | 50-VA-80001-01C02 CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 3137 | Rope Access | 2014-05-02 09:30 | 2014-05-02 10:30 | [36 empty] | 17.125 | CML-4 | CML: type TBC | 3 | 2018-08-02 | 2019-02-20 | 2014-05-02 09:30 | 2.5 | 0.58766 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-VA-80001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.5 | 5 | 5.3 | 0.24495
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-25 | 50-DH-56062-01C02 CML-25 | yes | FPSO 2015 | Pipe Wall Thickness | 9112 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.6 | CML-25 | CML: type TBC | 3 | 2017-09-15 | 2018-03-02 | 2015-03-02 07:00 | 2.5 | 0.70797 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 4.8 | 4.5 | 4.8 | 0.24495
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43019-01C02 | CML-5 | 80-FH-43019-01C02 CML-5 | yes | FPSO 2013 | Pipe Wall Thickness | 10624 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.7 | CML-5 | CML: type TBC | 3 | 2014-10-24 | 2014-12-22 | 2013-11-17 | 2.5 | 2.1382 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 6 O'Clock | 80 | 5.49 | 80-FH-43019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.8 | 4.5 | 5 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-13 | 50-FL-43306-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7629 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-13 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-4 | 50-FG-45018-03C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10503 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5 | CML-4 | CML: type TBC | 3 | 2015-01-26 | 2015-01-22 | 2013-11-15 | 2.5 | 1.8359 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 4.9 | 4.7 | 5.2 | 0.24495
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-4 | 50-FG-45302-01C02 CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 5772 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 5.3 | CML-4 | CML: Elbow | 3 | 2019-05-22 | 2020-01-11 | 2014-06-23 11:00 | 2.5 | 0.5087 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.5 | 5.2 | 5.5 | 0.24495
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56113-01C02 | CML-2 | 50-DH-56113-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5241 | Rope Access | 2014-05-20 14:00 | 2014-05-20 15:00 | [36 empty] | 5.2 | CML-2 | CML: Elbow | 3 | 2018-11-12 | 2019-06-14 | 2014-05-20 14:00 | 2.5 | 0.55744 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-DH-56113-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.5 | 5 | 5.3 | 0.24495
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-2 | 200-PW-44021-01X01 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10707 | Deck Level. Line is FFS. High CR. Line rechecked (refer to Jan. 15 values) | 2013-11-10 | 2013-11-10 |  |  | Administrator | 2015-09-13 11:03 | [32 empty] | 7.925 | CML-2 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2013-11-10 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 12 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 8.2 | 8.5 | 7.9 | 0.60208
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20057-01C02-P | CML-1 | 100-PW-20057-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21838 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.15 | CML-1 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 9 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.4 | 7.3 | 7.3 | 6.6 | 0.36968
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-7 | 200-PW-44019-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21898 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 7.9 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 | 0 | 8.4 | 8.1 | 7.1 | 8 | 0.55976
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40044-01C02 | CML-1 | 300-WC-40044-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1116 |  | 2014-03-21 11:30 | 2014-03-21 12:00 | [36 empty] | 7.425 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-21 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 12 O'Clock | 300 | 6.35 | 300-WC-40044-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.4 | 7.5 | 7.5 | 0.095743
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-26 | 200-PL-20035-03C02-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 21358 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 9.575 | CML-26 | CML: Elbow | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 9.4 | 6 O'Clock | 250 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.79 |  | 9.7 | 9.4 | 9.4 | 9.8 | 0.20616
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-4 | 100-FH-43104-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12755 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 6.1 | CML-4 | CML: type TBC | 3 | 2032-07-20 | 2033-03-08 | 2014-01-25 07:00 | 2.5 | 0.18381 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.4 | 5.9 | 6.2 | 0.24495
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-7 | 200-PW-44019-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5573 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 7.9 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8.4 | 8.1 | 7.1 | 8 | 0.55976
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-26 | 80-PW-44001-01C02-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 22017 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.9 | CML-26 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.6 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.1 | 7 | 6.6 | 6.9 | 0.21602
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56139-01C02 | CML-1 | 50-DH-56139-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21064 | Rope Access | 2014-05-15 11:00 | 2014-05-15 12:00 | [36 empty] | 6.7 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-15 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-DH-56139-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7 | 6.8 | 6.5 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-12 | 50-FL-43306-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 7628 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-12 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-11 | 50-FL-43306-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 7627 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-11 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45048-03C02 | CML-3 | 50-FG-45048-03C02 CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 2278 |  | 2014-03-16 14:00 | 2014-03-16 14:30 | [36 empty] | 6.7 | CML-3 | CML: type TBC | 3 |  |  | 2014-03-16 14:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.5 | 6 O'Clock | 50 |  | 50-PG-45048-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.8 | 6.5 | 6.5 | 7 | 0.24495
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43124-01C02 | CML-2 | 80-FH-43124-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12844 |  | 2014-02-05 11:00 | 2014-02-05 13:00 | [36 empty] | 5.5 | CML-2 | CML: Pipe Length | 3 | 2031-03-18 | 2028-12-08 | 2014-02-05 11:00 | 0.54 | 0.278 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-FH-43124-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.6 | 5.3 | 5.8 | 5.3 | 0.24495
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-6 | 50-WC-40048-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 883 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 7.375 | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.4 | 7.4 | 7.3 | 7.4 | 0.05
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-9 | 250-PW-44004-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5628 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 6.7 | CML-9 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-06-20 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.8 | 6.7 | 6.6 | 0.08165
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-20 | 50-FG-45024-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 1203 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.4 | CML-20 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.6 | 6.3 | 6.6 | 0.24495
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-6 | 50-WC-40048-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1547 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 7.375 | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.4 | 7.4 | 7.3 | 7.4 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40061-01C02 | CML-8 | 400-WC-40061-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1132 |  | 2014-03-21 08:30 | 2014-03-21 09:00 | Check Corrosion Rate of 0.523mm/ yr | [35 empty] | 8.075 | CML-8 | CML: type TBC | 3 | 2023-08-03 | 2022-04-26 | 2014-03-21 08:30 | 2.6 | 0.52258 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 7.5 | 6 O'Clock | 400 | 7.92 | 400-WC-40061-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 9 | 8 | 7.5 | 7.8 | 0.65
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20057-01C02-P | CML-3 | 100-PW-20057-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21840 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.025 | CML-3 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.7 | 6 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.1 | 7.3 | 6.7 | 7 | 0.25
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45035-03C02 | CML-3 | 50-FG-45035-03C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 2580 |  | 2014-04-26 14:00 | 2014-04-26 15:00 | [36 empty] | 5 | CML-3 | CML: type TBC | 3 | 2016-09-05 | 2016-08-28 | 2014-04-26 14:00 | 2.5 | 0.93027 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FG-45035-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 4.7 | 5 | 5.3 | 0.24495
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-2 | 25-VA-23054-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1471 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 5.5 | CML-2 | CML: type TBC | 3 | 2021-07-21 | 2022-06-05 | 2014-04-29 10:00 | 2.5 | 0.37333 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.5 | 5.2 | 5.8 | 0.24495
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40018-01C02 | CML-3 | 50-WC-40018-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1697 | Rope Access | 2014-04-13 09:15 | 2014-04-13 10:15 | [36 empty] | 8.1333 | CML-3 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 09:15 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40018-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  |  | 8.5 | 8.5 | 7.4 | 0.63509
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-5 | 80-FH-43111-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12803 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 6.2 | CML-5 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-02-01 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 3 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.5 | 5.9 | 6.2 | 6.2 | 0.24495
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-17 | 100-DH-56082-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 3385 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.5 | CML-17 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.5 | 6.5 | 6.8 | 0.24495
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57402-01C03 | CML-3 | 50-DC-57402-01C03 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8360 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.475 | CML-3 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 12 O'Clock | 50 | 8.74 | 50-DC-57402-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.6 | 9.5 | 9.8 | 0.34034
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 150-DH-56080-01C02 | CML-7 | 150-DH-56080-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3330 | Rope Access | 2014-05-08 07:00 | 2014-05-08 09:00 | [36 empty] | 7 | CML-7 | CML: type TBC | 3 | 2023-12-03 | 2023-02-06 | 2014-05-08 07:00 | 2.5 | 0.43848 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 3 O'Clock | 150 | 7.11 | 150-DH-56080-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.3 | 6.7 | 7 | 7 | 0.24495
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45038-03C02 | CML-3 | 150-FG-45038-03C02 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24344 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.3 | CML-3 | CML: Elbow | 3 | 2139-10-13 | 2117-09-18 | 2016-06-06 07:00 | 2.5 | 0.03646 | A1: Outside Quadrant |  | 4.11 | 2.5 | 3.305 | 7 | 12 O'Clock | 150 | 7.11 | 150-FG-45038-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.3 | 7.6 | 7.3 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-10 | 50-FL-43306-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7626 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-10 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-9 | 50-FL-43306-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7625 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-9 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-7 | 80-FH-43009-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12585 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.5 | CML-7 | CML: Pipe Length | 3 | 2025-01-24 | 2023-07-31 | 2014-02-05 08:00 | 0.54 | 0.42453 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 5.8 | 5.2 | 5.5 | 5.5 | 0.24495
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-4 | 400-FH-43508-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6553 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.5 | CML-4 | CML: Elbow | 3 | 2027-03-03 | 2025-05-09 | 2015-03-30 07:00 | 2.5 | 0.39383 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 7.2 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.5 | 7.5 | 7.8 | 7.2 | 0.24495
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56087-01C02 | CML-3 | 100-DH-56087-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8033 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:31 | [32 empty] | 8.1 | CML-3 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-20 14:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.9 | 6 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.2 | 7.9 | 7.9 | 8.4 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-8 | 50-FL-43306-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7624 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-8 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-1 | 50-FG-45020-03C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10573 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 8.4 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2013-11-17 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 8.1 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.4 | 8.4 | 8.7 | 0.24495
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-7 | 50-FL-43306-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7623 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-7 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-17 | 50-PL-24003-09C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 13156 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 9.25 | CML-17 | CML: type TBC | 3 | 2022-05-28 | 2020-01-27 | 2014-01-18 13:00 | 2.5 | 0.69361 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 12 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.3 | 9.1 | 10.3 | 0.8226
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-14 | 200-PL-20019-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21265 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 8.625 | CML-14 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 9 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.4 | 8.3 | 8.5 | 8.3 | 0.5252
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-57 | 400-FH-43508-01C02 CML-57 |  | FPSO 2015 | Pipe Wall Thickness | 6583 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.3 | CML-57 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 9 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.3 | 9 | 9.6 | 9.3 | 0.24495
PL03 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-57066-01C03 | CML-3 | 50-PL-57066-01C03 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23101 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.6 | CML-3 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2015-05-10 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.3 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | 0 | 9.9 | 9.3 | 9.6 | 9.6 | 0.24495
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-4 | 200-FH-43025-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2477 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 10 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 9 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10.2 | 9.9 | 10.2 | 9.7 | 0.24495
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38471-01C02-P | CML-1 | 50-CG-38471-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23620 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 12.1 | CML-1 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 11.9 | 9 O'Clock | 50 | 5.54 | 50-CG-38471-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 12.2 | 11.9 | 12.4 | 11.9 | 0.24495
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-4 | 200-PW-44020-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23011 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 7.7 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 12 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 | -0.3425 | 7.1 | 7.8 | 7.8 | 8.1 | 0.42426
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-9 | 50-FH-43137-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22683 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.25 | CML-9 | CML: Elbow | 3 | 2024-02-18 | 2025-04-13 | 2015-04-27 07:00 | 2.5 | 0.28348 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.23858 | 5 | 5.4 | 5.1 | 5.5 | 0.23805
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-21 | 25-FG-45455-01C02-E CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 23821 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.25 | CML-21 | CML: Fitting | 3 | 2027-11-29 | 2027-10-21 | 2014-09-25 07:00 | 2.5 | 0.26543 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6 | 6.1 | 6.4 | 0.23805
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-7 | 50-CG-38457-01C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23725 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.15 | CML-7 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.9 | 6 O'Clock | 50 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9 | 9.3 | 8.9 | 9.4 | 0.23805
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-6 | 50-FL-43306-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7622 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45031-03C03 | CML-5 | 50-PL-45031-03C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10473 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 8.15 | CML-5 | CML: type TBC | 6 | 2017-08-10 | 2017-02-18 | 2013-11-14 | 0.99 | 1.847 | A3: Inside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.9 | 6 O'Clock | 50 | 8.74 | 50-PL-45031-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.91 |  | 8.3 | 8.4 | 7.9 | 8 | 0.23805
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-3 | 50-PL-23052-09C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10167 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.25 | CML-3 | CML: type TBC | 6 | 2016-10-25 | 2016-05-08 | 2013-11-09 | 2.81 | 2.4258 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 10 | 6 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.19 |  | 10.4 | 10.5 | 10 | 10.1 | 0.23805
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-21 | 80-CG-38459-09C02-P CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 23718 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 11.25 | CML-21 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11 | 12 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11 | 11.1 | 11.5 | 11.4 | 0.23805
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-2 | 80-CG-38459-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6514 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 17.55 | CML-2 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-24 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 17.3 | 3 O'Clock | 300 | 14.27 | 300-PF-20002-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.4 |  | 17.7 | 17.3 | 17.4 | 17.8 | 0.23805
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-5 | 200-PW-44021-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7702 | Re-check. CR reported in 2013 was 1.70. It appears that it was an error. Point need to be rechecked | 2015-01-08 15:30 | 2015-01-08 16:30 |  |  | Administrator | 2015-09-04 14:28 | [32 empty] | 7.7 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-08 15:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 12 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 | -1.2893 | 7.1 | 7.8 | 7.9 | 8 | 0.40825
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43076-01C02 | CML-2 | 150-FL-43076-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2343 | Rope Access | 2014-03-17 11:00 | 2014-03-17 11:30 | [36 empty] | 8.05 | CML-2 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-03-17 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.8 | 6 O'Clock | 150 | 7.11 | 150-FL-43076-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.2 | 8.3 | 7.8 | 7.9 | 0.23805
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-3 | 80-FL-43015-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22946 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.15 | CML-3 | CML: Elbow | 3 | 2021-09-21 | 2022-09-09 | 2015-05-02 07:00 | 2.5 | 0.35964 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 9 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.17548 | 5.3 | 5.2 | 5.3 | 4.8 | 0.23805
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23038-03D01-A | CML-2 | 300-PG-23038-03D01-A CML-2 | High Priority | FPSO 2013 | Pipe Wall Thickness | 10702 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 6.65 | CML-2 | CML: type TBC | 1 | 2035-08-14 | 2028-11-13 | 2013-11-07 | 3.8 | 0.11478 | A2: Right Quadrant |  | 5.35 | 3.8 | 4.575 | 6.3 | 3 O'Clock | 300 | 6.35 | 300-PG-23038-03D01 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.7 | 6.3 | 6.8 | 6.8 | 0.23805
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-1 | 250-PW-44006-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1898 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 7.175 | CML-1 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 9 O'Clock | 150 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.2 | 7.3 | 7.1 | 7.1 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43154-01C02 | CML-9 | 100-FL-43154-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12879 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 5.85 | CML-9 | CML: type TBC | 3 | 2017-12-31 | 2018-02-24 | 2014-02-03 08:00 | 2.5 | 0.76739 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 9 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6 | 6 | 5.9 | 5.5 | 0.23805
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-15 | 100-FG-45043-03C02-E CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 22661 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.35 | CML-15 | CML: Elbow | 3 | 2021-02-21 | 2020-01-29 | 2015-04-27 07:00 | 1.88 | 0.53546 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 5 | 12 O'Clock | 50 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 12 O'Clock | 6 O'Clock | 9 O'Clock | 3.12 |  | 5.4 | 5 | 5.5 | 5.5 | 0.23805
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43176-01C02 | CML-3 | 300-FL-43176-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20433 | Protective mesh removed/Rope access | 2014-06-27 10:30 | 2014-06-27 12:00 | [36 empty] | 6.15 | CML-3 | CML: Elbow | 3 | 2020-12-01 | 2020-11-11 | 2014-06-27 10:30 | 2.5 | 0.51285 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 300 | 6.35 | 300-FL-43176-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 5.8 | 6.3 | 6.2 | 0.23805
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12568 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.725 | CML-7 | CML: Elbow | 3 | 2024-03-22 | 2022-11-04 | 2014-01-18 07:00 | 0.54 | 0.45765 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 5.8 | 6.1 | 5.2 | 5.8 | 0.37749
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45028-03C02-E | CML-1 | 80-FG-45028-03C02-E CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24325 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.15 | CML-1 | CML: Elbow | 3 | 2038-02-06 | 2034-12-12 | 2016-06-01 07:00 | 1.46 | 0.16314 | A2: Right Quadrant |  | 2.49 | 1.46 | 1.975 | 5 | 9 O'Clock | 80 | 5.49 | 80-FG-45028-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.54 |  | 5.5 | 5 | 5.1 | 5 | 0.23805
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-24 | 300-FL-43070-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 12717 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.85 | CML-24 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 6.9 | 6.5 | 7 | 0.23805
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20012-01C02-P | CML-5 | 200-PL-20012-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21207 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.65 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 9 O'Clock | 200 | 6.35 | 200-PL-20012-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.7 | 9 | 8.6 | 8.3 | 0.28868
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-15 | 200-PL-20008-01C02-H CML-15 | yes | FPSO 2015 | Pipe Wall Thickness | 8812 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 8 | CML-15 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.1 | 8.2 | 7.5 | 8.2 | 0.33665
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43029-01C02 | CML-6 | 400-FH-43029-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10022 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 8.05 | CML-6 | CML: Elbow | 3 | 2129-08-04 | 2114-02-09 | 2013-11-04 | 2.48 | 0.04679 | A2: Right Quadrant |  | 4.92 | 2.48 | 3.205 | 7.9 | 6 O'Clock | 400 | 7.92 | 400-FH-43029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.42 |  | 8 | 7.9 | 7.9 | 8.4 | 0.23805
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-5 | 50-FL-43306-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7621 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40051-01C02 | CML-3 | 50-WC-40051-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 902 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 7.725 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 8.6 | 7.5 | 7.4 | 0.58523
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-23 | 200-FH-43025-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 2496 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 8.95 | CML-23 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.6 | 6 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9 | 9.1 | 8.6 | 9.1 | 0.23805
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38490-09C02 | CML-4 | 50-CG-38490-09C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2532 |  | 2014-04-03 07:00 | 2014-04-03 08:00 | [36 empty] | 9.35 | CML-4 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9 | 9 O'Clock | 50 | 8.74 | 50-CG-38490-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.5 | 9.5 | 9.4 | 9 | 0.23805
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-3 | 200-PW-44019-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23031 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 7.625 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 | 0.56872 | 8.5 | 7.5 | 7.2 | 7.3 | 0.59652
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-18 | 50-FL-43454-01C02-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 22883 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.55 | CML-18 | CML: Elbow | 6 | 2026-11-20 | 2025-04-29 | 2015-05-01 07:00 | 2.5 | 0.57937 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 0 | 9.6 | 9.7 | 9.2 | 9.7 | 0.23805
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43302-01C02 | CML-21 | 250-FH-43302-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 12937 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 9.45 | CML-21 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 9 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.8 | 9.3 | 9.4 | 9.3 | 0.23805
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-4 | 250-PW-20040-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21388 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.4 | CML-4 | CML: Elbow | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 12.8 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 13.8 | 12.8 | 14.2 | 12.8 | 0.71181
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-24 | 250-PL-20006-01C02-P CML-24 | yes | FPSO 2014 | Pipe Wall Thickness | 13194 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 10.1 | CML-24 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A2: Right Quadrant |  | 3.35 | 3.61 | 3.0831 | 9.5 | 6 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.89 |  | 11.8 | 9.5 | 9.5 | 9.6 | 1.1343
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-22 | 300-PG-20005-03C03-P CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 22784 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 13.85 | CML-22 | CML: Reducing Tee | 6 | 2036-08-24 | 2032-06-20 | 2015-04-29 07:00 | 4.9 | 0.40306 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 | -0.12501 | 14 | 14 | 13.9 | 13.5 | 0.23805
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43509-01C02 | CML-3 | 300-FL-43509-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2397 | Rope Access | 2014-03-19 09:30 | 2014-03-19 11:00 | [36 empty] | 11.45 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.3 | 3 O'Clock | 300 | 6.35 | 300-FL-43509-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 11.3 | 11.3 | 11.4 | 11.8 | 0.23805
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-16 | 250-PW-20041-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21425 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.3 | CML-16 | CML: Reducer | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 12.9 | 3 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 13.8 | 12.9 | 13.2 | 13.3 | 0.37417
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-8 | 150-FL-43174-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5979 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.65 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 9 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.5 | 3.6 | 4 | 3.5 | 0.23805
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-7 | 250-PG-23003-06C02-PA CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7686 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:15 | [32 empty] | 4.85 | CML-7 | CML: Elbow | 3 | 2018-08-10 | 2019-03-02 | 2015-01-08 13:00 | 2.5 | 0.58495 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0 | 4.7 | 5.1 | 4.6 | 5 | 0.23805
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-10 | 100-DC-57307-01C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2318 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | [36 empty] | 9.225 | CML-10 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 9 | 9 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.3 | 9.4 | 9.2 | 9 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-1 | 200-PW-44021-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23016 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 7.75 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 12 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 | 0 | 7.2 | 7.5 | 8.5 | 7.8 | 0.55678
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40051-01C02 | CML-3 | 50-WC-40051-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1566 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 7.725 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 8.6 | 7.5 | 7.4 | 0.58523
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43138-01C02 | CML-2 | 50-FH-43138-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22688 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.25 | CML-2 | CML: Elbow | 3 | 2022-06-16 | 2023-06-06 | 2015-04-27 07:00 | 2.5 | 0.33597 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FH-43138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0 | 4.9 | 5.4 | 5.4 | 5.3 | 0.23805
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-4 | 50-FL-43306-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7620 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-4 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-3 | 50-FL-43306-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7619 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-2 | 50-FL-43306-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7618 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21063 | Rope Access | 2014-05-15 07:00 | 2014-05-15 08:00 | [36 empty] | 5.35 | CML-2 | CML: type TBC | 3 | 2020-01-02 | 2020-09-16 | 2014-05-15 07:00 | 2.5 | 0.46111 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-DH-56131-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.6 | 5.5 | 5.2 | 0.23805
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40404-01C02 | CML-1 | 150-WC-40404-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20391 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 7.625 | CML-1 | CML: Pipe Length | 3 | 2059-07-07 | 2055-11-27 | 2014-10-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.4 | 9 O'Clock | 150 | 7.11 | 150-WC-40404-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.3 | 7.4 | 7.4 | 7.4 | 0.45
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3493 | Rope Access | 2014-05-14 14:00 | 2014-05-14 15:00 | [36 empty] | 5.65 | CML-3 | CML: type TBC | 3 | 2034-01-29 | 2036-04-18 | 2014-05-14 14:00 | 2.5 | 0.14702 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DN-56075-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.8 | 5.4 | 5.9 | 0.23805
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-8 | 50-FG-45018-03C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2590 | Rope Access | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 5.75 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | -2.0241 | 6.1 | 5.7 | 5.6 | 5.6 | 0.23805
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-2 | 50-CG-38454-01C02-H CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 23666 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.85 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 6.1 | 6 | 0.23805
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56142-01C02 | CML-2 | 25-DH-56142-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7523 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 |  |  | Nestor | 2014-11-24 09:39 | [32 empty] | 5.95 | CML-2 | CML: Elbow | 3 | 2026-06-22 | 2026-05-18 | 2015-04-13 07:00 | 2.5 | 0.29466 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 25 | 6.35 | 25-DH-56142-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 5.8 | 5.8 | 5.9 | 0.23805
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-23 | 250-PL-20006-01C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 13193 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 10.65 | CML-23 | CML: Tee | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A1: Outside Quadrant |  | 3.35 | 3.61 | 3.0831 | 9.5 | 12 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.89 |  | 9.5 | 11.1 | 10.7 | 11.3 | 0.80623
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-11 | 50-FG-45023-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1159 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.15 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | -3.584 | 6 | 6.4 | 5.9 | 6.3 | 0.23805
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-9 | 50-FG-45023-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1157 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.25 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | -3.584 | 5.9 | 6.4 | 6.3 | 6.4 | 0.23805
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43303-01C02 | CML-1 | 50-FL-43303-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 20457 | This is a dead leg | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 6.55 | CML-1 | CML: Cap End | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 3 O'Clock | 50 | 5.54 | 50-FL-43303-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 6.2 | 6.6 | 6.7 | 0.23805
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-27 | 50-FG-45023-01C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 1175 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.45 | CML-27 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 6.6 | 6.3 | 6.2 | 0.23805
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-5 | 50-FG-45024-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1209 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.45 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.7 | 6.2 | 6.6 | 0.23805
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-1 | 200-WC-40008-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7807 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 7.875 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 12 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.6 | 8.3 | 8.2 | 0.44253
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-12 | 150-FL-43174-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12910 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.45 | CML-12 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 12 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.7 | 7.6 | 7.3 | 0.23805
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-8 | 200-FH-43114-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12816 |  | 2014-02-01 12:00 | 2014-02-01 14:00 | [36 empty] | 7.55 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 12:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 6 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.6 | 7.7 | 7.2 | 7.7 | 0.23805
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40009-01C02 | CML-5 | 200-WC-40009-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3124 | Rope Access | 2014-05-04 07:00 | 2014-05-04 08:00 | [36 empty] | 7.7 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-05-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 6 O'Clock | 200 | 6.35 | 200-WC-40009-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.3 | 7.4 | 7.4 | 7.7 | 0.42426
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-8 | 200-FH-43003-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12531 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.65 | CML-8 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 11:30 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.4 | 12 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.06 |  | 6.4 | 6.5 | 6.8 | 6.9 | 0.23805
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-9 | 50-PL-23040-03C03 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10194 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 7.85 | CML-9 | CML: type TBC | 6 | 2015-10-24 | 2015-10-07 | 2013-11-08 | 2.5 | 2.6006 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 7.6 | 9 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8 | 8.1 | 7.7 | 7.6 | 0.23805
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FL-43306-01C02 | CML-1 | 50-FL-43306-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7617 | Decommissioned | 2015-01-08 07:00 | 2015-01-08 09:00 | [37 empty] | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FL-43306-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-3 | 150-FH-43136-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2764 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.05 | CML-3 | CML: Pipe Length | 3 | 2024-12-31 | 2022-11-30 | 2014-03-13 09:00 | 1.03 | 0.5244 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.7 | 6 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.67 |  | 7.2 | 7.2 | 6.7 | 7.1 | 0.23805
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-12 | 150-FH-43518-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2712 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.25 | CML-12 | CML: Pipe Length | 3 | 208638 | 2393-09-16 | 2014-03-12 09:00 | 1.23 | 0.01284 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7.1 | 9 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.87 | 0 | 7.6 | 7.2 | 7.1 | 7.1 | 0.23805
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-12 | 150-FH-43518-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 351 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.25 | CML-12 | CML: Pipe Length | 3 | 208418 | 2393-03-17 | 2014-03-12 | 1.23 | 0.01285 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7.1 | 9 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.87 |  | 7.6 | 7.2 | 7.1 | 7.1 | 0.23805
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20045 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 20.85 | CML-8 | CML: Pipe Length | 3 | 2017-07-26 | 2016-07-08 | 2014-05-29 07:00 | 15.88 | 1.4608 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 3 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 | 0 | 21 | 20.5 | 20.9 | 21 | 0.23805
FG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-FG-45024-01C02 | CML-3 | 50-FG-45024-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2531 |  | 2014-04-03 07:00 | 2014-04-03 08:00 | [36 empty] | 9.35 | CML-3 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 6 O'Clock | 50 | 8.74 | 50-CG-38490-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.3 | 9.2 | 9.2 | 9.7 | 0.23805
CG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-CG-38459-09C02-P | CML-2 | 80-CG-38459-09C02-P CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10417 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 17.65 | CML-2 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2013-11-13 | 4.7 | 0 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 17.3 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.6 |  | 17.7 | 17.3 | 17.8 | 17.8 | 0.23805
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-5 | 50-DH-56137-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20731 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 17.65 | CML-5 | CML: Reducing Tee | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 17.5 | 9 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15 |  | 18 | 17.6 | 17.5 | 17.5 | 0.23805
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-5 | 50-DH-56137-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5446 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 3.576mm/ yr | [34 empty] | Low alarm breach | 18.05 | CML-5 | CML: Straight | 3 | 2018-09-16 | 2016-06-24 | 2014-05-28 07:00 | 2.5 | 3.5763 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 17.9 | 6 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 |  | 18.4 | 17.9 | 17.9 | 18 | 0.23805
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43107-01C02 | CML-3 | 300-FH-43107-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20426 | Protective mesh removed | 2014-07-02 13:00 | 2014-07-02 14:00 | [36 empty] | 9.45 | CML-3 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-02 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 6 O'Clock | 300 | 6.35 | 300-FH-43107-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.7 | 9.3 | 9.2 | 9.6 | 0.23805
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-8 | 150-PG-20507-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2852 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.45 | CML-8 | CML: type TBC | 6 | 2022-02-05 | 2020-10-30 | 2014-03-16 07:00 | 2.5 | 0.97488 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 10.2 | 3 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.3 | 10.2 | 10.7 | 10.6 | 0.23805
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20062-01C03-P | CML-5 | 250-PG-20062-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21542 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 10.95 | CML-5 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-07-13 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 10.7 | 3 O'Clock | 150 | 9.27 | 250-PG-20062-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.8 | 10.7 | 11.1 | 11.2 | 0.23805
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43029-01C02 | CML-2 | 400-FH-43029-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10018 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.85 | CML-2 | CML: Elbow | 3 | 2023-12-23 | 2022-07-27 | 2013-11-04 | 2.48 | 0.51474 | A2: Right Quadrant |  | 4.92 | 2.48 | 3.205 | 7.7 | 6 O'Clock | 400 | 7.92 | 400-FH-43029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 |  | 7.8 | 7.7 | 7.7 | 8.2 | 0.23805
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-30 | 50-FL-43454-01C02-P CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 2804 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.75 | CML-30 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 22.5 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.62 |  | 22.6 | 22.5 | 23 | 22.9 | 0.23805
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-20 | 250-PL-20006-01C02-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 13190 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 10.2333 | CML-20 | CML: Pipe Length | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A2: Right Quadrant |  | 3.35 | 3.61 | 3.0831 | 9.5 | 3 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.89 |  | 10.5 | 9.5 | 10.7 |  | 0.64291
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-34 | 50-CG-38452-09C02-P CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 21285 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.525 | CML-34 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.7 | 7.2 | 7.5 | 7.7 | 0.23629
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43119-01C02 | CML-5 | 80-FH-43119-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12832 |  | 2014-01-18 10:00 | 2014-01-18 11:30 | [36 empty] | 5.725 | CML-5 | CML: Pipe Length | 3 | 2048-04-05 | 2043-10-25 | 2014-01-18 10:00 | 0.54 | 0.14195 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 12 O'Clock | 80 | 5.49 | 80-FH-43119-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.4 | 5.9 | 5.7 | 5.9 | 0.23629
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40500-1CG | CML-16 | 400-WC-40500-1CG CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 5684 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [35 empty] | Low alarm breach | 18.875 | CML-16 | CML: Pipe Length | 3 | 2019-03-24 | 2016-10-12 | 2014-06-21 14:00 | 2.5 | 3.2564 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 18 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.5 |  | 19.4 | 19.4 | 18.7 | 18 | 0.6702
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-18 | 400-FH-43508-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6567 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.225 | CML-18 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 8.9 | 6 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.2 | 9.4 | 8.9 | 9.4 | 0.23629
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-22 | 150-FL-43174-01C02 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6274 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.825 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 3 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4 | 3.5 | 3.8 | 4 | 0.23629
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-15 | 250-PG-23003-06C02-PA CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 7694 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-13 13:50 | [32 empty] | 4.775 | CML-15 | CML: Elbow | 3 | 2018-08-10 | 2019-03-02 | 2015-01-08 13:00 | 2.5 | 0.58495 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0.34967 | 4.6 | 5.1 | 4.6 | 4.8 | 0.23629
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43074-01C02 | CML-2 | 50-FL-43074-01C02 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 1787 | Rope access | 2014-04-28 09:30 | 2014-04-28 10:30 | [36 empty] | 5.025 | CML-2 | CML: Elbow | 3 | 2016-09-12 | 2017-01-19 | 2014-04-28 09:30 | 2.5 | 0.92518 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-FL-43074-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 5 | 5.2 | 4.7 | 0.23629
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-12 | 100-DH-56561-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 7944 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 5.125 | CML-12 | CML: Elbow | 3 | 2018-02-13 | 2018-04-11 | 2015-01-17 13:00 | 2.5 | 0.74772 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 9 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 5.3 | 5.1 | 4.8 | 0.23629
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-4 | 50-PW-44015-01X01 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10287 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 7.7667 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2013-11-10 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8.3 | 7.8 |  | 7.2 | 0.55076
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-10 | 50-FH-43450-01C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10677 | Deck Level. High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.958 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 16:56 | [32 empty] | 5.175 | CML-10 | CML: Elbow | 3 | 2016-01-08 | 2016-04-19 | 2013-11-17 | 2.5 | 1.1663 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5 | 5.5 | 0.23629
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-17 | 25-FG-45455-01C02-E CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12636 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.325 | CML-17 | CML: type TBC | 3 | 2017-01-21 | 2017-06-13 | 2014-01-23 10:00 | 2.5 | 0.8337 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.3 | 5 | 5.5 | 0.23629
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56141-01C02 | CML-3 | 50-DH-56141-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21070 | Rope Access | 2014-05-15 08:00 | 2014-05-15 09:00 | [36 empty] | 5.175 | CML-3 | CML: type TBC | 3 |  |  | 2014-05-15 08:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5 | 6 O'Clock | 80 |  | 80-DH-56141-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5 | 5 | 5.2 | 0.23629
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-11 | 50-FG-45501-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6594 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.275 | CML-11 | CML: Pipe Length | 3 | 2026-01-14 | 2027-05-24 | 2015-03-30 07:00 | 2.5 | 0.24067 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.1 | 5.3 | 5.6 | 0.23629
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-1 | 200-PW-44021-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7698 | Re-check. Line is FFS. CR reported in 2013 was 2.14. It appears that it was an error. Point need to be rechecked | 2015-01-08 15:30 | 2015-01-08 16:30 |  |  | Administrator | 2015-09-04 14:23 | [32 empty] | 7.625 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-08 15:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 12 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 | -1.5472 | 7.2 | 8 | 7.8 | 7.5 | 0.35
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-4 | 50-FG-45021-03C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10532 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.375 | CML-4 | CML: type TBC | 3 | 2017-07-12 | 2017-07-02 | 2013-11-16 | 2.5 | 0.73869 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.7 | 5.2 | 0.23629
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-4 | 25-VA-23054-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1473 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 5.375 | CML-4 | CML: type TBC | 3 | 2021-07-21 | 2022-06-05 | 2014-04-29 10:00 | 2.5 | 0.37333 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.7 | 5.2 | 0.23629
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40009-01C02 | CML-4 | 200-WC-40009-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3123 | Rope Access | 2014-05-04 07:00 | 2014-05-04 08:00 | [36 empty] | 7.8 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-05-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 12 O'Clock | 200 | 6.35 | 200-WC-40009-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 8.1 | 7.8 | 7.9 | 0.29439
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-16 | 50-FG-45302-01C02 CML-16 | Yes | FPSO 2014 | Pipe Wall Thickness | 5784 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 5.825 | CML-16 | CML: Pipe Length | 3 | 2094-01-13 | 2102-09-10 | 2014-06-23 11:00 | 2.5 | 0.03768 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 25 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6 | 5.8 | 6 | 0.23629
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-3 | 50-FH-43137-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12855 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 5.675 | CML-3 | CML: Pipe Length | 3 | 2062-08-04 | 2067-11-13 | 2014-01-23 08:00 | 2.5 | 0.06178 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 6 | 5.5 | 5.5 | 0.23629
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40001-01C02 | CML-4 | 150-WC-40001-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20333 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.675 | CML-4 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.4 | 3 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.5 | 7.4 | 8 | 7.8 | 0.27538
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-14 | 50-FG-45301-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 5800 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.475 | CML-14 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.3 | 6.5 | 6.8 | 0.23629
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-35 | 50-FG-45023-01C02 CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 1183 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.625 | CML-35 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.6 | 6.3 | 6.8 | 6.8 | 0.23629
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-12 | 50-FG-45024-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1216 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.675 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.5 | 7 | 6.5 | 0.23629
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-5 | 200-FH-43003-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12528 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.375 | CML-5 | CML: Pipe Length | 3 | 2034-08-01 | 2032-01-05 | 2014-01-18 11:30 | 1.34 | 0.23652 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.2 | 9 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 6.7 | 6.2 | 6.4 | 6.2 | 0.23629
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43074-01C02 | CML-7 | 50-FL-43074-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1792 | Rope access | 2014-04-28 09:30 | 2014-04-28 10:30 | [36 empty] | 5.075 | CML-7 | CML: Elbow | 3 | 2017-09-22 | 2018-03-10 | 2014-04-28 09:30 | 2.5 | 0.7049 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FL-43074-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 4.9 | 5.1 | 0.23629
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-14 | 200-PW-44018-01X01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12575 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.675 | CML-14 | CML: Elbow | 3 | 2029-11-29 | 2027-10-22 | 2014-01-18 07:00 | 0.54 | 0.29984 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.9 | 5.6 | 5.3 | 5.9 | 0.28723
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-9 | 150-WC-40004-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1811 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 7.65 | CML-9 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-04-29 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.4 | 3 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.6 | 7.4 | 8 | 7.6 | 0.25166
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-7 | 80-PW-44001-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21998 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.875 | CML-7 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 3 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.4 | 6.8 | 8.3 | 9 | 0.97082
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5579 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 7.975 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.8 | 8.1 | 7.3 | 8.7 | 0.58523
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-12 | 250-PL-20006-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 13182 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 9.825 | CML-12 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A3: Inside Quadrant |  | 3.35 | 3.61 | 3.0831 | 9.5 | 6 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.89 |  | 10.1 | 9.8 | 9.5 | 9.9 | 0.25
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-21 | 350-FL-43511-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 2302 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 8.075 | CML-21 | CML: type TBC | 3 | 2228-02-04 | 2199-10-09 | 2014-03-17 08:00 | 2.5 | 0.02523 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.1 | 8.4 | 7.9 | 7.9 | 0.23629
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43300-01C02-E | CML-7 | 200-PL-43300-01C02-E CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 8593 | Line is FFS. Current RBI frequency is 36m. Action: CML’s to Inspect in 48m. RBI to be updated | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-08 14:58 | [32 empty] | 6.85 | CML-7 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2015-02-08 11:00 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.4 | 12 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.06 |  | 6.4 | 6.5 | 7.4 | 7.1 | 0.47958
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-18 | 50-PL-23042-09C03 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10083 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.575 | CML-18 | CML: type TBC | 6 | 2018-12-25 | 2018-02-23 | 2013-11-07 | 2.5 | 1.538 | A1: Outside Quadrant |  | 5.07 | 2.5 | 3.785 | 10.4 | 6 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 10.9 | 10.4 | 10.6 | 0.23629
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-3 | 200-PG-23051-09C02-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13108 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.85 | CML-3 | CML: type TBC | 3 | 2103-01-05 | 2073-03-18 | 2014-02-07 11:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 18.7 | 12 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 18.7 | 20.4 | 20.1 | 20.2 | 0.77675
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-19 | 300-PG-23001-03C03 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 10969 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.475 | CML-19 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 14.3 | 9 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.08 |  | 14.3 | 14.5 | 14.8 | 14.3 | 0.23629
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-6 | 150-PG-20009-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2700 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 12.575 | CML-6 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-12 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 12.4 | 3 O'Clock | 100 | 8.56 | 100-PG-20009-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 12.4 | 12.4 | 12.6 | 12.9 | 0.23629
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-6 | 25-VA-23054-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 671 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 12.575 | CML-6 | CML: Pipe Length | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 09:00 | 2.03 | 0 | A1: Outside Quadrant |  | 1.11 | 2.03 | 1.57 | 12.4 | 3 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.37 | 0 | 12.4 | 12.4 | 12.6 | 12.9 | 0.23629
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-6 | 25-VA-23054-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 389 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 12.575 | CML-6 | CML: Pipe Length | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 | 2.03 | 0 | A1: Outside Quadrant |  | 1.11 | 2.03 | 1.57 | 12.4 | 3 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.37 |  | 12.4 | 12.4 | 12.6 | 12.9 | 0.23629
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38009-01C02 | CML-3 | 50-CG-38009-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7861 |  | 2015-01-14 08:00 | 2015-01-14 09:00 | [36 empty] | 5.2 | CML-3 | CML: Pipe Length | 3 | 2022-07-18 | 2023-07-11 | 2015-01-14 08:00 | 2.5 | 0.33275 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 15 | 5.54 | 50-CG-38009-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5 | 5.4 | 5 | 0.23094
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-15 | 80-FH-43158-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12896 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.5 | CML-15 | CML: type TBC | 3 | 2023-07-24 | 2024-09-27 | 2014-01-22 11:00 | 2.5 | 0.29453 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.7 | 5.3 | 5.3 | 0.23094
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40047-01C02 | CML-2 | 50-WC-40047-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1702 | Rope Access | 2014-04-13 10:15 | 2014-04-13 11:15 | [36 empty] | 7.7 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 10:15 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 6 O'Clock | 50 | 5.54 | 50-WC-40047-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.9 | 7.6 | 7.4 | 7.9 | 0.24495
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-12 | 50-DH-56062-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 9099 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 7.8 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.6 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8 | 8 | 7.6 | 7.6 | 0.23094
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-1 | 50-FG-45021-03C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10529 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 8.8 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2013-11-16 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 8.6 | 6 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9 | 8.6 | 9 | 0.23094
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40069-01C02 | CML-2 | 100-WC-40069-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1711 | Rope access | 2014-04-21 07:00 | 2014-04-21 08:00 | [36 empty] | 7.675 | CML-2 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.4 | 6 O'Clock | 100 | 6.02 | 100-WC-40069-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.7 | 7.9 | 7.4 | 7.7 | 0.20616
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38492-01C02 | CML-1 | 50-CG-38492-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2535 |  | 2014-04-03 08:00 | 2014-04-03 09:00 | [36 empty] | 9.8333 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-03 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38492-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  |  | 9.7 | 10.1 | 9.7 | 0.23094
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-23 | 50-DH-56137-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21107 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 9.9 | CML-23 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 9.7 | 6 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 10.1 | 9.7 | 10.1 | 0.23094
PL03 | Montara_Topside | Yes | Flare (43) | Pipework | 50-PL-57066-01C03 | CML-2 | 50-PL-57066-01C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12642 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 8.6667 | CML-2 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 8.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.37 |  | 8.8 | 8.8 | 8.4 |  | 0.23094
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-6 | 50-PG-23063-09C02 CML-6 | Yes | FPSO 2013 | Pipe Wall Thickness | 10732 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 12.5333 | CML-6 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2013-11-19 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 12.4 | 6 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  |  | 12.4 | 12.4 | 12.8 | 0.23094
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-4 | 400-WC-40060-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1052 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | Check Corrosion Rate of 0.399mm/ yr | [35 empty] | 8.175 | CML-4 | CML: type TBC | 3 | 2026-09-25 | 2025-01-25 | 2014-03-20 14:00 | 2.6 | 0.3992 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 7.6 | 3 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.7 | 7.6 | 8.7 | 8.7 | 0.60759
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56121-01C02 | CML-4 | 50-DH-56121-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21042 | Rope Access | 2014-05-19 07:00 | 2014-05-19 08:00 | [36 empty] | 5.4 | CML-4 | CML: type TBC | 3 | 2022-01-14 | 2022-12-18 | 2014-05-19 07:00 | 2.5 | 0.35226 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-DH-56121-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.6 | 5.6 | 0.23094
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43124-01C02 | CML-4 | 80-FH-43124-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12846 |  | 2014-02-05 11:00 | 2014-02-05 13:00 | [36 empty] | 5.6 | CML-4 | CML: Elbow | 3 | 2050-12-24 | 2046-03-08 | 2014-02-05 11:00 | 0.54 | 0.13169 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43124-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.8 | 5.4 | 5.4 | 5.8 | 0.23094
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-20 | 80-FH-43009-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 12598 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.6 | CML-20 | CML: Pipe Length | 3 | 2050-12-17 | 2046-03-02 | 2014-02-05 08:00 | 0.54 | 0.13175 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.4 | 5.8 | 5.4 | 5.8 | 0.23094
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-3 | 50-CG-38466-01C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 2517 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.3333 | CML-3 | CML: type TBC | 3 | 2020-11-22 | 2021-09-12 | 2014-04-02 13:00 | 2.5 | 0.40616 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 5.2 |  | 5.2 | 5.2 | 5.6 | 0.23094
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-26 | 250-PG-23004-06C03-A CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 23393 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 18.475 | CML-26 | CML: Elbow | 6 | 2359-02-25 | 2293-02-06 | 2015-07-21 07:00 | 8.55 | 0.02807 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.2 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.65 | 0 | 18.2 | 18.4 | 18.6 | 18.7 | 0.22174
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-13 | 80-PW-44001-01C02-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23222 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 7.8 | CML-13 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 | 4.5407 | 6.8 | 8.5 | 7.9 | 8 | 0.71647
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-15 | 50-PF-20301-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 3013 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.675 | CML-15 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 9.4 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.79 | 0 | 9.9 | 9.6 | 9.8 | 9.4 | 0.22174
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-15 | 50-PF-20301-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 22292 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.675 | CML-15 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 9.4 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.79 |  | 9.9 | 9.6 | 9.8 | 9.4 | 0.22174
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-10 | 25-VA-23054-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1479 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 8.675 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-29 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 6 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.8 | 8.6 | 8.4 | 8.9 | 0.22174
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-22 | 250-PW-20040-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21406 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.175 | CML-22 | CML: Reducer | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A1: Outside Quadrant |  | 6.7 | 4.1 | 5.4 | 12.9 | 12 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 12.9 | 13 | 13.3 | 13.5 | 0.27538
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-13 | 250-PW-20041-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21422 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.975 | CML-13 | CML: Elbow | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 13 | 3 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 13.7 | 13 | 14.2 | 15 | 0.84212
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-17 | 150-WC-40004-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1819 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 8.35 | CML-17 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-29 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 3 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.5 | 7.5 | 8.5 | 8.9 | 0.59722
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45022-01C02 | CML-1 | 100-FG-45022-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22051 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 10.275 | CML-1 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10 | 6 O'Clock | 100 | 6.02 | 100-FG-45022-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.5 | 10.4 | 10 | 10.2 | 0.22174
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-14 | 50-PL-23300-09C03 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 13130 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.675 | CML-14 | CML: type TBC | 6 | 2021-10-18 | 2020-08-25 | 2014-02-04 07:00 | 2.81 | 0.98493 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.4 | 6 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.59 |  | 10.9 | 10.8 | 10.4 | 10.6 | 0.22174
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-13 | 250-PG-23003-06C02-PA CML-13 | Yes | FPSO 2014 | Pipe Wall Thickness | 24251 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.725 | CML-13 | CML: Pipe Length | 3 | 2085-04-24 | 2073-10-17 | 2014-09-24 07:00 | 7.9 | 0 | A2: Right Quadrant |  | 12.09 | 7.9 | 9.0519 | 15.5 | 3 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 15.8 | 15.5 | 16 | 15.6 | 0.22174
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-11 | 50-PL-23042-09C03 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10076 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.675 | CML-11 | CML: type TBC | 6 | 2018-12-25 | 2018-02-23 | 2013-11-07 | 2.5 | 1.538 | A1: Outside Quadrant |  | 5.07 | 2.5 | 3.785 | 10.4 | 12 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 10.8 | 10.9 | 10.6 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40009-01C02 | CML-2 | 200-WC-40009-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3121 | Rope Access | 2014-05-04 07:00 | 2014-05-04 08:00 | [36 empty] | 7.975 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-05-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 6 O'Clock | 200 | 6.35 | 200-WC-40009-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.6 | 7.7 | 7.5 | 8.1 | 0.48563
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-13 | 200-PL-20020-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21317 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 8.95 | CML-13 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.4 | 6 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9 | 9.2 | 8.4 | 9.2 | 0.37859
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56057-01C02 | CML-4 | 50-DH-56057-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3172 | Rope Access | 2014-05-07 08:00 | 2014-05-07 09:00 | [36 empty] | 5.125 | CML-4 | CML: type TBC | 3 | 2017-03-30 | 2017-08-27 | 2014-05-07 08:00 | 2.5 | 0.79363 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56057-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 5.2 | 4.8 | 5.2 | 0.22174
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-4 | 50-DH-56056-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20124 | Rope Access | 2014-05-07 08:00 | 2014-05-07 09:00 | [36 empty] | 5.125 | CML-4 | CML: type TBC | 3 | 2017-03-30 | 2017-08-27 | 2014-05-07 08:00 | 2.5 | 0.79363 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 5.2 | 4.8 | 5.2 | 0.22174
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-14 | 50-FG-45020-03C02 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10586 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.125 | CML-14 | CML: type TBC | 3 | 2015-04-26 | 2015-04-21 | 2013-11-17 | 2.5 | 1.5982 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5.2 | 5.3 | 4.8 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40005-01C02 | CML-2 | 150-WC-40005-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3155 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 7.95 | CML-2 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-05-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 9 O'Clock | 150 | 7.11 | 150-WC-40005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.8 | 7.9 | 8.6 | 7.5 | 0.46547
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-8 | 80-PW-44001-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21999 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.55 | CML-8 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.4 | 8.5 | 7.5 | 0.70475
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38302-01C02-P |  | 50-CG-38302-01C02-P | yes | FPSO 2014 | Pipe Wall Thickness | 22099 | Rope access | 2014-06-02 09:30 | 2014-06-02 11:00 | [36 empty] | 5.325 | 50-CG-38302-01C02-P | Piping | 3 | 2019-01-23 |  | 2014-06-02 09:30 |  | 0.53794 | A4: Left Quadrant |  |  | 2.5 |  | 5 | 9 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 5 | 5.4 | 5.5 | 5.4 | 5 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40044-01C02 | CML-3 | 300-WC-40044-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1118 |  | 2014-03-21 11:30 | 2014-03-21 12:00 | [36 empty] | 8 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-21 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 12 O'Clock | 300 | 6.35 | 300-WC-40044-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8.1 | 8.1 | 8.3 | 0.34641
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20014-01C02-P | CML-2 | 200-PL-20014-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21221 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.725 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.4 | 3 O'Clock | 200 | 6.35 | 200-PL-20014-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.2 | 8.4 | 8.7 | 8.6 | 0.34034
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21888 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 7.975 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.8 | 8.1 | 7.3 | 8.7 | 0.58523
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38460-01C02-P | CML-6 | 80-CG-38460-01C02-P CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 20887 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.575 | CML-6 | CML: Fitting | 3 | 2058-01-04 | 2063-03-16 | 2014-10-04 07:00 | 2.5 | 0.067 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 50 | 5.49 | 80-CG-38460-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.9 | 5.4 | 5.5 | 0.22174
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38007-01C02 | CML-2 | 50-CG-38007-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3109 | Rope Access | 2014-05-04 09:30 | 2014-05-04 10:00 | [36 empty] | 5.825 | CML-2 | CML: Elbow | 3 | 2083-08-15 | 2091-02-25 | 2014-05-04 09:30 | 2.5 | 0.04327 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 15 | 5.54 | 50-CG-38007-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 6 | 5.5 | 5.9 | 0.22174
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-4 | 80-DH-56074-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20949 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 5.925 | CML-4 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6 | 6 | 6.1 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43105-01C02 | CML-2 | 100-FH-43105-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12765 |  | 2014-01-25 09:00 | 2014-01-25 10:00 | [36 empty] | 6.125 | CML-2 | CML: type TBC | 3 | 2023-11-10 | 2024-03-14 | 2014-01-25 09:00 | 2.5 | 0.33686 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-FH-43105-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 6.3 | 6.2 | 5.8 | 0.22174
FG02 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 25-FG-45455-01C02-E | CML-7 | 25-FG-45455-01C02-E CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8478 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.325 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-GN-67007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6 | 6.4 | 6.4 | 0.22174
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-17 | 25-FG-45455-01C02-E CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 23817 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.325 | CML-17 | CML: Fitting | 3 | 2027-11-29 | 2027-10-21 | 2014-09-25 07:00 | 2.5 | 0.26543 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6.4 | 6.4 | 6 | 0.22174
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-32 | 200-PL-20008-01C02-H CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 8829 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 8.6 | CML-32 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 12 O'Clock | 300 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 8.4 | 10.1 | 8.3 | 1.0614
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-6 | 50-PL-24003-09C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13145 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.6 | CML-6 | CML: type TBC | 3 | 2025-01-18 | 2022-01-11 | 2014-01-18 13:00 | 2.5 | 0.53597 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.7 | 8.9 | 8.4 | 8.4 | 0.24495
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-5 | 50-PL-23040-03C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10190 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 7.925 | CML-5 | CML: type TBC | 6 | 2015-10-24 | 2015-10-07 | 2013-11-08 | 2.5 | 2.6006 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.6 | 3 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.1 | 7.6 | 8 | 8 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-4 | 150-FH-43518-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2704 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.325 | CML-4 | CML: Pipe Length | 3 | 2055-01-13 | 2047-12-27 | 2014-03-12 09:00 | 1.23 | 0.14119 | A2: Right Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 3 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 | 0 | 7.5 | 7 | 7.4 | 7.4 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-4 | 150-FH-43518-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 343 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.325 | CML-4 | CML: Pipe Length | 3 | 2054-12-24 | 2047-12-10 | 2014-03-12 | 1.23 | 0.14137 | A2: Right Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 3 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 |  | 7.5 | 7 | 7.4 | 7.4 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40005-01C02 | CML-1 | 150-WC-40005-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3154 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 7.725 | CML-1 | CML: Fitting | 3 | 2059-07-07 | 2055-11-27 | 2014-05-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 9 O'Clock | 150 | 7.11 | 150-WC-40005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.7 | 7.5 | 8.2 | 7.5 | 0.3304
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-5 | 50-PL-45016-03C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10445 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.225 | CML-5 | CML: type TBC | 6 | 2017-08-01 | 2017-02-10 | 2013-11-13 | 0.99 | 1.8582 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 7.9 | 3 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.91 |  | 8.3 | 7.9 | 8.4 | 8.3 | 0.22174
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-8 | 100-PG-23071-01C03 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2406 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 10.325 | CML-8 | CML: type TBC | 6 | 2020-05-20 | 2019-05-15 | 2014-03-19 13:00 | 2.5 | 1.2144 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10 | 12 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 10.5 | 10.4 | 10.4 | 0.22174
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80005-01C02 | CML-6 | 50-VA-80005-01C02 CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 3132 | Rope Access | 2014-05-02 10:30 | 2014-05-02 11:30 | [36 empty] | 4.875 | CML-6 | CML: type TBC | 3 | 2016-05-20 | 2016-09-14 | 2014-05-02 10:30 | 2.5 | 1.0228 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-VA-80005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5 | 4.8 | 5.1 | 0.22174
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56045-01C02 | CML-1 | 80-DH-56045-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20933 | Rope Access | 2014-05-16 11:00 | 2014-05-16 12:00 | [36 empty] | 5.075 | CML-1 | CML: type TBC | 3 | 2017-07-24 | 2018-01-16 | 2014-05-16 11:00 | 2.5 | 0.72069 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 3 O'Clock | 80 | 5.49 | 80-DH-56045-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 4.8 | 5 | 5.3 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-16 | 100-WC-40035-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1749 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.775 | CML-16 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.5 | 9 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.9 | 8.1 | 7.6 | 7.5 | 0.27538
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56005-01C02 | CML-1 | 80-DH-56005-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3443 | Rope Access | 2014-05-12 09:30 | 2014-05-12 10:30 | [36 empty] | 5.125 | CML-1 | CML: type TBC | 3 | 2018-03-17 | 2018-10-07 | 2014-05-12 09:30 | 2.5 | 0.62349 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-DH-56005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.2 | 4.9 | 5.4 | 0.22174
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-49 | 50-DH-56070-01C02 CML-49 |  | FPSO 2014 | Pipe Wall Thickness | 3265 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.125 | CML-49 | CML: type TBC | 3 | 2017-11-12 | 2018-05-06 | 2014-05-09 07:00 | 2.5 | 0.68246 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.2 | 4.9 | 5.4 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-6 | 50-FH-43450-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10673 | Deck Level.High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.149 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 16:19 | [32 empty] | 5.125 | CML-6 | CML: Pipe Length | 3 | 2015-08-12 | 2015-11-06 | 2013-11-17 | 2.5 | 1.3822 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 5 | 4.9 | 5.2 | 0.22174
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38300-01C02-P |  | 50-CG-38300-01C02-P | yes | FPSO 2014 | Pipe Wall Thickness | 22098 | Rope access | 2014-06-02 08:00 | 2014-06-02 09:00 |  |  | Administrator | 2015-09-07 10:56 | [32 empty] | 5.275 | 50-CG-38300-01C02-P | Piping | 3 | 2019-01-23 |  | 2014-06-02 08:00 |  | 0.53803 | A1: Outside Quadrant |  |  | 2.5 |  | 5 | 12 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 5 | 5 | 5.2 | 5.4 | 5.5 | 0.22174
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3352 | Rope Access | 2014-05-08 14:00 | 2014-05-08 14:30 | [36 empty] | 5.375 | CML-2 | CML: type TBC | 3 | 2019-11-17 | 2020-07-27 | 2014-05-08 14:00 | 2.5 | 0.47016 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DH-56068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.1 | 5.5 | 5.6 | 0.22174
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56120-01C02 | CML-5 | 50-DH-56120-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21037 | Rope Access | 2014-05-19 08:00 | 2014-05-19 09:00 | [36 empty] | 5.425 | CML-5 | CML: type TBC | 3 | 2022-01-15 | 2022-12-19 | 2014-05-19 08:00 | 2.5 | 0.35222 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DH-56120-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.7 | 5.2 | 5.3 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43021-01C02 | CML-3 | 80-FH-43021-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12619 |  | 2014-01-27 07:00 | 2014-01-27 08:00 | [36 empty] | 5.575 | CML-3 | CML: type TBC | 3 | 2023-10-08 | 2024-12-21 | 2014-01-27 07:00 | 2.5 | 0.28861 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-FH-43021-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.8 | 5.3 | 5.7 | 0.22174
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-11 | 250-PG-23003-06C02-PA CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 3434 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.625 | CML-11 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.4 | 9 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.9 | 5.5 | 5.4 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40405-01C02 | CML-3 | 150-WC-40405-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20397 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 7.8 | CML-3 | CML: Equal Tee | 3 | 2059-07-07 | 2055-11-27 | 2014-10-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 12 O'Clock | 150 | 7.11 | 150-WC-40405-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.7 | 8 | 8 | 0.24495
FG02 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8474 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.225 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-GN-67007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.3 | 6.5 | 0.22174
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22054 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 6.225 | CML-2 | CML: Fitting | 3 | 2257-05-20 | 2265-06-10 | 2014-10-20 07:00 | 2.5 | 0.01442 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 12 O'Clock | 100 | 6.02 | 100-FG-45041-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.3 | 6.5 | 0.22174
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-18 | 25-FG-45455-01C02-E CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 23818 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.275 | CML-18 | CML: Fitting | 3 | 2027-11-29 | 2027-10-21 | 2014-09-25 07:00 | 2.5 | 0.26543 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6.4 | 6.2 | 6 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-6 | 50-FH-43011-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7956 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.225 | CML-6 | CML: Elbow | 3 | 2018-01-09 | 2017-06-01 | 2015-01-18 08:00 | 2.5 | 1.1752 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 6 | 12 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.5 | 6.3 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-5 | 200-FH-43004-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12545 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 6.575 | CML-5 | CML: type TBC | 3 | 2065-02-15 | 2064-09-30 | 2014-02-01 07:00 | 2.5 | 0.0744 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.5 | 6.8 | 6.3 | 0.22174
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-1 | 80-PW-44001-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21992 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.45 | CML-1 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 3 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.4 | 6.8 | 7.2 | 8.4 | 0.68069
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-8 | 150-FH-43027-01C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10570 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 6.775 | CML-8 | CML: type TBC | 3 | 2016-11-21 | 2016-08-14 | 2013-11-16 | 2.5 | 1.3253 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.5 | 6 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 6.9 | 6.5 | 6.7 | 0.22174
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-14 | 50-PL-24003-09C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 13153 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.6 | CML-14 | CML: type TBC | 3 | 2025-01-18 | 2022-01-11 | 2014-01-18 13:00 | 2.5 | 0.53597 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.7 | 8.7 | 8.6 | 8.4 | 0.14142
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43176-01C02 | CML-5 | 300-FL-43176-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20435 | Protective mesh removed/Rope access | 2014-06-27 10:30 | 2014-06-27 12:00 | [36 empty] | 7.575 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-27 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 3 O'Clock | 300 | 6.35 | 300-FL-43176-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.8 | 7.3 | 7.5 | 7.7 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43108-01C02 | CML-6 | 200-FH-43108-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12781 |  | 2014-01-18 15:30 | 2014-01-18 16:30 | [36 empty] | 6.425 | CML-6 | CML: Pipe Length | 3 | 2034-08-06 | 2032-01-10 | 2014-01-18 15:30 | 1.34 | 0.23635 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-FH-43108-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 6.7 | 6.3 | 6.2 | 6.5 | 0.22174
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-5 | 50-CG-38457-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23723 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 7.625 | CML-5 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 6 O'Clock | 100 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.7 | 7.9 | 7.4 | 7.5 | 0.22174
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-49 | 350-FL-43512-01C02 CML-49 |  | FPSO 2015 | Pipe Wall Thickness | 23560 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.725 | CML-49 | CML: Pipe Length | 3 | 2041-09-09 | 2037-12-17 | 2015-08-10 07:30 | 2.5 | 0.19155 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.5 | 3 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.6 | 7.5 | 7.8 | 8 | 0.22174
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-14 | 50-FL-43454-01C02-P CML-14 | Yes | FPSO 2014 | Pipe Wall Thickness | 20517 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 7.775 | CML-14 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 9 O'Clock | 25 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8 | 7.7 | 7.9 | 7.5 | 0.22174
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PL-20029-01C02-P | CML-1 | 150-PL-20029-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21331 | Protective mesh removed | 2014-06-26 07:00 | 2014-06-26 08:00 | [36 empty] | 7.6 | CML-1 | CML: Elbow | 3 | 2035-01-10 | 2030-12-03 | 2014-06-26 07:00 | 0.84 | 0.28991 | A1: Outside Quadrant |  | 4.11 | 0.84 | 2.0306 | 6.8 | 12 O'Clock | 150 | 7.11 | 150-PL-20029-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.96 |  | 6.8 | 7.5 | 8.2 | 7.9 | 0.60553
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-11 | 50-CG-24002-09C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2557 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 9.225 | CML-11 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.9 | 3 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.4 | 8.9 | 9.3 | 9.3 | 0.22174
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23070-01C03-P | CML-4 | 300-PG-23070-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20601 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 9.975 | CML-4 | CML: Fitting | 6 | 2030-12-30 | 2028-12-16 | 2014-07-25 07:30 | 2.5 | 0.44394 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.8 | 3 O'Clock | 300 | 10.31 | 300-PG-23070-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.3 | 9.8 | 9.9 | 9.9 | 0.22174
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-14 | 300-PF-20003-03C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21752 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 13.725 | CML-14 | CML: Fitting | 6 | 2027-10-14 | 2025-03-14 | 2014-10-01 07:00 | 4.9 | 0.65166 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 6 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 13.8 | 13.9 | 13.4 | 13.8 | 0.22174
FL01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FL-43174-01C02 | CML-14 | 150-FL-43174-01C02 CML-14 | yes | FPSO 2015 | Pipe Wall Thickness | 7886 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:44 | [32 empty] | 3.725 | CML-14 | CML: Pipe Length | 3 | 2015-09-20 | 2015-12-19 | 2015-01-14 10:30 | 2.5 | 1.3184 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.8 | 3.4 | 3.8 | 3.9 | 0.22174
FL01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FL-43174-01C02 | CML-8 | 150-FL-43174-01C02 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 7880 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:42 | [32 empty] | 3.575 | CML-8 | CML: Pipe Length | 3 | 2015-09-20 | 2015-12-19 | 2015-01-14 10:30 | 2.5 | 1.3184 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.9 | 3.5 | 3.5 | 3.4 | 0.22174
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-6 | 50-FG-45019-03C02 CML-6 | yes | FPSO 2013 | Pipe Wall Thickness | 10488 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.675 | CML-6 | CML: type TBC | 3 | 2014-08-20 | 2014-08-17 | 2013-11-15 | 2.5 | 2.4916 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.4 | 3 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.8 | 4.4 | 4.9 | 4.6 | 0.22174
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45503-01C02 | CML-6 | 50-FG-45503-01C02 CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 7741 | Line is FFS despite the High CR on CML-1 to 6. Current RBI frequency is 48m. Action: Inspect in 24m. RBI to be updated. | 2015-01-10 08:00 | 2015-01-10 10:00 |  |  | Administrator | 2015-09-21 14:30 | [32 empty] | 5.175 | CML-6 | CML: Pipe Length | 3 | 2021-01-24 | 2021-11-20 | 2015-01-10 08:00 | 2.5 | 0.39705 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FG-45503-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 5.4 | 5.3 | 4.9 | 0.22174
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38463-01C02 | CML-1 | 50-CG-38463-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3112 | Rope Access | 2014-05-04 08:00 | 2014-05-04 09:00 | [36 empty] | 5.175 | CML-1 | CML: Elbow | 3 | 2017-10-20 | 2018-04-10 | 2014-05-04 08:00 | 2.5 | 0.69249 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-CG-38463-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5.1 | 5.3 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-11 | 50-FH-43137-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12863 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 5.175 | CML-11 | CML: Elbow | 3 | 2016-06-27 | 2016-10-26 | 2014-01-23 08:00 | 2.5 | 0.98843 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 5.4 | 5.1 | 0.22174
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-12 | 80-PW-44001-01C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23221 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 7.35 | CML-12 | CML: Reducing Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 | 2.9689 | 6.8 | 8.3 | 7.2 | 7.1 | 0.65574
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-14 | 50-FG-45501-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6597 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.325 | CML-14 | CML: Elbow | 3 | 2026-01-14 | 2027-05-24 | 2015-03-30 07:00 | 2.5 | 0.24067 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.2 | 5.4 | 5.6 | 0.22174
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-2 | 50-PG-23074-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20624 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.325 | CML-2 | CML: Elbow | 3 | 2021-05-13 | 2022-03-21 | 2014-07-26 07:00 | 2.5 | 0.38212 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.6 | 5.4 | 5.1 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-14 | 200-WC-40008-01C02-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7820 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 7.7 | CML-14 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 9 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.9 | 7.9 | 7.5 | 0.23094
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-12 | 150-WC-40002-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20351 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.725 | CML-12 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 3 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.9 | 7.5 | 7.6 | 7.9 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40009-01C02 | CML-6 | 200-WC-40009-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3125 | Rope Access | 2014-05-04 07:00 | 2014-05-04 08:00 | [36 empty] | 7.675 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-05-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 12 O'Clock | 200 | 6.35 | 200-WC-40009-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.6 | 7.8 | 7.8 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-10 | 150-WC-40004-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1812 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 8.125 | CML-10 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-29 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.6 | 12 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 8.8 | 8 | 8.1 | 0.49917
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-8 | 400-WC-40060-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1056 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 8.2 | CML-8 | CML: type TBC | 3 | 2032-10-14 | 2030-05-13 | 2014-03-20 14:00 | 2.6 | 0.27445 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 7.7 | 3 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.2 | 7.7 | 8.2 | 8.7 | 0.40825
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-17 | 200-WC-40008-01C02-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 7823 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 7.85 | CML-17 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 12 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 7.7 | 8.2 | 7.9 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43103-01C02 | CML-2 | 300-FH-43103-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20422 | Protective mesh removed | 2014-07-02 14:00 | 2014-07-02 15:00 | [36 empty] | 7.825 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-02 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 9 O'Clock | 300 | 6.35 | 300-FH-43103-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.9 | 8.1 | 7.7 | 7.6 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-WC-40068-01C02 | CML-4 | 80-WC-40068-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 928 |  | 2014-04-10 11:00 | 2014-04-10 12:00 | [36 empty] | 7.7 | CML-4 | CML: Pipe Length | 3 | 2043-04-25 | 2046-10-17 | 2014-04-10 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.6 | 9 O'Clock | 80 | 5.49 | 80-WC-40068-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.8 | 7.8 | 7.6 | 7.6 | 0.11547
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-3 | 200-PW-44018-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12581 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.675 | CML-3 | CML: Pipe Length | 3 | 2050-12-17 | 2046-03-02 | 2014-02-05 08:00 | 0.54 | 0.13175 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.7 | 6 | 5.6 | 5.4 | 0.25
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44037-01C03 | CML-5 | 300-PW-44037-01C03 CML-5 | Yes | FPSO 2015 | Pipe Wall Thickness | 22958 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.675 | CML-5 | CML: Elbow | 6 | 2031-12-15 | 2029-10-21 | 2015-05-04 07:00 | 2.5 | 0.42098 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 6 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 1.825 | 9.5 | 9.8 | 9.5 | 9.9 | 0.20616
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-12 | 250-PW-20041-03C03-P CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 21421 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 15.15 | CML-12 | CML: Pipe Length | 6 | 2039-07-23 | 2034-10-30 | 2014-07-12 07:30 | 3.3 | 0.35933 | A3: Inside Quadrant |  | 6.7 | 3.3 | 5 | 12.3 | 6 O'Clock | 200 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 12.8 | 17.6 | 12.3 | 17.9 | 3.0116
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-WC-40068-01C02 | CML-4 | 80-WC-40068-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1592 |  | 2014-04-10 11:00 | 2014-04-10 12:00 | [36 empty] | 7.7 | CML-4 | CML: Pipe Length | 3 | 2043-04-25 | 2046-10-17 | 2014-04-10 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.6 | 9 O'Clock | 80 | 5.49 | 80-WC-40068-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.8 | 7.8 | 7.6 | 7.6 | 0.11547
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-17 | 100-FG-45001-09C02 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10432 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 13.475 | CML-17 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2013-11-13 | 4.7 | 0 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 13.2 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 13.2 | 13.6 | 13.7 | 13.4 | 0.22174
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20509-03C03-P | CML-2 | 300-PF-20509-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6508 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 14.475 | CML-2 | CML: Fitting | 6 | 2166-09-21 | 2139-02-25 | 2014-07-24 07:30 | 4.9 | 0.06108 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 12 O'Clock | 300 | 14.27 | 300-PF-20509-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.2 | 14.7 | 14.4 | 14.6 | 0.22174
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-25 | 80-PW-44001-01C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 22016 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.525 | CML-25 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.4 | 8.2 | 7.7 | 0.58523
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-3 | 80-PW-44034-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21985 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.325 | CML-3 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 6 O'Clock | 20 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.3 | 7.8 | 6.8 | 7.4 | 0.4113
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56040-01C02 | CML-2 | 80-DH-56040-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20922 | Rope Access | 2014-05-21 07:00 | 2014-05-21 08:00 | [36 empty] | 4.975 | CML-2 | CML: Elbow | 3 | 2017-01-31 | 2017-07-07 | 2014-05-21 07:00 | 2.5 | 0.81388 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 12 O'Clock | 80 | 5.49 | 80-DH-56040-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.1 | 4.9 | 5.2 | 0.22174
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38007-01C02 | CML-1 | 50-CG-38007-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3108 | Rope Access | 2014-05-04 09:30 | 2014-05-04 10:00 | [36 empty] | 4.975 | CML-1 | CML: Elbow | 3 | 2016-10-04 | 2017-02-12 | 2014-05-04 09:30 | 2.5 | 0.90872 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 15 | 5.54 | 50-CG-38007-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 5.2 | 4.7 | 5.1 | 0.22174
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-12 | 80-SC-55002-01C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8842 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 10.55 | CML-12 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 9.3 | 9 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 10.9 | 11.2 | 10.8 | 9.3 | 0.85049
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-17 | 50-FG-45020-03C02 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10589 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.975 | CML-17 | CML: type TBC | 3 | 2015-02-02 | 2015-01-29 | 2013-11-17 | 2.5 | 1.8142 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 4.9 | 5.1 | 5.2 | 0.22174
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PL-57403-01C03 |  | 50-PL-57403-01C03 |  | FPSO 2015 | Pipe Wall Thickness | 8369 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 12.2 | 50-PL-57403-01C03 | Piping | 6 | 2075-10-24 |  | 2015-01-29 07:30 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 9.3 | 3 O'Clock | 50 | 8.74 | Pipework | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 12.2 | 9.3 | 13.1 | 14.2 | 2.0992
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-7 | 50-PG-23073-01C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20615 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 9.05 | CML-7 | CML: Elbow | 6 | 2029-09-25 | 2029-06-02 | 2014-07-26 07:00 | 2.5 | 0.38212 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 12 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.4 | 9.2 | 9.3 | 0.50662
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-9 | 50-PG-23073-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 22044 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.475 | CML-9 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-10-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.3 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.8 | 9.3 | 9.3 | 9.5 | 0.23629
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-8 | 50-PG-23073-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 22043 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.5 | CML-8 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-10-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.3 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.5 | 9.8 | 9.3 | 9.4 | 0.21602
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-7 | 50-PG-23073-01C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22042 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.45 | CML-7 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-10-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.3 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.4 | 9.4 | 9.3 | 9.7 | 0.17321
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21843 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 9.8 | CML-1 | CML: Elbow | 6 | 2024-02-11 | 2022-11-15 | 2014-10-19 07:00 | 2.5 | 0.72958 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.3 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.7 | 10.1 | 9.3 | 10.1 | 0.38297
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-2 | 50-PG-23073-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20767 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.7 | CML-2 | CML: Elbow | 6 | 2020-03-12 | 2019-03-17 | 2014-10-02 07:00 | 2.5 | 1.2483 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 9.3 | 3 O'Clock | 150 | 10.97 | 100-PG-23409-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.3 | 9.3 | 9.7 | 10.5 | 0.56569
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 23890 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 9.975 | CML-3 | CML: Elbow | 6 | 2023-08-17 | 2022-06-11 | 2014-09-26 07:00 | 2.5 | 0.76437 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.3 | 6 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 10.2 | 10.4 | 9.3 | 10 | 0.47871
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 23875 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.05 | CML-3 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 12 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.3 | 9.7 | 10.8 | 10.4 | 0.67577
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-4 | 50-PG-23073-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 23866 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.625 | CML-4 | CML: Elbow | 6 | 2020-02-11 | 2019-02-19 | 2014-09-26 07:00 | 2.5 | 1.2639 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 9.3 | 9 O'Clock | 150 | 10.97 | 150-PG-20031-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 11.1 | 11.8 | 10.3 | 9.3 | 1.0751
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-4 | 50-PG-23073-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 23856 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.75 | CML-4 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A1: Outside Quadrant |  |  | 2.7 |  | 9.5 | 12 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.5 | 11.1 | 11.3 | 11.1 | 0.83865
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20750 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 9.975 | CML-3 | CML: type TBC | 6 | 2023-08-17 | 2022-06-11 | 2014-09-26 07:00 | 2.5 | 0.76437 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.3 | 6 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 10.2 | 10.4 | 9.3 | 10 | 0.47871
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-6 | 50-PG-23073-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20614 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 9.325 | CML-6 | CML: Elbow | 6 | 2029-09-25 | 2029-06-02 | 2014-07-26 07:00 | 2.5 | 0.38212 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 10.2 | 9.4 | 9.4 | 8.3 | 0.78049
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20611 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 8.8 | CML-3 | CML: Elbow | 6 | 2034-07-14 | 2034-02-16 | 2014-07-26 07:00 | 2.5 | 0.29527 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 6 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.1 | 9 | 8.4 | 8.7 | 0.31623
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-PG-23073-01C03-P | CML-6 | 50-PG-23073-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12646 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 9.2333 | CML-6 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 8.8 | 12 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.77 |  | 8.8 | 9.4 | 9.5 |  | 0.37859
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20600 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 9.625 | CML-3 | CML: Elbow | 6 | 2022-04-17 | 2021-04-06 | 2014-07-25 07:30 | 2.5 | 0.87918 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.3 | 9 O'Clock | 300 | 10.31 | 300-PG-23070-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 10.3 | 9.5 | 9.4 | 9.3 | 0.45735
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-2 | 50-PG-23073-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20610 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 8.575 | CML-2 | CML: Elbow | 6 | 2034-07-14 | 2034-02-16 | 2014-07-26 07:00 | 2.5 | 0.29527 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.4 | 9.1 | 8.4 | 0.35
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-5 | 50-PG-23073-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20613 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 9.475 | CML-5 | CML: Elbow | 6 | 2043-05-02 | 2042-10-04 | 2014-07-26 07:00 | 2.5 | 0.20843 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10.5 | 9.5 | 9.4 | 8.5 | 0.81803
RP01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20821 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 10.075 | CML-3 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9.3 | 9 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 11 | 10.5 | 9.5 | 9.3 | 0.80984
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-7 | 50-PG-23073-01C03-P CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 3005 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.975 | CML-7 | CML: Elbow | 6 | 2036-08-26 | 2040-04-15 | 2014-05-01 07:00 | 3.61 | 0.19653 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 | 0 | 8.9 | 9.8 | 9.2 | 8 | 0.75
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-4 | 50-PG-23073-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21223 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 9.625 | CML-4 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 9 O'Clock | 200 | 6.35 | 200-PL-20014-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.7 | 9.4 | 10.1 | 9.3 | 0.3594
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21448 | Protective mesh removed | 2014-06-29 07:00 | 2014-06-29 08:00 | [36 empty] | 8.15 | CML-3 | CML: Elbow | 1 | 2077-07-06 | 2050-06-18 | 2014-06-29 07:00 | 0.7 | 0 | A3: Inside Quadrant |  | 6.11 | 0.7 | 3.405 | 7.5 | 6 O'Clock | 150 | 7.11 | 150-PG-20043-01D01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 7.8 | 9.2 | 7.5 | 8.1 | 0.74162
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5876 |  | 2014-06-25 13:00 | 2014-06-25 14:00 | [36 empty] | 11.1 | CML-1 | CML: Equal Tee | 6 | 2017-04-09 | 2016-07-28 | 2014-06-25 13:00 | 3.3 | 2.4362 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 10.1 | 9 O'Clock | 200 | 12.7 | 200-PG-20303-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 12 | 11.2 |  | 10.1 | 0.95394
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-10 | 50-PG-23073-01C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5842 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 9.675 | CML-10 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.3 | 12 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.3 | 9.9 | 9.9 | 9.6 | 0.28723
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-8 | 50-PG-23073-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5840 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 9.5 | CML-8 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.3 | 12 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.3 | 9.8 | 9.5 | 9.4 | 0.21602
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-4 | 50-PG-23073-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5836 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 9.625 | CML-4 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.3 | 9 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.3 | 9.8 | 10.1 | 9.3 | 0.39476
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-PG-23073-01C03-P | CML-8 | 50-PG-23073-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12648 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 9 | CML-8 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 8.9 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.87 |  | 9.1 | 8.9 | 9 |  | 0.1
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-PG-23073-01C03-P | CML-5 | 50-PG-23073-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3042 | Rope Access | 2014-05-03 09:30 | 2014-05-03 10:30 | [36 empty] | 5.075 | CML-5 | CML: type TBC | 3 | 2015-09-12 | 2015-10-10 | 2014-05-03 09:30 | 2.5 | 1.5407 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.6 | 9 O'Clock | 100 | 6.02 | 100-FH-43147-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.4 | 5 | 5.3 | 4.6 | 0.3594
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-9 | 50-PG-23073-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20617 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 8.975 | CML-9 | CML: Cap End | 6 | 2075-10-24 | 2074-08-12 | 2014-07-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 9 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9 | 9 | 9 | 8.9 | 0.05
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PG-23073-01C03-P | CML-15 | 50-PG-23073-01C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1656 | Rope Access | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.5333 | CML-15 | CML: Equal Tee | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.3 | 9 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.7 |  | 9.6 | 9.3 | 0.20817
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PG-23073-01C03-P | CML-5 | 50-PG-23073-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1646 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.9 | CML-5 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.3 | 3 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.6 | 9.3 | 10 | 10.7 | 0.60553
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PG-23073-01C03-P | CML-21 | 50-PG-23073-01C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 2084 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 9.775 | CML-21 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 10.2 | 10.3 | 9.3 | 9.3 | 0.55
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2046 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.325 | CML-3 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.3 | 12 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.3 | 10.4 | 11.1 | 10.5 | 0.75
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8031 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:30 | [32 empty] | 10.15 | CML-1 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-20 14:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.3 | 9 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 11.1 | 10.8 | 9.4 | 9.3 | 0.93274
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21120 | Reviewed on 20/11/14. FFS. Recheck in Oct. 18. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-20 16:37 | [32 empty] | 9.6 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-08 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56554-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.4 | 9.3 | 9.9 | 9.8 | 0.29439
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-PG-23073-01C03-P | CML-7 | 50-PG-23073-01C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20904 | Rope Access | 2014-05-22 07:00 | 2014-05-22 08:00 | [36 empty] | 9.975 | CML-7 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-22 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 9.3 | 6 O'Clock | 80 | 5.49 | 80-DH-56028-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 10.7 | 10.3 | 9.3 | 9.6 | 0.63966
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-PG-23073-01C03-P | CML-4 | 50-PG-23073-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3041 | Rope Access | 2014-05-03 09:30 | 2014-05-03 10:30 | [36 empty] | 5.35 | CML-4 | CML: type TBC | 3 | 2016-01-27 | 2016-02-28 | 2014-05-03 09:30 | 2.5 | 1.3237 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 6 O'Clock | 100 | 6.02 | 100-FH-43147-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.6 | 5.6 | 4.8 | 5.4 | 0.37859
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PG-23073-01C03-P | CML-22 | 50-PG-23073-01C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 1298 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 9.725 | CML-22 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 9 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.9 | 9.9 | 9.8 | 9.3 | 0.28723
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PG-23073-01C03-P | CML-12 | 50-PG-23073-01C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1081 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 9.475 | CML-12 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 9.4 | 6 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.5 | 9.5 | 9.4 | 9.5 | 0.05
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PG-23073-01C03-P | CML-22 | 50-PG-23073-01C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 2441 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | [36 empty] | 9.875 | CML-22 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.3 | 12 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.3 | 9.6 | 9.5 | 11.1 | 0.82614
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2409 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 10.35 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.3 | 3 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 11.3 | 9.3 | 10.7 | 10.1 | 0.8544
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2311 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | [36 empty] | 9.525 | CML-3 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 9.3 | 3 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.8 | 9.3 | 9.5 | 9.5 | 0.20616
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-PG-23073-01C03-P | CML-25 | 50-PG-23073-01C03-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 2306 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 9.75 | CML-25 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 9.3 | 6 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.9 | 9.8 | 9.3 | 10 | 0.31091
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2751 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 16.325 | CML-1 | CML: Pipe Length | 3 | 2019-12-21 | 2017-12-19 | 2014-03-13 09:00 | 9.4 | 1.1767 | A4: Left Quadrant |  | 14.12 | 9.4 | 11.76 | 16.2 | 9 O'Clock | 100 | 17.12 | 100-PG-23049-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 16.5 | 16.3 | 16.3 | 16.2 | 0.12583
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3040 | Rope Access | 2014-05-03 09:30 | 2014-05-03 10:30 | [36 empty] | 5.25 | CML-3 | CML: type TBC | 3 | 2016-01-27 | 2016-02-28 | 2014-05-03 09:30 | 2.5 | 1.3237 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 9 O'Clock | 100 | 6.02 | 100-FH-43147-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5.5 | 5.5 | 4.8 | 0.33166
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-PG-23073-01C03-P | CML-6 | 50-PG-23073-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3043 | Rope Access | 2014-05-03 09:30 | 2014-05-03 10:30 | [36 empty] | 5.4 | CML-6 | CML: type TBC | 3 | 2017-05-15 | 2017-07-01 | 2014-05-03 09:30 | 2.5 | 0.88973 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-FH-43147-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.5 | 5.5 | 0.14142
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-9 | 50-PG-23073-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 13179 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 9.7 | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-01-21 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.5 | 10.2 | 9.8 | 9.3 | 0.39158
RP01 | Montara_Topside | No | Gas Treatment (24) | Pipework | 50-PG-23073-01C03-P | CML-9 | 50-PG-23073-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 13148 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 9.7 | CML-9 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-01-18 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.3 | 6 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.6 | 10.4 | 9.3 | 9.5 | 0.48305
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-4 | 50-PG-23073-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10978 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 11.5 | CML-4 | CML: Elbow | 6 | 2016-10-11 | 2016-04-24 | 2014-01-09 | 4.4 | 2.4662 | A4: Left Quadrant |  | 6.7 | 4.4 | 5.55 | 11.2 | 9 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 12 | 11.3 | 11.5 | 11.2 | 0.3559
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10471 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 8.5 | CML-3 | CML: type TBC | 6 | 2017-02-28 | 2016-09-27 | 2013-11-14 | 0.99 | 2.0669 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.8 | 12 O'Clock | 50 | 8.74 | 50-PL-45031-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.81 |  | 7.8 | 8.6 | 8.7 | 8.9 | 0.48305
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PG-23073-01C03-P | CML-16 | 50-PG-23073-01C03-P CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10456 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.4 | CML-16 | CML: type TBC | 6 | 2017-02-20 | 2016-09-19 | 2013-11-13 | 0.99 | 2.0794 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 7.8 | 3 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.81 |  | 8.5 | 7.8 | 8.7 | 8.6 | 0.40825
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PG-23073-01C03-P | CML-4 | 50-PG-23073-01C03-P CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10444 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.775 | CML-4 | CML: type TBC | 6 | 2017-02-20 | 2016-09-19 | 2013-11-13 | 0.99 | 2.0794 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 7.8 | 3 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.81 |  | 8.9 | 7.8 | 9.6 | 8.8 | 0.74106
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10441 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 9.05 | CML-1 | CML: type TBC | 6 | 2017-02-20 | 2016-09-19 | 2013-11-13 | 0.99 | 2.0794 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.8 | 12 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.81 |  | 7.8 | 9.2 | 9.2 | 10 | 0.91469
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-31 | 50-PG-23073-01C03-P CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 2805 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 24.5 | CML-31 | CML: Elbow | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.7 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.82 |  | 22.7 | 24.4 | 27.6 | 23.3 | 2.1833
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-17 | 50-PG-23073-01C03-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2791 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 23.075 | CML-17 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.7 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.82 |  | 23.1 | 23.8 | 22.7 | 22.7 | 0.51881
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13091 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 23.1 | CML-1 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-01-10 09:00 | 15.88 | 0 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 22.7 | 6 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.82 |  | 23.1 | 22.7 | 22.7 | 23.9 | 0.56569
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-6 | 50-PG-23073-01C03-P CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10038 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 8.1 | CML-6 | CML: Pipe Length | 6 | 2016-12-28 | 2016-08-01 | 2013-11-06 | 0.97 | 2.1715 | A1: Outside Quadrant |  | 2.74 | 0.97 | 1.855 | 7.8 | 12 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.83 |  | 7.8 | 8.1 | 8.3 | 8.2 | 0.21602
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-14 | 50-PG-23073-01C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2730 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 12.65 | CML-14 | CML: Pipe Length | 6 | 2068-02-11 | 2070-10-05 | 2014-03-13 09:00 | 5.66 | 0 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 12.5 | 3 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.84 |  | 12.5 | 12.5 | 13 | 12.6 | 0.23805
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-15 | 50-PG-23073-01C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2731 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 12.7 | CML-15 | CML: Pipe Length | 6 | 2068-02-11 | 2070-10-05 | 2014-03-13 09:00 | 5.66 | 0 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 12.5 | 12 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.84 |  | 12.5 | 12.6 | 13 | 12.7 | 0.21602
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3038 | Rope Access | 2014-05-03 09:30 | 2014-05-03 10:30 | [36 empty] | 6.15 | CML-1 | CML: type TBC | 3 | 2023-07-19 | 2023-11-18 | 2014-05-03 09:30 | 2.5 | 0.34721 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 6 O'Clock | 100 | 6.02 | 100-FH-43147-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 6.5 | 5.7 | 5.9 | 0.41231
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-PG-23073-01C03-P | CML-2 | 50-PG-23073-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3039 | Rope Access | 2014-05-03 09:30 | 2014-05-03 10:30 | [36 empty] | 6.075 | CML-2 | CML: type TBC | 3 | 2175-07-07 | 2180-11-12 | 2014-05-03 09:30 | 2.5 | 0.0217 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-FH-43147-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.1 | 6.2 | 0.095743
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PG-23073-01C03-P | CML-2 | 50-PG-23073-01C03-P CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24390 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 28.275 | CML-2 | CML: Elbow | 1 | 2035-06-01 | 2029-05-31 | 2016-06-07 07:00 | 1.71 | 0 | A2: Right Quadrant |  | 2.91 | 1.71 | 2.31 | 8.6 | 3 O'Clock | 50 | 3.91 | 50-FG-45049-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.89 |  | 8.7 | 8.6 | 8.8 | 87 | 39.1501
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-4 | 50-PG-23073-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20612 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 9.075 | CML-4 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-07-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 6 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.2 | 9 | 9 | 9.1 | 0.095743
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-17 | 50-PG-23073-01C03-P CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10181 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.1 | CML-17 | CML: type TBC | 6 | 2016-01-27 | 2015-09-16 | 2013-11-09 | 2.81 | 3.1059 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 9.7 | 12 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.89 |  | 9.7 | 9.9 | 10.1 | 10.7 | 0.43205
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-15 | 50-PG-23073-01C03-P CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10179 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.025 | CML-15 | CML: type TBC | 6 | 2016-01-27 | 2015-09-16 | 2013-11-09 | 2.81 | 3.1059 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 9.7 | 3 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.89 |  | 10.4 | 9.7 | 10.2 | 9.8 | 0.3304
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-14 | 50-PG-23073-01C03-P CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10178 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 12.375 | CML-14 | CML: type TBC | 6 | 2016-01-27 | 2015-09-16 | 2013-11-09 | 2.81 | 3.1059 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 9.7 | 6 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.89 |  | 13.8 | 13.6 | 9.7 | 12.4 | 1.8875
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20609 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 9.525 | CML-1 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-07-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 9.3 | 9 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 10 | 9.4 | 9.4 | 9.3 | 0.32016
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23087 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 10.15 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 12 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | 4.738 | 9.4 | 10.1 | 11.2 | 9.9 | 0.75939
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-9 | 50-PG-23073-01C03-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22994 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.575 | CML-9 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2015-05-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.4 | 3 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | -0.18528 | 9.4 | 9.4 | 9.8 | 9.7 | 0.20616
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-PG-23073-01C03-P | CML-5 | 50-PG-23073-01C03-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22969 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.575 | CML-5 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2015-05-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.4 | 3 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | -0.58167 | 9.5 | 9.4 | 9.6 | 9.8 | 0.17078
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22898 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-01 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 3 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | -3.6139 | 10.5 | 9.4 | 9.9 | 10.2 | 0.46904
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-25 | 50-PG-23073-01C03-P CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 22890 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.65 | CML-25 | CML: Pipe Length | 6 | 2029-11-05 | 2027-12-11 | 2015-05-01 07:00 | 2.5 | 0.47498 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.4 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | 2.0696 | 9.7 | 9.5 | 9.4 | 10 | 0.26458
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-16 | 50-PG-23073-01C03-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 22881 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.55 | CML-16 | CML: Elbow | 6 | 2029-11-05 | 2027-12-11 | 2015-05-01 07:00 | 2.5 | 0.47498 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.4 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | 0 | 9.7 | 9.4 | 9.5 | 9.6 | 0.1291
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-6 | 50-PG-23073-01C03-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22871 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.675 | CML-6 | CML: Elbow | 6 | 2029-11-05 | 2027-12-11 | 2015-05-01 07:00 | 2.5 | 0.47498 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.4 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | 0.75258 | 9.8 | 9.4 | 9.8 | 9.7 | 0.1893
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-14 | 50-PG-23073-01C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20622 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 11.325 | CML-14 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-07-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 10.7 | 6 O'Clock | 40 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11.3 | 10.7 | 10.7 | 12.6 | 0.89582
RP01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-PG-23073-01C03-P | CML-1 | 50-PG-23073-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8746 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 9.625 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.4 | 9.5 | 10.2 | 9.4 | 0.38622
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PG-23073-01C03-P | CML-3 | 50-PG-23073-01C03-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8676 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:54 | [32 empty] | 9.7 | CML-3 | CML: Elbow | 3 | 2074-01-04 | 2058-09-17 | 2015-02-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 9.4 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.9 | 9.7 | 9.4 | 9.8 | 0.21602
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-11 | 50-PG-23073-01C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20619 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 11.9 | CML-11 | CML: Reducer | 6 | 2075-10-24 | 2074-08-12 | 2014-07-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 11.5 | 12 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 11.5 | 11.8 | 12 | 12.3 | 0.33665
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-8 | 50-PG-23073-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20616 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 13.175 | CML-8 | CML: Equal Tee | 6 | 2075-10-24 | 2074-08-12 | 2014-07-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 12.7 | 3 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 13.2 | 12.7 | 12.8 | 14 | 0.5909
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PG-23073-01C03-P | CML-16 | 50-PG-23073-01C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21858 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 9.675 | CML-16 | CML: Elbow | 6 | 2025-04-15 | 2023-11-30 | 2014-10-19 07:00 | 2.5 | 0.65734 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.4 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10 | 9.8 | 9.5 | 9.4 | 0.27538
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-10 | 50-PG-23073-01C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20618 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 13.15 | CML-10 | CML: Reducing Tee | 6 | 2075-10-24 | 2074-08-12 | 2014-07-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 13 | 9 O'Clock | 50 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.5 |  | 13.5 | 13 | 13.1 | 13 | 0.23805
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-13 | 50-PG-23073-01C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20621 | Casting - No UT | 2014-07-26 07:00 | 2014-07-26 15:00 | [37 empty] | CML-13 | CML: Pipe Length | 6 | 2075-10-24 | 2074-08-12 | 2014-07-26 07:00 | 2.5 | 0 |  |  | 2.74 | 2.5 | 2.62 |  | 9 O'Clock | 15 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23073-01C03-P | CML-12 | 50-PG-23073-01C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20620 | Casting - No UT | 2014-07-26 07:00 | 2014-07-26 15:00 | [37 empty] | CML-12 | CML: Fitting | 6 | 2075-10-24 | 2074-08-12 | 2014-07-26 07:00 | 2.5 | 0 |  |  | 2.74 | 2.5 | 2.62 |  | 9 O'Clock | 40 | 8.74 | 50-PG-23073-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-17 | 80-DC-57002-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20246 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 9.8 | CML-17 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 9.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  |  | 10.2 | 9.8 | 9.4 | 0.4
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1661 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.5 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 3 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.8 | 7.7 | 9 | 9.5 | 0.89069
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-2 | 250-DC-57064-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20282 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 9.925 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 12 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.4 | 9.6 | 10.5 | 10.2 | 0.51235
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-5 | 50-PG-23075-03C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20642 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.25 | CML-5 | CML: Elbow | 3 | 2019-11-17 | 2019-11-02 | 2014-07-25 07:30 | 2.5 | 0.47006 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5.4 | 5.2 | 5 | 0.19149
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-3 | 150-DC-57308-01C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20300 | Reviewed 24/11/14. FFS. CML to be checked in Oct.16 | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 1.174mm/ yr |  | Nestor | 2014-11-24 08:45 | [32 empty] | 10.075 | CML-3 | CML: Pipe Length | 6 | 2020-08-17 | 2019-07-30 | 2014-10-02 07:00 | 2.5 | 1.1736 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 9.4 | 3 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.5 | 9.4 | 10.5 | 9.9 | 0.53151
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40034-01C02 | CML-13 | 100-WC-40034-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1727 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 8.3 | CML-13 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.9 | 8.7 | 7.7 | 7.9 | 0.58878
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12586 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.55 | CML-8 | CML: Pipe Length | 3 | 2050-12-17 | 2046-03-02 | 2014-02-05 08:00 | 0.54 | 0.13175 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.6 | 5.6 | 5.6 | 5.4 | 0.1
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-4 | 50-PG-23075-03C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20641 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.3 | CML-4 | CML: Elbow | 3 | 2019-11-17 | 2019-11-02 | 2014-07-25 07:30 | 2.5 | 0.47006 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.5 | 5 | 5.2 | 0.24495
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-25 | 50-DH-56070-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 3241 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.525 | CML-25 | CML: type TBC | 3 | 2025-04-14 | 2026-07-23 | 2014-05-09 07:00 | 2.5 | 0.25592 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.6 | 5.3 | 5.8 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-1 | 50-FH-43016-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12600 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.525 | CML-1 | CML: Pipe Length | 3 | 2021-08-14 | 2022-07-01 | 2014-01-23 13:00 | 2.5 | 0.37034 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.8 | 5.3 | 5.4 | 0.22174
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-2 | 50-PG-23075-03C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20639 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.325 | CML-2 | CML: Elbow | 3 | 2019-11-17 | 2019-11-02 | 2014-07-25 07:30 | 2.5 | 0.47006 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 3 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5 | 5.4 | 5.4 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40034-01C02 | CML-9 | 100-WC-40034-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1723 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 8.3 | CML-9 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.9 | 8.7 | 7.7 | 7.9 | 0.58878
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-15 | 250-WC-40017-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2078 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 8.275 | CML-15 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 6 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.7 | 8.4 | 7.7 | 8.3 | 0.41932
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-13 | 100-WC-40035-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1746 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.975 | CML-13 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.7 | 6 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.8 | 8.5 | 7.7 | 7.9 | 0.3594
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-20 | 50-FG-45301-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 5806 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.525 | CML-20 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.6 | 6.7 | 6.2 | 0.22174
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-2 | 50-FG-45023-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1150 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.525 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | -7.7654 | 6.3 | 6.4 | 6.6 | 6.8 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-16 | 200-WC-40008-01C02-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 7822 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 8.1 | CML-16 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 3 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.5 | 7.7 | 8.1 | 8.1 | 0.3266
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42041-01S01 | CML-1 | 50-CI-42041-01S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3094 | Rope Access | 2014-05-04 11:00 | 2014-05-04 11:30 | [36 empty] | 9.75 | CML-1 | CML: Reducer | 1 | 2043-10-24 | 2037-01-28 | 2014-05-04 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 9.4 | 9 O'Clock | 50 | 5.54 | 50-CI-42041-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.8 | 10.2 | 9.6 | 9.4 | 0.34157
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43135-01C02 | CML-3 | 200-FH-43135-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7851 | Line is FFS. Current RBI frequency is 48m. Action: CML’s to Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-08 13:39 | [32 empty] | 7.025 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 9 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.3 | 6.9 | 7.1 | 6.8 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-9 | 80-FH-43009-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12587 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.725 | CML-9 | CML: Elbow | 3 | 2050-12-17 | 2046-03-02 | 2014-02-05 08:00 | 0.54 | 0.13175 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.8 | 5.8 | 5.4 | 5.9 | 0.22174
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45503-01C02 | CML-4 | 50-FG-45503-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 7739 | Line is FFS despite the High CR on CML-1 to 6. Current RBI frequency is 48m. Action: Inspect in 24m. RBI to be updated. | 2015-01-10 08:00 | 2015-01-10 10:00 |  |  | Administrator | 2015-09-21 14:30 | [32 empty] | 5.025 | CML-4 | CML: Elbow | 3 | 2019-03-31 | 2019-11-14 | 2015-01-10 08:00 | 2.5 | 0.52113 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FG-45503-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.2 | 5.1 | 5.1 | 0.22174
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-5 | 50-CG-38467-01C02 CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 22276 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.025 | CML-5 | CML: Elbow | 3 | 2017-03-05 | 2017-07-31 | 2014-05-01 11:00 | 2.5 | 0.80757 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0 | 4.8 | 5.3 | 4.9 | 5.1 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57014-01C02 | CML-2 | 50-DC-57014-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1363 | Rope access | 2014-04-04 13:00 | 2014-04-04 15:00 | [36 empty] | 10.1 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-04 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.1 | 11.1 | 9.4 | 9.8 | 0.72572
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-5 | 50-CG-38467-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2997 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.025 | CML-5 | CML: Elbow | 3 | 2017-03-05 | 2017-07-31 | 2014-05-01 11:00 | 2.5 | 0.80757 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.3 | 4.9 | 5.1 | 0.22174
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-10 | 50-PG-23075-03C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20647 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.55 | CML-10 | CML: Elbow | 3 | 2023-09-06 | 2023-08-12 | 2014-07-25 07:30 | 2.5 | 0.29596 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6.2 | 5.4 | 5.4 | 0.44347
PG06 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PG-23008-15S01-A | CML-4 | 200-PG-23008-15S01-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21927 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 5.275 | CML-4 | CML: Elbow | 3 | 2023-10-24 | 2025-01-08 | 2014-10-09 07:00 | 2.5 | 0.28741 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 20 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.6 | 5.1 | 5.2 | 0.22174
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56106-01C02 | CML-11 | 80-DH-56106-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2037 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 5.525 | CML-11 | CML: type TBC | 3 | 2021-11-15 | 2022-11-09 | 2014-03-27 14:30 | 2.5 | 0.3533 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.2 | 5.6 | 5.6 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43129-01C02 | CML-3 | 50-FH-43129-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1782 | Rope access | 2014-04-28 08:00 | 2014-04-28 09:00 | [36 empty] | 5.525 | CML-3 | CML: Pipe Length | 3 | 2021-07-11 | 2022-05-25 | 2014-04-28 08:00 | 2.5 | 0.37455 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FH-43129-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.7 | 5.2 | 5.6 | 0.22174
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-14 | 250-PG-23003-06C02-PA CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20260 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 5.725 | CML-14 | CML: type TBC | 3 | 2046-10-03 | 2050-08-21 | 2014-06-02 13:00 | 2.5 | 0.08962 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 12 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 5.9 | 5.8 | 0.22174
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-8 | 50-PG-23075-03C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20645 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.6 | CML-8 | CML: Elbow | 3 | 2023-09-06 | 2023-08-12 | 2014-07-25 07:30 | 2.5 | 0.29596 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.8 | 5.8 | 5.2 | 0.28284
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38477-01C02-P | CML-2 | 50-CG-38477-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20892 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.775 | CML-2 | CML: type TBC | 3 | 2020-04-21 | 2020-04-03 | 2014-10-04 07:00 | 2.5 | 0.55834 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 12 O'Clock | 25 | 6.35 | 25-CG-38485-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 6.1 | 5.7 | 0.22174
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-1 | 200-PL-20034-03C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21598 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 10.35 | CML-1 | CML: Reducer | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 9.6 | 9 O'Clock | 300 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.99 |  | 10.4 | 10.3 | 11.1 | 9.6 | 0.61373
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-8 | 50-FG-45024-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1191 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.525 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.8 | 6.3 | 6.6 | 6.4 | 0.22174
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-3 | 50-PG-23075-03C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20640 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.375 | CML-3 | CML: Elbow | 3 | 2027-12-16 | 2027-11-11 | 2014-07-25 07:30 | 2.5 | 0.20891 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.4 | 5.3 | 5.3 | 0.095743
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-10 | 250-PG-23003-06C02-PA CML-10 | Yes | FPSO 2014 | Pipe Wall Thickness | 24248 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 16.375 | CML-10 | CML: Equal Tee | 3 | 2085-04-24 | 2073-10-17 | 2014-09-24 07:00 | 7.9 | 0 | A3: Inside Quadrant |  | 12.09 | 7.9 | 9.0519 | 16.1 | 6 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 16.6 | 16.3 | 16.1 | 16.5 | 0.22174
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-3 | 200-PW-44018-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5580 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 8.175 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | 0 | 8.2 | 8.3 | 7.4 | 8.8 | 0.57951
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-17 | 100-FG-45001-09C02 CML-17 | Yes | FPSO 2015 | Pipe Wall Thickness | 23322 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 14.075 | CML-17 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 13.8 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 | -0.36181 | 13.8 | 14 | 14.2 | 14.3 | 0.22174
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-19 | 300-PG-20005-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 6175 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 16.425 | CML-19 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 16.2 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 16.7 | 16.3 | 16.5 | 16.2 | 0.22174
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-58 | 80-CG-38459-09C02-P CML-58 |  | FPSO 2014 | Pipe Wall Thickness | 21196 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 17.225 | CML-58 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 17 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.1 |  | 17.3 | 17.1 | 17.5 | 17 | 0.22174
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-5 | 200-PG-23051-09C02-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13110 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.625 | CML-5 | CML: type TBC | 3 | 2103-01-05 | 2073-03-18 | 2014-02-07 11:00 | 9.3 | 0 | A2: Right Quadrant |  | 15.26 | 9.3 | 12.28 | 18.7 | 3 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 19.3 | 18.7 | 20.4 | 20.1 | 0.7719
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-8 | 200-PG-23051-09C02-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13113 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.425 | CML-8 | CML: type TBC | 3 | 2103-01-05 | 2073-03-18 | 2014-02-07 11:00 | 9.3 | 0 | A4: Left Quadrant |  | 15.26 | 9.3 | 12.28 | 18.7 | 9 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 19.6 | 20.2 | 19.2 | 18.7 | 0.63443
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-27 | 300-PG-20005-03C03-P CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 22789 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 9.375 | CML-27 | CML: Elbow | 6 | 2017-11-05 | 2016-10-04 | 2015-04-29 07:00 | 2.5 | 2.6539 | A2: Right Quadrant |  | 8.27 | 2.5 | 5.385 | 9.2 | 3 O'Clock | 50 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | -0.37503 | 9.3 | 9.2 | 9.3 | 9.7 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-8 | 200-WC-40008-01C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7814 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 7.925 | CML-8 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 3 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.2 | 7.7 | 7.9 | 7.9 | 0.20616
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20017-01C02-P | CML-1 | 200-PL-20017-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21240 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.775 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.5 | 9 O'Clock | 200 | 6.35 | 200-PL-20017-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.5 | 9.6 | 8.5 | 0.55
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-9 | 50-PG-23075-03C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20646 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.5 | CML-9 | CML: Elbow | 3 | 2027-12-16 | 2027-11-11 | 2014-07-25 07:30 | 2.5 | 0.20891 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.3 | 5.6 | 5.5 | 0.14142
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24036-09C02 | CML-2 | 50-PL-24036-09C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13161 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 8.975 | CML-2 | CML: type TBC | 3 | 2029-11-26 | 2025-08-15 | 2014-01-18 15:00 | 2.5 | 0.3782 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 6 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.7 | 9.3 | 8.5 | 9.4 | 0.44253
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-14 | 150-PG-23506-25C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2788 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.5 | CML-14 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 22.3 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.42 |  | 22.4 | 22.5 | 22.8 | 22.3 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43108-01C02 | CML-7 | 200-FH-43108-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12782 |  | 2014-01-18 15:30 | 2014-01-18 16:30 | [36 empty] | 8 | CML-7 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 15:30 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.8 | 9 O'Clock | 200 | 6.35 | 200-FH-43108-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.46 |  | 7.9 | 8 | 8.3 | 7.8 | 0.21602
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56119-01C02 | CML-3 | 50-DH-56119-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21029 | Rope Access | 2014-05-19 09:30 | 2014-05-19 11:00 | [36 empty] | 5.1 | CML-3 | CML: type TBC | 3 | 2017-05-18 | 2017-10-21 | 2014-05-19 09:30 | 2.5 | 0.76647 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56119-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 5.2 | 5.3 | 4.8 | 0.21602
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-7 | 50-PG-23075-03C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20644 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.35 | CML-7 | CML: Elbow | 3 | 2027-12-16 | 2027-11-11 | 2014-07-25 07:30 | 2.5 | 0.20891 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.4 | 5.3 | 0.057735
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-6 | 50-PG-23075-03C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20643 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.3 | CML-6 | CML: Elbow | 3 | 2027-12-16 | 2027-11-11 | 2014-07-25 07:30 | 2.5 | 0.20891 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.3 | 5.3 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-1 | 50-PG-23075-03C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20638 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.475 | CML-1 | CML: Elbow | 3 | 2038-05-06 | 2038-03-07 | 2014-07-25 07:30 | 2.5 | 0.12187 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 5.4 | 5.4 | 0.15
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-7 | 50-FG-45018-03C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2589 | Rope Access | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 5.1 | CML-7 | CML: type TBC | 3 | 2017-02-12 | 2017-02-03 | 2014-04-26 07:00 | 2.5 | 0.82025 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0 | 5.1 | 4.8 | 5.2 | 5.3 | 0.21602
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-3 | 250-DC-57064-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23089 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 10.15 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 3 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 0 | 9.7 | 9.5 | 10.1 | 11.3 | 0.80623
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-3 | 200-PW-44018-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21889 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 8.175 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.2 | 8.3 | 7.4 | 8.8 | 0.57951
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-7 | 50-PW-44013-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22726 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 8.2 | CML-7 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-04-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | 0.23567 | 7.4 | 8.5 | 8.7 | 8.2 | 0.57155
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43300-01C02 | CML-3 | 50-FL-43300-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20450 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.1 | CML-3 | CML: Elbow | 3 | 2019-10-21 | 2020-06-28 | 2014-10-05 07:00 | 2.5 | 0.47548 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FL-43300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.4 | 5.1 | 4.9 | 0.21602
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56117-01C02 | CML-2 | 50-DH-56117-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21015 | Rope Access | 2014-05-19 13:00 | 2014-05-19 14:00 | [36 empty] | 5.1 | CML-2 | CML: type TBC | 3 | 2017-12-31 | 2018-06-29 | 2014-05-19 13:00 | 2.5 | 0.66262 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 | 5.1 | 5.4 | 0.21602
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-4 | 50-FG-45020-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2603 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.1 | CML-4 | CML: type TBC | 3 | 2017-09-12 | 2017-09-02 | 2014-04-26 09:30 | 2.5 | 0.70918 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.22756 | 5.1 | 4.9 | 5.4 | 5 | 0.21602
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24036-09C02 | CML-8 | 50-PL-24036-09C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13167 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 8.8 | CML-8 | CML: type TBC | 3 | 2029-11-26 | 2025-08-15 | 2014-01-18 15:00 | 2.5 | 0.3782 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.8 | 9.1 | 8.8 | 8.5 | 0.24495
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-9 | 100-DH-56561-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7941 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 5.3 | CML-9 | CML: Elbow | 3 | 2019-01-16 | 2019-03-25 | 2015-01-17 13:00 | 2.5 | 0.62515 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 9 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5.4 | 5.5 | 5 | 0.21602
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56113-01C02 | CML-5 | 50-DH-56113-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5244 | Rope Access | 2014-05-20 14:00 | 2014-05-20 15:00 | [36 empty] | 5.2 | CML-5 | CML: Elbow | 3 | 2018-11-12 | 2019-06-14 | 2014-05-20 14:00 | 2.5 | 0.55744 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DH-56113-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.5 | 5.1 | 5.2 | 0.21602
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56118-01C02 | CML-5 | 50-DH-56118-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21024 | Rope Access | 2014-05-19 11:00 | 2014-05-19 12:00 | [36 empty] | 5.3 | CML-5 | CML: type TBC | 3 | 2018-11-06 | 2019-06-07 | 2014-05-19 11:00 | 2.5 | 0.55922 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DH-56118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5 | 5.4 | 5.3 | 0.21602
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DH-56L9003-AC21M-00 | CML-11 | 0200-DH-56L9003-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5096 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 10.925 | CML-11 | CML: type TBC | 3 | 2075-05-31 | 2064-09-03 | 2015-03-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 3.5737 | 9.5 | 6 O'Clock | 50 | 8.74 | 0200-DH-56L9003-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 11.8 | 11 | 9.5 | 11.4 | 1.0046
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56131-01C02 | CML-1 | 50-DH-56131-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21062 | Rope Access | 2014-05-15 07:00 | 2014-05-15 08:00 | [36 empty] | 5.2 | CML-1 | CML: type TBC | 3 | 2018-10-13 | 2019-05-12 | 2014-05-15 07:00 | 2.5 | 0.56591 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DH-56131-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5.2 | 5.5 | 0.21602
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-5 | 100-DH-56009-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3428 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.2 | CML-5 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5 | 3 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5 | 5.2 | 5.1 | 0.21602
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-10 | 400-WC-40060-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1058 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 7.975 | CML-10 | CML: type TBC | 3 | 2048-12-05 | 2044-06-27 | 2014-03-20 14:00 | 2.6 | 0.1497 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 7.8 | 12 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.8 | 7.9 | 8 | 8.2 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-9 | 50-FG-45020-03C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2608 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.2 | CML-9 | CML: type TBC | 3 | 2018-06-29 | 2018-06-17 | 2014-04-26 09:30 | 2.5 | 0.59837 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.45512 | 5 | 5.2 | 5.1 | 5.5 | 0.21602
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-19 | 250-PW-44006-01X01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 23190 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 8.225 | CML-19 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | 1.6451 | 8.6 | 8.5 | 7.4 | 8.4 | 0.55603
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-30 | 50-DH-56137-01C02 CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 21114 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 5.3 | CML-30 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.4 | 5.3 | 5 | 0.21602
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-9 | 50-FG-45501-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6592 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.4 | CML-9 | CML: Elbow | 3 | 2026-01-14 | 2027-05-24 | 2015-03-30 07:00 | 2.5 | 0.24067 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.4 | 5.1 | 5.5 | 0.21602
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-14 | 50-PG-23075-03C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20651 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 5.625 | CML-14 | CML: Elbow | 3 | 2038-05-06 | 2038-03-07 | 2014-07-25 07:30 | 2.5 | 0.12187 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.4 | 5.8 | 5.4 | 0.263
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-3 | 250-DC-57064-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20283 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 9.95 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 12 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.5 | 11.1 | 9.6 | 9.6 | 0.76811
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-6 | 200-PW-44021-01X01 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10711 | Deck Level. Line is FFS. High CR. Line rechecked (refer to Jan. 15 values) | 2013-11-10 | 2013-11-10 |  |  | Administrator | 2015-09-13 11:06 | [32 empty] | 7.7667 | CML-6 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2013-11-10 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 3 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.1 | 7.4 |  | 7.8 | 0.35119
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 200-PG-23504-15S01 | CML-1 | 200-PG-23504-15S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20761 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [35 empty] | Low alarm breach | 20.7 | CML-1 | CML: Elbow | 1 | 2018-01-13 | 2015-12-17 | 2014-09-27 07:00 | 13.2 | 2.1222 | A4: Left Quadrant |  | 22.01 | 13.2 | 17.605 | 20.2 | 9 O'Clock | 200 | 23.01 | 200-PG-23504-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 20.9 | 20.8 | 20.9 | 20.2 | 0.33665
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-11 | 50-PG-23075-03C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20648 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 6.225 | CML-11 | CML: Elbow | 3 | 2043-10-24 | 2043-08-12 | 2014-07-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 6.2 | 6.4 | 0.12583
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-5 | 50-FG-45019-03C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10487 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.4 | CML-5 | CML: type TBC | 3 | 2017-07-03 | 2017-06-23 | 2013-11-15 | 2.5 | 0.74311 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 5.7 | 5.4 | 0.21602
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-1 | 200-PW-44020-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23008 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 7.6 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 12 O'Clock | 200 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | 0.45667 | 7.4 | 7.7 | 7.8 | 7.5 | 0.18257
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56564-01C02 | CML-3 | 50-DH-56564-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21119 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18.Update RBI study to include this line. | 2014-10-09 07:00 | 2014-10-09 15:00 |  |  | Nestor | 2014-11-21 14:26 | [32 empty] | 5.4 | CML-3 | CML: Elbow | 3 | 2025-07-16 | 2026-11-03 | 2014-10-09 07:00 | 2.5 | 0.25056 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-DH-56564-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.3 | 5.7 | 0.21602
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-10 | 250-PG-23003-06C02-PA CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 3433 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.6 | CML-10 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.4 | 6 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.6 | 5.4 | 5.9 | 0.21602
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1826 |  | 2014-04-29 14:30 | 2014-04-29 15:00 | [36 empty] | 5.6 | CML-1 | CML: Fitting | 3 | 2033-03-10 | 2035-04-24 | 2014-04-29 14:30 | 2.5 | 0.15364 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DH-56123-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 5.6 | 5.9 | 0.21602
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-19 | 300-PW-44002-01X01-P CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 22865 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 7.5 | CML-19 | CML: Pipe Length | 6 | 2018-07-21 | 2017-12-16 | 2015-05-01 07:00 | 2.5 | 1.5189 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 7.4 | 6 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.6 | 7.4 | 7.6 | 0.11547
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42042-01S01 | CML-1 | 50-CI-42042-01S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3448 | Rope Access | 2014-05-13 07:00 | 2014-05-13 08:00 | [36 empty] | 10.2 | CML-1 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2014-05-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 9.5 | 9 O'Clock | 50 | 5.54 | 50-CI-42042-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.1 | 10.4 | 10.8 | 9.5 | 0.54772
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42046-01S01 | CML-1 | 50-CI-42046-01S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3088 | Rope Access | 2014-05-04 10:30 | 2014-05-04 11:00 | [36 empty] | 9.9 | CML-1 | CML: Reducer | 1 | 2043-10-24 | 2037-01-28 | 2014-05-04 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 9.5 | 3 O'Clock | 50 | 5.54 | 50-CI-42046-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.8 | 9.5 | 10.2 | 10.1 | 0.31623
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-4 | 100-VA-80006-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2173 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 5.9 | CML-4 | CML: type TBC | 3 | 2020-05-10 | 2020-08-02 | 2014-03-30 13:00 | 2.5 | 0.50671 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 6.1 | 6 | 5.6 | 0.21602
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38477-01C02-P | CML-1 | 50-CG-38477-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20895 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.9 | CML-1 | CML: type TBC | 3 | 2020-04-21 | 2020-04-03 | 2014-10-04 07:00 | 2.5 | 0.55834 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 9 O'Clock | 25 | 6.35 | 25-CG-38484-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 5.9 | 6.1 | 5.6 | 0.21602
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-19 | 200-PW-44018-01X01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 12597 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.75 | CML-19 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-02-05 08:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 5.5 | 6.2 | 5.5 | 5.8 | 0.33166
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56122-01C02 | CML-1 | 50-DH-56122-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1821 |  | 2014-04-29 14:00 | 2014-04-29 14:30 | [36 empty] | 5.9 | CML-1 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-29 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 6.2 | 5.8 | 5.7 | 0.21602
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40036-01C02 | CML-1 | 200-WC-40036-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7705 |  | 2015-01-09 07:00 | 2015-01-09 10:00 | [36 empty] | 7.85 | CML-1 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-01-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 12 O'Clock | 200 | 6.35 | 200-WC-40036-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 7.9 | 8 | 0.1291
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80002-01C02 | CML-7 | 100-VA-80002-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2167 | Rope Access | 2014-03-30 09:30 | 2014-03-30 11:00 | [36 empty] | 6.1 | CML-7 | CML: type TBC | 3 | 2037-09-13 | 2038-07-03 | 2014-03-30 09:30 | 2.5 | 0.14484 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-VA-80002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 6.4 | 5.9 | 6 | 0.21602
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24036-09C02 | CML-6 | 50-PL-24036-09C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13165 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 8.625 | CML-6 | CML: type TBC | 3 | 2029-11-26 | 2025-08-15 | 2014-01-18 15:00 | 2.5 | 0.3782 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.7 | 8.6 | 8.7 | 8.5 | 0.095743
FG02 | Montara_Topside | Yes | Potable Water (53) | Pipework | 25-FG-45455-01C02-E | CML-7 | 25-FG-45455-01C02-E CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8222 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.2 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.2 | 6.5 | 0.21602
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 23874 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.3 | CML-2 | CML: Fitting | 3 | 2027-12-10 | 2027-11-01 | 2014-09-26 07:00 | 2.5 | 0.26488 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 40 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 6 | 6.5 | 6.3 | 0.21602
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1409 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 6.2 | CML-3 | CML: type TBC | 3 | 2162-12-08 | 2167-11-15 | 2014-04-07 07:00 | 2.5 | 0.02353 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.2 | 6.5 | 0.21602
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-12 | 50-PG-23075-03C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20649 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 6.525 | CML-12 | CML: Equal Tee | 3 | 2043-10-24 | 2043-08-12 | 2014-07-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.6 | 6.7 | 6.4 | 0.15
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-5 | 300-FL-43070-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12698 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.4 | CML-5 | CML: type TBC | 3 | 2023-10-05 | 2023-09-08 | 2014-02-01 09:00 | 2.5 | 0.37188 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.6 | 6.1 | 6.4 | 6.5 | 0.21602
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-12 | 100-WC-40035-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1745 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.825 | CML-12 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.7 | 12 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 8 | 7.8 | 0.12583
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-13 | 50-FG-45301-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5799 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.6 | CML-13 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.3 | 6.6 | 6.8 | 0.21602
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-9 | 150-FL-43453-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2253 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.6 | CML-9 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.4 | 3 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.9 | 6.4 | 6.5 | 6.6 | 0.21602
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-7 | 300-FL-43070-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12700 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.6 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.9 | 6.6 | 6.5 | 6.4 | 0.21602
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57028-01C02 | CML-6 | 50-DC-57028-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20273 | Rope Access | 2014-05-26 08:00 | 2014-05-26 09:00 | [36 empty] | 7.925 | CML-6 | CML: type TBC | 3 | 2065-02-10 | 2057-09-22 | 2014-05-26 08:00 | 0.37 | 0 | A4: Left Quadrant |  | 2.54 | 0.37 | 1.1087 | 7.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.03 |  | 7.6 | 8.8 | 7.9 | 7.4 | 0.61847
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PL-20051-01C02-P | CML-3 | 150-PL-20051-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21507 | Protective mesh removed | 2014-06-30 08:00 | 2014-06-30 09:00 | [36 empty] | 7.275 | CML-3 | CML: Reducer | 3 | 2045-08-25 | 2039-07-12 | 2014-06-30 08:00 | 0.84 | 0.19438 | A1: Outside Quadrant |  | 4.11 | 0.84 | 2.0306 | 6.9 | 12 O'Clock | 100 | 7.11 | 150-PL-20051-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.06 |  | 6.9 | 7.6 | 7.3 | 7.3 | 0.28723
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-4 | 80-PW-44034-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21986 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.1 | CML-4 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 3 O'Clock | 20 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.5 | 6.8 | 6.9 | 7.2 | 0.31623
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24036-09C02 | CML-11 | 50-PL-24036-09C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 13170 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 9.425 | CML-11 | CML: type TBC | 3 | 2041-09-05 | 2034-05-05 | 2014-01-18 15:00 | 2.5 | 0.22062 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 3 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.4 | 8.6 | 10.2 | 9.5 | 0.65511
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-16 | 50-PL-24003-09C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 13155 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.9 | CML-16 | CML: type TBC | 3 | 2041-09-02 | 2034-05-02 | 2014-01-18 13:00 | 2.5 | 0.22069 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.7 | 8.6 | 8.7 | 0.53541
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-17 | 250-FH-43303-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12955 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 7.4 | CML-17 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.7 | 7.2 | 7.4 | 7.3 | 0.21602
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-11 | 50-CG-38452-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1813 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 7.4 | CML-11 | CML: Fitting | 3 | 2059-07-07 | 2055-11-27 | 2014-04-29 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 12 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.4 | 7.3 | 7.7 | 0.21602
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20678 | Rope Access | 2014-03-30 07:00 | 2014-03-30 08:00 | [36 empty] | 7.4 | CML-1 | CML: type TBC | 3 |  |  | 2014-03-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 7.2 | 9 O'Clock | 150 |  | 150-VA-80007-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.4 | 7.7 | 7.3 | 7.2 | 0.21602
CG04 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2154 | Rope Access | 2014-03-30 07:00 | 2014-03-30 08:00 | [36 empty] | 7.4 | CML-1 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-03-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-VA-80003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.4 | 7.7 | 7.3 | 7.2 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43124-01C02 | CML-5 | 80-FH-43124-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12847 |  | 2014-02-05 11:00 | 2014-02-05 13:00 | [36 empty] | 5.6 | CML-5 | CML: Pipe Length | 3 | 2031-03-18 | 2028-12-08 | 2014-02-05 11:00 | 0.54 | 0.278 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 12 O'Clock | 80 | 5.49 | 80-FH-43124-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.3 | 5.8 | 5.6 | 5.7 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43017-01C02 | CML-1 | 150-FH-43017-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10647 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 7.6 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-18 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.4 | 12 O'Clock | 100 | 6.02 | 100-FH-43017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.6 | 7.9 | 7.5 | 0.21602
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-4 | 100-PG-23503-03C03-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2720 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.9 | CML-4 | CML: Pipe Length | 6 | 2021-06-24 | 2021-11-13 | 2014-03-13 09:00 | 5.66 | 0.67788 | A3: Inside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.6 | 6 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.94 |  | 11.1 | 10.9 | 10.6 | 11 | 0.21602
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23075-03C02-P | CML-13 | 50-PG-23075-03C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20650 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [37 empty] | CML-13 | CML: Fitting | 3 | 2043-10-24 | 2043-08-12 | 2014-07-25 07:30 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.52 |  | 9 O'Clock | 50 | 5.54 | 50-PG-23075-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-15 | 150-WC-40006-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1675 | Rope Access | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.475 | CML-15 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 3 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.8 | 8.9 | 9.4 | 0.80571
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-19 | 150-WC-40006-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1679 | Rope Access | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.525 | CML-19 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 12 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.9 | 9.1 | 9.3 | 0.78475
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-15 | 200-FH-43025-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2488 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 9 | CML-15 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.8 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 8.9 | 9 | 9.3 | 0.21602
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-12 | 50-PL-24003-09C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 13151 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.7 | CML-12 | CML: type TBC | 3 | 2041-09-02 | 2034-05-02 | 2014-01-18 13:00 | 2.5 | 0.22069 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.8 | 8.6 | 8.7 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-12 | 150-FH-43136-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2773 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.9 | CML-12 | CML: Elbow | 3 | 2074-03-18 | 2063-04-04 | 2014-03-13 09:00 | 1.03 | 0 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.6 | 6 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.57 |  | 8 | 7.9 | 7.6 | 8.1 | 0.21602
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-8 | 50-FL-43454-01C02-P CML-8 | Yes | FPSO 2014 | Pipe Wall Thickness | 20511 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 9.3 | CML-8 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.1 | 12 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.2 | 9.3 | 9.6 | 0.21602
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42312-01S01 | CML-4 | 40-CI-42312-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7513 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 10.675 | CML-4 | CML: type TBC | 1 | 2059-10-24 | 2046-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 9.6 | 12 O'Clock | 40 | 7.14 | 40-CI-42312-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.6 | 12 | 11.3 | 9.8 | 1.1644
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-3 | 250-PW-44010-01C03-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23025 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 10 | CML-3 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2015-05-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.8 | 3 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 | 0 | 10 | 9.8 | 9.9 | 10.3 | 0.21602
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-16 | 150-WC-40006-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1676 | Rope Access | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.475 | CML-16 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 3 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.9 | 7.8 | 8.8 | 9.4 | 0.76322
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-10 | 100-PG-23071-01C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2408 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 10.5 | CML-10 | CML: type TBC | 6 | 2022-03-12 | 2020-11-30 | 2014-03-19 13:00 | 2.5 | 0.96401 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.2 | 6 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.7 | 10.6 | 10.2 | 10.5 | 0.21602
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-15 | 250-PW-20041-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21424 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.925 | CML-15 | CML: Fitting | 6 | 2065-09-12 | 2056-03-30 | 2014-07-12 07:30 | 3.3 | 0.17966 | A3: Inside Quadrant |  | 6.7 | 3.3 | 5 | 12.5 | 6 O'Clock | 200 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 12.8 | 13.3 | 12.5 | 13.1 | 0.35
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-17 | 300-PG-20005-03C03-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 6173 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 13.5 | CML-17 | CML: Reducing Tee | 6 | 2024-02-19 | 2022-03-17 | 2014-07-11 07:30 | 4.9 | 0.87352 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 13.8 | 13.5 | 13.3 | 13.4 | 0.21602
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44023-01C03-P | CML-2 | 250-PW-44023-01C03-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23037 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 12.5 | CML-2 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2015-05-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 12.3 | 6 O'Clock | 250 | 9.27 | 250-PW-44023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 | 0.23104 | 12.5 | 12.4 | 12.3 | 12.8 | 0.21602
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-20 | 50-DH-56062-01C02 CML-20 | yes | FPSO 2015 | Pipe Wall Thickness | 9107 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.5 | CML-20 | CML: type TBC | 3 | 2017-09-15 | 2018-03-02 | 2015-03-02 07:00 | 2.5 | 0.70797 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.5 | 4.3 | 4.4 | 4.8 | 0.21602
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-7 | 200-PW-44021-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23022 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 7.825 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-05 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 3 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 | 0.31291 | 8.5 | 7.5 | 7.7 | 7.6 | 0.45735
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-20 | 150-WC-40006-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 1680 | Rope Access | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.5 | CML-20 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 12 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8 | 9 | 9.2 | 0.70238
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5584 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 8.15 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 6 O'Clock | 20 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.3 | 8.4 | 7.5 | 8.4 | 0.43589
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20057-01C02-P | CML-2 | 100-PW-20057-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21839 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 6.85 | CML-2 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.8 | 6 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.9 | 6.8 | 6.9 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43122-01C02 | CML-2 | 50-FH-43122-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1760 | Rope access | 2014-04-27 08:30 | 2014-04-27 09:00 | [36 empty] | 5.2 | CML-2 | CML: Elbow | 3 | 2017-09-17 | 2018-03-04 | 2014-04-27 08:30 | 2.5 | 0.70712 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FH-43122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 5.2 | 5.4 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-9 | 80-FH-43158-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12890 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.3 | CML-9 | CML: type TBC | 3 | 2018-05-11 | 2018-12-07 | 2014-01-22 11:00 | 2.5 | 0.60457 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 12 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.6 | 5.3 | 5.2 | 0.21602
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45037-03C03 | CML-2 | 50-PL-45037-03C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10476 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 8.1 | CML-2 | CML: type TBC | 6 | 2017-08-10 | 2017-02-18 | 2013-11-14 | 0.99 | 1.847 | A3: Inside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.9 | 6 O'Clock | 50 | 8.74 | 50-PL-45037-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.91 |  | 8.2 | 8.2 | 7.9 | 8.1 | 0.14142
PG06 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PG-23008-15S01-A | CML-7 | 200-PG-23008-15S01-A CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 5793 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.3 | CML-7 | CML: Elbow | 3 | 2020-09-29 | 2021-07-13 | 2014-06-23 13:00 | 2.5 | 0.41441 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.2 | 5.6 | 5.1 | 0.21602
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12580 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.925 | CML-2 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-02-05 08:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.06 |  | 5.6 | 5.9 | 5.7 | 6.5 | 0.40311
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43302-01C02 | CML-2 | 50-FL-43302-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20455 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.5 | CML-2 | CML: Elbow | 3 | 2025-06-10 | 2026-09-25 | 2014-10-05 07:00 | 2.5 | 0.2526 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FL-43302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.7 | 5.5 | 5.2 | 0.21602
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42040-01S01 | CML-7 | 50-CI-42040-01S01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3087 | Rope Access | 2014-05-04 11:30 | 2014-05-04 12:00 | [36 empty] | 9.975 | CML-7 | CML: Reducer | 1 | 2043-10-24 | 2037-01-28 | 2014-05-04 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 9.6 | 3 O'Clock | 50 | 5.54 | 50-CI-42040-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.6 | 9.6 | 10.6 | 10.1 | 0.47871
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45037-03C03 | CML-3 | 50-PL-45037-03C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10477 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 8.825 | CML-3 | CML: type TBC | 6 | 2019-12-09 | 2019-03-15 | 2013-11-14 | 0.99 | 1.1873 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 8.2 | 3 O'Clock | 50 | 8.74 | 50-PL-45037-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.21 |  | 8.9 | 8.2 | 8.7 | 9.5 | 0.53774
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45037-03C03 | CML-1 | 50-PL-45037-03C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10475 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 8.625 | CML-1 | CML: type TBC | 6 | 2019-12-09 | 2019-03-15 | 2013-11-14 | 0.99 | 1.1873 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 8.2 | 9 O'Clock | 50 | 8.74 | 50-PL-45037-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.21 |  | 9.7 | 8.2 | 8.4 | 8.2 | 0.72284
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-25 | 250-WC-40017-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 2088 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 8.575 | CML-25 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 9.1 | 8.6 | 8.8 | 7.8 | 0.55603
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-13 | 50-FH-43450-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7692 | Re-check. FFS | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-13 13:50 | [32 empty] | 5.5 | CML-13 | CML: Pipe Length | 3 | 2027-10-10 | 2029-04-25 | 2015-01-08 13:00 | 2.5 | 0.21158 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0 | 5.7 | 5.2 | 5.6 | 5.5 | 0.21602
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45037-03C03 | CML-4 | 50-PL-45037-03C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10478 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 8.475 | CML-4 | CML: type TBC | 6 | 2021-06-02 | 2020-07-07 | 2013-11-14 | 0.99 | 0.96747 | A4: Left Quadrant |  | 2.74 | 0.99 | 1.865 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-PL-45037-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.31 |  | 8.5 | 8.6 | 8.5 | 8.3 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43128-01C02 | CML-1 | 50-FH-43128-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1800 |  | 2014-04-28 14:00 | 2014-04-28 14:30 | [36 empty] | 5.5 | CML-1 | CML: Fitting | 3 | 2021-07-13 | 2022-05-27 | 2014-04-28 14:00 | 2.5 | 0.37426 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FH-43128-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.6 | 5.2 | 5.7 | 0.21602
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-20 | 50-FG-45501-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6603 | Rope Access. No access to CML''s 21 - 41 due to Flare | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.5 | CML-20 | CML: Pipe Length | 3 | 2036-07-22 | 2039-01-15 | 2015-03-30 07:00 | 2.5 | 0.13128 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.5 | 5.8 | 0.21602
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-10 | 50-PL-45517-03C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21728 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 8.925 | CML-10 | CML: Elbow | 6 | 2023-04-16 | 2023-02-06 | 2014-09-29 13:00 | 2.5 | 0.63146 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.9 | 9.3 | 9.6 | 0.74106
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56107-01C02 | CML-4 | 80-DH-56107-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2043 |  | 2014-03-27 14:00 | 2014-03-27 14:30 | [36 empty] | 5.5 | CML-4 | CML: type TBC | 3 | 2026-04-28 | 2027-10-29 | 2014-03-27 14:00 | 2.5 | 0.23149 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 12 O'Clock | 80 | 5.49 | 80-DH-56107-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.8 | 5.5 | 5.4 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43106-01C02 | CML-4 | 100-FH-43106-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12773 |  | 2014-01-25 10:00 | 2014-01-25 11:00 | [36 empty] | 5.8 | CML-4 | CML: type TBC | 3 | 2018-11-20 | 2019-01-25 | 2014-01-25 10:00 | 2.5 | 0.64299 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 6 O'Clock | 100 | 6.02 | 100-FH-43106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.1 | 5.7 | 5.6 | 5.8 | 0.21602
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-9 | 50-PW-44015-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5719 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 8.125 | CML-9 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-06-22 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.6 | 12 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | -4.2287 | 7.6 | 8 | 9 | 7.9 | 0.60759
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38005-01C02 | CML-4 | 50-CG-38005-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3104 | Rope Access | 2014-05-04 10:00 | 2014-05-04 10:30 | [36 empty] | 6 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-04 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 15 | 5.54 | 50-CG-38005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6 | 6.3 | 5.9 | 0.21602
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-10 | 50-FG-45023-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1158 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.5 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | -5.3761 | 6.7 | 6.5 | 6.6 | 6.2 | 0.21602
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-16 | 50-FG-45023-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1164 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.5 | CML-16 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.2 | 6.7 | 6.5 | 0.21602
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-7 | 50-PW-44013-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5731 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 8.175 | CML-7 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-06-22 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.6 | 9 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | -4.3889 | 8.7 | 8.6 | 7.8 | 7.6 | 0.55603
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-5 | 150-FH-43157-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10661 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.7 | CML-5 | CML: type TBC | 3 | 2016-06-08 | 2016-03-14 | 2013-11-18 | 2.5 | 1.5244 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 12 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.7 | 6.9 | 6.8 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43126-01C02 | CML-2 | 100-FH-43126-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2511 | Rope Access | 2014-03-24 14:30 | 2014-03-24 15:00 | [36 empty] | 6.7 | CML-2 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-24 14:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.4 | 12 O'Clock | 100 | 6.02 | 100-FH-43126-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.9 | 6.8 | 6.7 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-8 | 200-FH-43004-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12548 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 7.5 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 12 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.5 | 7.6 | 7.7 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-10 | 200-FH-43003-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12533 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.5 | CML-10 | CML: Pipe Length | 3 | 2034-08-01 | 2032-01-05 | 2014-01-18 11:30 | 1.34 | 0.23652 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.2 | 12 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 6.2 | 6.7 | 6.6 | 6.5 | 0.21602
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-14 | 50-PG-23063-09C02 CML-14 | Yes | FPSO 2013 | Pipe Wall Thickness | 10739 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.6 | CML-14 | CML: type TBC | 3 | 2020-01-21 | 2018-05-01 | 2013-11-19 | 2.5 | 0.93918 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 3 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.7 | 8.3 | 8.6 | 8.8 | 0.21602
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-4 | 50-CG-38500-01C02 CML-4 | Yes | FPSO 2016 | Pipe Wall Thickness | 24491 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.8 | CML-4 | CML: Pipe Length | 3 | 2018-04-13 | 2018-10-21 | 2016-07-09 07:00 | 2.5 | 0.62427 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.6 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 | 0.19682 | 4.1 | 3.8 | 3.6 | 3.7 | 0.21602
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40014-01C02 | CML-3 | 50-WC-40014-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1550 | Rope Access | 2014-04-09 08:00 | 2014-04-09 09:00 | [36 empty] | 8.4333 | CML-3 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.8 | 6 O'Clock | 50 | 5.54 | 50-WC-40014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  |  | 8.7 | 7.8 | 8.8 | 0.55076
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-11 | 250-PW-20041-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21420 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.7 | CML-11 | CML: Reducer | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 13.4 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 13.5 | 14.4 | 13.5 | 13.4 | 0.46904
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-7 | 200-PW-44021-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7704 | Re-check. Line is FFS. | 2015-01-08 15:30 | 2015-01-08 16:30 |  |  | Administrator | 2015-09-13 11:02 | [32 empty] | 7.775 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-08 15:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 6 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | -1.5472 | 7.7 | 7.6 | 7.6 | 8.2 | 0.28723
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-31 | 300-PF-20501-03C03-P CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 21707 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.4 | CML-31 | CML: type TBC | 6 | 2190-11-25 | 2158-12-26 | 2014-09-28 07:00 | 4.9 | 0.05276 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.3 | 14.4 | 14.7 | 14.2 | 0.21602
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-13 | 50-PL-45517-03C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21731 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 8.55 | CML-13 | CML: Pipe Length | 6 | 2024-08-16 | 2024-05-29 | 2014-09-29 13:00 | 2.5 | 0.55629 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 3 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.8 | 8 | 8.8 | 8.6 | 0.37859
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57065-01C02 | CML-1 | 250-DC-57065-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23158 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 10.3 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 12 O'Clock | 250 | 6.35 | 250-DC-57065-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 | 1.9211 | 9.7 | 10.2 | 11.1 | 10.2 | 0.5831
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-21 | 300-PW-44003-01C03 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 22886 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 12.525 | CML-21 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 11.9 | 12 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 | 1.5052 | 11.9 | 12.2 | 13.6 | 12.4 | 0.74554
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-8 | 50-PL-45517-03C03 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21726 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 9.4 | CML-8 | CML: Elbow | 6 | 2026-05-18 | 2026-02-15 | 2014-09-29 13:00 | 2.5 | 0.48111 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 6 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 10.7 | 9.8 | 8.1 | 9 | 1.1106
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-6 | 50-PL-45517-03C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21724 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 8.625 | CML-6 | CML: Pipe Length | 6 | 2026-05-18 | 2026-02-15 | 2014-09-29 13:00 | 2.5 | 0.48111 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 9 | 9.2 | 8.2 | 0.55603
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-23 | 50-PL-23021-03C03 CML-23 |  | FPSO 2013 | Pipe Wall Thickness | 10255 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8 | CML-23 | CML: type TBC | 6 | 2016-01-17 | 2015-12-29 | 2013-11-08 | 2.5 | 2.3725 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.7 | 6 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.2 | 8 | 7.7 | 8.1 | 0.21602
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-9 | 400-WC-40060-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1057 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 8.175 | CML-9 | CML: type TBC | 3 | 2226-07-02 | 2199-11-11 | 2014-03-20 14:00 | 2.6 | 0.02495 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 7.9 | 6 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8 | 7.9 | 7.9 | 8.9 | 0.48563
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-2 | 150-FH-43027-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10564 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 8.2333 | CML-2 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2013-11-16 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8 | 6 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  |  | 8.3 | 8 | 8.4 | 0.20817
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-18 | 50-PL-45517-03C03 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21736 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 8.9 | CML-18 | CML: Elbow | 6 | 2028-10-10 | 2028-06-24 | 2014-09-29 13:00 | 2.5 | 0.40594 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 9 | 9.4 | 9 | 0.50332
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43076-01C02 | CML-3 | 150-FL-43076-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2344 | Rope Access | 2014-03-17 11:00 | 2014-03-17 11:30 | [36 empty] | 8.9333 | CML-3 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-03-17 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.7 | 9 O'Clock | 150 | 7.11 | 150-FL-43076-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9 |  | 9.1 | 8.7 | 0.20817
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-7 | 50-PL-45517-03C03 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21725 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 8.225 | CML-7 | CML: Pipe Length | 6 | 2028-10-10 | 2028-06-24 | 2014-09-29 13:00 | 2.5 | 0.40594 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 9 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.2 | 8.3 | 8.2 | 0.05
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-11 | 50-PL-23052-09C03 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10175 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 15.8333 | CML-11 | CML: type TBC | 6 | 2096-01-05 | 2084-09-16 | 2013-11-09 | 2.81 | 0 | A4: Left Quadrant |  | 5.07 | 2.81 | 3.94 | 15.6 | 9 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.79 |  |  | 16 | 15.9 | 15.6 | 0.20817
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-5 | 250-DC-57064-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20285 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 10.675 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 6 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10.1 | 10.8 | 9.7 | 12.1 | 1.0532
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-6 | 150-DC-57308-01C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20303 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 0.949mm/ yr | [35 empty] | 9.925 | CML-6 | CML: Equal Tee | 6 | 2022-05-01 | 2021-01-11 | 2014-10-02 07:00 | 2.5 | 0.94933 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 9.7 | 6 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10.2 | 9.8 | 9.7 | 10 | 0.22174
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-17 | 25-FG-45455-01C02-E CML-17 |  | FPSO 2016 | Pipe Wall Thickness | 24362 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 8.25 | CML-17 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 12 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.2 | 8.3 | 8.5 | 0.20817
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PG-20030-01C03-P | CML-2 | 50-PG-20030-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21670 | Protective mesh removed | 2014-06-26 09:30 | 2014-06-26 11:00 | [36 empty] | 8.75 | CML-2 | CML: type TBC | 6 | 2016-12-03 | 2016-05-21 | 2014-06-26 09:30 | 2.5 | 2.4589 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 8.5 | 3 O'Clock | 80 | 11.13 | 80-PG-20030-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9 | 8.5 | 8.8 | 8.7 | 0.20817
PL03 | Montara_Topside | Yes | Wellstream (57) | Pipework | 50-PL-57066-01C03 | CML-5 | 50-PL-57066-01C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22111 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 8.75 | CML-5 | CML: type TBC | 6 | 2049-04-24 | 2048-08-15 | 2014-10-18 07:00 | 2.5 | 0.17371 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-PF-57066-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 9 | 8.7 | 8.8 | 0.20817
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-20 | 250-PW-20040-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21404 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.55 | CML-20 | CML: Reducer | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 13.5 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 13.7 | 13.5 | 13.5 | 13.5 | 0.1
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-10 | 80-CG-38486-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21480 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 18.05 | CML-10 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-06-28 09:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.8 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.9 |  | 17.8 | 18.1 | 18.3 | 18 | 0.20817
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-21 | 200-PW-44018-01X01 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 12599 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.8 | CML-21 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-02-05 08:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.16 |  | 5.7 | 5.9 | 5.8 | 5.8 | 0.08165
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-16 | 250-PG-23003-06C02-PA CML-16 | yes | FPSO 2013 | Pipe Wall Thickness | 10544 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 4.85 | CML-16 | CML: type TBC | 3 | 2014-11-26 | 2014-11-22 | 2013-11-16 | 2.5 | 2.0423 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.8 | 4.9 | 5.1 | 0.20817
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45503-01C02 | CML-1 | 50-FG-45503-01C02 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 7736 | Line is FFS despite the High CR on CML-1 to 6. Current RBI frequency is 48m. Action: Inspect in 24m. RBI to be updated. | 2015-01-10 08:00 | 2015-01-10 10:00 |  |  | Administrator | 2015-09-21 14:30 | [32 empty] | 5.15 | CML-1 | CML: Elbow | 3 | 2021-01-24 | 2021-11-20 | 2015-01-10 08:00 | 2.5 | 0.39705 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FG-45503-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.2 | 5.4 | 5.1 | 0.20817
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-15 | 50-PL-45517-03C03 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21733 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 8.425 | CML-15 | CML: Pipe Length | 6 | 2032-04-07 | 2031-11-27 | 2014-09-29 13:00 | 2.5 | 0.33076 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.4 | 8.4 | 8.6 | 8.3 | 0.12583
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-14 | 50-PL-45517-03C03 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21732 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 8.575 | CML-14 | CML: Pipe Length | 6 | 2032-04-07 | 2031-11-27 | 2014-09-29 13:00 | 2.5 | 0.33076 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.6 | 8.7 | 8.7 | 0.1893
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-31 | 50-FG-45501-01C02 CML-31 | Yes | FPSO 2015 | Pipe Wall Thickness | 23550 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 5.35 | CML-31 | CML: Pipe Length | 3 | 2028-07-21 | 2030-03-06 | 2015-08-10 07:30 | 2.5 | 0.20067 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.4 | 5.6 | 5.1 | 0.20817
PG06 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PG-23008-15S01-A | CML-7 | 200-PG-23008-15S01-A CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 5775 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 5.35 | CML-7 | CML: Elbow | 3 | 2020-09-28 | 2021-07-13 | 2014-06-23 11:00 | 2.5 | 0.4145 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.3 | 5.6 | 5.1 | 0.20817
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-3 | 200-PW-44019-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21894 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 8.275 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 3 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9 | 7.7 | 8 | 8.4 | 0.56199
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-4 | 50-FH-43450-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7683 | Re-check. FFS. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:10 | [32 empty] | 5.35 | CML-4 | CML: Pipe Length | 3 | 2024-07-05 | 2025-09-13 | 2015-01-08 13:00 | 2.5 | 0.27381 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | -0.5245 | 5.3 | 5.6 | 5.1 | 5.4 | 0.20817
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43105-01C02 | CML-5 | 100-FH-43105-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12768 |  | 2014-01-25 09:00 | 2014-01-25 10:00 | [36 empty] | 6.15 | CML-5 | CML: type TBC | 3 | 2032-07-23 | 2033-03-11 | 2014-01-25 09:00 | 2.5 | 0.18374 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-FH-43105-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.4 | 5.9 | 6.1 | 0.20817
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-20 | 50-PL-45517-03C03 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21738 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 9.475 | CML-20 | CML: Elbow | 6 | 2047-12-24 | 2047-04-25 | 2014-09-29 13:00 | 2.5 | 0.18042 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 3 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.3 | 8.5 | 9.4 | 10.7 | 0.91059
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42044-01S01 | CML-1 | 50-CI-42044-01S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3455 | Rope Access | 2014-05-13 08:00 | 2014-05-13 09:00 | [36 empty] | 9.95 | CML-1 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2014-05-13 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 9.7 | 12 O'Clock | 50 | 5.54 | 50-CI-42044-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 9.9 | 10.1 | 10.1 | 0.19149
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-17 | 50-PL-45517-03C03 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21735 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 9.15 | CML-17 | CML: Elbow | 6 | 2047-12-24 | 2047-04-25 | 2014-09-29 13:00 | 2.5 | 0.18042 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 6 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10.5 | 8.6 | 8.5 | 9 | 0.92556
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-6 | 80-PW-44001-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23215 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 7.825 | CML-6 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.3 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 | 2.0957 | 8.8 | 7.5 | 7.3 | 7.7 | 0.6702
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-3 | 50-FG-45023-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1151 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.35 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 | -6.5707 | 6.4 | 6.1 | 6.6 | 6.3 | 0.20817
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-9 | 50-FG-45301-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5795 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.85 | CML-9 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 3 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.6 | 6.9 | 7.1 | 0.20817
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43505-01C02 | CML-1 | 150-FH-43505-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20466 | Rope Access | 2014-05-27 13:00 | 2014-05-27 14:00 | [36 empty] | 7.15 | CML-1 | CML: type TBC | 3 |  |  | 2014-05-27 13:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.9 | 6 O'Clock | 150 |  | 150-FH-43505-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.1 | 7.2 | 6.9 | 7.4 | 0.20817
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-5 | 150-FG-45505-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22341 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.85 | CML-5 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.6 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.8 | 7.9 | 7.6 | 8.1 | 0.20817
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-16 | 250-PG-23003-06C02-PA CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10683 | Deck Level | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-13 13:55 | [32 empty] | 4.85 | CML-16 | CML: Pipe Length | 3 | 2014-11-29 | 2015-01-27 | 2013-11-17 | 2.5 | 2.0302 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.1 | 4.9 | 4.8 | 0.20817
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-3 | 200-PW-44019-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5569 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 8.275 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 3 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9 | 7.7 | 8 | 8.4 | 0.56199
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-3 | 200-PW-44018-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23040 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 7.95 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 9 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 | -0.34128 | 8 | 8.3 | 7.8 | 7.7 | 0.26458
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-21 | 100-PW-20021-01C02-P CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 22839 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 7.475 | CML-21 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-04-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.3 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 | 0.54478 | 7.5 | 7.6 | 7.5 | 7.3 | 0.12583
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56066-01C02 | CML-3 | 50-DH-56066-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3280 | Rope Access | 2014-05-09 14:00 | 2014-05-09 15:00 | [36 empty] | 5.05 | CML-3 | CML: type TBC | 3 | 2017-04-08 | 2017-09-06 | 2014-05-09 14:00 | 2.5 | 0.78842 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56066-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 5.3 | 5 | 4.8 | 0.20817
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-5 | 50-FG-45019-03C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2596 | Rope Access | 2014-04-26 08:00 | 2014-04-26 09:00 | [36 empty] | 5.05 | CML-5 | CML: type TBC | 3 | 2017-02-12 | 2017-02-04 | 2014-04-26 08:00 | 2.5 | 0.82014 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.89938 | 4.8 | 5.1 | 5 | 5.3 | 0.20817
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-14 | 200-PW-44018-01X01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12592 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 6.0333 | CML-14 | CML: Elbow | 3 | 2062-11-29 | 2056-08-05 | 2014-02-05 08:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.8 | 12 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.26 |  | 5.8 | 6.4 | 5.9 |  | 0.32146
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44029-01C02 | CML-1 | 250-PW-44029-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21905 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 7.55 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 3 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.7 | 7.4 | 7.5 | 7.6 | 0.1291
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56113-01C02 | CML-3 | 50-DH-56113-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5242 | Rope Access | 2014-05-20 14:00 | 2014-05-20 15:00 | [36 empty] | 5.25 | CML-3 | CML: Elbow | 3 | 2018-11-12 | 2019-06-14 | 2014-05-20 14:00 | 2.5 | 0.55744 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DH-56113-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 5.5 | 5.2 | 0.20817
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-5 | 100-DC-57038-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2368 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 10.2 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.7 | 9 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 10.7 | 10.7 | 9.7 | 0.57735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-15 | 50-FH-43450-01C02 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10682 | Deck Level | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-13 13:52 | [32 empty] | 5.25 | CML-15 | CML: Elbow | 3 | 2016-01-08 | 2016-04-19 | 2013-11-17 | 2.5 | 1.1663 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.5 | 5.3 | 5 | 0.20817
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-1 | 50-PL-45517-03C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21719 |  | 2014-09-29 08:30 | 2014-09-29 11:30 | [36 empty] | 9.1 | CML-1 | CML: Elbow | 6 | 2047-12-19 | 2047-04-20 | 2014-09-29 08:30 | 2.5 | 0.18049 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.9 | 9.8 | 9.2 | 0.54772
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-3 | 50-PL-45517-03C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21721 |  | 2014-09-29 08:30 | 2014-09-29 11:30 | [36 empty] | 8.825 | CML-3 | CML: Pipe Length | 6 | 2072-08-22 | 2071-07-03 | 2014-09-29 08:30 | 2.5 | 0.10528 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9 | 9 | 8.7 | 0.20616
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-12 | 250-PW-44006-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8004 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 8.775 | CML-12 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 | 1.3381 | 9.5 | 9 | 7.8 | 8.8 | 0.71356
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-19 | 50-PL-45517-03C03 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21737 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 9.35 | CML-19 | CML: Elbow | 6 | 2220-10-18 | 2216-10-22 | 2014-09-29 13:00 | 2.5 | 0.03007 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.7 | 6 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 10 | 9.2 | 8.7 | 9.5 | 0.54467
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57077-15C02 | CML-6 | 50-DC-57077-15C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10366 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 3.068mm/ yr | [35 empty] | 11.075 | CML-6 | CML: type TBC | 3 | 2016-03-16 | 2015-07-11 | 2013-11-11 | 2.5 | 3.0678 | A1: Outside Quadrant |  | 8.07 | 2.5 | 4.5931 | 9.7 | 12 O'Clock | 50 | 11.07 | 50-DC-57077-15C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 10.7 | 10.7 | 13.2 | 1.493
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57077-15C02 | CML-4 | 50-DC-57077-15C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10364 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 3.068mm/ yr | [35 empty] | 11.4 | CML-4 | CML: type TBC | 3 | 2016-03-16 | 2015-07-11 | 2013-11-11 | 2.5 | 3.0678 | A1: Outside Quadrant |  | 8.07 | 2.5 | 4.5931 | 9.7 | 12 O'Clock | 50 | 11.07 | 50-DC-57077-15C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 11.9 | 11.6 | 12.4 | 1.1804
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57076-25C02 | CML-6 | 50-DC-57076-25C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10359 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 3.068mm/ yr | [35 empty] | 10.05 | CML-6 | CML: type TBC | 3 | 2016-03-16 | 2015-04-20 | 2013-11-11 | 2.5 | 3.0678 | A1: Outside Quadrant |  | 8.07 | 2.5 | 5.285 | 9.7 | 12 O'Clock | 50 | 11.07 | 50-DC-57076-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 10.2 | 9.8 | 10.5 | 0.36968
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-5 | 50-PL-45517-03C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21723 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 9.025 | CML-5 | CML: Pipe Length | 6 | 2075-10-24 | 2074-08-12 | 2014-09-29 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.8 | 6 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.9 | 9.4 | 8.8 | 9 | 0.263
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-4 | 50-PL-45517-03C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21722 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 9.075 | CML-4 | CML: Pipe Length | 6 | 2075-10-24 | 2074-08-12 | 2014-09-29 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.8 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9.3 | 9.1 | 9.1 | 0.20616
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56004-01C02 | CML-2 | 80-DH-56004-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3405 | Rope Access | 2014-05-11 07:00 | 2014-05-11 09:00 | [36 empty] | 5.75 | CML-2 | CML: type TBC | 3 |  |  | 2014-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.5 | 6 O'Clock | 100 |  | 100-DH-56004-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6 | 5.8 | 5.5 | 5.7 | 0.20817
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-10 | 100-FL-43455-01C02-P CML-10 | Yes | FPSO 2014 | Pipe Wall Thickness | 20493 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 5.75 | CML-10 | CML: Reducer | 3 | 2022-06-26 | 2022-10-13 | 2014-10-03 07:00 | 2.5 | 0.38791 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 6 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6 | 5.7 | 5.5 | 5.8 | 0.20817
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-13 | 25-FG-45455-01C02-E CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2076 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 6.25 | CML-13 | CML: type TBC | 3 | 2022-06-18 | 2022-05-25 | 2014-03-28 09:30 | 2.5 | 0.42527 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.3 | 6.2 | 6.5 | 0.20817
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-6 | 50-FG-45024-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1210 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.55 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 12 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.6 | 6.8 | 6.5 | 0.20817
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57017-01C02 | CML-6 | 20-DC-57017-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2901 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 7.475 | CML-6 | CML: type TBC | 3 | 2067-05-31 | 2058-11-20 | 2014-04-25 08:00 | 0.16 | 0 | A3: Inside Quadrant |  | 2.56 | 0.16 | 1.0125 | 7.4 | 9 O'Clock | 20 | 5.56 | 20-DC-57017-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.24 |  | 7.6 | 7.5 | 7.4 | 7.4 | 0.095743
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43300-01C02-E | CML-3 | 200-PL-43300-01C02-E CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8589 | Line is FFS. Current RBI frequency is 36m. Action: CML’s to Inspect in 48m. RBI to be updated | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-08 14:57 | [32 empty] | 6.725 | CML-3 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2015-02-08 11:00 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.5 | 9 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.16 |  | 6.5 | 7.3 | 6.6 | 6.5 | 0.38622
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-1 | 50-DH-56056-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20118 | Rope Access | 2014-05-07 07:00 | 2014-05-07 08:00 | [36 empty] | 4.95 | CML-1 | CML: type TBC | 3 | 2016-10-14 | 2017-02-23 | 2014-05-07 07:00 | 2.5 | 0.90099 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.2 | 4.9 | 5 | 0.20817
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-11 | 50-PL-45517-03C03 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21729 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 9.875 | CML-11 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-09-29 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9.3 | 11.1 | 10.2 | 0.98107
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-1 | 50-DH-56056-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3166 | Rope Access | 2014-05-07 07:00 | 2014-05-07 08:00 | [36 empty] | 4.95 | CML-1 | CML: type TBC | 3 | 2016-10-14 | 2017-02-23 | 2014-05-07 07:00 | 2.5 | 0.90099 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.2 | 4.9 | 5 | 0.20817
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-2 | 250-DC-57064-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23088 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 10.4 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.8 | 6 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 | -0.70192 | 11.1 | 10.5 | 9.8 | 10.2 | 0.54772
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56064-01C02 | CML-5 | 50-DH-56064-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3275 | Rope Access | 2014-05-09 13:00 | 2014-05-09 14:00 | [36 empty] | 5.05 | CML-5 | CML: type TBC | 3 | 2017-04-08 | 2017-09-06 | 2014-05-09 13:00 | 2.5 | 0.78852 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56064-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 5 | 4.8 | 5.3 | 0.20817
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-VA-23056-01C02 | CML-7 | 50-VA-23056-01C02 CML-7 | High Priority | FPSO 2015 | Pipe Wall Thickness | 8067 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 5.25 | CML-7 | CML: type TBC | 3 | 2022-09-01 | 2023-08-30 | 2015-01-22 07:30 | 2.5 | 0.32833 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-VA-23056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.5 | 5.2 | 5.3 | 0.20817
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-7 | 100-PW-20021-01C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22825 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 7.4 | CML-7 | CML: Reducer | 3 | 2048-08-12 | 2049-10-10 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.4 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | -1.8159 | 7.4 | 7.4 | 7.4 | 7.4 | 0
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-11 | 50-FH-43450-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 7690 | Re-check. FFS | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 21:02 | [32 empty] | 5.45 | CML-11 | CML: Pipe Length | 3 | 2027-10-10 | 2029-04-25 | 2015-01-08 13:00 | 2.5 | 0.21158 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.5245 | 5.5 | 5.4 | 5.2 | 5.7 | 0.20817
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67010-01E01 | CML-4 | 50-GN-67010-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8707 |  | 2015-02-14 07:00 | 2015-02-14 09:00 | [36 empty] | 10.125 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.8 | 6 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.4 | 10 | 9.8 | 10.3 | 0.27538
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-12 | 50-CG-38458-01C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23740 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.45 | CML-12 | CML: Pipe Length | 3 | 2034-12-27 | 2037-04-21 | 2015-10-30 07:00 | 2.5 | 0.14082 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.5 | 5.7 | 5.2 | 0.20817
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-6 | 200-FH-43038-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12687 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 6.45 | CML-6 | CML: type TBC | 3 | 2031-01-04 | 2030-11-18 | 2014-02-06 09:00 | 2.5 | 0.21867 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.5 | 6.7 | 6.2 | 0.20817
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-5 | 400-WC-40060-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1053 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 8.35 | CML-5 | CML: type TBC | 3 | 2226-07-02 | 2199-11-11 | 2014-03-20 14:00 | 2.6 | 0.02495 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 7.9 | 3 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.7 | 7.9 | 8.7 | 8.1 | 0.41231
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-7 | 250-DC-57064-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20287 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 10.3 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.8 | 12 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.8 | 10 | 11.1 | 10.3 | 0.57155
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-17 | 50-FG-45302-01C02 CML-17 | Yes | FPSO 2014 | Pipe Wall Thickness | 5785 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 6.55 | CML-17 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 25 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.8 | 6.3 | 6.5 | 6.6 | 0.20817
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 200-PG-23504-15S01 | CML-2 | 200-PG-23504-15S01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20762 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [35 empty] | Low alarm breach | 20.775 | CML-2 | CML: Elbow | 1 | 2018-08-02 | 2016-04-06 | 2014-09-27 07:00 | 13.2 | 1.8957 | A4: Left Quadrant |  | 22.01 | 13.2 | 17.605 | 20.5 | 9 O'Clock | 200 | 23.01 | 200-PG-23504-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 20.9 | 20.9 | 20.8 | 20.5 | 0.1893
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43124-01C02 | CML-9 | 80-FH-43124-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12851 |  | 2014-02-05 11:00 | 2014-02-05 13:00 | [36 empty] | 5.75 | CML-9 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-02-05 11:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-FH-43124-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 5.5 | 6 | 5.8 | 5.7 | 0.20817
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-9 | 100-PG-23503-03C03-A CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2725 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.95 | CML-9 | CML: Pipe Length | 6 | 2023-05-10 | 2023-11-02 | 2014-03-13 09:00 | 5.66 | 0.54998 | A4: Left Quadrant |  | 5.13 | 5.66 | 5.395 | 10.7 | 9 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.04 |  | 10.9 | 11.2 | 11 | 10.7 | 0.20817
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-3 | 100-FG-45001-09C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10418 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.05 | CML-3 | CML: type TBC | 3 | 2015-08-07 | 2015-01-06 | 2013-11-13 | 4.7 | 2.9421 | A4: Left Quadrant |  | 8.13 | 4.7 | 6.415 | 9.8 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 10 | 10.1 | 10.3 | 9.8 | 0.20817
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40005-01C02 | CML-6 | 150-WC-40005-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3159 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 8.2 | CML-6 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.8 | 12 O'Clock | 150 | 7.11 | 150-WC-40005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.1 | 8.5 | 8.4 | 0.31623
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-1 | 200-PW-44020-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5591 |  | 2014-06-19 14:00 | 2014-06-19 15:00 | [36 empty] | 8.3 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 12 O'Clock | 200 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.2 | 9.1 | 8.1 | 0.55976
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-20 | 50-PF-20300-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21586 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 8.85 | CML-20 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.8 | 9.1 | 8.6 | 8.9 | 0.20817
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-4 | 50-WC-40451-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3066 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | [36 empty] | 8.075 | CML-4 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-03 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.8 | 9 O'Clock | 100 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 | -6.2452 | 8.2 | 8.4 | 7.9 | 7.8 | 0.27538
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40044-01C02 | CML-6 | 300-WC-40044-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1121 |  | 2014-03-21 11:30 | 2014-03-21 12:00 | [36 empty] | 8.05 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-21 11:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 3 O'Clock | 300 | 6.35 | 300-WC-40044-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.3 | 7.8 | 8.1 | 8 | 0.20817
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40038-01C02 | CML-2 | 200-WC-40038-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7710 |  | 2015-01-09 10:00 | 2015-01-09 12:00 | [36 empty] | 8.025 | CML-2 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2015-01-09 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 3 O'Clock | 200 | 6.35 | 200-WC-40038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.2 | 7.8 | 8.1 | 8 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-18 | 150-WC-40004-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1820 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 7.9 | CML-18 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-29 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.8 | 6 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.1 | 7.8 | 7.9 | 0.14142
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-19 | 300-PF-20500-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21639 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.15 | CML-19 | CML: Pipe Length | 6 | 2046-12-04 | 2040-11-24 | 2014-09-27 07:00 | 4.9 | 0.27944 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 3 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.1 | 13.9 | 14.2 | 14.4 | 0.20817
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-21 | 300-PG-20506-03C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 13235 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.15 | CML-21 | CML: type TBC | 6 | 2030-08-27 | 2027-07-22 | 2014-02-04 15:00 | 4.9 | 0.54319 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 6 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.4 | 14.2 | 13.9 | 14.1 | 0.20817
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-2 | 300-PG-20506-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13216 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.65 | CML-2 | CML: type TBC | 6 | 2107-02-11 | 2090-04-05 | 2014-02-04 15:00 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.4 | 3 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 14.7 | 14.4 | 14.6 | 14.9 | 0.20817
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-9 | 50-PL-45517-03C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21727 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 9.525 | CML-9 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-09-29 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9.2 | 10.2 | 9.8 | 0.58523
CG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-CG-38459-09C02-P | CML-8 | 80-CG-38459-09C02-P CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10423 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 16.5333 | CML-8 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2013-11-13 | 4.7 | 0 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 16.3 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.6 |  |  | 16.3 | 16.6 | 16.7 | 0.20817
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-15 | 100-DC-57038-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2378 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 10.925 | CML-15 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.8 | 12 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.8 | 10.6 | 10.9 | 12.4 | 1.0874
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-6 | 100-DC-57037-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2357 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 10.7 | CML-6 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.8 | 12 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.8 | 10.8 | 10.4 | 11.8 | 0.84063
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-4 | 100-DC-57037-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2355 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 10.475 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.8 | 12 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.8 | 10.5 | 10.6 | 11 | 0.49917
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-14 | 100-DC-57307-01C03 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2322 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | [36 empty] | 10.4 | CML-14 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 9.8 | 9 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  |  | 11 | 10.4 | 9.8 | 0.6
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-1 | 150-FG-45505-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22337 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 8.025 | CML-1 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.8 | 3 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8 | 7.8 | 8 | 8.3 | 0.20616
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-16 | 50-PL-45517-03C03 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21734 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 9.7 | CML-16 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-09-29 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.4 | 10.5 | 9.9 | 0.64807
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-12 | 50-PL-45517-03C03 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21730 |  | 2014-09-29 13:00 | 2014-09-29 15:45 | [36 empty] | 11.5 | CML-12 | CML: Reducing Tee | 6 | 2075-10-24 | 2074-08-12 | 2014-09-29 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 10.5 | 12 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.5 | 12 | 11.7 | 11.8 | 0.67823
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PL-45517-03C03 | CML-2 | 50-PL-45517-03C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21720 |  | 2014-09-29 08:30 | 2014-09-29 11:30 | [36 empty] | 17.2 | CML-2 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-09-29 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 15.3 | 3 O'Clock | 50 | 8.74 | 50-PL-45517-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.8 |  | 20.5 | 15.3 | 17.3 | 15.7 | 2.3636
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-26 | 250-WC-40017-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 2089 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 7.925 | CML-26 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 3 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8 | 7.8 | 7.9 | 8 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-8 | 50-PW-44015-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22713 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 8.15 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-04-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.8 | 12 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 | -1.0601 | 7.8 | 8.2 | 8.7 | 7.9 | 0.40415
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-17 | 250-PW-44006-01X01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23188 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 8.225 | CML-17 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 12 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 | 1.3161 | 7.8 | 8.5 | 8.6 | 8 | 0.38622
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-7 | 80-FH-43005-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12557 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 5.775 | CML-7 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-20 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 5.6 | 5.6 | 6 | 0.20616
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-8 | 100-PW-20021-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21811 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 8.5 | CML-8 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.5 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 9.3 | 8.1 | 9.1 | 7.5 | 0.84853
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57077-15C02 | CML-3 | 50-DC-57077-15C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10363 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 2.844mm/ yr | [35 empty] | 10.775 | CML-3 | CML: type TBC | 3 | 2016-06-04 | 2015-09-10 | 2013-11-11 | 2.5 | 2.8439 | A1: Outside Quadrant |  | 8.07 | 2.5 | 4.5931 | 9.8 | 12 O'Clock | 50 | 11.07 | 50-DC-57077-15C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.8 | 10 | 12.3 | 11 | 1.1442
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57076-25C02 | CML-4 | 50-DC-57076-25C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10357 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 2.844mm/ yr | [35 empty] | 10.3 | CML-4 | CML: type TBC | 3 | 2016-06-04 | 2015-06-13 | 2013-11-11 | 2.5 | 2.8439 | A4: Left Quadrant |  | 8.07 | 2.5 | 5.285 | 9.8 | 9 O'Clock | 50 | 11.07 | 50-DC-57076-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.4 | 10.4 | 10.6 | 9.8 | 0.34641
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57076-25C02 | CML-2 | 50-DC-57076-25C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10355 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 2.844mm/ yr | [35 empty] | 10.1 | CML-2 | CML: type TBC | 3 | 2016-06-04 | 2015-06-13 | 2013-11-11 | 2.5 | 2.8439 | A4: Left Quadrant |  | 8.07 | 2.5 | 5.285 | 9.8 | 9 O'Clock | 50 | 11.07 | 50-DC-57076-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.2 | 10 | 10.4 | 9.8 | 0.2582
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-2 | 150-PG-23043-06C02-P CML-2 | yes | FPSO 2016 | Pipe Wall Thickness | 23764 | re-check line | 2016-02-13 07:00 | 2016-02-13 15:00 | [36 empty] | 8.275 | CML-2 | CML: Elbow | 3 | 2019-04-27 | 2018-06-05 | 2016-02-13 07:00 | 4.7 | 1.061 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.1 | 9 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 0 | 8.5 | 8.1 | 8.4 | 8.1 | 0.20616
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-2 | 150-PG-23043-06C02-P CML-2 | yes | FPSO 2016 | Pipe Wall Thickness | 24153 | re-check line | 2016-02-13 | 2016-02-13 | [36 empty] | 8.275 | CML-2 | CML: Elbow | 3 | 2019-04-27 | 2018-06-04 | 2016-02-13 | 4.7 | 1.0614 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.1 | 9 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 1.0751 | 8.5 | 8.1 | 8.4 | 8.1 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-12 | 200-WC-40008-01C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 7818 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 7.85 | CML-12 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.9 | 7.8 | 7.9 | 7.8 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43127-01C02 | CML-3 | 150-FH-43127-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1796 | Rope access | 2014-04-28 10:30 | 2014-04-28 12:00 | [36 empty] | 7.225 | CML-3 | CML: Fitting | 3 | 2051-06-12 | 2048-06-20 | 2014-04-28 10:30 | 2.5 | 0.12114 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 3 O'Clock | 150 | 7.11 | 150-FH-43127-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7 | 7.4 | 7.4 | 0.20616
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-11 | 50-CG-38452-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2255 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 7.275 | CML-11 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.1 | 3 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.1 | 7.4 | 7.5 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-19 | 400-WC-40024-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1088 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.975 | CML-19 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8 | 9 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9.2 | 9.4 | 9.3 | 8 | 0.65511
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-48 | 350-FL-43512-01C02 CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 23559 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.775 | CML-48 | CML: Pipe Length | 3 | 2050-07-12 | 2045-08-19 | 2015-08-10 07:30 | 2.5 | 0.14594 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.6 | 3 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 7.6 | 7.9 | 8 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-9 | 400-WC-40024-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1078 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.775 | CML-9 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8 | 9 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9 | 9.1 | 9 | 8 | 0.51881
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-15 | 300-PW-44003-01C03 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21857 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 12.65 | CML-15 | CML: Reducer | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 12 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 13.7 | 12 | 12.4 | 12.5 | 0.73258
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-8 | 50-PL-23022-03C03 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1864 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.875 | CML-8 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.7 | 9 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10.1 | 10 | 9.7 | 9.7 | 0.20616
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-5 | 100-PG-23071-01C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2403 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 10.375 | CML-5 | CML: type TBC | 6 | 2022-03-12 | 2020-11-30 | 2014-03-19 13:00 | 2.5 | 0.96401 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.2 | 6 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.2 | 10.6 | 10.2 | 10.5 | 0.20616
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-34 | 300-PF-20001-03C03-P CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 21172 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 14.375 | CML-34 | CML: Fitting | 6 | 2163-10-16 | 2136-09-30 | 2014-07-16 07:30 | 4.9 | 0.06227 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.5 | 14.6 | 14.2 | 14.2 | 0.20616
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-10 | 300-PG-20005-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 6166 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.725 | CML-10 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.5 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 14.9 | 14.5 | 14.6 | 14.9 | 0.20616
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40500-1CG | CML-12 | 400-WC-40500-1CG CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 5680 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [36 empty] | 19.4 | CML-12 | CML: Reducing Tee | 3 | 2020-03-19 | 2017-05-09 | 2014-06-21 14:00 | 2.5 | 2.7831 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 18.5 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16 |  | 18.6 | 19.5 | 21 | 18.5 | 1.1576
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23050-25C02-P | CML-1 | 80-PG-23050-25C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2736 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 14.275 | CML-1 | CML: Pipe Length | 3 | 2096-09-16 | 2070-01-23 | 2014-03-13 09:00 | 2.8 | 0 | A1: Outside Quadrant |  | 8.13 | 2.8 | 5.465 | 14.1 | 3 O'Clock | 80 | 11.13 | 80-PG-23050-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 14.1 | 14.1 | 14.4 | 14.5 | 0.20616
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-4 | 80-CG-38459-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21327 | Protective mesh removed | 2014-06-27 09:30 | 2014-06-27 10:30 | [36 empty] | 14.625 | CML-4 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-06-27 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 14.4 | 3 O'Clock | 100 | 11.13 | 80-PG-20027-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 |  | 14.8 | 14.4 | 14.5 | 14.8 | 0.20616
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38300-01C02-P |  | 50-CG-38300-01C02-P | yes | FPSO 2014 | Pipe Wall Thickness | 22095 | Rope access | 2014-06-02 08:00 | 2014-06-02 09:00 |  |  | Administrator | 2015-09-07 10:57 | [32 empty] | 4.975 | 50-CG-38300-01C02-P | Piping | 3 | 2017-07-14 |  | 2014-06-02 08:00 |  | 0.73731 | A1: Outside Quadrant |  |  | 2.5 |  | 4.8 | 3 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 4.8 | 4.8 | 4.8 | 5.2 | 5.1 | 0.20616
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-9 | 50-PL-23514-01C03 CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 8642 | This CML is on a straight piping section. It appears that CML-10 together with CML-8 & 9 below are located in the same spool. This spool was confirmed to have being wrongly fabricated with Sched. Extra strong (NWT: 5.54 mm) instead of sched. 160 (NWT: 8.74). | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:21 | [32 empty] | 5.175 | CML-9 | CML: Pipe Length | 6 | 2016-03-30 | 2016-03-10 | 2015-02-10 11:30 | 2.5 | 2.2036 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 5 | 6 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5 | 5 | 5.3 | 0.20616
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-9 | 50-FG-45021-03C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2621 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.325 | CML-9 | CML: type TBC | 3 | 2019-08-25 | 2019-08-10 | 2014-04-26 10:45 | 2.5 | 0.48748 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | -1.3565 | 5.1 | 5.5 | 5.2 | 5.5 | 0.20616
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML 1 | 200-PW-44021-01X01 CML 1 |  | FPSO 2014 | Pipe Wall Thickness | 22365 |  | 2014-06-19 13:00 | 2014-06-19 14:00 | [36 empty] | 8.3 | CML 1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 12 O'Clock | 200 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.2 | 8.6 | 8.6 | 0.38297
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-17 | 250-PW-44004-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 5636 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 8.075 | CML-17 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-06-20 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 3 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.5 | 8.8 | 8.5 | 0.67515
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-7 | 50-FL-43454-01C02-P CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 20510 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.825 | CML-7 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 5.6 | 6 | 5.7 | 0.20616
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45004-03C02 | CML-6 | 150-FG-45004-03C02 CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24338 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.025 | CML-6 | CML: Pipe Length | 3 | 2024-01-10 | 2022-03-04 | 2016-06-06 07:00 | 2.5 | 0.43417 | A1: Outside Quadrant |  | 4.11 | 2.5 | 3.305 | 5.8 | 12 O'Clock | 20 | 7.11 | 150-FG-45004-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.2 | 6.2 | 5.9 | 0.20616
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56087-01C02 | CML-5 | 100-DH-56087-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8035 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:31 | [32 empty] | 6.025 | CML-5 | CML: Pipe Length | 3 | 2039-08-21 | 2040-07-02 | 2015-01-20 14:30 | 2.5 | 0.13415 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 12 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.2 | 6.2 | 5.9 | 0.20616
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-5 | 250-DC-57064-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23091 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 10.4 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 6 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 | -0.35096 | 11.1 | 10.5 | 9.9 | 10.1 | 0.52915
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-29 | 50-FG-45023-01C02 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 1177 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 5.975 | CML-29 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.1 | 5.8 | 6.2 | 0.20616
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-26 | 50-FG-45023-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 1174 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.325 | CML-26 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.5 | 6.1 | 6.5 | 0.20616
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-3 | 50-DC-57450-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20319 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 10.925 | CML-3 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.9 | 9 O'Clock | 40 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 11.4 | 11.3 | 11.1 | 9.9 | 0.69462
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21792 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 10.5 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 9.9 | 3 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.4 | 9.9 | 10.7 | 11 | 0.46904
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-10 | 50-PL-24003-09C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 13149 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.65 | CML-10 | CML: type TBC | 3 | 2041-09-02 | 2034-05-02 | 2014-01-18 13:00 | 2.5 | 0.22069 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 3 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.6 | 8.7 | 8.7 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-10 | 200-FH-43037-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12679 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 6.475 | CML-10 | CML: type TBC | 3 | 2066-03-20 | 2065-10-30 | 2014-02-06 11:00 | 2.5 | 0.07287 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.6 | 6.3 | 6.7 | 6.3 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-7 | 400-WC-40060-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1055 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 8.4 | CML-7 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-20 14:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8 | 12 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8 | 8.5 | 9 | 8.1 | 0.45461
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-21 | 400-WC-40024-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 1090 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.625 | CML-21 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8 | 3 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.7 | 8 | 8.8 | 9 | 0.43493
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43125-01C02 | CML-2 | 200-FH-43125-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2756 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 6.825 | CML-2 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-13 09:00 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.6 | 9 O'Clock | 200 | 6.35 | 200-FH-43125-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.26 |  | 6.7 | 7 | 7 | 6.6 | 0.20616
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-8 | 250-PG-23004-06C03-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13008 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.475 | CML-8 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 19.2 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.65 |  | 19.2 | 19.5 | 19.5 | 19.7 | 0.20616
FH01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-FH-43141-01C02 | CML-2 | 150-FH-43141-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 5001 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [35 empty] | Low alarm breach | 3.575 | CML-2 | CML: type TBC | 0 | 2036-09-11 | 2030-07-16 | 2015-03-03 07:00 | 2.5 | 0.03714 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.3 | 12 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.6 | 3.8 | 3.6 | 0.20616
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-11 | 50-FG-45019-03C02 CML-11 | yes | FPSO 2013 | Pipe Wall Thickness | 10493 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.875 | CML-11 | CML: type TBC | 3 | 2014-11-23 | 2014-11-19 | 2013-11-15 | 2.5 | 2.0545 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.9 | 4.9 | 5.1 | 0.20616
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-10 | 250-PG-23003-06C02-PA CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2452 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 5.625 | CML-10 | CML: type TBC | 3 | 2030-10-19 | 2032-08-30 | 2014-03-20 09:30 | 2.5 | 0.17476 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.6 | 5.9 | 5.6 | 0.20616
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-11 | 200-PG-23013-09C03-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10995 | Rope Access | 2014-01-10 | 2014-01-10 | [35 empty] | Low alarm breach | 14.275 | CML-11 | CML: Elbow | 6 | 2014-05-17 | 2014-03-04 | 2014-01-10 | 10.22 | 10.8354 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 14 | 9 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.78 |  | 14.3 | 14.5 | 14.3 | 14 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40005-01C02 | CML-3 | 150-WC-40005-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3156 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 8.35 | CML-3 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-05-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.9 | 6 O'Clock | 150 | 7.11 | 150-WC-40005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.7 | 8.1 | 7.9 | 8.7 | 0.41231
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5660 | Rope access | 2014-06-21 11:00 | 2014-06-21 12:00 | [36 empty] | 8.875 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-21 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.6 | 6 O'Clock | 200 | 6.35 | 200-FH-43503-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.9 | 8.9 | 8.6 | 9.1 | 0.20616
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-8 | 300-PG-20502-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 23895 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 9.975 | CML-8 | CML: Pipe Length | 6 | 2030-04-27 | 2028-05-12 | 2014-09-26 07:00 | 2.5 | 0.46165 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 9 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10 | 10.2 | 10 | 9.7 | 0.20616
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-8 | 300-PG-20502-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20755 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 9.975 | CML-8 | CML: type TBC | 6 | 2030-04-27 | 2028-05-12 | 2014-09-26 07:00 | 2.5 | 0.46165 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 9 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10 | 10.2 | 10 | 9.7 | 0.20616
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-7 | 300-PG-20005-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 6163 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 12.725 | CML-7 | CML: Pipe Length | 6 | 2019-04-16 | 2018-03-26 | 2014-07-11 07:30 | 4.9 | 1.594 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.5 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 12.5 | 12.7 | 12.7 | 13 | 0.20616
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-21 | 300-PF-20501-03C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21697 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.375 | CML-21 | CML: Pipe Length | 6 | 2086-07-01 | 2073-05-09 | 2014-09-28 07:00 | 4.9 | 0.12813 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 14.4 | 14.1 | 14.6 | 14.4 | 0.20616
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-10 | 150-PG-20054-01C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21521 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 12.775 | CML-10 | CML: Reducer | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 12.5 | 12 O'Clock | 200 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 12.5 | 12.8 | 12.8 | 13 | 0.20616
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23302-01C02 | CML-5 | 80-VA-23302-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22521 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.775 | CML-5 | CML: Pipe Length | 3 | 2016-03-31 | 2016-07-29 | 2015-04-20 07:00 | 2.5 | 1.0553 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.5 | 12 O'Clock | 50 | 5.49 | 80-VA-23302-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.5 | 4 | 3.8 | 3.8 | 0.20616
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-7 | 200-PG-23008-15S01-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3277 | Rope Access | 2014-05-09 13:00 | 2014-05-09 14:00 | [36 empty] | 5.325 | CML-7 | CML: type TBC | 3 | 2019-11-23 | 2020-08-03 | 2014-05-09 13:00 | 2.5 | 0.46885 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DH-56064-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.6 | 5.1 | 5.3 | 0.20616
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML 7 | 200-PW-44021-01X01 CML 7 |  | FPSO 2014 | Pipe Wall Thickness | 22371 |  | 2014-06-19 13:00 | 2014-06-19 14:00 | [36 empty] | 8.15 | CML 7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 6 O'Clock | 200 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.2 | 8.6 | 7.8 | 8 | 0.34157
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-8 | 50-PL-24003-09C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13147 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.65 | CML-8 | CML: type TBC | 3 | 2041-09-02 | 2034-05-02 | 2014-01-18 13:00 | 2.5 | 0.22069 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.7 | 8.6 | 8.7 | 0.057735
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-7 | 50-DH-56070-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3223 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 4.825 | CML-7 | CML: type TBC | 3 | 2016-06-11 | 2016-10-08 | 2014-05-09 07:00 | 2.5 | 1.0024 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.1 | 4.6 | 4.8 | 4.8 | 0.20616
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-7 | 50-CG-38470-01C02-P CML-7 | Yes | FPSO 2015 | Pipe Wall Thickness | 23613 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 4.825 | CML-7 | CML: Elbow | 3 | 2021-03-14 | 2022-01-13 | 2015-10-28 07:00 | 2.5 | 0.3902 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.8 | 4.8 | 5.1 | 4.6 | 0.20616
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-4 | 50-CG-38470-01C02-P CML-4 | Yes | FPSO 2015 | Pipe Wall Thickness | 23610 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 4.825 | CML-4 | CML: Elbow | 3 | 2021-03-14 | 2022-01-13 | 2015-10-28 07:00 | 2.5 | 0.3902 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.1 | 4.8 | 4.8 | 4.6 | 0.20616
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-21 | 50-DH-56137-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21105 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 4.925 | CML-21 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 4.7 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 4.9 | 4.9 | 4.7 | 0.20616
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38455-01C02-H | CML-6 | 50-CG-38455-01C02-H CML-6 | High Priority | FPSO 2015 | Pipe Wall Thickness | 23690 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.075 | CML-6 | CML: Elbow | 3 | 2023-04-30 | 2024-05-22 | 2015-10-30 07:00 | 2.5 | 0.30648 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 80 | 5.54 | 50-CG-38455-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 4.8 | 5.1 | 5.1 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-7 | 100-WC-40035-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1740 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 8.3333 | CML-7 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.9 | 9 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.7 | 8.4 |  | 7.9 | 0.40415
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-2 | 50-FG-45019-03C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2593 | Rope Access | 2014-04-26 08:00 | 2014-04-26 09:00 | [36 empty] | 5.025 | CML-2 | CML: type TBC | 3 | 2017-02-12 | 2017-02-04 | 2014-04-26 08:00 | 2.5 | 0.82014 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.89938 | 4.8 | 5 | 5 | 5.3 | 0.20616
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43020-01C02 | CML-3 | 80-FH-43020-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12615 |  | 2014-01-23 07:00 | 2014-01-23 08:00 | [36 empty] | 5.225 | CML-3 | CML: type TBC | 3 | 2017-05-12 | 2017-10-27 | 2014-01-23 07:00 | 2.5 | 0.7569 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 3 O'Clock | 80 | 5.49 | 80-FH-43020-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5.2 | 5.5 | 0.20616
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-5 | 200-PW-44020-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5595 |  | 2014-06-19 14:00 | 2014-06-19 15:00 | [36 empty] | 8.05 | CML-5 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 6 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.9 | 8.3 | 7.8 | 8.2 | 0.23805
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-9 | 150-FG-45002-03C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10412 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 10.4333 | CML-9 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 9.9 | 6 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.9 | 10.5 | 9.9 |  | 0.50332
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57076-25C02 | CML-3 | 50-DC-57076-25C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10356 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 2.62mm/ yr | [35 empty] | 11.575 | CML-3 | CML: type TBC | 3 | 2016-09-06 | 2015-08-15 | 2013-11-11 | 2.5 | 2.6199 | A1: Outside Quadrant |  | 8.07 | 2.5 | 5.285 | 9.9 | 12 O'Clock | 50 | 11.07 | 50-DC-57076-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 11.1 | 11.6 | 13.7 | 1.5861
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-14 | 250-PW-44006-01X01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23185 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 7.975 | CML-14 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 | 1.9741 | 7.8 | 8.1 | 8.2 | 7.8 | 0.20616
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-2 | 100-VA-80006-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2171 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 5.475 | CML-2 | CML: type TBC | 3 | 2016-12-20 | 2017-02-01 | 2014-03-30 13:00 | 2.5 | 0.98929 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.2 | 5.5 | 5.5 | 0.20616
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-3 | 50-PL-24003-09C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13142 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.65 | CML-3 | CML: type TBC | 3 | 2041-09-02 | 2034-05-02 | 2014-01-18 13:00 | 2.5 | 0.22069 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.7 | 8.6 | 8.7 | 0.057735
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43301-01C02 | CML-1 | 50-FL-43301-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20451 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.525 | CML-1 | CML: Fitting | 3 | 2030-06-15 | 2032-04-12 | 2014-10-05 07:00 | 2.5 | 0.17831 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-FL-43301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.5 | 5.3 | 5.8 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40013-01C02 | CML-8 | 50-WC-40013-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1563 | Rope Access | 2014-04-09 10:00 | 2014-04-09 11:00 | [36 empty] | 8.1667 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  |  | 8.6 | 8 | 7.9 | 0.37859
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1975 |  | 2014-03-26 14:00 | 2014-03-26 15:00 | [36 empty] | 5.675 | CML-3 | CML: type TBC | 3 | 2031-03-02 | 2033-01-26 | 2014-03-26 14:00 | 2.5 | 0.17114 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56104-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.7 | 5.7 | 5.4 | 0.20616
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-4 | 50-FL-43454-01C02-P CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 20507 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.675 | CML-4 | CML: Pipe Length | 3 | 2042-08-16 | 2045-10-03 | 2014-10-05 07:00 | 2.5 | 0.10401 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 5.9 | 5.7 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-5 | 200-WC-40008-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7811 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 8.225 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 9 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.4 | 8.5 | 8.1 | 7.9 | 0.27538
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-7 | 250-PW-44006-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7999 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 9.725 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 2.4328 | 7.9 | 10.5 | 10.1 | 10.4 | 1.2285
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-3 | 50-FG-45024-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1186 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.425 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 3 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.7 | 6.4 | 0.20616
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43120-01C02 | CML-1 | 200-FH-43120-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12835 |  | 2014-02-06 07:00 | 2014-02-06 09:00 | [36 empty] | 6.575 | CML-1 | CML: type TBC | 3 | 2066-03-07 | 2065-10-17 | 2014-02-06 07:00 | 2.5 | 0.07291 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 3 O'Clock | 200 | 6.35 | 200-FH-43120-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.6 | 6.3 | 6.8 | 6.6 | 0.20616
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-1 | 50-PL-24003-09C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13140 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.65 | CML-1 | CML: type TBC | 3 | 2041-09-02 | 2034-05-02 | 2014-01-18 13:00 | 2.5 | 0.22069 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.6 | 8.7 | 8.6 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43306-01C02 | CML-2 | 80-FH-43306-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5761 | Rope access | 2014-06-23 09:30 | 2014-06-23 11:00 | [36 empty] | 5.175 | CML-2 | CML: Elbow | 3 | 2022-04-25 | 2021-03-06 | 2014-06-23 09:30 | 0.54 | 0.55589 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-FH-43306-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.36 |  | 5.4 | 4.9 | 5.2 | 5.2 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-16 | 50-WC-40451-01C02 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10156 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 8.25 | CML-16 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2013-11-09 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.3 | 8.5 | 8.3 | 0.25166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43109-01C02 | CML-6 | 200-FH-43109-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12790 |  | 2014-01-18 14:30 | 2014-01-18 15:30 | [36 empty] | 6.575 | CML-6 | CML: Pipe Length | 3 | 2076-12-13 | 2069-03-28 | 2014-01-18 14:30 | 1.34 | 0.0788 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.3 | 6 O'Clock | 200 | 6.35 | 200-FH-43109-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 6.8 | 6.6 | 6.3 | 6.6 | 0.20616
FH02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23062-25S01 | CML-4 | 50-PG-23062-25S01 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 20596 | Rope Access | 2014-05-26 14:00 | 2014-05-26 15:00 | [36 empty] | 8.925 | CML-4 | CML: type TBC | 1 | 2058-06-15 | 2048-03-29 | 2014-05-26 14:00 | 6.91 | 0.0406 | A1: Outside Quadrant |  | 7.74 | 6.91 | 7.325 | 8.7 | 12 O'Clock | 50 | 8.74 | 50-PG-23062-25S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.79 |  | 8.7 | 8.8 | 9.1 | 9.1 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40005-01C02 | CML-5 | 150-WC-40005-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3158 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 8.125 | CML-5 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.9 | 12 O'Clock | 150 | 7.11 | 150-WC-40005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.4 | 8 | 8.2 | 0.22174
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-31 | 250-PW-44006-01X01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 8023 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 9.125 | CML-31 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 1.3381 | 9.7 | 7.9 | 9.6 | 9.3 | 0.83417
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-9 | 400-FH-43508-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6558 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 8.925 | CML-9 | CML: Pipe Length | 3 | 2062-08-12 | 2057-12-18 | 2015-03-30 07:00 | 3 | 0 | A4: Left Quadrant |  | 4.92 | 3 | 3.465 | 8.7 | 9 O'Clock | 500 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.9 | 9.2 | 8.9 | 8.7 | 0.20616
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-22 | 80-SC-55002-01C02-P CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 8852 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 11.225 | CML-22 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 10 | 3 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 12.3 | 10 | 11.3 | 11.3 | 0.94296
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57303-03C03 | CML-6 | 20-DC-57303-03C03 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7931 |  | 2015-01-17 10:30 | 2015-01-17 12:00 | [36 empty] | 13.55 | CML-6 | CML: type TBC | 6 | 2044-01-06 | 2058-09-17 | 2015-01-17 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | -0.44 | 2.5 | 1.03 | 10 | 12 O'Clock | 20 | 5.56 | 20-DC-57303-03C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 13.3 | 15.5 | 15.4 | 2.5749
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43084-01C02 | CML-1 | 150-FL-43084-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2566 | Rope Access | 2014-04-08 07:30 | 2014-04-08 08:30 | [36 empty] | 8.425 | CML-1 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-04-08 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.2 | 3 O'Clock | 150 | 7.11 | 150-FL-43084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.4 | 8.2 | 8.4 | 8.7 | 0.20616
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24036-09C02 | CML-3 | 50-PL-24036-09C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13162 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 8.625 | CML-3 | CML: type TBC | 3 | 2041-09-05 | 2034-05-05 | 2014-01-18 15:00 | 2.5 | 0.22062 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.6 | 8.7 | 8.6 | 0.05
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-19 | 250-PW-44006-01X01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8011 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 8.55 | CML-19 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 0.36492 | 9 | 8.6 | 8.7 | 7.9 | 0.46547
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-18 | 50-CG-38500-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23305 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.875 | CML-18 | CML: Elbow | 3 | 2016-09-09 | 2017-01-15 | 2015-07-04 09:30 | 2.5 | 0.92757 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.6 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 | -0.2135 | 4.1 | 3.9 | 3.6 | 3.9 | 0.20616
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21796 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 10.575 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 10 | 3 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 11.5 | 10 | 10.4 | 10.4 | 0.64485
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-17 | 250-PW-44006-01X01 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1914 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 8.375 | CML-17 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 12 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.4 | 8.2 | 9 | 0.46458
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-6 | 200-PW-44020-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23013 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 8.125 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-05 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 9 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | -2.055 | 8.1 | 8.6 | 7.9 | 7.9 | 0.3304
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43021-01C02 | CML-1 | 80-FH-43021-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12617 |  | 2014-01-27 07:00 | 2014-01-27 08:00 | [36 empty] | 5.575 | CML-1 | CML: Pipe Length | 3 | 2035-04-10 | 2037-10-25 | 2014-01-27 07:00 | 2.5 | 0.13671 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FH-43021-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.7 | 5.4 | 5.4 | 0.20616
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-8 | 200-PL-20020-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21312 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 9.125 | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 3 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.9 | 8.7 | 8.9 | 9 | 0.53151
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-8 | 80-FH-43007-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12569 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.575 | CML-8 | CML: Pipe Length | 3 | 2048-03-30 | 2043-10-19 | 2014-01-18 07:00 | 0.54 | 0.14203 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.7 | 5.4 | 5.4 | 5.8 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-1 | 400-WC-40060-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1049 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 8.3 | CML-1 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-20 14:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8 | 9 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.5 | 8.4 | 8.3 | 8 | 0.21602
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-15 | 50-WC-40451-01C02 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10155 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 8.15 | CML-15 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2013-11-09 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 3 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.1 | 7.9 | 8.2 | 8.4 | 0.20817
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-8 | 50-FG-45018-03C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10507 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.925 | CML-8 | CML: type TBC | 3 | 2015-01-26 | 2015-01-22 | 2013-11-15 | 2.5 | 1.8359 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.8 | 4.7 | 5.1 | 5.1 | 0.20616
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-2 | 200-PW-44019-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21893 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 8.475 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8.5 | 8 | 9.1 | 0.46458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-14 | 50-FH-43450-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7693 | Re-check. FFS | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-13 13:50 | [32 empty] | 5.875 | CML-14 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-01-08 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | -0.78675 | 5.7 | 6.1 | 6 | 5.7 | 0.20616
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38460-01C02-P | CML-4 | 80-CG-38460-01C02-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 20885 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.875 | CML-4 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 9 O'Clock | 80 | 5.49 | 80-CG-38460-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.1 | 6 | 5.7 | 0.20616
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43102-01C02 | CML-6 | 100-FH-43102-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12751 |  | 2014-01-24 08:00 | 2014-01-24 09:00 | [36 empty] | 5.875 | CML-6 | CML: type TBC | 3 | 2020-07-24 | 2020-10-18 | 2014-01-24 08:00 | 2.5 | 0.49213 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-FH-43102-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.1 | 6 | 5.7 | 0.20616
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38489-01C02-P | CML-6 | 50-CG-38489-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20863 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 7.975 | CML-6 | CML: Reducer | 3 | 2031-10-25 | 2041-01-28 | 2014-10-02 07:00 | 3.7 | 0 | A1: Outside Quadrant |  | 2.54 | 3.7 | 2.7738 | 7.8 | 9 O'Clock | 80 | 5.54 | 50-CG-38489-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.8 | 8.1 | 8.2 | 7.8 | 0.20616
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-2 | 200-PW-44019-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5568 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 8.475 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 6 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8.5 | 8 | 9.1 | 0.46458
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45028-03C02-E | CML-4 | 80-FG-45028-03C02-E CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24328 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.375 | CML-4 | CML: Equal Tee | 3 | 2053-09-17 | 2048-07-24 | 2016-06-01 07:00 | 1.46 | 0 | A2: Right Quadrant |  | 2.49 | 1.46 | 1.975 | 7.2 | 6 O'Clock | 80 | 5.49 | 80-FG-45028-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.74 |  | 7.6 | 7.2 | 7.2 | 7.5 | 0.20616
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-1 | 50-PL-23020-01C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10115 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 7.975 | CML-1 | CML: type TBC | 6 | 2016-01-17 | 2015-12-29 | 2013-11-08 | 2.5 | 2.3725 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.7 | 3 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8 | 7.7 | 8 | 8.2 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-4 | 200-WC-40008-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7810 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 8.175 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 9 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.4 | 8.2 | 8.2 | 7.9 | 0.20616
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-17 | 50-CG-38452-09C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 3015 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.525 | CML-17 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.3 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.69 | 0 | 8.3 | 8.7 | 8.4 | 8.7 | 0.20616
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-17 | 50-CG-38452-09C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 22294 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.525 | CML-17 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.3 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.69 |  | 8.3 | 8.7 | 8.4 | 8.7 | 0.20616
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-24 | 250-PG-23004-06C03-A CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 20535 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 17.8 | CML-24 | CML: Pipe Length | 6 | 2030-09-01 | 2027-05-16 | 2014-05-30 09:30 | 8.55 | 0.56247 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 17.7 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.15 | -0.52605 | 18.1 | 17.7 | 17.7 | 17.7 | 0.2
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43020-01C02 | CML-4 | 80-FH-43020-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12616 |  | 2014-01-23 07:00 | 2014-01-23 08:00 | [36 empty] | 16.9 | CML-4 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-23 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 16.7 | 12 O'Clock | 80 | 5.49 | 80-FH-43020-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.2 |  | 16.7 | 16.9 | 17.1 |  | 0.2
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-8 | 100-DC-57038-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2371 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 10.5 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10 | 12 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 11.4 | 10.3 | 10.3 | 0.61644
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-3 | 100-DC-57038-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2366 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 10.325 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 10 | 3 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.4 | 10 | 10.4 | 10.5 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-11 | 100-DC-57037-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2362 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 10.575 | CML-11 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10 | 6 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 11 | 10 | 11.3 | 0.67515
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-47 | 400-FH-43508-01C02 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 23566 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 25.575 | CML-47 | CML: Pipe Length | 3 | 2041-09-09 | 2037-12-17 | 2015-08-10 07:30 | 2.5 | 0.19155 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.5 | 12 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.9 | 7.9 | 7.9 | 0.2
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-7 | 50-FG-45019-03C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10489 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.1 | CML-7 | CML: type TBC | 3 | 2015-04-18 | 2015-04-13 | 2013-11-15 | 2.5 | 1.6174 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 4.8 | 5.2 | 5.2 | 0.2
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-5 | 50-FG-45020-03C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10577 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.1 | CML-5 | CML: type TBC | 3 | 2016-01-08 | 2016-01-02 | 2013-11-17 | 2.5 | 1.1663 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5 | 5.4 | 0.2
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43021-01C02 | CML-2 | 80-FH-43021-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12618 |  | 2014-01-27 07:00 | 2014-01-27 08:00 | [36 empty] | 5.7 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-01-27 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 9 O'Clock | 80 | 5.49 | 80-FH-43021-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 6 | 5.6 | 0.2
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57077-15C02 | CML-9 | 50-DC-57077-15C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10369 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 2.396mm/ yr | [35 empty] | 10.375 | CML-9 | CML: type TBC | 3 | 2016-12-27 | 2016-02-12 | 2013-11-11 | 2.5 | 2.396 | A2: Right Quadrant |  | 8.07 | 2.5 | 4.5931 | 10 | 3 O'Clock | 50 | 11.07 | 50-DC-57077-15C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.9 | 10 | 10.2 | 10.4 | 0.38622
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57077-15C02 | CML-8 | 50-DC-57077-15C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10368 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 2.396mm/ yr | [35 empty] | 10.8 | CML-8 | CML: type TBC | 3 | 2016-12-27 | 2016-02-12 | 2013-11-11 | 2.5 | 2.396 | A1: Outside Quadrant |  | 8.07 | 2.5 | 4.5931 | 10 | 12 O'Clock | 50 | 11.07 | 50-DC-57077-15C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 10.4 | 11 | 11.8 | 0.78316
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57076-25C02 | CML-7 | 50-DC-57076-25C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10360 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 2.396mm/ yr | [35 empty] | 11.5 | CML-7 | CML: type TBC | 3 | 2016-12-27 | 2015-10-30 | 2013-11-11 | 2.5 | 2.396 | A1: Outside Quadrant |  | 8.07 | 2.5 | 5.285 | 10 | 12 O'Clock | 50 | 11.07 | 50-DC-57076-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 11.5 | 11.1 | 13.4 | 1.4166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43036-01C02 | CML-3 | 100-FH-43036-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12667 |  | 2014-01-26 10:00 | 2014-01-26 11:00 | [36 empty] | 5.9 | CML-3 | CML: type TBC | 3 | 2018-11-28 | 2019-02-02 | 2014-01-26 10:00 | 2.5 | 0.64031 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 3 O'Clock | 100 | 6.02 | 100-FH-43036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 5.6 | 6 | 6 | 0.2
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-5 | 80-PW-44001-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21996 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.975 | CML-5 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.5 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.9 | 8.6 | 7.9 | 0.45735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-13 | 50-FH-43011-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7963 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.1 | CML-13 | CML: Fitting | 3 | 2018-01-09 | 2017-06-01 | 2015-01-18 08:00 | 2.5 | 1.1752 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 6 | 9 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.4 | 6 | 6 | 0.2
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20016-01C02-P | CML-6 | 200-PL-20016-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21237 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 9.125 | CML-6 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 6 O'Clock | 200 | 6.35 | 200-PL-20016-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.1 | 9.1 | 8.7 | 9.6 | 0.36856
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-10 | 50-FG-45302-01C02 CML-10 | Yes | FPSO 2014 | Pipe Wall Thickness | 5778 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 6.9 | CML-10 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 25 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.8 | 7.2 | 6.8 | 0.2
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40404-01C02 | CML-3 | 150-WC-40404-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20393 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 8.1 | CML-3 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-10-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.9 | 9 O'Clock | 150 | 7.11 | 150-WC-40404-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.3 | 8.2 | 8 | 7.9 | 0.18257
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40403-01C02 | CML-1 | 100-WC-40403-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20381 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 8.75 | CML-1 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 8 | 9 O'Clock | 100 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 9.2 | 9.4 | 8.4 | 8 | 0.66081
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38495-01C02 | CML-2 | 25-CG-38495-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10398 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.9 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2013-11-12 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 6 O'Clock | 25 | 6.35 | 25-CG-38495-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 | 6.8 | 6.8 | 6.8 | 6.8 | 7.2 | 0.2
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-10 | 50-PF-20301-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 3008 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.8 | CML-10 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.5 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.89 | 0 | 8.5 | 8.9 | 8.9 | 8.9 | 0.2
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-10 | 50-PF-20301-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 22287 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.8 | CML-10 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.5 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.89 |  | 8.5 | 8.9 | 8.9 | 8.9 | 0.2
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43030-01C02 | CML-2 | 400-FH-43030-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10026 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 8 | CML-2 | CML: type TBC | 3 | 2129-03-01 | 2113-11-23 | 2013-11-04 | 2.5 | 0.04679 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 6 O'Clock | 400 | 7.92 | 400-FH-43030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 7.9 | 7.9 | 8.3 | 0.2
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-13 | 200-FH-43012-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2843 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.4 | CML-13 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.96 |  | 7.7 | 7.3 | 7.3 | 7.3 | 0.2
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-5 | 50-PL-23516-03C03 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7793 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:03 | [32 empty] | 8.8 | CML-5 | CML: Elbow | 6 | 2055-07-04 | 2054-09-11 | 2015-01-13 07:00 | 2.5 | 0.14815 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.9 | 8.9 | 8.9 | 8.5 | 0.2
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-9 | 100-PG-23028-25C02-P CML-9 | Yes | FPSO 2014 | Pipe Wall Thickness | 20554 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 15.9 | CML-9 | CML: Pipe Length | 3 | 2018-06-20 | 2016-12-03 | 2014-05-30 09:30 | 9.4 | 1.5267 | A1: Outside Quadrant |  | 14.12 | 9.4 | 11.76 | 15.6 | 12 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 | 0.4619 | 15.6 | 16 | 16 | 16 | 0.2
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-13 | 50-PL-23022-03C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1869 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.3 | CML-13 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 3 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.4 | 9 | 9.4 | 9.4 | 0.2
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-18 | 50-PL-24003-09C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 13157 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.8 | CML-18 | CML: type TBC | 3 | 2112-04-23 | 2086-08-20 | 2014-01-18 13:00 | 2.5 | 0.06306 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 3 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 8.7 | 9 | 8.8 | 0.14142
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-5 | 50-PL-24003-09C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13144 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 8.7 | CML-5 | CML: type TBC | 3 | 2112-04-23 | 2086-08-20 | 2014-01-18 13:00 | 2.5 | 0.06306 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 8.7 | 8.7 | 8.7 | 0
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-9 | 150-WC-40006-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20687 | Rope Access | 2014-05-26 13:00 | 2014-05-26 14:00 | [36 empty] | 10.725 | CML-9 | CML: type TBC | 3 | 2020-08-15 | 2018-09-19 | 2014-05-26 13:00 | 4.7 | 0.88321 | A3: Inside Quadrant |  | 8.07 | 4.7 | 6.385 | 10.2 | 6 O'Clock | 50 | 11.07 | 50-PG-23061-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 11.6 | 10.7 | 10.2 | 10.4 | 0.61847
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-11 | 150-PG-20054-01C03-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23352 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 12.8 | CML-11 | CML: Fitting | 6 | 2098-02-09 | 2085-10-05 | 2015-07-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 12.5 | 9 O'Clock | 200 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 | -0.37556 | 12.9 | 12.9 | 12.9 | 12.5 | 0.2
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML57 | 150-FL-43174-01C02 CML57 |  | FPSO 2015 | Pipe Wall Thickness | 7589 |  | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 17:09 | [32 empty] | 3.8 | CML57 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.9 | 3.5 | 3.9 | 3.9 | 0.2
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-6 | 250-DC-57064-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23092 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 10.325 | CML-6 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.1 | 9 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 | -2.4567 | 10.3 | 10.6 | 10.3 | 10.1 | 0.20616
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-1 | 80-CG-38459-09C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23698 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.5 | CML-1 | CML: Pipe Length | 3 | 2019-01-03 | 2019-08-29 | 2015-10-30 07:00 | 2.5 | 0.53427 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.2 | 3 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.6 | 4.2 | 4.6 | 4.6 | 0.2
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-24 | 250-WC-40017-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 2087 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 8.475 | CML-24 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 3 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.1 | 8 | 9.2 | 8.6 | 0.55
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42309-01S01 | CML-6 | 40-CI-42309-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7502 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 10.825 | CML-6 | CML: type TBC | 1 | 2059-10-24 | 2046-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 6.14 | 2.5 | 3.8737 | 10.1 | 9 O'Clock | 40 | 7.14 | 40-CI-42309-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 11.1 | 10.4 | 11.7 | 10.1 | 0.71822
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-14 | 150-WC-40006-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1655 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 8.775 | CML-14 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8 | 12 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 9 | 9.2 | 8.9 | 0.53151
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-13 | 400-WC-40060-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1061 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 8.825 | CML-13 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-20 14:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.1 | 6 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 9 | 9.1 | 8.1 | 9.1 | 0.48563
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PL-20051-01C02-P | CML-2 | 150-PL-20051-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21506 | Protective mesh removed | 2014-06-30 08:00 | 2014-06-30 09:00 | [36 empty] | 7.15 | CML-2 | CML: Fitting | 3 | 288673 | 241722 | 2014-06-30 08:00 | 0.84 | 0.00926 | A1: Outside Quadrant |  | 4.11 | 0.84 | 2.0306 | 7.1 | 6 O'Clock | 150 | 7.11 | 150-PL-20051-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.26 |  | 7.1 | 7.1 | 7.1 | 7.3 | 0.1
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-11 | 80-DC-57002-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20240 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 10.325 | CML-11 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 10.1 | 3 O'Clock | 20 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.3 | 10.1 | 10.7 | 10.2 | 0.263
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43091-01C02 | CML-6 | 80-FL-43091-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5831 | Rope access | 2014-06-24 10:30 | 2014-06-24 12:00 | [36 empty] | 7.2 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-24 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.9 | 12 O'Clock | 80 | 5.49 | 80-FL-43091-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.3 | 7.3 | 7.3 | 0.2
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43116-01C02 | CML-2 | 150-FH-43116-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7866 | Line is FFS. It has been check twice. The higher values reported here are from the data collected in Apr. 2014. The rechecked CR’s from data from Jan. 2015 are lower. Current RBI frequency is 48m. Action: to recheck line in a 24m (Jan. 2017) to confirm CR. | 2015-01-14 09:30 | 2015-01-14 10:30 |  |  | Administrator | 2015-09-07 17:04 | [32 empty] | 7.3 | CML-2 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2015-01-14 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 6 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 | 0.41817 | 7.2 | 7.2 | 7.2 | 7.6 | 0.2
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43030-01C02 | CML-3 | 400-FH-43030-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10027 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.9 | CML-3 | CML: type TBC | 3 | 2032-09-15 | 2030-02-28 | 2013-11-04 | 2.5 | 0.28077 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.8 | 6 O'Clock | 400 | 7.92 | 400-FH-43030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.8 | 7.8 | 8.2 | 0.2
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-10 | 50-PL-23023-03C03 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10210 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.1 | CML-10 | CML: type TBC | 6 | 2016-04-28 | 2016-04-07 | 2013-11-08 | 2.5 | 2.1444 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.8 | 6 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.2 | 8.2 | 7.8 | 8.2 | 0.2
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-21 | 150-PG-23506-25C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 2795 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.4 | CML-21 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 22.1 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.22 |  | 22.5 | 22.5 | 22.5 | 22.1 | 0.2
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-3 | 50-PL-23300-09C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13119 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.6 | CML-3 | CML: type TBC | 6 | 2020-09-15 | 2019-09-17 | 2014-02-04 07:00 | 2.81 | 1.1319 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.3 | 12 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.49 |  | 10.3 | 10.7 | 10.7 | 10.7 | 0.2
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-5 | 300-PG-20502-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 23892 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.4 | CML-5 | CML: Pipe Length | 6 | 418095 | 374448 | 2014-09-26 07:00 | 2.5 | 0.00757 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.3 | 9 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 10.7 | 10.3 | 10.3 | 0.2
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-5 | 300-PG-20502-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20752 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.4 | CML-5 | CML: type TBC | 6 | 418095 | 374448 | 2014-09-26 07:00 | 2.5 | 0.00757 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.3 | 9 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 10.7 | 10.3 | 10.3 | 0.2
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-15 | 100-PG-23028-25C02-P CML-15 | Yes | FPSO 2014 | Pipe Wall Thickness | 20558 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 15.85 | CML-15 | CML: Pipe Length | 3 | 2018-10-28 | 2017-03-03 | 2014-05-30 09:30 | 9.4 | 1.4263 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 15.7 | 9 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 | -0.4619 | 15.9 | 15.7 | 16.1 | 15.7 | 0.19149
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-9 | 50-DH-56137-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5450 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 3.576mm/ yr | [34 empty] | Low alarm breach | 18.15 | CML-9 | CML: Straight | 3 | 2018-09-16 | 2016-06-24 | 2014-05-28 07:00 | 2.5 | 3.5763 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.9 | 12 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 |  | 17.9 | 18.3 | 18.3 | 18.1 | 0.19149
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-13 | 300-PG-20502-01C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 23900 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 11.15 | CML-13 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 10.9 | 9 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.1 | 11.3 | 11.3 | 10.9 | 0.19149
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-13 | 300-PG-20502-01C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20760 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 11.15 | CML-13 | CML: type TBC | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 10.9 | 9 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.1 | 11.3 | 11.3 | 10.9 | 0.19149
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-34 | 50-CG-38001-09C02 CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 10949 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.35 | CML-34 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0.89186 | A1: Outside Quadrant |  | 5.74 |  |  | 8.2 | 6 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.2 | 8.2 | 8.4 | 8.2 | 8.6 | 0.19149
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-10 | 50-WC-40028-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1690 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 8.2667 | CML-10 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8 | 3 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.6 | 8 | 8.2 |  | 0.30551
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-6 | 50-PL-23516-03C03 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7794 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:03 | [32 empty] | 9.35 | CML-6 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2015-01-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.2 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.6 | 9.4 | 9.2 | 9.2 | 0.19149
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40035-01C02 | CML-15 | 100-WC-40035-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1748 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 8.4 | CML-15 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8 | 12 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.6 | 8.4 | 8.6 | 0.28284
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-1 | 50-FG-45019-03C02 CML-1 | yes | FPSO 2013 | Pipe Wall Thickness | 10483 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.65 | CML-1 | CML: type TBC | 3 | 2014-10-02 | 2014-09-28 | 2013-11-15 | 2.5 | 2.2731 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.5 | 4.9 | 4.7 | 0.19149
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-9 | 100-DC-57038-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2372 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 10.475 | CML-9 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.1 | 12 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.1 | 10.9 | 10.5 | 10.4 | 0.3304
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-7 | 100-DC-57038-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2370 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 10.65 | CML-7 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.1 | 12 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.1 | 11.2 | 11 | 10.3 | 0.53229
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-3 | 300-PW-44002-01X01-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22849 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 8.375 | CML-3 | CML: Elbow | 6 | 2019-11-21 | 2019-02-20 | 2015-05-01 07:00 | 2.5 | 1.2057 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 8 | 9 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 | 2.2347 | 8.9 | 8.3 | 8.3 | 8 | 0.37749
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-7 | 50-FG-45018-03C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10506 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.95 | CML-7 | CML: type TBC | 3 | 2015-04-18 | 2015-04-13 | 2013-11-15 | 2.5 | 1.6174 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 5.2 | 4.8 | 4.8 | 0.19149
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-10 | 50-FG-45020-03C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10582 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.05 | CML-10 | CML: type TBC | 3 | 2015-04-26 | 2015-04-21 | 2013-11-17 | 2.5 | 1.5982 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5 | 4.8 | 5.2 | 0.19149
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-3 | 50-FG-45020-03C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10575 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.05 | CML-3 | CML: type TBC | 3 | 2015-04-26 | 2015-04-21 | 2013-11-17 | 2.5 | 1.5982 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.2 | 5 | 5.2 | 0.19149
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-5 | 50-FG-45018-03C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2587 | Rope Access | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 5.25 | CML-5 | CML: type TBC | 3 | 2018-06-28 | 2018-06-16 | 2014-04-26 07:00 | 2.5 | 0.59856 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0 | 5 | 5.4 | 5.2 | 5.4 | 0.19149
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57077-15C02 | CML-5 | 50-DC-57077-15C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10365 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 2.172mm/ yr | [35 empty] | 10.3 | CML-5 | CML: type TBC | 3 | 2017-05-11 | 2016-05-24 | 2013-11-11 | 2.5 | 2.1721 | A1: Outside Quadrant |  | 8.07 | 2.5 | 4.5931 | 10.1 | 3 O'Clock | 50 | 11.07 | 50-DC-57077-15C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.1 | 10.1 | 10.3 | 10.7 | 0.28284
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-5 | 50-FG-45018-03C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10504 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.15 | CML-5 | CML: type TBC | 3 | 2015-12-28 | 2015-12-21 | 2013-11-15 | 2.5 | 1.1802 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5 | 5 | 5.2 | 0.19149
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-4 | 50-FG-45501-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6587 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.25 | CML-4 | CML: Elbow | 3 | 2023-09-13 | 2024-10-20 | 2015-03-30 07:00 | 2.5 | 0.29537 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5.2 | 5.4 | 5 | 0.19149
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56113-01C02 | CML-1 | 50-DH-56113-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5240 | Rope Access | 2014-05-20 14:00 | 2014-05-20 15:00 | [36 empty] | 5.25 | CML-1 | CML: Elbow | 3 | 2018-11-12 | 2019-06-14 | 2014-05-20 14:00 | 2.5 | 0.55744 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DH-56113-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.4 | 5.2 | 0.19149
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-1 | 50-DH-56116-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5211 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.25 | CML-1 | CML: Elbow | 3 | 2018-11-11 | 2019-06-12 | 2014-05-20 09:30 | 2.5 | 0.55773 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.4 | 5.4 | 0.19149
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-11 | 50-FG-45021-03C02 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10539 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.15 | CML-11 | CML: type TBC | 3 | 2016-01-02 | 2015-12-27 | 2013-11-16 | 2.5 | 1.1732 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5.2 | 5 | 5 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43122-01C02 | CML-3 | 50-FH-43122-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1761 | Rope access | 2014-04-27 08:30 | 2014-04-27 09:00 | [36 empty] | 5.25 | CML-3 | CML: Elbow | 3 | 2018-07-04 | 2019-01-20 | 2014-04-27 08:30 | 2.5 | 0.59663 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-FH-43122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.4 | 5 | 5.4 | 0.19149
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-6 | 50-FG-45021-03C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10534 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.15 | CML-6 | CML: type TBC | 3 | 2016-01-02 | 2015-12-27 | 2013-11-16 | 2.5 | 1.1732 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 3 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5.4 | 5.2 | 0.19149
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44020-01X01 | CML-7 | 200-PW-44020-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5597 |  | 2014-06-19 14:00 | 2014-06-19 15:00 | [36 empty] | 8.45 | CML-7 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 6 O'Clock | 40 | 6.35 | 200-PW-44020-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.4 | 8.8 | 8 | 8.6 | 0.34157
PG06 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21550 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 5.35 | CML-2 | CML: Elbow | 3 | 2017-09-21 | 2017-11-12 | 2014-07-17 07:30 | 2.5 | 0.81641 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 6 O'Clock | 100 | 6.02 | 100-PL-20068-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.5 | 5.5 | 5.1 | 5.3 | 0.19149
PG06 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-PG-23008-15S01-A | CML-9 | 200-PG-23008-15S01-A CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 3071 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 0.477mm/ yr | [35 empty] | 5.25 | CML-9 | CML: Elbow | 3 | 2019-10-11 | 2020-06-17 | 2014-05-03 08:00 | 2.5 | 0.4775 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.62452 | 5.1 | 5.5 | 5.3 | 5.1 | 0.19149
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-9 | 50-FG-45300-01C02 CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 7832 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:37 | [32 empty] | 5.55 | CML-9 | CML: Elbow | 3 | 2033-12-05 | 2036-02-17 | 2015-01-13 13:00 | 2.5 | 0.14809 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.7 | 5.7 | 5.3 | 0.19149
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-1 | 100-FL-43455-01C02-P CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 20484 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 5.75 | CML-1 | CML: Reducer | 3 | 2022-06-26 | 2022-10-13 | 2014-10-03 07:00 | 2.5 | 0.38791 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 9 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 5.9 | 5.9 | 5.5 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43126-01C02 | CML-1 | 100-FH-43126-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2510 | Rope Access | 2014-03-24 14:30 | 2014-03-24 15:00 | [36 empty] | 5.85 | CML-1 | CML: type TBC | 3 | 2020-03-21 | 2020-06-11 | 2014-03-24 14:30 | 2.5 | 0.51685 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 12 O'Clock | 100 | 6.02 | 100-FH-43126-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6 | 5.8 | 6 | 0.19149
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-25 | 50-DH-56137-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 21109 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 5.85 | CML-25 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.6 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 5.8 | 6 | 5.6 | 0.19149
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45006-03C02-E | CML-2 | 100-FG-45006-03C02-E CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24318 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.25 | CML-2 | CML: Elbow | 3 | 2025-08-06 | 2023-12-03 | 2016-06-01 07:00 | 1.88 | 0.3396 | A3: Inside Quadrant |  | 3.02 | 1.88 | 2.45 | 5 | 6 O'Clock | 100 | 6.02 | 100-FG-45006-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.12 |  | 5.2 | 5.4 | 5 | 5.4 | 0.19149
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21256 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.25 | CML-5 | CML: Fitting | 3 | 2028-01-23 | 2027-12-15 | 2014-09-30 07:00 | 2.5 | 0.2627 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 6.2 | 6 | 6.4 | 0.19149
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-15 | 25-FG-45455-01C02-E CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 22071 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.25 | CML-15 | CML: type TBC | 3 | 2186-01-24 | 2173-04-24 | 2014-05-25 07:00 | 2.5 | 0.02037 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.76 | 6 | 3 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.4 | 6.4 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43036-01C02 | CML-1 | 100-FH-43036-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12665 |  | 2014-01-26 10:00 | 2014-01-26 11:00 | [36 empty] | 6.15 | CML-1 | CML: type TBC | 3 | 2128-10-13 | 2132-08-04 | 2014-01-26 10:00 | 2.5 | 0.03049 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 9 O'Clock | 100 | 6.02 | 100-FH-43036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.4 | 6 | 0.19149
VA02 | Montara_Topside | No | Main Power (80) | Pipework | 50-VA-80012-01S01 | CML-3 | 50-VA-80012-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8515 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 10.35 | CML-3 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 10.2 | 6 O'Clock | 50 | 5.54 | 50-VA-80012-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.4 | 10.5 | 10.2 | 10.3 | 0.1291
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-13 | 50-FG-45023-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1161 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.25 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 | 16.1282 | 6.5 | 6.1 | 6.3 | 6.1 | 0.19149
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PL-20029-01C02-P | CML-2 | 150-PL-20029-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21332 | Protective mesh removed | 2014-06-26 07:00 | 2014-06-26 08:00 | [36 empty] | 7.175 | CML-2 | CML: Fitting | 3 | 286138 | 239669 | 2014-06-26 07:00 | 0.84 | 0.00935 | A3: Inside Quadrant |  | 4.11 | 0.84 | 2.0306 | 7.1 | 6 O'Clock | 150 | 7.11 | 150-PL-20029-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.26 |  | 7.2 | 7.2 | 7.1 | 7.2 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57065-01C02 | CML-2 | 250-DC-57065-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20290 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 11.175 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.2 | 12 O'Clock | 250 | 6.35 | 250-DC-57065-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.2 | 11.2 | 12.7 | 10.6 | 1.0966
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-9 | 150-DC-57308-01C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20306 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 0.576mm/ yr | [35 empty] | 10.525 | CML-9 | CML: Pipe Length | 6 | 2028-02-14 | 2025-12-23 | 2014-10-02 07:00 | 2.5 | 0.57558 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.2 | 12 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.2 | 10.8 | 10.8 | 10.3 | 0.32016
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-7 | 150-DC-57308-01C03 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20304 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 0.576mm/ yr | [35 empty] | 10.55 | CML-7 | CML: Pipe Length | 6 | 2028-02-14 | 2025-12-23 | 2014-10-02 07:00 | 2.5 | 0.57558 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.2 | 6 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.6 | 10.6 | 10.2 | 10.8 | 0.25166
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-1 | 150-DC-57308-01C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20298 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 0.576mm/ yr | [35 empty] | 10.725 | CML-1 | CML: Reducing Tee | 6 | 2028-02-14 | 2025-12-23 | 2014-10-02 07:00 | 2.5 | 0.57558 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 10.2 | 3 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.5 | 10.2 | 11.1 | 11.1 | 0.45
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 200-PG-23504-15S01 | CML-5 | 200-PG-23504-15S01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20765 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [35 empty] | Low alarm breach | 20.9 | CML-5 | CML: Pipe Length | 1 | 2019-07-26 | 2016-10-21 | 2014-09-27 07:00 | 13.2 | 1.5936 | A1: Outside Quadrant |  | 22.01 | 13.2 | 17.605 | 20.9 | 9 O'Clock | 200 | 23.01 | 200-PG-23504-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 20.9 | 20.9 | 20.9 | 20.9 | 0
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 200-PG-23504-15S01 | CML-4 | 200-PG-23504-15S01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20764 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [35 empty] | Low alarm breach | 20.9 | CML-4 | CML: Elbow | 1 | 2019-07-26 | 2016-10-21 | 2014-09-27 07:00 | 13.2 | 1.5936 | A1: Outside Quadrant |  | 22.01 | 13.2 | 17.605 | 20.9 | 9 O'Clock | 200 | 23.01 | 200-PG-23504-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 20.9 | 20.9 | 20.9 | 20.9 | 0
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 200-PG-23504-15S01 | CML-3 | 200-PG-23504-15S01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20763 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [35 empty] | Low alarm breach | 20.9 | CML-3 | CML: Elbow | 1 | 2019-07-26 | 2016-10-21 | 2014-09-27 07:00 | 13.2 | 1.5936 | A1: Outside Quadrant |  | 22.01 | 13.2 | 17.605 | 20.9 | 9 O'Clock | 200 | 23.01 | 200-PG-23504-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 20.9 | 20.9 | 20.9 | 20.9 | 0
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24036-09C02 | CML-9 | 50-PL-24036-09C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 13168 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | [36 empty] | 9.225 | CML-9 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-01-18 15:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.8 | 6 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.3 | 9.4 | 8.8 | 9.4 | 0.28723
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43121-01C02 | CML-6 | 150-FH-43121-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1769 | Rope access | 2014-04-27 09:30 | 2014-04-27 11:00 | [36 empty] | 7.65 | CML-6 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-04-27 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 6 O'Clock | 150 | 7.11 | 150-FH-43121-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.7 | 7.5 | 7.5 | 7.9 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-19 | 150-FH-43026-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 12659 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.15 | CML-19 | CML: Reducing Tee | 3 | 2049-01-08 | 2042-08-09 | 2014-01-22 07:00 | 1.03 | 0.17064 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 |  | 7.4 | 7 | 7.2 | 7 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-9 | 150-FH-43026-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12649 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.25 | CML-9 | CML: Pipe Length | 3 | 2405-02-03 | 2334-07-07 | 2014-01-22 07:00 | 1.03 | 0.01551 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.1 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.07 |  | 7.5 | 7.3 | 7.1 | 7.1 | 0.19149
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38492-01C02 | CML-3 | 50-CG-38492-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2537 |  | 2014-04-03 08:00 | 2014-04-03 09:00 | [36 empty] | 8.05 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-03 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 6 O'Clock | 50 | 5.54 | 50-CG-38492-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.3 | 7.9 | 7.9 | 8.1 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-1 | 80-FH-43111-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12799 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 8.45 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-02-01 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.2 | 3 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.4 | 8.2 | 8.6 | 8.6 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-22 | 200-FH-43025-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 2495 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 8.85 | CML-22 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.6 | 6 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9 | 9 | 8.6 | 8.8 | 0.19149
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-15 | 50-PL-23022-03C03 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1871 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.15 | CML-15 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 9 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.2 | 9.4 | 9 | 9 | 0.19149
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PL-20050-01C02-P | CML-1 | 150-PL-20050-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21502 | Protective mesh removed | 2014-06-30 09:30 | 2014-06-30 10:30 | [36 empty] | 7.625 | CML-1 | CML: Elbow | 3 | 2076-02-10 | 2064-03-16 | 2014-06-30 09:30 | 0.84 | 0 | A4: Left Quadrant |  | 4.11 | 0.84 | 2.0306 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-PL-20050-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.36 |  | 7.4 | 7.7 | 8.2 | 7.2 | 0.43493
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-17 | 350-FL-43511-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2298 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 9.95 | CML-17 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 9.7 | 3 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10.1 | 9.7 | 9.9 | 10.1 | 0.19149
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-9 | 50-PL-23041-06C03 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10222 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.05 | CML-9 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 2.6691 | A3: Inside Quadrant |  | 5.07 |  |  | 9.9 | 9 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.3 | 10.1 | 9.9 | 9.9 | 0.19149
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23301-01C02 | CML-9 | 80-VA-23301-01C02 CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 22516 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.55 | CML-9 | CML: Elbow | 3 | 2016-02-10 | 2016-06-04 | 2015-04-20 07:00 | 2.5 | 1.1083 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.4 | 9 O'Clock | 50 | 5.49 | 80-VA-23301-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.6 | 3.8 | 3.4 | 0.19149
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45017-03C02 | CML-1 | 100-FG-45017-03C02 CML-1 | yes | FPSO 2013 | Pipe Wall Thickness | 10625 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 4.85 | CML-1 | CML: type TBC | 3 | 2014-08-28 | 2014-07-25 | 2013-11-18 | 2.5 | 2.8341 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 4.7 | 9 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 4.9 | 4.7 | 4.7 | 0.19149
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-2 | 50-CG-38457-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23720 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.85 | CML-2 | CML: Elbow | 3 | 2022-02-23 | 2023-01-31 | 2015-10-30 07:00 | 2.5 | 0.3479 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 4.7 | 4.9 | 4.7 | 0.19149
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-1 | 50-FG-45501-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6584 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.15 | CML-1 | CML: Elbow | 3 | 2022-02-03 | 2023-01-09 | 2015-03-30 07:00 | 2.5 | 0.35007 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 5.3 | 4.9 | 5.3 | 0.19149
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56064-01C02 | CML-6 | 50-DH-56064-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3276 | Rope Access | 2014-05-09 13:00 | 2014-05-09 14:00 | [36 empty] | 5.15 | CML-6 | CML: type TBC | 3 | 2017-11-14 | 2018-05-07 | 2014-05-09 13:00 | 2.5 | 0.68196 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56064-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 4.9 | 5.3 | 5.1 | 0.19149
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40044-01C02 | CML-8 | 300-WC-40044-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1123 |  | 2014-03-21 11:30 | 2014-03-21 12:00 | [36 empty] | 8.3 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-21 11:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 9 O'Clock | 300 | 6.35 | 300-WC-40044-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.5 | 8.5 | 8.2 | 8 | 0.24495
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-9 | 300-PW-44002-01X01-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22855 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.1 | CML-9 | CML: Equal Tee | 6 | 2020-03-07 | 2019-05-25 | 2015-05-01 07:00 | 2.5 | 1.1535 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 8.1 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | 5.773 | 8.9 | 8.1 | 10.6 | 8.8 | 1.0614
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PL-20050-01C02-P | CML-2 | 150-PL-20050-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21503 | Protective mesh removed | 2014-06-30 09:30 | 2014-06-30 10:30 | [36 empty] | 7.3 | CML-2 | CML: Fitting | 3 | 2076-02-10 | 2064-03-16 | 2014-06-30 09:30 | 0.84 | 0 | A3: Inside Quadrant |  | 4.11 | 0.84 | 2.0306 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-PL-20050-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.36 |  | 7.4 | 7.4 | 7.2 | 7.2 | 0.11547
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-13 | 200-FH-43025-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2486 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 7.15 | CML-13 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.1 | 7.3 | 7.3 | 0.19149
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-10 | 200-WC-40008-01C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7816 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 8.1 | CML-10 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 9 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8.1 | 8 | 8 | 0.14142
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-31 | 250-PW-44006-01X01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 23202 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 9.1 | CML-31 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | -0.65803 | 9.4 | 9.2 | 8.1 | 9.7 | 0.69761
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43020-01C02 | CML-1 | 80-FH-43020-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12613 |  | 2014-01-23 07:00 | 2014-01-23 08:00 | [36 empty] | 5.55 | CML-1 | CML: type TBC | 3 | 2034-11-28 | 2037-05-30 | 2014-01-23 07:00 | 2.5 | 0.13902 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43020-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.6 | 5.4 | 5.8 | 0.19149
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-1 | 50-PW-44013-01X01 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10315 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 8.475 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2013-11-10 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.1 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.6 | 8.8 | 8.1 | 8.4 | 0.29861
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20252 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 5.55 | CML-6 | CML: type TBC | 3 | 2046-10-03 | 2050-08-21 | 2014-06-02 13:00 | 2.5 | 0.08962 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.6 | 5.8 | 5.4 | 0.19149
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-9 | 50-FG-45302-01C02 CML-9 | Yes | FPSO 2014 | Pipe Wall Thickness | 5777 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 6.55 | CML-9 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 25 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.8 | 6.4 | 6.4 | 0.19149
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45009-01C02-E | CML-6 | 150-FG-45009-01C02-E CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24300 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.55 | CML-6 | CML: Reducer | 3 | 2074-03-18 | 2063-04-04 | 2016-05-27 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.4 | 9 O'Clock | 150 | 7.11 | 150-FG-45009-01C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.37 |  | 7.4 | 7.6 | 7.8 | 7.4 | 0.19149
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-9 | 100-FG-45001-09C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10424 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 9.95 | CML-9 | CML: type TBC | 3 | 2015-08-07 | 2015-01-06 | 2013-11-13 | 4.7 | 2.9421 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 9.8 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 10 | 9.8 | 10.2 | 9.8 | 0.19149
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-53 | 50-DH-56137-01C02 CML-53 |  | FPSO 2014 | Pipe Wall Thickness | 21191 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 18.65 | CML-53 | CML: Equal Tee | 6 | 2115-02-10 | 2094-04-05 | 2014-07-16 07:30 | 4.1 | 0 | A2: Right Quadrant |  | 8.27 | 4.1 | 6.185 | 18.5 | 6 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.4 |  | 18.9 | 18.5 | 18.5 | 18.7 | 0.19149
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-23 | 50-FG-45021-03C02 CML-23 | yes | FPSO 2013 | Pipe Wall Thickness | 10551 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 4.875 | CML-23 | CML: type TBC | 3 | 2014-11-26 | 2014-11-22 | 2013-11-16 | 2.5 | 2.0423 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5 | 4.9 | 5 | 4.6 | 0.1893
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-11 | 25-FG-45455-01C02-E CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12630 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.125 | CML-11 | CML: type TBC | 3 | 2017-01-21 | 2017-06-13 | 2014-01-23 10:00 | 2.5 | 0.8337 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.1 | 5 | 0.1893
PG06 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PG-23008-15S01-A | CML-8 | 200-PG-23008-15S01-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21940 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.375 | CML-8 | CML: Elbow | 3 | 2023-10-31 | 2025-01-16 | 2014-10-10 07:00 | 2.5 | 0.28683 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.4 | 5.5 | 5.5 | 0.1893
PG06 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PG-23008-15S01-A | CML-9 | 200-PG-23008-15S01-A CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5746 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.375 | CML-9 | CML: Reducing Tee | 3 | 2021-07-12 | 2022-06-22 | 2014-06-22 14:00 | 2.5 | 0.36823 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 40 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.5 | 5.4 | 5.1 | 5.5 | 0.1893
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-25 | 100-PW-20021-01C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 21828 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 8.2 | CML-25 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-10-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.6 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8 | 8 | 7.6 | 9.2 | 0.69282
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43115-01C02 | CML-3 | 80-FH-43115-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12823 |  | 2014-01-20 09:00 | 2014-01-20 10:00 | [36 empty] | 5.875 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-20 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 9 O'Clock | 80 | 5.49 | 80-FH-43115-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 6 | 5.9 | 5.6 | 0.1893
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML 5 | 200-PW-44021-01X01 CML 5 |  | FPSO 2014 | Pipe Wall Thickness | 22369 |  | 2014-06-19 13:00 | 2014-06-19 14:00 | [36 empty] | 8.3 | CML 5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-19 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 6 O'Clock | 200 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.7 | 8.1 | 8.1 | 8.3 | 0.28284
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-11 | 50-FG-45024-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1194 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.375 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.5 | 6.4 | 6.5 | 0.1893
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-6 | 50-WC-40451-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10146 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 8.2 | CML-6 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2013-11-09 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8 | 12 O'Clock | 100 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.3 | 8.2 | 8.3 | 0.14142
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-12 | 50-PL-23516-03C03 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 7800 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 15:58 | [32 empty] | 8.125 | CML-12 | CML: Pipe Length | 6 | 2027-01-25 | 2026-10-21 | 2015-01-13 07:00 | 2.5 | 0.4568 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.4 | 8.1 | 8 | 0.1893
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-8 | 50-PL-23021-03C03 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10240 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.225 | CML-8 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.2 | 8.5 | 0.1893
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-9 | 100-FG-45043-03C02-E CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22655 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 8.025 | CML-9 | CML: Reducing Tee | 3 | 2054-10-24 | 2049-02-10 | 2015-04-27 07:00 | 1.88 | 0 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 7.9 | 9 O'Clock | 50 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.02 |  | 7.9 | 8.3 | 8 | 7.9 | 0.1893
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38490-09C02 | CML-1 | 50-CG-38490-09C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2529 |  | 2014-04-03 07:00 | 2014-04-03 08:00 | [36 empty] | 8.725 | CML-1 | CML: type TBC | 3 | 2050-10-16 | 2041-02-01 | 2014-04-03 07:00 | 2.5 | 0.16683 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-CG-38490-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9 | 8.6 | 8.7 | 0.1893
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44023-01C03-P | CML-1 | 250-PW-44023-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23036 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 9.125 | CML-1 | CML: Fitting | 6 | 2061-10-06 | 2059-01-06 | 2015-05-06 07:00 | 2.5 | 0.13993 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9 | 9 O'Clock | 250 | 9.27 | 250-PW-44023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | 0 | 9 | 9.4 | 9.1 | 9 | 0.1893
FL02 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FL-43454-01C02-P | CML-5 | 50-FL-43454-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21571 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.375 | CML-5 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 3 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.4 | 9.1 | 9.5 | 9.5 | 0.1893
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-29 | 300-PW-44003-01C03 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 21871 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 17:31 | [32 empty] | 12.575 | CML-29 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 12 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 13 | 12.7 | 12.6 | 12 | 0.41932
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-42 | 300-PF-20500-03C03-P CML-42 |  | FPSO 2014 | Pipe Wall Thickness | 21662 | Reviewed on 27/11/14. FFS. Recheck on Sep. 15 | 2014-09-27 07:00 | 2014-09-27 15:00 |  |  | Nestor | 2014-11-27 17:41 | [32 empty] | 12.475 | CML-42 | CML: Fitting | 6 | 2019-05-28 | 2018-04-30 | 2014-09-27 07:00 | 4.9 | 1.5633 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.2 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 12.2 | 12.5 | 12.6 | 12.6 | 0.1893
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45030-03C03 | CML-4 | 50-PL-45030-03C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10467 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.525 | CML-4 | CML: type TBC | 6 | 2023-09-18 | 2022-07-20 | 2013-11-13 | 0.99 | 0.75212 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-PL-45030-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.41 |  | 8.8 | 8.4 | 8.5 | 8.4 | 0.1893
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-22 | 300-PW-44003-01C03 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 22887 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 12.525 | CML-22 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 12.1 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 | 0.75258 | 12.4 | 13 | 12.6 | 12.1 | 0.37749
VA02 | Montara_Topside | No | Main Power (80) | Pipework | 50-VA-80013-01S01 | CML-4 | 50-VA-80013-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8522 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 10.575 | CML-4 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 10.3 | 12 O'Clock | 50 | 5.54 | 50-VA-80013-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 10.8 | 10.7 | 10.5 | 0.22174
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20061-01C03-P | CML-3 | 80-PG-20061-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21675 | Protective mesh removed | 2014-06-26 11:00 | 2014-06-26 12:00 | [36 empty] | 11.025 | CML-3 | CML: Fitting | 6 | 2053-07-11 | 2047-06-01 | 2014-06-26 11:00 | 2.5 | 0.215 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 9 O'Clock | 80 | 11.13 | 80-PG-20061-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 10.9 | 11 | 11.3 | 10.9 | 0.1893
PG01 | Montara_Topside | Yes | Process Gas (23) | Pipework | 50-PG-23044-03C03 | CML-2 | 50-PG-23044-03C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5484 | Rope Access | 2014-05-28 14:00 | 2014-05-28 15:00 | [36 empty] | 11.375 | CML-2 | CML: Reducer | 6 | 2075-10-24 | 2074-08-12 | 2014-05-28 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 11.1 | 3 O'Clock | 50 | 8.74 | 50-PG-23044-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.5 | 11.1 | 11.4 | 11.5 | 0.1893
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-11 | 150-DC-57308-01C03 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20308 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 0.501mm/ yr | [35 empty] | 10.65 | CML-11 | CML: Pipe Length | 6 | 2030-04-25 | 2027-11-07 | 2014-10-02 07:00 | 2.5 | 0.50083 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.3 | 12 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 10.9 | 10.6 | 10.8 | 0.26458
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21793 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 10.7 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 10.3 | 3 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.6 | 10.3 | 10.9 | 11 | 0.31623
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38300-01C02-P |  | 50-CG-38300-01C02-P | yes | FPSO 2014 | Pipe Wall Thickness | 22096 | Rope access | 2014-06-02 08:00 | 2014-06-02 09:00 |  |  | Administrator | 2015-09-07 10:57 | [32 empty] | 5.075 | 50-CG-38300-01C02-P | Piping | 3 | 2017-07-14 |  | 2014-06-02 08:00 |  | 0.73731 | A1: Outside Quadrant |  |  | 2.5 |  | 4.8 | 12 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 4.8 | 4.8 | 5.1 | 5.2 | 5.2 | 0.1893
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56063-01C02 | CML-3 | 50-DH-56063-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3363 | Rope Access | 2014-05-10 07:00 | 2014-05-10 08:00 | [36 empty] | 5.075 | CML-3 | CML: type TBC | 3 | 2017-04-11 | 2017-09-09 | 2014-05-10 07:00 | 2.5 | 0.78679 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.2 | 5.2 | 5.1 | 0.1893
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-9 | 50-FG-45018-03C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10508 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.075 | CML-9 | CML: type TBC | 3 | 2015-04-18 | 2015-04-13 | 2013-11-15 | 2.5 | 1.6174 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.1 | 5.2 | 5.2 | 0.1893
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-18 | 250-PG-23003-06C02-PA CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10546 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 4.925 | CML-18 | CML: type TBC | 3 | 2015-04-22 | 2015-04-17 | 2013-11-16 | 2.5 | 1.6077 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 5.2 | 4.8 | 4.8 | 0.1893
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10670 | Deck Level.High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.5849 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 16:14 | [32 empty] | 5.075 | CML-3 | CML: Elbow | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.1 | 5.2 | 5.2 | 0.1893
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-2 | 250-PW-44006-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23173 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 8.475 | CML-2 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | 1.6451 | 8.1 | 8.6 | 8.5 | 8.7 | 0.263
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-21 | 100-PW-20021-01C02-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21824 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 8.275 | CML-21 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-10-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.6 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.8 | 8 | 7.6 | 8.7 | 0.57373
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-25 | 100-PW-20021-01C02-P CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 22843 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 8.05 | CML-25 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-04-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.6 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | 0 | 7.7 | 8.1 | 8.8 | 7.6 | 0.54467
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-7 | 100-VA-80006-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2176 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 5.275 | CML-7 | CML: type TBC | 3 | 2016-04-10 | 2016-05-14 | 2014-03-30 13:00 | 2.5 | 1.2306 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 3 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5 | 5.4 | 5.3 | 0.1893
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-9 | 50-CG-38454-01C02-H CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 23673 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.225 | CML-9 | CML: Elbow | 3 | 2030-01-31 | 2031-11-16 | 2015-10-30 07:00 | 2.5 | 0.18223 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.1 | 5.5 | 5.1 | 0.1893
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-7 | 50-CG-38454-01C02-H CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 23671 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.225 | CML-7 | CML: Elbow | 3 | 2030-01-31 | 2031-11-16 | 2015-10-30 07:00 | 2.5 | 0.18223 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 25 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.5 | 5.1 | 5.1 | 5.2 | 0.1893
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56559-01C02 | CML-1 | 50-DH-56559-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21136 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-21 09:11 | [32 empty] | 5.575 | CML-1 | CML: Cap End | 3 | 2030-07-23 | 2032-05-24 | 2014-10-08 07:00 | 2.5 | 0.17722 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56559-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.3 | 5.7 | 5.6 | 0.1893
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-3 | 50-CG-38470-01C02-P CML-3 | Yes | FPSO 2015 | Pipe Wall Thickness | 23609 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.425 | CML-3 | CML: Elbow | 3 | 2043-11-28 | 2047-03-07 | 2015-10-28 07:00 | 2.5 | 0.09963 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.4 | 5.3 | 5.3 | 0.1893
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43154-01C02 | CML-8 | 100-FL-43154-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12878 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 5.725 | CML-8 | CML: type TBC | 3 | 2019-02-02 | 2019-04-12 | 2014-02-03 08:00 | 2.5 | 0.61981 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 6 | 5.6 | 0.1893
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-3 | 80-FH-43151-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2237 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 6.275 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 12 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.4 | 6.4 | 6.3 | 0.1893
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-17 | 250-PW-44006-01X01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8009 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 8.55 | CML-17 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 9 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | -0.36492 | 8.3 | 8.7 | 9 | 8.2 | 0.36968
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-19 | 50-FG-45023-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1167 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.575 | CML-19 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.6 | 6.7 | 6.7 | 6.3 | 0.1893
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-2 | 50-FH-43011-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7952 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.925 | CML-2 | CML: Equal Tee | 3 | 2021-04-25 | 2020-04-10 | 2015-01-18 08:00 | 2.5 | 0.68552 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 6.8 | 3 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.8 | 6.9 | 7.2 | 0.1893
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43407-01C02 | CML-3 | 150-FH-43407-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7949 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-18 07:00 | 2015-01-18 08:00 |  |  | Administrator | 2015-09-08 13:27 | [32 empty] | 7.075 | CML-3 | CML: Elbow | 3 | 2037-09-10 | 2035-10-17 | 2015-01-18 07:00 | 2.5 | 0.18976 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 3 O'Clock | 150 | 7.11 | 150-FH-43407-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.1 | 6.8 | 7.2 | 7.2 | 0.1893
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-45 | 350-FL-43512-01C02 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 23556 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.775 | CML-45 | CML: Elbow | 3 | 2041-09-09 | 2037-12-17 | 2015-08-10 07:30 | 2.5 | 0.19155 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.5 | 6 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.8 | 7.9 | 7.5 | 7.9 | 0.1893
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-11 | 100-DC-57038-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2374 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 11.425 | CML-11 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.3 | 12 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 11.1 | 11.8 | 12.5 | 0.94296
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-10 | 150-FH-43136-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2771 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.225 | CML-10 | CML: Pipe Length | 3 | 214934 | 2402-11-10 | 2014-03-13 09:00 | 1.03 | 0.01279 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.1 | 9 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.07 |  | 7.5 | 7.1 | 7.2 | 7.1 | 0.1893
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56061-01C02 | CML-1 | 50-DH-56061-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3365 | Rope Access | 2014-05-10 08:00 | 2014-05-10 09:00 | [36 empty] | 8.175 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-10 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56061-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.3 | 8.3 | 8.2 | 0.1893
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80001-01C02 | CML-7 | 50-VA-80001-01C02 CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 3140 | Rope Access | 2014-05-02 09:30 | 2014-05-02 10:30 | [36 empty] | 4.975 | CML-7 | CML: type TBC | 3 | 2016-09-26 | 2017-02-04 | 2014-05-02 09:30 | 2.5 | 0.91414 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-VA-80001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.1 | 5.1 | 5 | 0.1893
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-19 | 250-PW-44006-01X01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1916 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 8.425 | CML-19 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.6 | 8.6 | 8.3 | 8.2 | 0.20616
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-4 | 250-PW-44006-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23175 | New Spool not painted | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 8.425 | CML-4 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | -9.2124 | 8.4 | 8.5 | 8.6 | 8.2 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-22 | 250-PW-44006-01X01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 23193 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 10.4 | CML-22 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | 6.9093 | 8.3 | 12.6 | 9.9 | 10.8 | 1.7944
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-11 | 400-WC-40060-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1059 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 8.225 | CML-11 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-20 14:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.1 | 6 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8.2 | 8.1 | 8.3 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-12 | 400-WC-40060-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1060 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 8.125 | CML-12 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-20 14:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.1 | 9 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.1 | 8.1 | 8.1 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43142-01C02 | CML-2 | 100-FH-43142-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10520 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.525 | CML-2 | CML: type TBC | 3 | 2016-01-05 | 2016-02-05 | 2013-11-15 | 2.5 | 1.3551 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 6 O'Clock | 100 | 6.02 | 100-FH-43142-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 5.4 | 5.8 | 0.1893
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45008-03C02-E | CML-3 | 100-FG-45008-03C02-E CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24303 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 | Wet CO2 Gas Corrosion, downstream of super heaters and approaching dew point temperature (36 Deg C) |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.175 | CML-3 | CML: Elbow | 3 | 2024-06-16 | 2022-12-09 | 2016-05-27 07:00 | 1.88 | 0.3746 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 4.9 | 3 O'Clock | 100 | 6.02 | 100-FG-45008-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.02 |  | 5.3 | 4.9 | 5.2 | 5.3 | 0.1893
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57012-01C02 | CML-1 | 50-DC-57012-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2880 | Rope Access | 2014-04-24 14:00 | 2014-04-24 15:00 | [36 empty] | 8.875 | CML-1 | CML: type TBC | 3 | 2065-02-10 | 2057-09-22 | 2014-04-24 14:00 | 0.37 | 0 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 8.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.83 |  | 8.2 | 9.1 | 9.2 | 9 | 0.45735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-14 | 300-PW-44002-01X01-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 22031 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 9.35 | CML-14 | CML: Elbow | 6 | 2018-10-08 | 2018-02-23 | 2014-10-17 07:00 | 2.5 | 1.4577 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 8.3 | 12 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.9 | 10.1 | 9.1 | 0.8226
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43102-01C02 | CML-3 | 100-FH-43102-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12748 |  | 2014-01-24 08:00 | 2014-01-24 09:00 | [36 empty] | 6.025 | CML-3 | CML: type TBC | 3 | 2032-06-22 | 2033-02-07 | 2014-01-24 08:00 | 2.5 | 0.18455 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-FH-43102-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.3 | 6 | 5.9 | 5.9 | 0.1893
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-4 | 100-DH-56082-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3372 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.475 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.5 | 6.6 | 6.6 | 0.1893
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-7 | 200-PL-20035-03C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21342 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 11 | CML-7 | CML: Equal Tee | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 10 | 6 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.39 |  | 11.9 | 10.6 | 10 | 11.5 | 0.86023
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43510-01C02 | CML-2 | 300-FL-43510-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20473 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 6.675 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 300 | 6.35 | 300-FL-43510-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.7 | 6.8 | 6.8 | 0.1893
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43141-01C02 | CML-4 | 150-FH-43141-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10655 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.975 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-18 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.7 | 12 O'Clock | 100 | 6.02 | 100-FH-43141-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7 | 7.1 | 7.1 | 0.1893
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-11 | 80-FH-43009-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12589 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.525 | CML-11 | CML: Pipe Length | 3 | 2050-12-17 | 2046-03-02 | 2014-02-05 08:00 | 0.54 | 0.13175 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.4 | 5.8 | 5.4 | 5.5 | 0.1893
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-44 | 350-FL-43512-01C02 CML-44 |  | FPSO 2015 | Pipe Wall Thickness | 23555 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.525 | CML-44 | CML: Pipe Length | 3 | 2036-04-02 | 2033-03-29 | 2015-08-10 07:30 | 2.5 | 0.23716 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 6 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.5 | 7.4 | 7.4 | 7.8 | 0.1893
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43307-01C02-E | CML-1 | 200-PL-43307-01C02-E CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8790 | LAGGING REMOVAL REQUIRED | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 8.05 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-02-15 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 9 O'Clock | 200 | 6.35 | 200-PL-43307-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8 | 8.2 | 8.3 | 7.7 | 0.26458
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67009-01E01 | CML-4 | 50-GN-67009-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8782 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 10.45 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.6 | 10.4 | 10.4 | 10.4 | 0.1
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-12 | 50-PL-23514-01C03 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8645 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:22 | [32 empty] | 8.425 | CML-12 | CML: Pipe Length | 6 | 2037-06-20 | 2037-01-02 | 2015-02-10 11:30 | 2.5 | 0.25925 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.7 | 8.4 | 8.3 | 8.3 | 0.1893
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-32 | 150-PG-23506-25C02 CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 20659 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | [36 empty] | 21.125 | CML-32 | CML: Pipe Length | 3 | 2019-09-26 | 2018-02-19 | 2014-05-28 07:00 | 15.88 | 0.95975 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 21 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.12 | -2.469 | 21.4 | 21 | 21.1 | 21 | 0.1893
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-10 | 100-PG-23028-25C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 449 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 17.375 | CML-10 | CML: Pipe Length | 3 | 2313-12-14 | 2222-01-29 | 2014-03-12 09:00 | 9.4 | 0.02567 | A4: Left Quadrant |  | 14.12 | 9.4 | 11.76 | 17.1 | 9 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 17.5 | 17.4 | 17.5 | 17.1 | 0.1893
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-8 | 200-PG-23013-09C03-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10992 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 20.375 | CML-8 | CML: Elbow | 6 | 2025-08-17 | 2023-01-16 | 2014-01-10 | 10.22 | 0.85112 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 20.1 | 12 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.88 |  | 20.1 | 20.5 | 20.5 | 20.4 | 0.1893
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-23 | 250-PG-23004-06C03-A CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 23390 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 18.1 | CML-23 | CML: Pipe Length | 6 | 2071-01-14 | 2060-01-11 | 2015-07-21 07:00 | 8.55 | 0.1684 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.9 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.35 | -0.96307 | 17.9 | 18 | 18.2 | 18.3 | 0.18257
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-7 | 50-CG-38487-09C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23576 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | Check Corrosion Rate of %vmm/ yr |  | John Wilson | 2017-03-24 11:20 | [32 empty] | 8.2 | CML-7 | CML: Pipe Length | 3 | 2032-08-09 | 2027-08-16 | 2015-09-10 07:00 | 2.5 | 0.32492 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 | -0.10641 | 8.1 | 8 | 8.3 | 8.4 | 0.18257
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-15 | 100-PG-23028-25C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 454 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 15.8 | CML-15 | CML: Pipe Length | 3 | 2017-05-15 | 2016-02-28 | 2014-03-12 09:00 | 9.4 | 1.9509 | A4: Left Quadrant |  | 14.12 | 9.4 | 11.76 | 15.6 | 9 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 15.9 | 15.7 | 16 | 15.6 | 0.18257
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-13 | 350-FL-43511-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2294 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 10.2 | CML-13 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 10 | 3 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.1 | 10 | 10.4 | 10.3 | 0.18257
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-34 | 300-PF-20501-03C03-P CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 23534 | Re-check | 2015-07-29 07:00 | 2015-07-29 12:00 | [36 empty] | 13.7 | CML-34 | CML: type TBC | 6 | 2039-09-05 | 2034-12-15 | 2015-07-29 07:00 | 4.9 | 0.35653 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 12 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 | -0.24013 | 13.5 | 13.6 | 13.9 | 13.8 | 0.18257
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-37 | 300-PF-20501-03C03-P CML-37 |  | FPSO 2014 | Pipe Wall Thickness | 21713 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.3 | CML-37 | CML: type TBC | 6 | 2086-07-01 | 2073-05-09 | 2014-09-28 07:00 | 4.9 | 0.12813 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 14.5 | 14.2 | 14.1 | 14.4 | 0.18257
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-7 | 50-CG-38001-09C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10920 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.2 | CML-7 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.2222 | A4: Left Quadrant |  | 5.74 |  |  | 8 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8 | 8.3 | 8.4 | 8.1 | 8 | 0.18257
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-11 | 80-DH-56004-01C02 CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 22564 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [36 empty] | 3.5 | CML-11 | CML: Reducer | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 3.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.7 | 3.6 | 3.4 | 3.3 | 0.18257
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-11 | 50-FG-45018-03C02 CML-11 | yes | FPSO 2013 | Pipe Wall Thickness | 10510 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.8 | CML-11 | CML: type TBC | 3 | 2014-11-23 | 2014-11-19 | 2013-11-15 | 2.5 | 2.0545 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.7 | 5 | 4.9 | 0.18257
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7682 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: Re-check point to confirm values in Jan. 2016 | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:15 | [32 empty] | 4.8 | CML-3 | CML: Elbow | 3 | 2018-08-10 | 2019-03-02 | 2015-01-08 13:00 | 2.5 | 0.58495 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0.17483 | 5 | 4.7 | 4.9 | 4.6 | 0.18257
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43074-01C02 | CML-3 | 50-FL-43074-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1788 | Rope access | 2014-04-28 09:30 | 2014-04-28 10:30 | [36 empty] | 5.2 | CML-3 | CML: Elbow | 3 | 2018-07-10 | 2019-01-26 | 2014-04-28 09:30 | 2.5 | 0.59476 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FL-43074-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.3 | 5.1 | 0.18257
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-4 | 400-WC-40024-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1073 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.8 | CML-4 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8.2 | 9 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 9.7 | 9 | 8.3 | 8.2 | 0.69761
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38477-01C02-P | CML-5 | 50-CG-38477-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2617 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.2 | CML-5 | CML: type TBC | 3 | 2018-06-29 | 2018-06-17 | 2014-04-26 10:45 | 2.5 | 0.59827 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -1.8086 | 5 | 5.4 | 5.1 | 5.3 | 0.18257
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-10 | 50-CG-38500-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23297 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 5.3 | CML-10 | CML: Pipe Length | 3 | 2027-11-09 | 2029-05-28 | 2015-07-04 09:30 | 2.5 | 0.21038 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | -0.427 | 5.4 | 5.2 | 5.5 | 5.1 | 0.18257
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-14 | 200-PG-23008-15S01-A CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 5224 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.3 | CML-14 | CML: Elbow | 3 | 2020-02-06 | 2020-10-25 | 2014-05-20 09:30 | 2.5 | 0.45445 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.5 | 5.4 | 5.2 | 0.18257
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43171-01C02 | CML-1 | 80-FL-43171-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20523 |  | 2014-10-06 07:00 | 2014-10-06 15:00 | [36 empty] | 5.7 | CML-1 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 9 O'Clock | 80 | 5.49 | 80-FL-43171-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 5.9 | 5.6 | 5.5 | 0.18257
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38463-01C02 | CML-7 | 50-CG-38463-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3118 | Rope Access | 2014-05-04 08:00 | 2014-05-04 09:00 | [36 empty] | 5.7 | CML-7 | CML: Pipe Length | 3 | 2083-08-10 | 2091-02-20 | 2014-05-04 08:00 | 2.5 | 0.04328 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-CG-38463-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 5.9 | 5.6 | 5.5 | 0.18257
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-5 | 250-PW-44006-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23176 | New Spool not painted | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 8.7 | CML-5 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | -8.8834 | 8.3 | 8.5 | 9.2 | 8.8 | 0.39158
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43308-01C02-E | CML-1 | 200-PL-43308-01C02-E CML-1 | Yes | FPSO 2015 | Pipe Wall Thickness | 8794 | LAGGING REMOVAL REQUIRED | 2015-02-15 13:00 | 2015-02-15 15:00 | [36 empty] | 8.075 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-02-15 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 3 O'Clock | 200 | 6.35 | 200-PL-43308-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.2 | 7.8 | 8.2 | 8.1 | 0.1893
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-7 | 50-FH-43137-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22681 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 7.3 | CML-7 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 | 0.31811 | 7.2 | 7.5 | 7.4 | 7.1 | 0.18257
CG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20270 | Rope Access | 2014-05-26 08:00 | 2014-05-26 09:00 | Check Corrosion Rate of 0.549mm/ yr | [35 empty] | 5.2 | CML-3 | CML: type TBC | 3 | 2022-11-01 | 2021-06-27 | 2014-05-26 08:00 | 0.37 | 0.54852 | A4: Left Quadrant |  | 2.54 | 0.37 | 1.1087 | 5 | 9 O'Clock | 50 | 5.54 | 50-DC-57028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.63 |  | 5.4 | 5.1 | 5.3 | 5 | 0.18257
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-2 | 150-FH-43518-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2702 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.2 | CML-2 | CML: Pipe Length | 3 | 2055-01-13 | 2047-12-27 | 2014-03-12 09:00 | 1.23 | 0.14119 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 | 0 | 7 | 7.4 | 7.3 | 7.1 | 0.18257
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-2 | 150-FH-43518-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 341 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.2 | CML-2 | CML: Pipe Length | 3 | 2054-12-24 | 2047-12-10 | 2014-03-12 | 1.23 | 0.14137 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 |  | 7 | 7.4 | 7.3 | 7.1 | 0.18257
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-VA-23056-01C02 | CML-6 | 50-VA-23056-01C02 CML-6 | High Priority | FPSO 2015 | Pipe Wall Thickness | 8066 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 5 | CML-6 | CML: type TBC | 3 | 2020-03-02 | 2020-11-21 | 2015-01-22 07:30 | 2.5 | 0.44993 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-VA-23056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 5.2 | 4.8 | 5.1 | 0.18257
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-9 | 100-DC-57037-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2360 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 11.05 | CML-9 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.4 | 9 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 11.7 | 11.7 | 10.4 | 0.75056
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57076-25C02 | CML-5 | 50-DC-57076-25C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10358 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 1.5mm/ yr | [35 empty] | 12.2 | CML-5 | CML: type TBC | 3 | 2019-02-14 | 2017-04-08 | 2013-11-11 | 2.5 | 1.5003 | A1: Outside Quadrant |  | 8.07 | 2.5 | 5.285 | 10.4 | 12 O'Clock | 50 | 11.07 | 50-DC-57076-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 12.5 | 12.5 | 13.4 | 1.2728
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57076-25C02 | CML-1 | 50-DC-57076-25C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10354 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 1.5mm/ yr | [35 empty] | 10.65 | CML-1 | CML: type TBC | 3 | 2019-02-14 | 2017-04-08 | 2013-11-11 | 2.5 | 1.5003 | A3: Inside Quadrant |  | 8.07 | 2.5 | 5.285 | 10.4 | 6 O'Clock | 50 | 11.07 | 50-DC-57076-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.5 | 10.9 | 10.4 | 10.8 | 0.23805
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56554-01C02 | CML-2 | 50-DH-56554-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21121 | Reviewed on 20/11/14. FFS. Recheck in Oct. 18. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-20 16:37 | [32 empty] | 5 | CML-2 | CML: Elbow | 3 | 2018-12-22 | 2019-07-28 | 2014-10-08 07:00 | 2.5 | 0.54644 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56554-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 4.9 | 5.2 | 4.8 | 0.18257
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-7 | 50-FG-45021-03C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2619 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5 | CML-7 | CML: type TBC | 3 | 2017-02-13 | 2017-02-04 | 2014-04-26 10:45 | 2.5 | 0.81986 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | -0.45216 | 4.8 | 5.1 | 4.9 | 5.2 | 0.18257
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-1 | 50-CG-38467-01C02 CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 22272 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.5 | CML-1 | CML: Fitting | 3 | 2025-01-05 | 2026-04-05 | 2014-05-01 11:00 | 2.5 | 0.26192 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0 | 5.3 | 5.7 | 5.6 | 5.4 | 0.18257
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-1 | 50-CG-38467-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2993 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.5 | CML-1 | CML: Fitting | 3 | 2025-01-05 | 2026-04-05 | 2014-05-01 11:00 | 2.5 | 0.26192 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.7 | 5.6 | 5.4 | 0.18257
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-11 | 300-PW-44002-01X01-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22857 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 8.675 | CML-11 | CML: Elbow | 6 | 2020-11-08 | 2019-12-29 | 2015-05-01 07:00 | 2.5 | 1.0491 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 8.3 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | 0.93112 | 8.9 | 8.3 | 8.8 | 8.7 | 0.263
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-15 | 50-PL-24003-09C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 13154 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 9.425 | CML-15 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-01-18 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.9 | 6 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.1 | 9.7 | 8.9 | 10 | 0.51235
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PL-20050-01C02-P | CML-3 | 150-PL-20050-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21504 | Protective mesh removed | 2014-06-30 09:30 | 2014-06-30 10:30 | [36 empty] | 7.625 | CML-3 | CML: Reducer | 3 | 2076-02-10 | 2064-03-16 | 2014-06-30 09:30 | 0.84 | 0 | A2: Right Quadrant |  | 4.11 | 0.84 | 2.0306 | 7.3 | 3 O'Clock | 150 | 7.11 | 150-PL-20050-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.46 |  | 7.6 | 7.3 | 7.6 | 8 | 0.28723
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-6 | 400-WC-40024-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1075 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.825 | CML-6 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.2 | 3 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 9.1 | 8.2 | 9.5 | 8.5 | 0.58523
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-10 | 200-FH-43038-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12691 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 7.5 | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 12 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.4 | 7.7 | 7.6 | 0.18257
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43505-01C02 | CML-2 | 150-FH-43505-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20467 | Rope Access | 2014-05-27 13:00 | 2014-05-27 14:00 | [36 empty] | 7.5 | CML-2 | CML: type TBC | 3 |  |  | 2014-05-27 13:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.3 | 12 O'Clock | 150 |  | 150-FH-43505-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.4 | 7.7 | 7.6 | 0.18257
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-3 | 50-CG-38457-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23721 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.1 | CML-3 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 3 O'Clock | 100 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.2 | 7.9 | 8 | 8.3 | 0.18257
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-20 | 400-WC-40022-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 1114 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.875 | CML-20 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.2 | 6 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 9.1 | 9.1 | 8.2 | 9.1 | 0.45
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-17 | 150-PG-20054-01C03-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23355 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 8.4 | CML-17 | CML: Pipe Length | 6 | 2019-12-09 | 2018-12-27 | 2015-07-20 07:00 | 2.5 | 1.2974 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 8.2 | 6 O'Clock | 100 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | -0.37556 | 8.5 | 8.6 | 8.2 | 8.3 | 0.18257
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38460-01C02-P | CML-9 | 80-CG-38460-01C02-P CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 20890 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 8.6 | CML-9 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.4 | 12 O'Clock | 50 | 5.49 | 80-CG-38460-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.8 | 8.5 | 8.7 | 0.18257
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1664 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.55 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 6 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.5 | 8.8 | 8.1 | 8.8 | 0.33166
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43176-01C02 | CML-2 | 300-FL-43176-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20432 | Protective mesh removed/Rope access | 2014-06-27 10:30 | 2014-06-27 12:00 | [36 empty] | 10.1 | CML-2 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-06-27 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 3 O'Clock | 300 | 6.35 | 300-FL-43176-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10 | 9.9 | 10.2 | 10.3 | 0.18257
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-21 | 50-PL-23042-09C03 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10086 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.6 | CML-21 | CML: type TBC | 6 | 2018-12-25 | 2018-02-23 | 2013-11-07 | 2.5 | 1.538 | A2: Right Quadrant |  | 5.07 | 2.5 | 3.785 | 10.4 | 3 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.7 | 10.4 | 10.8 | 10.5 | 0.18257
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-7 | 400-WC-40022-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1101 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.675 | CML-7 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.2 | 3 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.9 | 8.2 | 8.7 | 8.9 | 0.3304
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-16 | 50-CG-38001-09C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 10930 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.1 | CML-16 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.3873 | A1: Outside Quadrant |  | 5.74 |  |  | 7.9 | 12 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.9 | 7.9 | 8 | 8.3 | 8.2 | 0.18257
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38483-01C02 | CML-7 | 25-CG-38483-01C02 CML-7 | Yes | FPSO 2013 | Pipe Wall Thickness | 10396 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 4.9 | CML-7 | CML: type TBC | 3 | 2014-06-18 | 2014-06-15 | 2013-11-12 | 2.5 | 3.6723 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.7 | 9 O'Clock | 25 | 6.35 | 25-CG-38483-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 4.7 | 4.8 | 5.1 | 5 | 4.7 | 0.18257
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-28 | 50-DH-56070-01C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 3244 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.1 | CML-28 | CML: type TBC | 3 | 2017-11-12 | 2018-05-06 | 2014-05-09 07:00 | 2.5 | 0.68246 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 | 5.2 | 5.3 | 0.18257
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80001-01C02 | CML-5 | 50-VA-80001-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3138 | Rope Access | 2014-05-02 09:30 | 2014-05-02 10:30 | [36 empty] | 5.1 | CML-5 | CML: type TBC | 3 | 2017-10-11 | 2018-03-31 | 2014-05-02 09:30 | 2.5 | 0.69649 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-VA-80001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 4.9 | 5 | 5.3 | 0.18257
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-2 | 50-FH-43137-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22676 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.1 | CML-2 | CML: Elbow | 3 | 2022-06-16 | 2023-06-06 | 2015-04-27 07:00 | 2.5 | 0.33597 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0 | 4.9 | 5.2 | 5 | 5.3 | 0.18257
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-13 | 300-PW-44002-01X01-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 22030 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 9.35 | CML-13 | CML: Elbow | 6 | 2019-01-18 | 2018-05-25 | 2014-10-17 07:00 | 2.5 | 1.3852 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 8.4 | 6 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 10.2 | 9.7 | 8.4 | 9.1 | 0.77675
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-6 | 150-WC-40006-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1666 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.425 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 6 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.5 | 8.3 | 8.1 | 8.8 | 0.29861
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-17 | 50-FL-43454-01C02-P CML-17 | Yes | FPSO 2014 | Pipe Wall Thickness | 20520 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.4 | CML-17 | CML: Elbow | 3 | 2025-06-10 | 2026-09-25 | 2014-10-05 07:00 | 2.5 | 0.2526 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.6 | 5.3 | 5.2 | 0.18257
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-10 | 400-WC-40022-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1104 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.625 | CML-10 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.2 | 12 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.2 | 8.7 | 8.7 | 8.9 | 0.29861
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43300-01C02 | CML-1 | 50-FL-43300-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20448 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.6 | CML-1 | CML: Fitting | 3 | 2042-08-16 | 2045-10-03 | 2014-10-05 07:00 | 2.5 | 0.10401 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-FL-43300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 5.8 | 5.5 | 0.18257
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-2 | 400-WC-40060-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1050 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 8.55 | CML-2 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-20 14:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.2 | 6 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.5 | 8.6 | 8.2 | 8.9 | 0.28868
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56039-01C02 | CML-1 | 80-DH-56039-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20918 | Rope Access | 2014-05-21 11:00 | 2014-05-21 12:00 | [36 empty] | 6.6 | CML-1 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-21 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.4 | 9 O'Clock | 80 | 5.49 | 80-DH-56039-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.7 | 6.8 | 6.4 | 0.18257
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43121-01C02 | CML-4 | 150-FH-43121-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1767 | Rope access | 2014-04-27 09:30 | 2014-04-27 11:00 | [36 empty] | 6.6 | CML-4 | CML: Elbow | 3 | 2019-04-16 | 2018-10-30 | 2014-04-27 09:30 | 2.5 | 0.78436 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43121-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.5 | 6.4 | 6.8 | 0.18257
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7852 | Line is FFS. Current RBI frequency is 48m. Action: CML’s to Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-08 13:39 | [32 empty] | 6.9 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7 | 6.8 | 7.1 | 0.18257
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-6 | 50-CG-38470-01C02-P CML-6 | Yes | FPSO 2015 | Pipe Wall Thickness | 23612 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 7.1 | CML-6 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.9 | 3 O'Clock | 40 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.2 | 6.9 | 7.3 | 7 | 0.18257
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43108-01C02 | CML-1 | 200-FH-43108-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12776 |  | 2014-01-18 15:30 | 2014-01-18 16:30 | [36 empty] | 6.4 | CML-1 | CML: Pipe Length | 3 | 2034-08-06 | 2032-01-10 | 2014-01-18 15:30 | 1.34 | 0.23635 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-FH-43108-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 6.5 | 6.6 | 6.2 | 6.3 | 0.18257
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-18 | 80-SC-55002-01C02-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8848 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 11.25 | CML-18 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 10.5 | 6 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11.7 | 11.1 | 10.5 | 11.7 | 0.57446
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-14 | 250-PW-44006-01X01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8006 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 8.625 | CML-14 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.4 | 6 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 0.12164 | 8.9 | 8.4 | 8.4 | 8.8 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-14 | 400-FH-43508-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6563 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.6 | CML-14 | CML: Elbow | 3 | 2032-06-16 | 2029-12-11 | 2015-03-30 07:00 | 2.5 | 0.28443 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 12 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.7 | 7.8 | 7.5 | 0.18257
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56067-01C02 | CML-4 | 50-DH-56067-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3403 | Rope Access | 2014-05-10 14:00 | 2014-05-10 15:00 | [36 empty] | 5.1 | CML-4 | CML: type TBC | 3 | 2017-11-19 | 2018-05-13 | 2014-05-10 14:00 | 2.5 | 0.67989 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DH-56067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.3 | 4.9 | 5.2 | 0.18257
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43138-01C02 | CML-3 | 50-FH-43138-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12867 |  | 2014-01-21 09:30 | 2014-01-21 10:00 | [36 empty] | 5.4 | CML-3 | CML: Reducing Tee | 3 | 2019-02-25 | 2019-10-08 | 2014-01-21 09:30 | 2.5 | 0.52945 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-FH-43138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.5 | 5.6 | 5.3 | 0.18257
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23409-01C03 | CML-3 | 100-PG-23409-01C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20768 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 11.525 | CML-3 | CML: Equal Tee | 6 | 2037-07-04 | 2033-12-29 | 2014-10-02 07:00 | 2.5 | 0.35133 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.5 | 12 O'Clock | 150 | 10.97 | 100-PG-23409-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.5 | 11.5 | 11.5 | 12.6 | 0.85781
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 150-DH-56080-01C02 | CML-1 | 150-DH-56080-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3324 | Rope Access | 2014-05-08 07:00 | 2014-05-08 09:00 | [36 empty] | 7.6 | CML-1 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-05-08 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.4 | 6 O'Clock | 150 | 7.11 | 150-DH-56080-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.8 | 7.5 | 7.4 | 7.7 | 0.18257
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20013-01C02-P | CML-9 | 200-PL-20013-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21219 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 9.925 | CML-9 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9 | 9 O'Clock | 200 | 6.35 | 200-PL-20013-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 11.2 | 9.5 | 10 | 9 | 0.94296
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-28 | 100-FG-45001-09C02 CML-28 | Yes | FPSO 2015 | Pipe Wall Thickness | 23333 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11 | CML-28 |  | 3 | 2054-07-05 | 2043-07-19 | 2015-07-11 07:00 | 4.7 | 0.15637 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.8 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 11.1 | 10.8 | 10.9 | 11.2 | 0.18257
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-12 | 80-PG-23025-06C03 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 13083 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 11 | CML-12 | CML: Pipe Length | 6 | 2030-10-17 | 2028-05-12 | 2014-02-07 11:00 | 2.8 | 0.47901 | A3: Inside Quadrant |  | 5.13 | 2.8 | 3.965 | 10.8 | 6 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11.1 | 11.2 | 10.8 | 10.9 | 0.18257
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40513-1CG | CML-1 | 300-WC-40513-1CG CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5479 | Rope Access | 2014-05-28 11:30 | 2014-05-28 14:00 | [36 empty] | 19.075 | CML-1 | CML: Elbow | 3 | 2163-03-18 |  | 2014-05-28 11:30 |  | 0 | A4: Left Quadrant |  |  | 2.5 |  | 18.5 | 9 O'Clock | 300 | 17.48 | 300-WC-40513-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16 |  | 18.6 | 20.2 | 19 | 18.5 | 0.78049
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-18 | 400-WC-40022-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1112 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.4 | CML-18 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8.2 | 9 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.4 | 8.7 | 8.3 | 8.2 | 0.21602
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-12 | 100-PG-23028-25C02-P CML-12 | Yes | FPSO 2014 | Pipe Wall Thickness | 20556 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 15.95 | CML-12 | CML: Pipe Length | 3 | 2018-10-28 | 2017-03-03 | 2014-05-30 09:30 | 9.4 | 1.4263 | A3: Inside Quadrant |  | 14.12 | 9.4 | 11.76 | 15.7 | 6 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 | -0.92381 | 16 | 16 | 15.7 | 16.1 | 0.17321
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-17 | 100-PG-23406-03C03 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20743 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 10.825 | CML-17 | CML: Elbow | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 10.5 | 9 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.8 | 11 | 11 | 10.5 | 0.23629
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-7 | 250-PG-23005-06C03 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10053 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 16.65 | CML-7 | CML: Pipe Length | 6 | 2015-08-30 | 2015-03-28 | 2013-11-06 | 8.6 | 4.2968 | A3: Inside Quadrant |  | 12.26 | 8.6 | 10.43 | 16.4 | 6 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 16.7 | 16.7 | 16.4 | 16.8 | 0.17321
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-10 | 50-FG-45300-01C02 CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 7833 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:38 | [32 empty] | 4.75 | CML-10 | CML: Elbow | 3 | 2018-08-27 | 2019-03-20 | 2015-01-13 13:00 | 2.5 | 0.58001 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.9 | 4.9 | 4.6 | 0.17321
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-10 | 50-FG-45021-03C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10538 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.25 | CML-10 | CML: type TBC | 3 | 2016-08-04 | 2016-07-28 | 2013-11-16 | 2.5 | 0.95595 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.1 | 5.4 | 5.4 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40004-01C02 | CML-14 | 150-WC-40004-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1816 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 8.1 | CML-14 | CML: Reducing Tee | 3 | 2059-07-07 | 2055-11-27 | 2014-04-29 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.1 | 9 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 |  | 8.1 | 0
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-9 | 150-FH-43157-01C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10665 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.75 | CML-9 | CML: type TBC | 3 | 2017-08-15 | 2017-04-17 | 2013-11-18 | 2.5 | 1.095 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 9 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.9 | 6.9 | 6.6 | 6.6 | 0.17321
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-1 | 250-PL-20006-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13171 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 9.45 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-01-21 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9 | 6 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.5 | 9.8 | 9 | 9.5 | 0.33166
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20047-03C03-P | CML-1 | 80-PG-20047-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21468 | Protective mesh removed | 2014-06-28 07:00 | 2014-06-28 08:00 | [36 empty] | 11.25 | CML-1 | CML: Elbow | 6 | 2322-05-22 | 2275-04-22 | 2014-06-28 07:00 | 2.5 | 0.02791 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.1 | 6 O'Clock | 80 | 11.13 | 80-PG-20047-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.1 | 11.4 | 11.1 | 11.4 | 0.17321
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-1 | 250-PW-20022-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23099 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 12.5 | CML-1 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2015-05-10 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 12.2 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 | 0.71569 | 12.3 | 12.2 | 12.6 | 12.9 | 0.31623
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56141-01C02 | CML-4 | 50-DH-56141-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5445 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 3.475mm/ yr | [34 empty] | Low alarm breach | 18.15 | CML-4 | CML: Straight | 3 | 2018-11-11 | 2016-07-27 | 2014-05-28 07:00 | 2.5 | 3.4753 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 18 | 3 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.5 |  | 18 | 18 | 18.3 | 18.3 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-4 | 300-FH-43001-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12516 |  | 2014-01-24 13:00 | 2014-01-24 15:00 | [36 empty] | 9.4 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-24 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 12 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.5 | 9.5 |  | 0.17321
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-10 | 50-FG-45019-03C02 CML-10 | yes | FPSO 2013 | Pipe Wall Thickness | 10492 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.85 | CML-10 | CML: type TBC | 3 | 2014-11-23 | 2014-11-19 | 2013-11-15 | 2.5 | 2.0545 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 4.6 | 4.9 | 5 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40405-01C02 | CML-1 | 150-WC-40405-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20395 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 8.8 | CML-1 | CML: Equal Tee | 3 | 2059-07-07 | 2055-11-27 | 2014-10-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.2 | 9 O'Clock | 150 | 7.11 | 150-WC-40405-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.6 | 9.3 | 9.1 | 8.2 | 0.49666
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-11 | 250-PG-23003-06C02-PA CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10678 | Deck Level.High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.2115 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 16:17 | [32 empty] | 4.85 | CML-11 | CML: Pipe Length | 3 | 2014-11-29 | 2015-01-27 | 2013-11-17 | 2.5 | 2.0302 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 4.6 | 4.9 | 5 | 0.17321
VA01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-VA-43519-01C02 | CML-4 | 50-VA-43519-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7757 |  | 2015-01-11 09:30 | 2015-01-11 10:30 | [36 empty] | 5.15 | CML-4 | CML: Elbow | 3 | 2022-07-02 | 2023-06-23 | 2015-01-11 09:30 | 2.5 | 0.33441 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-VA-43519-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5 | 5.1 | 5.4 | 0.17321
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-8 | 50-PW-44015-01X01 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10291 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 8.6 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2013-11-10 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 12 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.7 | 8.6 | 8.7 | 0.14142
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-6 | 250-PW-44006-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23177 | New Spool not painted | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 8.45 | CML-6 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.4 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | -8.8834 | 8.4 | 8.5 | 8.4 | 8.5 | 0.057735
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-5 | 50-CG-38458-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23733 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 7.85 | CML-5 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.6 | 9 O'Clock | 100 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.9 | 7.9 | 8 | 7.6 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-46 | 400-FH-43508-01C02 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 23565 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 8.05 | CML-46 | CML: Pipe Length | 3 | 258310 | 229699 | 2015-08-10 07:30 | 2.5 | 0.00912 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8 | 8 | 8.3 | 7.9 | 0.17321
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-9 | 50-FL-43454-01C02-P CML-9 | Yes | FPSO 2014 | Pipe Wall Thickness | 20512 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 9.15 | CML-9 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9 | 12 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.4 | 9.1 | 9.1 | 0.17321
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-11 | 50-FL-43454-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1867 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.25 | CML-11 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.5 | 9.1 | 9.2 | 9.2 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-23 | 400-WC-40024-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 1092 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.7 | CML-23 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.3 | 3 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.8 | 8.3 |  | 9 | 0.36056
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80005-01C02 | CML-1 | 50-VA-80005-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3127 | Rope Access | 2014-05-02 10:30 | 2014-05-02 11:30 | [36 empty] | 10.05 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-02 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.9 | 6 O'Clock | 50 | 5.54 | 50-VA-80005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10 | 10 | 9.9 | 10.3 | 0.17321
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-32 | 200-PL-20010-01C02-P CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 23832 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 9.325 | CML-32 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9 | 3 O'Clock | 400 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.3 | 9 | 9.4 | 9.6 | 0.25
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-18 | 150-PG-20507-01C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2862 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 11.05 | CML-18 | CML: type TBC | 6 | 2108-12-03 | 2094-12-30 | 2014-03-16 07:00 | 2.5 | 0.08863 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.9 | 12 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 10.9 | 11 | 11 | 11.3 | 0.17321
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57077-15C02 | CML-7 | 50-DC-57077-15C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10367 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 1.276mm/ yr | [35 empty] | 10.775 | CML-7 | CML: type TBC | 3 | 2020-02-15 | 2018-06-27 | 2013-11-11 | 2.5 | 1.2764 | A3: Inside Quadrant |  | 8.07 | 2.5 | 4.5931 | 10.5 | 6 O'Clock | 50 | 11.07 | 50-DC-57077-15C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.8 | 10.7 | 10.5 | 11.1 | 0.25
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-15 | 300-PW-44003-01C03 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 22880 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 12.4 | CML-15 | CML: Reducer | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 12.2 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 | -0.37629 | 12.7 | 12.2 | 12.4 | 12.3 | 0.21602
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-22 | 300-PF-20500-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21642 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.85 | CML-22 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.6 | 3 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 14.9 | 14.6 | 15 | 14.9 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43127-01C02 | CML-1 | 150-FH-43127-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 1794 | Rope access | 2014-04-28 10:30 | 2014-04-28 12:00 | [36 empty] | 5.25 | CML-1 | CML: Elbow | 3 | 2015-05-26 | 2015-03-30 | 2014-04-28 10:30 | 2.5 | 2.3237 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 5 | 12 O'Clock | 150 | 7.11 | 150-FH-43127-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.3 | 5.3 | 5.4 | 0.17321
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-28 | 50-FG-45501-01C02 CML-28 | Yes | FPSO 2015 | Pipe Wall Thickness | 23547 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 5.25 | CML-28 | CML: Pipe Length | 3 | 2028-07-21 | 2030-03-06 | 2015-08-10 07:30 | 2.5 | 0.20067 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.2 | 5.1 | 5.5 | 0.17321
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45039-03C02 | CML-2 | 25-FG-45039-03C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10562 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.75 | CML-2 | CML: type TBC | 3 | 2015-07-01 | 2015-04-08 | 2013-11-16 | 2.5 | 1.8467 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.925 | 5.5 | 6 O'Clock | 25 | 6.35 | 25-FG-45039-03C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 5.8 | 5.5 | 5.8 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43129-01C02 | CML-1 | 50-FH-43129-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1780 | Rope access | 2014-04-28 08:00 | 2014-04-28 09:00 | [36 empty] | 5.75 | CML-1 | CML: Fitting | 3 | 2082-05-11 | 2089-10-03 | 2014-04-28 08:00 | 2.5 | 0.04406 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-FH-43129-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 5.5 | 5.8 | 5.8 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-1 | 150-FH-43027-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10563 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 6.75 | CML-1 | CML: type TBC | 3 | 2017-07-28 | 2017-03-31 | 2013-11-16 | 2.5 | 1.108 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.7 | 6.6 | 7 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-8 | 400-WC-40025-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1268 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 8.75 | CML-8 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.3 | 3 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.9 | 8.3 | 8.7 | 9.1 | 0.34157
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-3 | 400-WC-40024-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1072 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.6 | CML-3 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.3 | 3 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.5 | 8.3 | 8.7 | 8.9 | 0.2582
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56119-01C02 | CML-4 | 50-DH-56119-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21030 | Rope Access | 2014-05-19 09:30 | 2014-05-19 11:00 | [36 empty] | 4.95 | CML-4 | CML: type TBC | 3 | 2017-05-18 | 2017-10-21 | 2014-05-19 09:30 | 2.5 | 0.76647 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56119-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.9 | 4.9 | 5.2 | 0.17321
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-9 | 50-FG-45020-03C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10581 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.95 | CML-9 | CML: type TBC | 3 | 2015-04-26 | 2015-04-21 | 2013-11-17 | 2.5 | 1.5982 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.9 | 5.2 | 4.9 | 0.17321
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-14 | 250-PW-44006-01X01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1911 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 8.7 | CML-14 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.5 | 9 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 9.2 | 8.6 | 8.5 | 0.33665
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-31 | 50-DH-56070-01C02 CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 3247 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.25 | CML-31 | CML: type TBC | 3 | 2018-09-09 | 2019-04-04 | 2014-05-09 07:00 | 2.5 | 0.57582 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5.3 | 5 | 5.4 | 0.17321
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-15 | 250-PW-44004-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 22759 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 8.075 | CML-15 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-04-29 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | 0.23341 | 7.6 | 8.2 | 8.5 | 8 | 0.37749
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44029-01C02 | CML-2 | 250-PW-44029-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21906 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 7.8 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 3 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.8 | 7.6 | 8 | 7.8 | 0.1633
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20057-01C02-P | CML-4 | 100-PW-20057-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22817 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 7.975 | CML-4 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.7 | 12 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 | -1.2904 | 7.7 | 8.2 | 7.8 | 8.2 | 0.263
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-3 | 50-WC-40028-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1683 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 8.4333 | CML-3 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.2 | 9 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.4 | 8.7 |  | 8.2 | 0.25166
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42313-01S01 | CML-4 | 40-CI-42313-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7519 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 11.25 | CML-4 | CML: type TBC | 1 | 2059-10-24 | 2046-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 10.6 | 12 O'Clock | 40 | 7.14 | 40-CI-42313-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.6 | 11.3 | 11.4 | 11.7 | 0.46547
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42311-01S01 | CML-4 | 40-CI-42311-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7507 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 11.075 | CML-4 | CML: type TBC | 1 | 2059-10-24 | 2046-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 6.14 | 2.5 | 3.8737 | 10.6 | 3 O'Clock | 40 | 7.14 | 40-CI-42311-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 11.1 | 10.6 | 11.4 | 11.2 | 0.34034
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-28 | 250-WC-40017-01C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 2091 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 8.5 | CML-28 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.8 | 8.5 | 8.5 | 8.2 | 0.24495
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23302-01C02 | CML-4 | 80-VA-23302-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22520 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.75 | CML-4 | CML: Elbow | 3 | 2016-03-31 | 2016-07-29 | 2015-04-20 07:00 | 2.5 | 1.0553 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.5 | 3 O'Clock | 50 | 5.49 | 80-VA-23302-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.9 | 3.5 | 3.8 | 3.8 | 0.17321
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23301-01C02 | CML-3 | 80-VA-23301-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22510 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.85 | CML-3 | CML: Elbow | 3 | 2016-05-24 | 2016-09-28 | 2015-04-20 07:00 | 2.5 | 1.0023 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.6 | 6 O'Clock | 50 | 5.49 | 80-VA-23301-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 4 | 3.9 | 3.6 | 3.9 | 0.17321
FL02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-FL-43454-01C02-P | CML-3 | 50-FL-43454-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1127 |  | 2014-03-21 08:30 | 2014-03-21 09:00 | [36 empty] | 9.35 | CML-3 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 08:30 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 9.2 | 12 O'Clock | 400 | 7.92 | 400-WC-40061-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.2 | 9.3 | 9.6 | 9.3 | 0.17321
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-8 | 150-DC-57308-01C03 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20305 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 10.725 | CML-8 | CML: Pipe Length | 6 | 2044-01-07 | 2039-07-23 | 2014-10-02 07:00 | 2.5 | 0.27658 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.6 | 6 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.6 | 10.9 | 10.6 | 10.8 | 0.15
VA01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-VA-23054-01C02 | CML-10 | 25-VA-23054-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 22045 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 13.15 | CML-10 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-10-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 12.9 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 13.3 | 13.2 | 12.9 | 13.2 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43081-01C02 | CML-3 | 80-FH-43081-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12725 |  | 2014-01-27 08:00 | 2014-01-27 09:00 |  |  | Nestor | 2014-11-19 17:17 | [32 empty] | 5.55 | CML-3 | CML: Elbow | 3 | 2035-04-11 | 2037-10-27 | 2014-01-27 08:00 | 2.5 | 0.13669 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FH-43081-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 5.7 | 5.4 | 0.17321
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3424 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.55 | CML-1 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.4 | 9 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.7 | 5.4 | 5.4 | 0.17321
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1232 |  | 2014-03-22 08:30 | 2014-03-22 09:00 | [36 empty] | 6.15 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-WC-40049-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6 | 6 | 6.3 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43102-01C02 | CML-2 | 100-FH-43102-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12747 |  | 2014-01-24 08:00 | 2014-01-24 09:00 | [36 empty] | 6.15 | CML-2 | CML: type TBC | 3 | 2127-10-12 | 2131-07-23 | 2014-01-24 08:00 | 2.5 | 0.03076 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 6 O'Clock | 100 | 6.02 | 100-FH-43102-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.3 | 6 | 6.3 | 0.17321
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-7 | 50-FG-45024-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1190 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.85 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 3 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 6.7 | 7 | 7 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43517-01C02 | CML-1 | 150-FH-43517-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20469 | Rope Access | 2014-05-27 14:00 | 2014-05-27 15:00 | [36 empty] | 7.35 | CML-1 | CML: type TBC | 3 |  |  | 2014-05-27 14:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.2 | 9 O'Clock | 150 |  | 150-FH-43517-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.5 | 7.5 | 7.2 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43116-01C02 | CML-2 | 150-FH-43116-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1772 | Rope access | 2014-04-27 13:00 | 2014-04-27 14:00 | [36 empty] | 7.65 | CML-2 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-04-27 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 9 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.8 | 7.8 | 7.5 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-9 | 200-FH-43131-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2830 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.45 | CML-9 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.96 |  | 7.6 | 7.6 | 7.3 | 7.3 | 0.17321
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44037-01C03 | CML-5 | 300-PW-44037-01C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21915 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 10.625 | CML-5 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-10-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 10.5 | 9 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.6 | 10.5 | 10.9 | 10.5 | 0.1893
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56103-01C02 | CML-1 | 50-DH-56103-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8059 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 5.15 | CML-1 | CML: type TBC | 3 | 2021-03-22 | 2022-01-22 | 2015-01-22 07:30 | 2.5 | 0.38913 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56103-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.2 | 5.2 | 5.3 | 0.17321
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-43 | 50-DH-56070-01C02 CML-43 |  | FPSO 2014 | Pipe Wall Thickness | 3259 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.45 | CML-43 | CML: type TBC | 3 | 2021-10-17 | 2022-09-10 | 2014-05-09 07:00 | 2.5 | 0.36256 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.6 | 5.5 | 5.5 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43106-01C02 | CML-5 | 100-FH-43106-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12774 |  | 2014-01-25 10:00 | 2014-01-25 11:00 | [36 empty] | 6.05 | CML-5 | CML: type TBC | 3 | 2032-07-24 | 2033-03-12 | 2014-01-25 10:00 | 2.5 | 0.18371 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 12 O'Clock | 100 | 6.02 | 100-FH-43106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.3 | 6 | 6 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-11 | 50-WC-40451-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 3073 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | [36 empty] | 8.55 | CML-11 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-03 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.2 | 3 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | -7.7025 | 8.6 | 8.2 | 8.7 | 8.7 | 0.23805
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-15 | 250-PW-44004-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 5634 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 8.475 | CML-15 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-20 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 9.2 | 8.6 | 8.3 | 0.58523
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-34 | 50-DH-56070-01C02 CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 3250 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.15 | CML-34 | CML: type TBC | 3 | 2017-11-12 | 2018-05-06 | 2014-05-09 07:00 | 2.5 | 0.68246 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5.2 | 4.9 | 5.3 | 0.17321
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-4 | 50-FG-45023-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12990 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 5.45 | CML-4 | CML: type TBC | 3 | 2019-02-15 | 2019-09-27 | 2014-01-20 07:00 | 2.5 | 0.53195 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.5 | 5.6 | 5.2 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-1 | 50-WC-40452-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10598 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 8.5 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2013-11-17 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.2 | 12 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.5 | 8.6 | 8.7 | 0.21602
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20016-01C02-P | CML-5 | 200-PL-20016-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21236 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 9.2 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9 | 12 O'Clock | 200 | 6.35 | 200-PL-20016-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.2 | 9.5 | 9.1 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43036-01C02 | CML-5 | 100-FH-43036-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12669 |  | 2014-01-26 10:00 | 2014-01-26 11:00 | [36 empty] | 6.35 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-26 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-FH-43036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.3 | 6.6 | 6.2 | 0.17321
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38452-09C02-P | CML-5 | 50-CG-38452-09C02-P CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24323 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.55 | CML-5 | CML: Fitting | 3 | 2056-10-23 | 2050-02-10 | 2016-06-01 07:00 | 2.77 | 0 | A4: Left Quadrant |  | 4.11 | 2.77 | 3.44 | 7.4 | 9 O'Clock | 150 | 7.11 | 150-FG-45005-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.63 |  | 7.5 | 7.8 | 7.5 | 7.4 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43124-01C02 | CML-3 | 80-FH-43124-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12845 |  | 2014-02-05 11:00 | 2014-02-05 13:00 | [36 empty] | 5.55 | CML-3 | CML: Pipe Length | 3 | 2050-12-24 | 2046-03-08 | 2014-02-05 11:00 | 0.54 | 0.13169 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43124-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.5 | 5.5 | 5.4 | 5.8 | 0.17321
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-43 | 350-FL-43512-01C02 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 23554 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.55 | CML-43 | CML: Elbow | 3 | 2036-04-02 | 2033-03-29 | 2015-08-10 07:30 | 2.5 | 0.23716 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 9 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.8 | 7.5 | 7.5 | 7.4 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-5 | 200-FH-43131-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2826 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.45 | CML-5 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.2 | 12 O'Clock | 200 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.86 |  | 7.2 | 7.5 | 7.6 | 7.5 | 0.17321
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-11 | 250-PG-23015-06C03-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 13043 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 18.55 | CML-11 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 13:00 | 8.55 | 0 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.3 | 12 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.75 |  | 18.3 | 18.6 | 18.6 | 18.7 | 0.17321
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-46 | 50-DH-56137-01C02 CML-46 |  | FPSO 2014 | Pipe Wall Thickness | 21784 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 20.95 | CML-46 | CML: Reducer | 6 | 2090-02-10 | 2081-10-05 | 2014-10-01 07:00 | 6.6 | 0 | A1: Outside Quadrant |  | 8.27 | 6.6 | 7.435 | 20.8 | 12 O'Clock | 400 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.2 |  | 20.8 | 20.9 | 21.2 | 20.9 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40401-01C02 | CML-1 | 200-WC-40401-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7917 |  | 2015-01-17 08:00 | 2015-01-17 09:00 |  |  | Administrator | 2015-09-08 11:21 | [32 empty] | 8.35 | CML-1 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-01-17 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 9 O'Clock | 200 | 6.35 | 200-WC-40401-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.6 | 8.4 | 8.2 | 8.2 | 0.19149
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-4 | 400-WC-40025-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1264 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 8.45 | CML-4 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.3 | 6 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.6 | 8.3 | 8.3 | 8.6 | 0.17321
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-1 | 50-PL-23300-09C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13117 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.45 | CML-1 | CML: type TBC | 6 | 2020-09-15 | 2019-09-17 | 2014-02-04 07:00 | 2.81 | 1.1319 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 10.3 | 3 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.49 |  | 10.4 | 10.3 | 10.7 | 10.4 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-17 | 150-WC-40006-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1677 | Rope Access | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.35 | CML-17 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 6 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.4 | 8.3 | 8.2 | 8.5 | 0.1291
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57012-01C02 | CML-2 | 50-DC-57012-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2881 | Rope Access | 2014-04-24 14:00 | 2014-04-24 15:00 | [36 empty] | 9.25 | CML-2 | CML: type TBC | 3 | 2065-02-10 | 2057-09-22 | 2014-04-24 14:00 | 0.37 | 0 | A3: Inside Quadrant |  | 2.54 | 0.37 | 1.1087 | 8.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.13 |  | 10.3 | 9.2 | 8.5 | 9 | 0.75939
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38486-09C02-P | CML-10 | 80-CG-38486-09C02-P CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10075 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 15.5 | CML-10 | CML: type TBC | 6 | 2099-02-10 | 2086-04-06 | 2013-11-07 | 2.5 | 0 | A1: Outside Quadrant |  | 5.07 | 2.5 | 3.785 | 15.3 | 12 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.8 |  | 15.3 | 15.6 | 15.6 |  | 0.17321
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-4 | 100-FG-45001-09C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10419 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 16.15 | CML-4 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2013-11-13 | 4.7 | 0 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 16 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 16.4 | 16 | 16.1 | 16.1 | 0.17321
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-4 | 25-VA-23054-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20691 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 20.925 | CML-4 | CML: Fitting | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 20.7 | 12 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.48 |  | 20.7 | 21 | 21.1 | 20.9 | 0.17078
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-15 | 50-DH-56137-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 5683 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [35 empty] | Low alarm breach | 17.625 | CML-15 | CML: Pipe Length | 3 | 2018-05-13 | 2016-04-12 | 2014-06-21 14:00 | 2.5 | 3.8243 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.4 | 6 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.9 |  | 17.7 | 17.6 | 17.4 | 17.8 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-22 | 250-WC-40017-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 2085 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 8.3 | CML-22 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 12 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.3 | 8.3 | 8.4 | 0.08165
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-9 | 50-PL-23052-09C03 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10173 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.725 | CML-9 | CML: type TBC | 6 | 2019-10-21 | 2018-12-05 | 2013-11-09 | 2.81 | 1.2922 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 10.5 | 3 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.69 |  | 10.9 | 10.5 | 10.8 | 10.7 | 0.17078
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-12 | 50-PL-23052-09C03 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10176 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.775 | CML-12 | CML: type TBC | 6 | 2021-02-28 | 2020-02-07 | 2013-11-09 | 2.81 | 1.0655 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 10.6 | 3 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.79 |  | 10.7 | 10.6 | 11 | 10.8 | 0.17078
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20055-01C03-P | CML-1 | 150-PG-20055-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21529 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 11.225 | CML-1 | CML: Fitting | 6 | 2098-02-09 | 2085-10-05 | 2014-07-13 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 11 | 6 O'Clock | 150 | 10.97 | 150-PG-20055-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11.3 | 11.2 | 11 | 11.4 | 0.17078
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-4 | 100-FG-45043-03C02-E CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22650 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.175 | CML-4 | CML: Elbow | 3 | 2021-02-21 | 2020-01-29 | 2015-04-27 07:00 | 1.88 | 0.53546 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 5 | 12 O'Clock | 100 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.12 |  | 5 | 5.4 | 5.1 | 5.2 | 0.17078
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-5 | 50-CG-38452-09C02-P CML-5 | Yes | FPSO 2015 | Pipe Wall Thickness | 7853 | Line is FFS. Current RBI frequency is 48m. Action: CML’s to Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-08 13:39 | [32 empty] | 6.325 | CML-5 | CML: Fitting | 3 | 2038-05-22 | 2038-03-16 | 2015-01-14 07:00 | 2.5 | 0.15406 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.5 | 6.4 | 6.3 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-8 | 50-FH-43016-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22669 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 7.175 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 12 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 | -0.39782 | 7 | 7.4 | 7.1 | 7.2 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-18 | 50-DH-56109-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21007 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.175 | CML-18 | CML: Elbow | 3 | 2018-12-04 | 2019-07-08 | 2014-05-24 10:30 | 2.5 | 0.55143 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5.4 | 5.2 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-14 | 400-WC-40024-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1083 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.675 | CML-14 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.4 | 3 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.5 | 8.4 | 9.2 | 8.6 | 0.3594
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-8 | 50-FG-45021-03C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2620 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.175 | CML-8 | CML: type TBC | 3 | 2018-06-29 | 2018-06-17 | 2014-04-26 10:45 | 2.5 | 0.59827 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.90432 | 5.4 | 5.1 | 5.2 | 5 | 0.17078
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44036-01C02-P | CML-4 | 80-PW-44036-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22962 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 8.175 | CML-4 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-04 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.9 | 9 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 0.35437 | 8.4 | 8.1 | 8.3 | 7.9 | 0.22174
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-1 | 200-PG-23008-15S01-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21131 | Reviewed on 20/11/14. FFS. Recheck in Oct. 18. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-20 17:42 | [32 empty] | 5.325 | CML-1 | CML: Pipe Length | 3 | 2022-10-07 | 2023-10-08 | 2014-10-08 07:00 | 2.5 | 0.32491 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-DH-56557-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.4 | 5.3 | 5.5 | 0.17078
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-16 | 200-PG-23008-15S01-A CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20975 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 5.325 | CML-16 | CML: type TBC | 3 | 2017-01-28 | 2017-03-13 | 2014-05-16 13:00 | 2.5 | 0.96069 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 12 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.4 | 5.5 | 5.3 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43105-01C02 | CML-4 | 100-FH-43105-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12767 |  | 2014-01-25 09:00 | 2014-01-25 10:00 | [36 empty] | 5.675 | CML-4 | CML: type TBC | 3 | 2017-10-31 | 2017-12-23 | 2014-01-25 09:00 | 2.5 | 0.79622 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 12 O'Clock | 100 | 6.02 | 100-FH-43105-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.9 | 5.7 | 5.6 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56083-01C02 | CML-3 | 100-DH-56083-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22528 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.825 | CML-3 | CML: Pipe Length | 3 | 2029-03-17 | 2029-09-24 | 2015-04-20 07:00 | 2.5 | 0.22273 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-DH-56083-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 6 | 5.9 | 5.6 | 0.17078
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80002-01C02 | CML-8 | 100-VA-80002-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2168 | Rope Access | 2014-03-30 09:30 | 2014-03-30 11:00 | [36 empty] | 5.825 | CML-8 | CML: type TBC | 3 | 2020-05-09 | 2020-08-01 | 2014-03-30 09:30 | 2.5 | 0.50695 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 6 O'Clock | 100 | 6.02 | 100-VA-80002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.9 | 5.6 | 6 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-1 | 50-PW-44015-01X01 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10284 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 8.675 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2013-11-10 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.5 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.8 | 8.7 | 8.7 | 8.5 | 0.12583
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 7825 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:44 | [32 empty] | 6.175 | CML-2 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-01-13 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 25 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6.2 | 6.4 | 6 | 0.17078
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-16 | 100-PG-23406-03C03 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20742 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 11.975 | CML-16 | CML: Elbow | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 10.7 | 9 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11.8 | 11.6 | 13.8 | 10.7 | 1.3074
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-15 | 100-PG-23406-03C03 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20741 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 11.15 | CML-15 | CML: Fitting | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 10.7 | 12 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.7 | 11.2 | 10.9 | 11.8 | 0.47958
FG02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20947 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 6.175 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 3 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.4 | 6.1 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-3 | 100-FH-43104-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12754 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 6.175 | CML-3 | CML: type TBC | 3 | 2128-03-29 | 2132-01-13 | 2014-01-25 07:00 | 2.5 | 0.03063 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.4 | 6.1 | 0.17078
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44029-01C02 | CML-4 | 250-PW-44029-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21908 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 8.7 | CML-4 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 9 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 9.7 | 8.3 | 8.6 | 8.2 | 0.68799
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-7 | 150-FL-43514-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20500 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 6.825 | CML-7 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.6 | 3 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.9 | 6.6 | 7 | 6.8 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-5 | 300-PW-44002-01X01-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22851 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.35 | CML-5 | CML: Elbow | 6 | 2022-02-27 | 2021-02-22 | 2015-05-01 07:00 | 2.5 | 0.89255 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 8.6 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 1.8622 | 9.8 | 8.6 | 9.5 | 9.5 | 0.51962
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PL-20051-01C02-P | CML-1 | 150-PL-20051-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21505 | Protective mesh removed | 2014-06-30 08:00 | 2014-06-30 09:00 | [36 empty] | 7.525 | CML-1 | CML: Elbow | 3 | 2076-02-10 | 2064-03-16 | 2014-06-30 08:00 | 0.84 | 0 | A1: Outside Quadrant |  | 4.11 | 0.84 | 2.0306 | 7.4 | 12 O'Clock | 150 | 7.11 | 150-PL-20051-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.56 |  | 7.4 | 7.7 | 7.5 | 7.5 | 0.12583
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-5 | 200-PL-20008-01C02-H CML-5 | Yes | FPSO 2015 | Pipe Wall Thickness | 8802 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 7 | CML-5 | CML: Pipe Length | 3 | 2065-11-29 | 2058-08-19 | 2015-02-21 07:00 | 1.1 | 0 | A2: Right Quadrant |  | 3.35 | 1.1 | 1.8281 | 6.5 | 3 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7 | 6.5 | 7.2 | 7.3 | 0.3559
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-14 | 200-FH-43012-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2844 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.325 | CML-14 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.1 | 12 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.76 |  | 7.1 | 7.5 | 7.3 | 7.4 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-14 | 150-FH-43518-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2714 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.175 | CML-14 | CML: Elbow | 3 | 2055-01-13 | 2047-12-27 | 2014-03-12 09:00 | 1.23 | 0.14119 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 | 0 | 7 | 7.2 | 7.4 | 7.1 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-1 | 150-FH-43518-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2701 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.175 | CML-1 | CML: Pipe Length | 3 | 2055-01-13 | 2047-12-27 | 2014-03-12 09:00 | 1.23 | 0.14119 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 | 0 | 7 | 7.2 | 7.4 | 7.1 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-14 | 150-FH-43518-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 353 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.175 | CML-14 | CML: Elbow | 3 | 2054-12-24 | 2047-12-10 | 2014-03-12 | 1.23 | 0.14137 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 |  | 7 | 7.2 | 7.4 | 7.1 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-1 | 150-FH-43518-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 340 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.175 | CML-1 | CML: Pipe Length | 3 | 2054-12-24 | 2047-12-10 | 2014-03-12 | 1.23 | 0.14137 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 |  | 7 | 7.2 | 7.4 | 7.1 | 0.17078
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-5 | 150-PG-23043-06C02-P CML-5 | Yes | FPSO 2016 | Pipe Wall Thickness | 23767 | re-check line | 2016-02-13 07:00 | 2016-02-13 15:00 | Check Corrosion Rate of 0.47mm/ yr | [35 empty] | 9.925 | CML-5 | CML: Pipe Length | 3 | 2026-10-05 | 2024-09-27 | 2016-02-13 07:00 | 4.7 | 0.46952 | A3: Inside Quadrant |  | 7.97 | 4.7 | 5.6494 | 9.7 | 6 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 | 0 | 10 | 10.1 | 9.7 | 9.9 | 0.17078
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-5 | 150-PG-23043-06C02-P CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24156 | re-check line | 2016-02-13 | 2016-02-13 | [36 empty] | 9.925 | CML-5 | CML: Pipe Length | 3 | 2026-10-03 | 2024-09-26 | 2016-02-13 | 4.7 | 0.46966 | A3: Inside Quadrant |  | 7.97 | 4.7 | 5.6494 | 9.7 | 6 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 | 0.72034 | 10 | 10.1 | 9.7 | 9.9 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43030-01C02 | CML-6 | 400-FH-43030-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10030 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 8.075 | CML-6 | CML: type TBC | 3 | 2129-03-01 | 2113-11-23 | 2013-11-04 | 2.5 | 0.04679 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 12 O'Clock | 400 | 7.92 | 400-FH-43030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8 | 8.1 | 8.3 | 0.17078
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-5 | 50-PL-23514-01C03 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8638 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:19 | [32 empty] | 8.175 | CML-5 | CML: Pipe Length | 6 | 2027-09-19 | 2027-06-11 | 2015-02-10 11:30 | 2.5 | 0.43601 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 6 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.4 | 8.2 | 8 | 8.1 | 0.17078
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-VA-23058-01C02 | CML-2 | 200-VA-23058-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3142 | Rope Access | 2014-05-02 13:00 | 2014-05-02 14:00 | [36 empty] | 8.175 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-05-02 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 6 O'Clock | 200 | 6.35 | 200-VA-23058-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.1 | 8.2 | 8 | 8.4 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-14 | 50-PW-44015-01X01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 5724 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 8.875 | CML-14 | CML: Reducer | 3 | 2044-01-06 | 2047-03-10 | 2014-06-22 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.1825 | 8.6 | 3 O'Clock | 50 | 5.56 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | -6.831 | 9 | 8.6 | 9.1 | 8.8 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-2 | 100-DC-57036-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1408 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 11.8 | CML-2 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.7 | 3 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  |  | 10.7 | 11.7 | 13 | 1.1533
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-8 | 300-FL-43080-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2387 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 8.425 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.2 | 6 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.6 | 8.4 | 8.2 | 8.5 | 0.17078
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-18 | 50-PL-23516-03C03 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 7806 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:00 | [32 empty] | 8.575 | CML-18 | CML: Fitting | 6 | 2043-02-15 | 2042-07-22 | 2015-01-13 07:00 | 2.5 | 0.20988 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.8 | 8.4 | 8.6 | 8.5 | 0.17078
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38491-09C02 | CML-1 | 50-CG-38491-09C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2540 |  | 2014-04-03 10:00 | 2014-04-03 11:00 | [36 empty] | 8.675 | CML-1 | CML: type TBC | 3 | 2035-03-24 | 2029-07-25 | 2014-04-03 10:00 | 2.5 | 0.28589 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-CG-38491-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.6 | 8.9 | 8.7 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40034-01C02 | CML-6 | 100-WC-40034-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1720 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 8.4333 | CML-6 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.3 | 12 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.6 | 8.4 |  | 0.15275
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43109-01C02 | CML-2 | 200-FH-43109-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12786 |  | 2014-01-18 14:30 | 2014-01-18 15:30 | [36 empty] | 8.175 | CML-2 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 14:30 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 8 | 3 O'Clock | 200 | 6.35 | 200-FH-43109-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.66 |  | 8.4 | 8 | 8.2 | 8.1 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-9 | 50-FG-45018-03C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2591 | Rope Access | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 9.425 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 9.2 | 12 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | -9.8958 | 9.2 | 9.5 | 9.6 | 9.4 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-24 | 250-FH-43303-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 12962 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 9.825 | CML-24 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.6 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10 | 9.6 | 9.9 | 9.8 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40401-01C02 | CML-3 | 200-WC-40401-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7919 |  | 2015-01-17 08:00 | 2015-01-17 09:00 |  |  | Administrator | 2015-09-08 11:21 | [32 empty] | 8.425 | CML-3 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-17 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 12 O'Clock | 200 | 6.35 | 200-WC-40401-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.6 | 8.4 | 8.4 | 0.12583
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-12 | 300-PG-20502-01C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 23899 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.675 | CML-12 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.5 | 6 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.7 | 10.6 | 10.5 | 10.9 | 0.17078
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-12 | 300-PG-20502-01C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20759 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.675 | CML-12 | CML: type TBC | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.5 | 6 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.7 | 10.6 | 10.5 | 10.9 | 0.17078
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20026-03C03-P | CML-4 | 80-PG-20026-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21668 | Protective mesh removed | 2014-06-26 08:00 | 2014-06-26 09:00 | [36 empty] | 13.825 | CML-4 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-06-26 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 13.6 | 6 O'Clock | 100 | 11.13 | 80-PG-20026-03C03-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 13.8 | 13.9 | 13.6 | 14 | 0.17078
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-13 | 50-CG-38001-09C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10927 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.925 | CML-13 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0.06606 | A3: Inside Quadrant |  | 5.74 |  |  | 8.7 | 6 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.7 | 9 | 9.1 | 8.7 | 8.9 | 0.17078
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-12 | 50-CG-38001-09C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10926 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.075 | CML-12 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.3873 | A4: Left Quadrant |  | 5.74 |  |  | 7.9 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.9 | 8.3 | 8.1 | 8 | 7.9 | 0.17078
DH01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-DH-56004-01C02 | CML-17 | 80-DH-56004-01C02 CML-17 | yes | FPSO 2016 | Pipe Wall Thickness | 24502 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.525 | CML-17 | CML: Elbow | 3 | 2017-08-18 | 2018-01-30 | 2016-07-09 07:00 | 2.5 | 0.7208 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.3 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 | 0.39364 | 3.5 | 3.6 | 3.7 | 3.3 | 0.17078
FH01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-FH-43141-01C02 | CML-16 | 150-FH-43141-01C02 CML-16 | yes | FPSO 2015 | Pipe Wall Thickness | 5025 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.475 | CML-16 | CML: type TBC | 0 | 2036-09-22 | 2030-07-25 | 2015-03-04 07:00 | 2.5 | 0.03709 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.3 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.7 | 3.4 | 3.5 | 3.3 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56040-01C02 | CML-1 | 80-DH-56040-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20921 | Rope Access | 2014-05-21 07:00 | 2014-05-21 08:00 | [36 empty] | 4.775 | CML-1 | CML: Elbow | 3 | 2016-09-03 | 2017-01-19 | 2014-05-21 07:00 | 2.5 | 0.9169 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 12 O'Clock | 80 | 5.49 | 80-DH-56040-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.8 | 5 | 4.7 | 0.17078
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-13 | 250-PW-44004-01C02 CML-13 | Yes | FPSO 2014 | Pipe Wall Thickness | 5632 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 10 | CML-13 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-06-20 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 10.1 | 9.8 | 11.8 | 1.4353
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56564-01C02 | CML-2 | 50-DH-56564-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21118 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18.Update RBI study to include this line. | 2014-10-09 07:00 | 2014-10-09 15:00 |  |  | Nestor | 2014-11-21 14:25 | [32 empty] | 5.025 | CML-2 | CML: Elbow | 3 | 2018-12-26 | 2019-08-02 | 2014-10-09 07:00 | 2.5 | 0.54534 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-DH-56564-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 4.8 | 5.1 | 5 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-13 | 50-FG-45019-03C02 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10495 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.025 | CML-13 | CML: type TBC | 3 | 2015-04-18 | 2015-04-13 | 2013-11-15 | 2.5 | 1.6174 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 4.8 | 5 | 5.1 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-2 | 250-PW-44006-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7994 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 8.85 | CML-2 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.6 | 12 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 0.24328 | 8.6 | 9.1 | 8.9 | 8.8 | 0.20817
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-2 | 50-FG-45023-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12988 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 5.225 | CML-2 | CML: type TBC | 3 | 2017-01-04 | 2017-05-25 | 2014-01-20 07:00 | 2.5 | 0.84487 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.4 | 5 | 5.3 | 0.17078
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-5 | 200-PG-23008-15S01-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21043 | Rope Access | 2014-05-19 07:00 | 2014-05-19 08:00 | [36 empty] | 5.275 | CML-5 | CML: type TBC | 3 | 2020-01-30 | 2020-10-17 | 2014-05-19 07:00 | 2.5 | 0.45587 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-DH-56121-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.5 | 5.2 | 5.3 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45036-03C02 | CML-2 | 50-FG-45036-03C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2574 |  | 2014-04-26 13:00 | 2014-04-26 14:00 | [36 empty] | 5.275 | CML-2 | CML: type TBC | 3 | 2019-08-25 | 2019-08-10 | 2014-04-26 13:00 | 2.5 | 0.48734 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-FG-45036-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.5 | 5.3 | 5.2 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-8 | 50-PW-44013-01X01 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10322 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 8.675 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2013-11-10 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.6 | 9 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.8 | 8.7 | 8.6 | 8.6 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-13 | 50-WC-40451-01C02 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10153 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 8.35 | CML-13 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2013-11-09 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.3 | 8.5 | 8.3 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-6 | 50-FH-43450-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7685 | Re-check. FFS | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:20 | [32 empty] | 5.525 | CML-6 | CML: Pipe Length | 3 | 2033-10-03 | 2035-12-09 | 2015-01-08 13:00 | 2.5 | 0.14935 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | -0.34967 | 5.7 | 5.5 | 5.3 | 5.6 | 0.17078
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43014-01C02 | CML-2 | 250-FL-43014-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23074 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.525 | CML-2 | CML: Fitting | 3 | 2162-02-07 | 2161-01-06 | 2015-05-07 07:00 | 2.5 | 0.02588 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | -0.19366 | 6.3 | 6.5 | 6.7 | 6.6 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45004-03C02 | CML-8 | 150-FG-45004-03C02 CML-8 |  | FPSO 2016 | Pipe Wall Thickness | 24340 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.775 | CML-8 | CML: Fitting | 3 | 2040-09-01 | 2035-11-29 | 2016-06-06 07:00 | 2.5 | 0.16903 | A2: Right Quadrant |  | 4.11 | 2.5 | 3.305 | 6.6 | 3 O'Clock | 150 | 7.11 | 150-FG-45004-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.6 | 7 | 6.7 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-7 | 100-DH-56561-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7939 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 7.025 | CML-7 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-17 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.8 | 3 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.2 | 6.8 | 7 | 7.1 | 0.17078
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-25 | 50-CG-38452-09C02-P CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 8822 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.025 | CML-25 | CML: Elbow | 3 | 2029-11-20 | 2027-08-09 | 2015-02-21 07:00 | 1.1 | 0.3185 | A3: Inside Quadrant |  | 3.35 | 1.1 | 1.8281 | 5.8 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 6.2 | 6 | 5.8 | 6.1 | 0.17078
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-23 | 50-FG-45300-01C02 CML-23 | yes | FPSO 2015 | Pipe Wall Thickness | 7846 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:42 | [32 empty] | 5.025 | CML-23 | CML: Pipe Length | 3 | 2020-01-26 | 2020-10-12 | 2015-01-13 13:00 | 2.5 | 0.4566 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5 | 5.1 | 4.8 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-3 | 50-FG-45019-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2594 | Rope Access | 2014-04-26 08:00 | 2014-04-26 09:00 | [36 empty] | 5.025 | CML-3 | CML: type TBC | 3 | 2017-02-12 | 2017-02-04 | 2014-04-26 08:00 | 2.5 | 0.82014 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.89938 | 5.1 | 5 | 5.2 | 4.8 | 0.17078
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57065-01C02 | CML-1 | 250-DC-57065-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20289 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 11.725 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.8 | 12 O'Clock | 250 | 6.35 | 250-DC-57065-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 11.7 | 12 | 12.4 | 0.68007
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23410-01C03 | CML-3 | 100-PG-23410-01C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20773 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 11.35 | CML-3 | CML: Elbow | 6 | 2074-02-03 | 2073-10-17 | 2014-10-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 10.8 | 6 O'Clock | 100 | 8.56 | 100-PG-23410-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.1 | 11.3 | 10.8 | 12.2 | 0.60277
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21795 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 10.925 | 250-PL-43310-01C02 | Piping | 3 | 2051-11-30 |  | 2014-10-02 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 10.8 | 9 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 11.1 | 11 | 10.8 | 0.15
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-13 | 250-PW-44006-01X01 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1910 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 9.2 | CML-13 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.9 | 8.9 | 8.7 | 9.3 | 0.52915
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-17 | 250-PW-44004-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 22761 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 8.45 | CML-17 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-04-29 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | -0.93365 | 8.3 | 8.6 | 8.5 | 8.4 | 0.1291
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-14 | 250-PW-44004-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 22758 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 8.425 | CML-14 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-04-29 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | 0.11671 | 8.5 | 8.5 | 8.4 | 8.3 | 0.095743
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-22 | 80-PW-44001-01C02-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 22013 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 9.375 | CML-22 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.4 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 10 | 9.7 | 8.4 | 9.4 | 0.69462
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-9 | 200-PL-20008-01C02-H CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8806 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.675 | CML-9 | CML: Fitting | 3 | 2065-11-29 | 2058-08-19 | 2015-02-21 07:00 | 1.1 | 0 | A4: Left Quadrant |  | 3.35 | 1.1 | 1.8281 | 6.5 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 6.7 | 6.9 | 6.6 | 6.5 | 0.17078
FG02 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8475 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.225 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-GN-67007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.4 | 6.3 | 6 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-7 | 50-FH-43011-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7957 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.275 | CML-7 | CML: Y Fitting | 3 | 2018-04-11 | 2017-08-20 | 2015-01-18 08:00 | 2.5 | 1.114 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 6.1 | 3 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.1 | 6.3 | 6.5 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-6 | 50-DH-56070-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3222 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.525 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.6 | 6.5 | 6.3 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-18 | 150-WC-40006-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1678 | Rope Access | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.375 | CML-18 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 6 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.5 | 8.3 | 8.3 | 8.4 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-4 | 100-FH-43507-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7868 | Line is FFS. It has been check twice. The higher values reported here are from the data collected in Apr. 2014. The rechecked CR’s from data from Jan. 2015 are lower. Current RBI frequency is 48m. Action: to recheck line in a 24m (Jan. 2017) to confirm CR. | 2015-01-14 09:30 | 2015-01-14 10:30 |  |  | Administrator | 2015-09-07 17:02 | [32 empty] | 6.475 | CML-4 | CML: Elbow | 3 | 2022-08-24 | 2021-12-03 | 2015-01-14 09:30 | 2.5 | 0.49908 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.3 | 9 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | 0.13939 | 6.7 | 6.4 | 6.5 | 6.3 | 0.17078
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-1 | 50-FG-45024-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1205 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.775 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 12 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.8 | 6.7 | 7 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45003-03C02 | CML-8 | 150-FG-45003-03C02 CML-8 |  | FPSO 2016 | Pipe Wall Thickness | 24374 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.225 | CML-8 | CML: Elbow | 3 | 2139-10-13 | 2117-09-18 | 2016-06-06 07:00 | 2.5 | 0.03646 | A2: Right Quadrant |  | 4.11 | 2.5 | 3.305 | 7 | 3 O'Clock | 150 | 7.11 | 150-FG-45003-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.3 | 7 | 7.2 | 7.4 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-17 | 400-WC-40022-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1111 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.5 | CML-17 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.4 | 12 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.4 | 8.5 | 8.6 | 8.5 | 0.08165
DH01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 80-DH-56004-01C02 | CML-10 | 80-DH-56004-01C02 CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 5019 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.375 | CML-10 | CML: type TBC | 0 | 2023-07-21 | 2020-10-24 | 2015-03-04 07:00 | 2.5 | 0.08345 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.2 | 6 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.6 | 3.4 | 3.2 | 3.3 | 0.17078
DH01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 80-DH-56004-01C02 | CML-8 | 80-DH-56004-01C02 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 5007 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [35 empty] | Low alarm breach | 3.375 | CML-8 | CML: type TBC | 0 | 2023-07-17 | 2020-10-20 | 2015-03-03 07:00 | 2.5 | 0.08356 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.2 | 12 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.6 | 3.3 | 3.4 | 0.17078
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-5 | 150-PG-23043-06C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 24274 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 10.875 | CML-5 | CML: Pipe Length | 3 | 2043-12-14 | 2039-04-30 | 2014-09-24 07:00 | 4.7 | 0.20519 | A4: Left Quadrant |  | 7.97 | 4.7 | 5.6494 | 10.7 | 9 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 11.1 | 10.9 | 10.8 | 10.7 | 0.17078
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-12 | 50-PL-23042-09C03 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10077 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.625 | CML-12 | CML: type TBC | 6 | 2018-12-25 | 2018-02-23 | 2013-11-07 | 2.5 | 1.538 | A3: Inside Quadrant |  | 5.07 | 2.5 | 3.785 | 10.4 | 6 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.6 | 10.8 | 10.4 | 10.7 | 0.17078
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-22 | 50-CG-38452-09C02-P CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 23762 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 11.375 | CML-22 | CML: Reducer | 3 | 2075-10-24 | 2059-08-12 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 11.2 | 3 O'Clock | 80 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.4 | 11.2 | 11.3 | 11.6 | 0.17078
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-16 | 50-CG-38500-01C02 CML-16 | Yes | FPSO 2016 | Pipe Wall Thickness | 24501 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.825 | CML-16 | CML: Pipe Length | 3 | 2018-04-13 | 2018-10-21 | 2016-07-09 07:00 | 2.5 | 0.62427 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.6 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 | 0.19682 | 4 | 3.8 | 3.9 | 3.6 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-19 | 50-FG-45020-03C02 CML-19 | yes | FPSO 2013 | Pipe Wall Thickness | 10591 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.625 | CML-19 | CML: type TBC | 3 | 2014-08-25 | 2014-08-22 | 2013-11-17 | 2.5 | 2.4621 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.6 | 4.8 | 4.7 | 4.4 | 0.17078
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23403-01C03-A | CML-7 | 150-PG-23403-01C03-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5608 |  | 2014-06-20 08:00 | 2014-06-20 09:00 | [36 empty] | 11.2 | CML-7 | CML: Fitting | 6 | 2065-11-03 | 2058-03-13 | 2014-06-20 08:00 | 2.5 | 0.16145 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.8 | 6 O'Clock | 150 | 10.97 | 150-PG-23403-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.3 | 11.6 | 10.8 | 11.1 | 0.33665
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-25 | 50-FG-45020-03C02 CML-25 |  | FPSO 2013 | Pipe Wall Thickness | 10597 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.875 | CML-25 | CML: type TBC | 3 | 2015-02-02 | 2015-01-29 | 2013-11-17 | 2.5 | 1.8142 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 4.8 | 4.9 | 5.1 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-13 | 50-PW-44013-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22732 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 9.025 | CML-13 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-04-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.7 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 | 0.35351 | 9.4 | 8.7 | 9 | 9 | 0.28723
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62006-01S01 | CML-8 | 50-DO-62006-01S01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1468 | Rope access | 2014-04-25 11:00 | 2014-04-25 12:00 | [36 empty] | 11.575 | CML-8 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2014-04-25 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 10.8 | 9 O'Clock | 50 | 5.54 | 50-DO-62006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 12.1 | 12.3 | 11.1 | 10.8 | 0.73655
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-16 | 100-DC-57036-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1422 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 11.9667 | CML-16 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.8 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  |  | 12.1 | 13 | 10.8 | 1.106
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-1 | 50-CG-38500-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7873 |  | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:40 | [32 empty] | 5.125 | CML-1 | CML: Elbow | 3 | 2021-02-13 | 2021-12-12 | 2015-01-14 10:30 | 2.5 | 0.3943 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 5.2 | 5.3 | 4.9 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56117-01C02 | CML-1 | 50-DH-56117-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21014 | Rope Access | 2014-05-19 13:00 | 2014-05-19 14:00 | [36 empty] | 5.125 | CML-1 | CML: type TBC | 3 | 2017-12-31 | 2018-06-29 | 2014-05-19 13:00 | 2.5 | 0.66262 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DH-56117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 5.1 | 4.9 | 5.2 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-7 | 50-FG-45020-03C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2606 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.125 | CML-7 | CML: type TBC | 3 | 2017-09-12 | 2017-09-02 | 2014-04-26 09:30 | 2.5 | 0.70918 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.91025 | 5.1 | 5.3 | 4.9 | 5.2 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44025-01X01 | CML-2 | 50-PW-44025-01X01 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10341 | Deck Level | 2013-11-11 | 2013-11-11 | [36 empty] | 8.825 | CML-2 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2013-11-11 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.8 | 8.8 | 8.7 | 9 | 0.12583
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44030-01C02 | CML-1 | 250-PW-44030-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22895 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.275 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.4 | 12 O'Clock | 250 | 6.35 | 250-PW-44030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 0.36139 | 8.4 | 9.4 | 9.4 | 9.9 | 0.62915
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38486-09C02-P |  | 80-CG-38486-09C02-P |  | FPSO 2015 | Pipe Wall Thickness | 23655 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.375 | 80-CG-38486-01C02-H | Piping | 3 | 2038-03-27 |  | 2015-10-28 07:00 |  | 0.12038 | A4: Left Quadrant |  |  | 2.5 |  | 5.2 | 9 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.4 | 5.6 | 5.2 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44027-01X01 | CML-2 | 50-PW-44027-01X01 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10339 | Deck Level | 2013-11-11 | 2013-11-11 | [36 empty] | 8.775 | CML-2 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2013-11-11 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.8 | 8.7 | 8.7 | 8.9 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-6 | 80-FH-43151-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2240 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 6.125 | CML-6 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 12 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.3 | 6.2 | 6.1 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-27 | 250-WC-40017-01C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 2090 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 8.35 | CML-27 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 6 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.4 | 8.3 | 8.3 | 8.4 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-7 | 200-FH-43004-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12547 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 6.375 | CML-7 | CML: type TBC | 3 | 2030-08-26 | 2030-07-11 | 2014-02-01 07:00 | 2.5 | 0.2232 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.4 | 6.3 | 6.2 | 0.17078
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-23 | 200-PL-20035-03C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21355 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 10.425 | CML-23 | CML: Reducer | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 10.2 | 9 O'Clock | 40 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.59 |  | 10.9 | 10.3 | 10.3 | 10.2 | 0.32016
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57077-15C02 | CML-2 | 50-DC-57077-15C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10362 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 0.605mm/ yr | [35 empty] | 10.9 | CML-2 | CML: type TBC | 3 | 2027-07-31 | 2024-02-14 | 2013-11-11 | 2.5 | 0.6046 | A3: Inside Quadrant |  | 8.07 | 2.5 | 4.5931 | 10.8 | 6 O'Clock | 50 | 11.07 | 50-DC-57077-15C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.9 | 11 | 10.8 | 10.9 | 0.08165
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43014-01C02 | CML-5 | 250-FL-43014-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2895 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 6.625 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-04-25 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 6 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.8 | 6.4 | 6.7 | 0.17078
CG04 | Montara_Topside | Yes | Potable Water (53) | Pipework | 50-CG-38452-09C02-P | CML-14 | 50-CG-38452-09C02-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8290 | Reducing Hose Coupling | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 7.375 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 6 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.3 | 7.6 | 7.2 | 7.4 | 0.17078
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-15 | 50-CG-38452-09C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20354 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.375 | CML-15 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 12 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.6 | 7.3 | 7.4 | 0.17078
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20330 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.375 | CML-1 | CML: Pipe Length | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 12 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.4 | 7.3 | 7.6 | 0.17078
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-5 | 50-CG-38452-09C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21309 | Reading on larger diameter | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 7.375 | CML-5 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 9 O'Clock | 150 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.6 | 7.4 | 7.3 | 7.2 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-3 | 80-FH-43007-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12564 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.625 | CML-3 | CML: Pipe Length | 3 | 2048-03-30 | 2043-10-19 | 2014-01-18 07:00 | 0.54 | 0.14203 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.8 | 5.4 | 5.7 | 5.6 | 0.17078
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45028-03C02-E | CML-6 | 80-FG-45028-03C02-E CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24330 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.375 | CML-6 | CML: Reducer | 3 | 2053-09-17 | 2048-07-24 | 2016-06-01 07:00 | 1.46 | 0 | A3: Inside Quadrant |  | 2.49 | 1.46 | 1.975 | 7.2 | 6 O'Clock | 50 | 5.49 | 80-FG-45028-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.74 |  | 7.6 | 7.4 | 7.2 | 7.3 | 0.17078
PG06 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PG-23008-15S01-A | CML-12 | 200-PG-23008-15S01-A CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12590 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.575 | CML-12 | CML: Elbow | 3 | 2050-12-17 | 2046-03-02 | 2014-02-05 08:00 | 0.54 | 0.13175 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.6 | 5.4 | 5.8 | 5.5 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56034-01C02 | CML-2 | 80-DH-56034-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20917 | Rope Access | 2014-05-21 08:00 | 2014-05-21 09:00 | [36 empty] | 4.925 | CML-2 | CML: Elbow | 3 | 2017-02-01 | 2017-07-07 | 2014-05-21 08:00 | 2.5 | 0.81378 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 3 O'Clock | 80 | 5.49 | 80-DH-56034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 4.7 | 5.1 | 5 | 0.17078
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-4 | 50-FG-45019-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2595 | Rope Access | 2014-04-26 08:00 | 2014-04-26 09:00 | [36 empty] | 4.925 | CML-4 | CML: type TBC | 3 | 2016-09-04 | 2016-08-28 | 2014-04-26 08:00 | 2.5 | 0.93097 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | -0.44969 | 4.7 | 5.1 | 4.9 | 5 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-3 | 50-DH-56109-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20992 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.075 | CML-3 | CML: Elbow | 3 | 2018-01-23 | 2018-07-25 | 2014-05-24 10:30 | 2.5 | 0.65354 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 | 5.3 | 5.1 | 0.17078
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23302-01C02 | CML-1 | 80-VA-23302-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22517 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.075 | CML-1 | CML: Reducer | 3 | 2022-12-19 | 2024-01-29 | 2015-04-20 07:00 | 2.5 | 0.31288 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 9 O'Clock | 50 | 5.49 | 80-VA-23302-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 5 | 5.1 | 4.9 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-10 | 300-PW-44002-01X01-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22856 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.125 | CML-10 | CML: Reducing Tee | 6 | 2023-04-26 | 2022-03-03 | 2015-05-01 07:00 | 2.5 | 0.78815 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 8.8 | 12 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 | 0.37245 | 8.8 | 9.9 | 10.9 | 10.9 | 1.0012
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-11 | 50-PW-44015-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22716 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 9.175 | CML-11 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-04-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.8 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 | 0.11779 | 9.8 | 8.8 | 8.8 | 9.3 | 0.47871
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-14 | 250-PW-44004-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 5633 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 8.8 | CML-14 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-06-20 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.4 | 3 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.6 | 8.4 | 9.5 | 8.7 | 0.48305
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-19 | 200-PL-20034-03C02-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21616 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 10.225 | CML-19 | CML: Reducer | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 10.2 | 9 O'Clock | 40 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.59 |  | 10.2 | 10.3 | 10.2 | 10.2 | 0.05
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-10 | 100-VA-80006-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2179 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 5.425 | CML-10 | CML: type TBC | 3 | 2016-12-20 | 2017-02-01 | 2014-03-30 13:00 | 2.5 | 0.98929 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 9 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.6 | 5.5 | 5.2 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43140-01C02 | CML-1 | 50-FH-43140-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12868 |  | 2014-01-21 10:00 | 2014-01-21 10:30 | [36 empty] | 5.425 | CML-1 | CML: Pipe Length | 3 | 2019-02-25 | 2019-10-08 | 2014-01-21 10:00 | 2.5 | 0.5294 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-FH-43140-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.2 | 5.4 | 5.5 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43118-01C02 | CML-1 | 50-FH-43118-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1756 | Rope access | 2014-04-27 08:00 | 2014-04-27 08:30 | [36 empty] | 5.425 | CML-1 | CML: Fitting | 3 | 2021-07-02 | 2022-05-15 | 2014-04-27 08:00 | 2.5 | 0.37568 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FH-43118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.4 | 5.6 | 5.2 | 0.17078
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-13 | 250-PG-23003-06C02-PA CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2039 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 5.575 | CML-13 | CML: type TBC | 3 | 2040-08-31 | 2043-11-03 | 2014-03-27 14:30 | 2.5 | 0.10964 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.8 | 5.6 | 5.4 | 0.17078
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 | Yes | FPSO 2015 | Pipe Wall Thickness | 7856 | Line is FFS. Action: to recheck in two years CML-7 &8 (Jan. 2017) to confirm CR. | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-07 16:48 | [32 empty] | 5.575 | CML-8 | CML: Elbow | 3 | 2019-12-27 | 2019-12-09 | 2015-01-14 07:00 | 2.5 | 0.58544 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 9 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.6 | 5.5 | 5.4 | 0.17078
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-11 | 300-PW-44002-01X01-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 22028 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 9.225 | CML-11 | CML: Elbow | 6 | 2020-07-17 | 2019-09-19 | 2014-10-17 07:00 | 2.5 | 1.0951 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 8.8 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.1 | 8.8 | 9.4 | 9.6 | 0.35
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 20679 | Rope Access | 2014-05-26 13:00 | 2014-05-26 14:00 | [36 empty] | 12.3 | CML-1 | CML: type TBC | 3 | 2026-10-03 | 2023-03-24 | 2014-05-26 13:00 | 4.7 | 0.47714 | A3: Inside Quadrant |  | 8.07 | 4.7 | 6.385 | 10.6 | 6 O'Clock | 50 | 11.07 | 50-PG-23061-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 13.6 | 11.6 | 10.6 | 13.4 | 1.4468
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-15 | 300-FL-43070-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12708 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.425 | CML-15 | CML: type TBC | 3 | 2030-08-28 | 2030-07-13 | 2014-02-01 09:00 | 2.5 | 0.22313 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.6 | 6.5 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43017-01C02 | CML-5 | 150-FH-43017-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10651 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.925 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-18 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.7 | 12 O'Clock | 100 | 6.02 | 100-FH-43017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7 | 7.1 | 6.9 | 0.17078
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 20685 | Rope Access | 2014-05-26 13:00 | 2014-05-26 14:00 | [36 empty] | 12.175 | CML-7 | CML: type TBC | 3 | 2026-10-03 | 2023-03-24 | 2014-05-26 13:00 | 4.7 | 0.47714 | A4: Left Quadrant |  | 8.07 | 4.7 | 6.385 | 10.6 | 9 O'Clock | 50 | 11.07 | 50-PG-23061-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 12.9 | 11.9 | 13.3 | 10.6 | 1.2038
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-5 | 50-WC-40032-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1239 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 9.0667 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 3 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  |  | 8.4 | 9.5 | 9.3 | 0.58595
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-23 | 250-FH-43303-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 12961 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 7.975 | CML-23 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.2 | 8 | 7.9 | 7.8 | 0.17078
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-8 | 200-PL-20019-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21259 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 10.275 | CML-8 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 9 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 11.6 | 10.3 | 9.8 | 9.4 | 0.95699
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-15 | 80-DC-57002-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20244 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 10.9667 | CML-15 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 10.9 | 6 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  |  | 11 | 10.9 | 11 | 0.057735
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-13 | 300-PG-20004-03C03-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23365 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 12.475 | CML-13 | CML: Pipe Length | 6 | 2025-04-18 | 2022-08-09 | 2015-07-20 07:00 | 3.3 | 0.9227 | A2: Right Quadrant |  | 8.27 | 3.3 | 5.785 | 12.3 | 3 O'Clock | 200 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 | -0.68319 | 12.4 | 12.3 | 12.5 | 12.7 | 0.17078
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-19 | 150-DC-57308-01C03 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 20316 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 11.425 | CML-19 | CML: type TBC | 6 | 2175-03-07 | 2151-08-05 | 2014-10-02 07:00 | 2.5 | 0.05233 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 10.9 | 3 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.3 | 10.9 | 11.6 | 11.9 | 0.4272
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-4 | 50-PG-44022-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5847 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 12.475 | CML-4 | CML: Reducer | 6 | 2075-10-24 | 2074-08-12 | 2014-06-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 12.3 | 9 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 12.4 | 12.5 | 12.7 | 12.3 | 0.17078
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-7 | 25-VA-23054-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21477 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 15.525 | CML-7 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-06-28 09:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 15.3 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 15.3 | 15.6 | 15.5 | 15.7 | 0.17078
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-4 | 25-PW-44028-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5697 |  | 2014-06-22 07:00 | 2014-06-22 08:00 | [36 empty] | 9.475 | CML-4 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-06-22 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 3 O'Clock | 50 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | -6.6721 | 9.5 | 9.3 | 9.7 | 9.4 | 0.17078
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-13 | 50-DH-56137-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5454 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 3.576mm/ yr | [34 empty] | Low alarm breach | 18.1 | CML-13 | CML: Straight | 3 | 2018-09-16 | 2016-06-24 | 2014-05-28 07:00 | 2.5 | 3.5763 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 17.9 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 |  | 18.1 | 18.1 | 18.3 | 17.9 | 0.1633
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56041-01C02 | CML-2 | 80-DH-56041-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20925 | Rope Access | 2014-05-18 07:00 | 2014-05-18 08:00 | [36 empty] | 4.8 | CML-2 | CML: type TBC | 3 | 2016-08-24 | 2017-01-08 | 2014-05-18 07:00 | 2.5 | 0.92473 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 9 O'Clock | 80 | 5.49 | 80-DH-56041-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.8 | 5 | 4.8 | 4.6 | 0.1633
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-1 | 50-FG-45019-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2592 | Rope Access | 2014-04-26 08:00 | 2014-04-26 09:00 | [36 empty] | 5 | CML-1 | CML: type TBC | 3 | 2017-02-12 | 2017-02-04 | 2014-04-26 08:00 | 2.5 | 0.82014 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | -0.67454 | 5 | 5 | 4.8 | 5.2 | 0.1633
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-6 | 50-FG-45019-03C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2597 | Rope Access | 2014-04-26 08:00 | 2014-04-26 09:00 | [36 empty] | 5 | CML-6 | CML: type TBC | 3 | 2017-02-12 | 2017-02-04 | 2014-04-26 08:00 | 2.5 | 0.82014 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | -0.89938 | 5 | 5 | 4.8 | 5.2 | 0.1633
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-9 | 50-FG-45019-03C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10491 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.2 | CML-9 | CML: type TBC | 3 | 2015-12-28 | 2015-12-21 | 2013-11-15 | 2.5 | 1.1802 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.4 | 5.2 | 0.1633
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-2 | 50-DH-56116-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5212 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.2 | CML-2 | CML: Elbow | 3 | 2018-11-11 | 2019-06-12 | 2014-05-20 09:30 | 2.5 | 0.55773 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.4 | 5.2 | 0.1633
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-9 | 100-PG-23406-03C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20735 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 11.325 | CML-9 | CML: Fitting | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 10.9 | 6 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.4 | 12 | 10.9 | 11 | 0.49917
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-6 | 100-PG-23406-03C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20732 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 11.25 | CML-6 | CML: Fitting | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 10.9 | 6 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.6 | 11.3 | 10.9 | 11.2 | 0.28868
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-2 | 50-FH-43016-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22663 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.2 | CML-2 | CML: Elbow | 3 | 2024-02-18 | 2025-04-13 | 2015-04-27 07:00 | 2.5 | 0.28348 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.079564 | 5 | 5.2 | 5.2 | 5.4 | 0.1633
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-4 | 50-WC-40028-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1684 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 8.9333 | CML-4 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 12 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 |  | 9.1 | 9.3 | 0.47258
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-14 | 50-PW-44015-01X01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 22719 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 8.975 | CML-14 | CML: Reducer | 3 | 2044-01-06 | 2047-03-10 | 2015-04-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.1825 | 8.8 | 6 O'Clock | 50 | 5.56 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 | -0.23558 | 9.1 | 9.1 | 8.8 | 8.9 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-7 | 80-FH-43111-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12805 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 5.8 | CML-7 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-02-01 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 3 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.6 | 5.8 | 6 | 0.1633
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-9 | 100-FL-43455-01C02-P CML-9 | Yes | FPSO 2014 | Pipe Wall Thickness | 20492 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 6 | CML-9 | CML: Fitting | 3 | 2034-11-06 | 2035-07-23 | 2014-10-03 07:00 | 2.5 | 0.16411 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 6 | 6 | 5.8 | 0.1633
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-2 | 250-PW-44006-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1899 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 9 | CML-2 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.8 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9 | 8.8 | 9.1 | 9.1 | 0.14142
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-1 | 25-FG-45455-01C02-E CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8433 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 6.2 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-WC-40406-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.2 | 6.4 | 6.2 | 0.1633
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-4 | 300-PW-44002-01X01-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22850 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.725 | CML-4 | CML: Reducing Tee | 6 | 2024-01-08 | 2022-10-16 | 2015-05-01 07:00 | 2.5 | 0.73596 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 8.9 | 12 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | 0.37245 | 8.9 | 9.9 | 10.7 | 9.4 | 0.76757
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-20 | 250-FH-43303-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 12958 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.7 | CML-20 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.5 | 6.9 | 6.7 | 0.1633
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45003-03C02 | CML-4 | 150-FG-45003-03C02 CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24370 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7 | CML-4 | CML: Fitting | 3 | 2058-04-03 | 2050-06-04 | 2016-06-06 07:00 | 2.5 | 0.10274 | A2: Right Quadrant |  | 4.11 | 2.5 | 3.305 | 6.8 | 3 O'Clock | 150 | 7.11 | 150-FG-45003-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7 | 6.8 | 7 | 7.2 | 0.1633
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-1 | 25-PG-23300-25C02 CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 20668 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 8.9 | CML-1 | CML: Pipe Length | 3 | 2025-04-12 | 2023-02-22 | 2014-05-27 09:30 | 4.4 | 0.39498 | A4: Left Quadrant |  | 6.09 | 4.4 | 5.245 | 8.7 | 9 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 8.9 | 8.9 | 9.1 | 8.7 | 0.1633
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43505-01C02 | CML-3 | 150-FH-43505-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20468 | Rope Access | 2014-05-27 13:00 | 2014-05-27 14:00 | [36 empty] | 7.2 | CML-3 | CML: type TBC | 3 |  |  | 2014-05-27 13:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 7 | 6 O'Clock | 150 |  | 150-FH-43505-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7.2 | 7 | 7.4 | 0.1633
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-6 | 80-PW-44001-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21997 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 9.4 | CML-6 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.5 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10.2 | 9.7 | 9.2 | 8.5 | 0.72572
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-9 | 250-PG-20036-01C03-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23397 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 8.2 | CML-9 | CML: Elbow | 6 | 2024-10-20 | 2024-02-26 | 2015-07-21 07:00 | 2.5 | 0.59407 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 | 0.19625 | 8.4 | 8.2 | 8 | 8.2 | 0.1633
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-33 | 200-PL-20019-01C02 CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 21284 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 10.1 | CML-33 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.4 | 9.6 | 9.9 | 11.5 | 0.95568
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PG-20056-01C03-P | CML-1 | 100-PG-20056-01C03-P CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 21531 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 8.7 | CML-1 | CML: Fitting | 6 | 2127-02-26 | 2126-08-04 | 2014-07-17 07:30 | 2.5 | 0.05324 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 8.5 | 6 O'Clock | 100 | 8.56 | 100-PG-20056-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.9 | 8.7 | 8.5 | 8.7 | 0.1633
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-12 | 400-WC-40022-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1106 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 9.05 | CML-12 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 9 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.3 | 9.1 | 9.3 | 8.5 | 0.37859
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-11 | 100-FG-45001-09C02 CML-11 | Yes | FPSO 2015 | Pipe Wall Thickness | 23316 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.4 | CML-11 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 11.2 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | -0.60302 | 11.2 | 11.4 | 11.6 | 11.4 | 0.1633
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-6 | 50-PL-23042-09C03 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10071 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.6 | CML-6 | CML: type TBC | 6 | 2018-12-25 | 2018-02-23 | 2013-11-07 | 2.5 | 1.538 | A2: Right Quadrant |  | 5.07 | 2.5 | 3.785 | 10.4 | 3 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.6 | 10.4 | 10.6 | 10.8 | 0.1633
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-2 | 400-WC-40022-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1096 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.825 | CML-2 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 3 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.3 | 8.5 | 8.6 | 8.9 | 0.3594
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-22 | 300-PG-23001-03C03 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 10972 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.4 | CML-22 | CML: Elbow | 6 | 2091-12-30 | 2078-10-03 | 2014-01-09 | 5.22 | 0.11509 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 14.2 | 12 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.98 |  | 14.2 | 14.4 | 14.6 | 14.4 | 0.1633
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-9 | 250-PW-20022-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2052 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 12.775 | CML-9 | CML: Equal Tee | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 12.3 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 12.6 | 12.3 | 13 | 13.2 | 0.40311
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23403-01C03-A | CML-6 | 150-PG-23403-01C03-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5607 |  | 2014-06-20 08:00 | 2014-06-20 09:00 | [36 empty] | 11.45 | CML-6 | CML: Elbow | 6 | 2140-09-27 | 2122-03-05 | 2014-06-20 08:00 | 2.5 | 0.06648 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 10.9 | 9 O'Clock | 150 | 10.97 | 150-PG-23403-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.1 | 11.5 | 12.3 | 10.9 | 0.61914
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23050-25C02-P | CML-5 | 80-PG-23050-25C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2740 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 14.3 | CML-5 | CML: Pipe Length | 3 | 2096-09-16 | 2070-01-23 | 2014-03-13 09:00 | 2.8 | 0 | A3: Inside Quadrant |  | 8.13 | 2.8 | 5.465 | 14.1 | 6 O'Clock | 80 | 11.13 | 80-PG-23050-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 14.5 | 14.3 | 14.1 | 14.3 | 0.1633
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML17 | 150-FH-43141-01C02 CML17 | yes | FPSO 2015 | Pipe Wall Thickness | 7549 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 3.6 | CML17 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.6 | 3.6 | 3.8 | 0.1633
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-1 | 100-DC-57036-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1407 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 11.3333 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.9 | 6 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  |  | 11.1 | 10.9 | 12 | 0.58595
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-129 | 150-FH-43141-01C02 CML-129 | yes | FPSO 2015 | Pipe Wall Thickness | 6803 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.6 | CML-129 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.6 | 3.8 | 3.6 | 0.1633
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43144-01C02 | CML-4 | 100-FH-43144-01C02 CML-4 | Yes | FPSO 2013 | Pipe Wall Thickness | 10527 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.9 | CML-4 | CML: type TBC | 3 | 2014-08-20 | 2014-09-04 | 2013-11-15 | 2.5 | 2.885 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.7 | 12 O'Clock | 100 | 6.02 | 100-FH-43144-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.1 | 4.9 | 4.9 | 0.1633
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-7 | 300-PW-44002-01X01-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22853 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10 | CML-7 | CML: Reducing Tee | 6 | 2024-01-08 | 2022-10-16 | 2015-05-01 07:00 | 2.5 | 0.73596 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 8.9 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | 0.93112 | 10.5 | 8.9 | 10.4 | 10.2 | 0.74386
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-27 | 250-PW-44006-01X01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 23198 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 9.7 | CML-27 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.9 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | 2.6321 | 10 | 9.7 | 8.9 | 10.2 | 0.57155
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80002-01C02 | CML-4 | 100-VA-80002-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2164 | Rope Access | 2014-03-30 09:30 | 2014-03-30 11:00 | [36 empty] | 6.1 | CML-4 | CML: type TBC | 3 | 2037-09-13 | 2038-07-03 | 2014-03-30 09:30 | 2.5 | 0.14484 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-VA-80002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 6.3 | 5.9 | 6.1 | 0.1633
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-1 | 200-FH-43038-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12682 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 6.4 | CML-1 | CML: type TBC | 3 | 2031-01-04 | 2030-11-18 | 2014-02-06 09:00 | 2.5 | 0.21867 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.4 | 6.6 | 0.1633
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-5 | 50-FH-43137-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22679 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 7.4 | CML-5 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 3 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 | 0.23858 | 7.6 | 7.2 | 7.4 | 7.4 | 0.1633
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-14 | 50-CG-38452-09C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20353 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.4 | CML-14 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.4 | 7.6 | 7.4 | 7.2 | 0.1633
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-2 | 100-DH-56082-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3370 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 7.6 | CML-2 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.4 | 6 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.6 | 7.6 | 7.4 | 7.8 | 0.1633
CG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-CG-38459-09C02-P | CML-2 | 80-CG-38459-09C02-P CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10470 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 13.3667 | CML-2 | CML: type TBC | 6 | 2090-11-29 | 2082-02-28 | 2013-11-14 | 0.99 | 0 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 13.2 | 3 O'Clock | 50 | 8.74 | 50-PL-45031-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.21 |  | 13.4 | 13.2 | 13.5 |  | 0.15275
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-7 | 50-CG-38466-01C02 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 2521 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.2667 | CML-7 | CML: type TBC | 3 | 2019-03-13 | 2019-10-25 | 2014-04-02 13:00 | 2.5 | 0.52562 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 5.1 |  | 5.3 | 5.1 | 5.4 | 0.15275
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43120-01C02 | CML-4 | 200-FH-43120-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12838 |  | 2014-02-06 07:00 | 2014-02-06 09:00 | [36 empty] | 6.7333 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 3 O'Clock | 200 | 6.35 | 200-FH-43120-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.6 |  | 6.9 | 0.15275
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-8 | 200-FH-43012-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2838 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 10.3333 | CML-8 | CML: Equal Tee | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 10.2 | 9 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.86 |  |  | 10.5 | 10.3 | 10.2 | 0.15275
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20060-01C02 | CML-3 | 50-PL-20060-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21537 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 9.525 | CML-3 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-07-17 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.4 | 6 O'Clock | 50 | 5.54 | 50-PL-20060-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.6 | 9.4 | 9.4 | 9.7 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-2 | 400-WC-40024-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1071 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.775 | CML-2 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 6 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9 | 8.6 | 8.5 | 9 | 0.263
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-6 | 150-FL-43174-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12904 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.3333 | CML-6 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 12 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.5 | 7.3 |  | 0.15275
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-12 | 50-CG-38452-09C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1288 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.3667 | CML-12 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 12 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.4 |  | 7.5 | 0.15275
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-8 | 100-FH-43507-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2973 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 6.8667 | CML-8 | CML: Elbow | 3 | 2062-11-29 | 2056-08-05 | 2014-05-01 14:00 | 0.54 | 0 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 6.7 | 9 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.16 |  | 6.9 | 7 |  | 6.7 | 0.15275
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-8 | 100-FH-43507-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 22252 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 6.8667 | CML-8 | CML: Elbow | 3 | 2062-11-29 | 2056-08-05 | 2014-05-01 14:00 | 0.54 | 0 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 6.7 | 9 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.16 |  | 6.9 | 7 |  | 6.7 | 0.15275
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-12 | 200-FH-43038-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12693 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 6.4333 | CML-12 | CML: type TBC | 3 | 2066-03-13 | 2065-10-24 | 2014-02-06 09:00 | 2.5 | 0.07289 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.4 |  | 6.6 | 0.15275
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40061-01C02 | CML-5 | 400-WC-40061-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1129 |  | 2014-03-21 08:30 | 2014-03-21 09:00 | [36 empty] | 8.875 | CML-5 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 08:30 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 9 O'Clock | 400 | 7.92 | 400-WC-40061-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.1 | 9 | 8.9 | 8.5 | 0.263
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-22 | 200-PL-20035-03C02-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21354 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 10.7 | CML-22 | CML: Elbow | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 10.6 | 9 O'Clock | 40 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.99 |  | 10.7 | 10.7 | 10.8 | 10.6 | 0.08165
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-9 | 200-PG-23013-09C03-A CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10993 | Rope Access | 2014-01-10 | 2014-01-10 | [35 empty] | Low alarm breach | 14.325 | CML-9 | CML: Elbow | 6 | 2014-05-28 | 2014-03-12 | 2014-01-10 | 10.22 | 10.5081 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 14.2 | 9 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.98 |  | 14.4 | 14.5 | 14.2 | 14.2 | 0.15
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-19 | 50-FG-45018-03C02 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10518 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 8.325 | CML-19 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2013-11-15 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 8.2 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.5 | 8.2 | 8.4 | 0.15
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-1 | 50-PG-23063-09C02 CML-1 | Yes | FPSO 2013 | Pipe Wall Thickness | 10727 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.325 | CML-1 | CML: type TBC | 3 | 2018-10-29 | 2017-06-03 | 2013-11-19 | 2.5 | 1.1526 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.2 | 6 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.4 | 8.2 | 8.5 | 0.15
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45044-03C02 | CML-9 | 50-FG-45044-03C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20591 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 8.775 | CML-9 | CML: Fitting | 3 | 2063-09-30 | 2050-09-06 | 2014-07-18 11:00 | 2.5 | 0.12389 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.7 | 8.9 | 8.9 | 0.15
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-22 | 50-PF-20300-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21588 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 8.775 | CML-22 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.7 | 8.9 | 8.9 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43103-01C02 | CML-3 | 300-FH-43103-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20423 | Protective mesh removed | 2014-07-02 14:00 | 2014-07-02 15:00 | [36 empty] | 9.175 | CML-3 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-02 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9 | 9 O'Clock | 300 | 6.35 | 300-FH-43103-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.3 | 9.1 | 9.3 | 9 | 0.15
VA02 | Montara_Topside | No | Main Power (80) | Pipework | 50-VA-80014-01S01 | CML-3 | 50-VA-80014-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8518 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 11.375 | CML-3 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 11 | 12 O'Clock | 50 | 5.54 | 50-VA-80014-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11 | 11.3 | 11.8 | 11.4 | 0.3304
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-2 | 150-DC-57308-01C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20299 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 11.25 | CML-2 | CML: Elbow | 6 | 2098-02-09 | 2085-10-05 | 2014-10-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 11 | 9 O'Clock | 100 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11.4 | 11.3 | 11.3 | 11 | 0.17321
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-9 | 50-PL-23022-03C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1865 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.175 | CML-9 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 3 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.1 | 9 | 9.3 | 9.3 | 0.15
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-10 | 50-FG-45024-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23509 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 8.225 | CML-10 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2015-07-28 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 8.1 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.07 | -0.19837 | 8.1 | 8.3 | 8.1 | 8.4 | 0.15
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-1 | 250-PW-44010-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23023 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 9.725 | CML-1 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2015-05-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.6 | 9 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 | 0.34663 | 9.9 | 9.8 | 9.6 | 9.6 | 0.15
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45031-03C03 | CML-6 | 50-PL-45031-03C03 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10474 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 8.675 | CML-6 | CML: type TBC | 6 | 2028-02-03 | 2026-06-08 | 2013-11-14 | 0.99 | 0.52771 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-PL-45031-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.51 |  | 8.5 | 8.8 | 8.8 | 8.6 | 0.15
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38486-09C02-P | CML-1 | 80-CG-38486-09C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23648 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 11.225 | CML-1 | CML: Pipe Length | 3 | 2043-04-25 | 2046-10-17 | 2015-10-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.1 | 9 O'Clock | 80 | 5.49 | 80-CG-38486-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.1 | 11.4 | 11.3 | 11.1 | 0.15
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-13 | 50-CG-24002-09C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2559 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 8.725 | CML-13 | CML: type TBC | 3 | 2035-03-28 | 2029-07-27 | 2014-04-03 13:00 | 2.5 | 0.28577 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.8 | 8.8 | 8.8 | 8.5 | 0.15
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-20 | 300-PW-44003-01C03 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21862 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 16:58 | [32 empty] | 12.6 | CML-20 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 12.4 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 12.6 | 12.8 | 12.4 | 12.6 | 0.1633
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-12 | 80-PW-44001-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 22003 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 9.05 | CML-12 | CML: Reducing Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.5 | 3 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.7 | 8.5 | 9.4 | 9.6 | 0.53229
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56559-01C02 | CML-3 | 50-DH-56559-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21138 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-21 09:15 | [32 empty] | 4.775 | CML-3 | CML: Elbow | 3 | 2017-10-16 | 2018-04-06 | 2014-10-08 07:00 | 2.5 | 0.69412 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56559-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 4.6 | 4.9 | 4.7 | 0.15
PG06 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-PG-23008-15S01-A | CML-7 | 200-PG-23008-15S01-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3069 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 0.477mm/ yr | [35 empty] | 5.225 | CML-7 | CML: Elbow | 3 | 2019-10-11 | 2020-06-17 | 2014-05-03 08:00 | 2.5 | 0.4775 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 1.0409 | 5.1 | 5.3 | 5.1 | 5.4 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-16 | 400-WC-40024-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1085 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.8 | CML-16 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 12 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.5 | 9.1 | 8.9 | 8.7 | 0.2582
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-12 | 250-PW-44006-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1909 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 9.375 | CML-12 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.9 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10 | 9.2 | 8.9 | 9.4 | 0.46458
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-13 | 250-PW-44006-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8005 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 9.125 | CML-13 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.9 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | -0.24328 | 9.6 | 8.9 | 8.9 | 9.1 | 0.3304
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-2 | 80-FH-43151-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2236 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 6.275 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 6 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.2 | 6.1 | 6.4 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-17 | 400-WC-40024-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1086 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.825 | CML-17 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 9 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.9 | 9 | 8.9 | 8.5 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-10 | 200-FH-43114-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12818 |  | 2014-02-01 12:00 | 2014-02-01 14:00 | [36 empty] | 6.225 | CML-10 | CML: type TBC | 3 | 2023-10-07 | 2023-09-10 | 2014-02-01 12:00 | 2.5 | 0.37169 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 9 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.3 | 6.1 | 6.4 | 6.1 | 0.15
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-20 | 150-FL-43453-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 2264 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.725 | CML-20 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.6 | 6 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.6 | 6.6 | 6.9 | 0.15
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-7 | 50-FG-45024-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1211 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.725 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.8 | 6.9 | 6.6 | 0.15
FH01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FH-43141-01C02 | CML-17 | 150-FH-43141-01C02 CML-17 | yes | FPSO 2015 | Pipe Wall Thickness | 7889 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:45 | [32 empty] | 3.425 | CML-17 | CML: Elbow | 3 | 2015-08-14 | 2015-11-08 | 2015-01-14 10:30 | 2.5 | 1.3801 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.3 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.6 | 3.3 | 3.5 | 0.15
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-25 | 50-PL-23020-01C03 CML-25 |  | FPSO 2013 | Pipe Wall Thickness | 10139 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.125 | CML-25 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 6 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.3 | 8 | 8.2 | 0.15
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-4 | 100-DC-57036-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1410 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 11.4667 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 11 | 3 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  |  | 11 | 12.3 | 11.1 | 0.72342
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-12 | 50-PL-23020-01C03 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10126 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.125 | CML-12 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8 | 8.2 | 8 | 0.15
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-24 | 50-PL-23021-03C03 CML-24 |  | FPSO 2013 | Pipe Wall Thickness | 10256 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.125 | CML-24 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 6 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8 | 8 | 8.2 | 0.15
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-22 | 50-PL-23021-03C03 CML-22 |  | FPSO 2013 | Pipe Wall Thickness | 10254 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.125 | CML-22 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.3 | 8.2 | 8 | 0.15
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-4 | 150-PG-23506-25C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2778 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.425 | CML-4 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.3 | 6 O'Clock | 50 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.42 |  | 22.3 | 22.5 | 22.3 | 22.6 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-17 | 400-FH-43508-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6566 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.125 | CML-17 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 9 | 6 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.3 | 9 | 9.2 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43125-01C02 | CML-1 | 200-FH-43125-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2755 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 8.375 | CML-1 | CML: Reducer | 3 | 2063-07-07 | 2057-06-06 | 2014-03-13 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 8.2 | 6 O'Clock | 150 | 6.35 | 200-FH-43125-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.86 |  | 8.3 | 8.5 | 8.2 | 8.5 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-12 | 250-WC-40017-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2075 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 8.6 | CML-12 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.4 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.7 | 8.5 | 8.8 | 8.4 | 0.18257
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-10 | 200-PG-23051-09C02-A CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 13115 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.15 | CML-10 | CML: type TBC | 3 | 2103-01-05 | 2073-03-18 | 2014-02-07 11:00 | 9.3 | 0 | A3: Inside Quadrant |  | 15.26 | 9.3 | 12.28 | 18.7 | 6 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 19.5 | 19 | 18.7 | 19.4 | 0.36968
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-16 | 50-FG-45024-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1199 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 11.125 | CML-16 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 11 | 6 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11 | 11.2 | 11 | 11.3 | 0.15
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-7 | 200-PG-23051-09C02-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13112 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 18.875 | CML-7 | CML: type TBC | 3 | 2103-01-05 | 2073-03-18 | 2014-02-07 11:00 | 9.3 | 0 | A2: Right Quadrant |  | 15.26 | 9.3 | 12.28 | 18.7 | 3 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 18.8 | 18.7 | 19 | 19 | 0.15
CG03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-CG-38459-09C02-P | CML-23 | 80-CG-38459-09C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21865 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 17:08 | [32 empty] | 14.375 | CML-23 | CML: Pipe Length | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 14.2 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.7 |  | 14.5 | 14.5 | 14.3 | 14.2 | 0.15
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-14 | 50-CG-38001-09C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 10928 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.125 | CML-14 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.2222 | A2: Right Quadrant |  | 5.74 |  |  | 8 | 6 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8 | 8.2 | 8 | 8 | 8.3 | 0.15
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-1 | 80-DH-56004-01C02 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 6605 |  | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.425 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71342-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.6 | 3.5 | 3.3 | 3.3 | 0.15
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-11 | 150-FH-43141-01C02 CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 5964 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.575 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.7 | 3.7 | 3.5 | 3.4 | 0.15
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38009-01C02 | CML-5 | 50-CG-38009-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7863 |  | 2015-01-14 08:00 | 2015-01-14 09:00 | [36 empty] | 4.875 | CML-5 | CML: Elbow | 3 | 2019-04-14 | 2019-11-30 | 2015-01-14 08:00 | 2.5 | 0.51761 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 15 | 5.54 | 50-CG-38009-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 4.7 | 5 | 4.8 | 0.15
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43079-01C02 | CML-7 | 50-FL-43079-01C02 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 3050 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 4.875 | CML-7 | CML: type TBC | 3 | 2016-09-30 | 2017-02-07 | 2014-05-03 07:00 | 2.5 | 0.91171 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5 | 4.8 | 5 | 0.15
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56138-01C02 | CML-2 | 50-DH-56138-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22310 | Rope Access | 2014-05-06 14:00 | 2014-05-06 15:00 | [36 empty] | 4.925 | CML-2 | CML: type TBC | 3 | 2017-03-27 | 2017-08-23 | 2014-05-06 14:00 | 2.5 | 0.79539 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5 | 5.1 | 4.8 | 0.15
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-18 | 250-PG-23003-06C02-PA CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10685 | Deck Level | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-13 13:55 | [32 empty] | 4.925 | CML-18 | CML: Pipe Length | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.8 | 5 | 5.1 | 0.15
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45014-01C02-E | CML-1 | 50-FG-45014-01C02-E CML-1 | yes | FPSO 2016 | Pipe Wall Thickness | 24345 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.125 | CML-1 | CML: Elbow | 3 | 2030-05-22 | 2032-03-18 | 2016-06-06 07:00 | 2.5 | 0.17897 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45014-01C02-E | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5 | 5.3 | 0.15
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-11 | 80-SC-55002-01C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8841 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 11.375 | CML-11 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.1 | 12 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.1 | 11.6 | 11.6 | 11.2 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56104-01C02 | CML-1+F143F120:F145F1F120:F142 | 50-DH-56104-01C02 CML-1+F143F120:F145F1F120:F142 |  | FPSO 2014 | Pipe Wall Thickness | 1973 |  | 2014-03-26 14:00 | 2014-03-26 15:00 | [36 empty] | 5.175 | CML-1+F143F120:F145F1F120:F142 | CML: type TBC | 3 | 2018-01-06 | 2018-07-06 | 2014-03-26 14:00 | 2.5 | 0.66012 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DH-56104-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.3 | 5.1 | 5.3 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-4 | 400-WC-40022-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1098 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.7 | CML-4 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 6 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.8 | 8.7 | 8.5 | 8.8 | 0.14142
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-11 | 50-FG-45021-03C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2623 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.125 | CML-11 | CML: type TBC | 3 | 2018-06-29 | 2018-06-17 | 2014-04-26 10:45 | 2.5 | 0.59827 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0 | 5 | 5.3 | 5 | 5.2 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43140-01C02 | CML-2 | 50-FH-43140-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12869 |  | 2014-01-21 10:00 | 2014-01-21 10:30 | [36 empty] | 5.175 | CML-2 | CML: Elbow | 3 | 2017-01-10 | 2017-06-01 | 2014-01-21 10:00 | 2.5 | 0.84081 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-FH-43140-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5.3 | 5.3 | 0.15
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-1 | 50-CG-38457-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23719 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.125 | CML-1 | CML: Elbow | 3 | 2026-12-31 | 2028-06-15 | 2015-10-30 07:00 | 2.5 | 0.22365 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5.2 | 5.3 | 0.15
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-11 | 50-PW-44015-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5721 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 9.075 | CML-11 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-22 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.9 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | -5.8552 | 9.2 | 9.2 | 8.9 | 9 | 0.15
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-31 | 250-PW-44006-01X01 CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 1928 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 9.975 | CML-31 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.6 | 11.3 | 9 | 10 | 0.97425
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-10 | 300-PW-44002-01X01-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 22027 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 9.85 | CML-10 | CML: Reducing Tee | 6 | 2021-08-18 | 2020-09-04 | 2014-10-17 07:00 | 2.5 | 0.95005 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9 | 12 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 10.2 | 10.6 | 9.6 | 0.7
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56558-01C02 | CML-4 | 50-DH-56558-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21135 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-21 08:56 | [32 empty] | 5.375 | CML-4 | CML: Elbow | 3 | 2025-07-07 | 2026-10-24 | 2014-10-08 07:00 | 2.5 | 0.25107 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DH-56558-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.5 | 5.5 | 5.2 | 0.15
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-4 | 50-DH-56109-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20993 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.325 | CML-4 | CML: Elbow | 3 | 2022-03-01 | 2023-02-07 | 2014-05-24 10:30 | 2.5 | 0.34719 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.5 | 5.2 | 0.15
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-13 | 50-PW-44013-01X01 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5737 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 9.275 | CML-13 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-22 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | -6.3396 | 9 | 9.7 | 9.3 | 9.1 | 0.30957
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-3 | 50-PG-23074-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20625 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.325 | CML-3 | CML: Elbow | 3 | 2023-09-14 | 2024-10-22 | 2014-07-26 07:00 | 2.5 | 0.29527 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.5 | 5.2 | 5.2 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43021-01C02 | CML-1 | 80-FH-43021-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23520 | Re-check on line as Per RBI 2014 Report | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 5.425 | CML-1 | CML: Pipe Length | 3 | 2047-05-03 | 2051-04-14 | 2015-07-28 07:00 | 2.5 | 0.08809 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-FH-43021-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | -0.12373 | 5.5 | 5.3 | 5.3 | 5.6 | 0.15
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-3 | 50-FG-45301-01C02 CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 5789 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.425 | CML-3 | CML: Elbow | 3 | 2026-11-08 | 2028-04-18 | 2014-06-23 13:00 | 2.5 | 0.22604 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.6 | 5.3 | 5.5 | 0.15
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-3 | 50-FG-45302-01C02 CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 5771 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 5.425 | CML-3 | CML: Fitting | 3 | 2026-11-07 | 2028-04-17 | 2014-06-23 11:00 | 2.5 | 0.22609 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.5 | 5.6 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-10 | 150-WC-40006-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1670 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 8.55 | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.4 | 9 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.6 | 8.5 | 8.7 | 8.4 | 0.1291
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45032-03C02 | CML-3 | 100-FG-45032-03C02 CML-3 | yes | FPSO 2013 | Pipe Wall Thickness | 10644 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.575 | CML-3 | CML: type TBC | 3 |  |  | 2013-11-18 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5.4 | 3 O'Clock | 100 |  | 100-FG-45032-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 5.7 | 5.7 | 0.15
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-3 | 50-FG-45021-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2615 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.675 | CML-3 | CML: type TBC | 3 | 2081-12-19 | 2081-07-07 | 2014-04-26 10:45 | 2.5 | 0.04432 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -1.1304 | 5.5 | 5.8 | 5.6 | 5.8 | 0.15
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45006-03C02-E | CML-1 | 100-FG-45006-03C02-E CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24317 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 | Wet Fuel Gas, downstream of super heaters approaching dew point of gas (36 degC) |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.175 | CML-1 | CML: Elbow | 3 | 2025-08-06 | 2023-12-03 | 2016-06-01 07:00 | 1.88 | 0.3396 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 5 | 12 O'Clock | 100 | 6.02 | 100-FG-45006-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.12 |  | 5 | 5.3 | 5.1 | 5.3 | 0.15
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44029-01C02 | CML-2 | 250-PW-44029-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22899 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.225 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-01 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 9 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 | -1.9876 | 9.6 | 8.8 | 9.8 | 8.7 | 0.55603
VA01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-VA-43519-01C02 | CML-5 | 50-VA-43519-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7758 |  | 2015-01-11 09:30 | 2015-01-11 10:30 | [36 empty] | 5.925 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-01-11 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-VA-43519-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.8 | 5.8 | 6.1 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-5 | 400-WC-40022-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1099 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.675 | CML-5 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 6 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.7 | 8.8 | 8.5 | 8.7 | 0.12583
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80002-01C02 | CML-2 | 100-VA-80002-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2162 | Rope Access | 2014-03-30 09:30 | 2014-03-30 11:00 | [36 empty] | 6.075 | CML-2 | CML: type TBC | 3 | 2037-09-13 | 2038-07-03 | 2014-03-30 09:30 | 2.5 | 0.14484 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-VA-80002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.2 | 5.9 | 6 | 0.15
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43154-01C02 | CML-3 | 100-FL-43154-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12873 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 6.075 | CML-3 | CML: type TBC | 3 | 2033-04-12 | 2033-12-07 | 2014-02-03 08:00 | 2.5 | 0.17709 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6.2 | 6.2 | 5.9 | 0.15
FG02 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8499 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.125 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-GN-67003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.2 | 6 | 6.3 | 0.15
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20267 | Rope access | 2014-06-02 11:00 | 2014-06-02 12:00 | [36 empty] | 6.175 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-06-02 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 9 O'Clock | 80 | 5.49 | 80-DC-57007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6.3 | 6.1 | 6 | 0.15
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-11 | 25-FG-45455-01C02-E CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 22067 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.125 | CML-11 | CML: type TBC | 3 | 2186-01-24 | 2173-04-24 | 2014-05-25 07:00 | 2.5 | 0.02037 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 6 | 9 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.2 | 6.3 | 6 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-5 | 300-FH-43001-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12517 |  | 2014-01-24 13:00 | 2014-01-24 15:00 | [36 empty] | 6.175 | CML-5 | CML: type TBC | 3 | 2020-07-26 | 2020-07-07 | 2014-01-24 13:00 | 2.5 | 0.5378 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.3 | 6.1 | 6.3 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43101-01C02 | CML-1 | 100-FH-43101-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12740 |  | 2014-01-24 07:00 | 2014-01-24 08:00 | [36 empty] | 6.175 | CML-1 | CML: Pipe Length | 3 | 2127-10-05 | 2131-07-15 | 2014-01-24 07:00 | 2.5 | 0.03076 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-FH-43101-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6 | 6.3 | 6.1 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-14 | 400-WC-40025-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1274 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 8.6333 | CML-14 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 3 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.7 | 8.5 |  | 8.7 | 0.11547
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-12 | 150-FL-43453-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2256 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.375 | CML-12 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.2 | 6 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.5 | 6.2 | 6.5 | 0.15
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-13 | 150-FL-43453-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2257 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.425 | CML-13 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.3 | 9 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 6.3 | 6.6 | 6.3 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-8 | 200-FH-43037-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12677 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 6.575 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 3 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.4 | 6.7 | 6.5 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-7 | 200-FH-43037-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12676 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 6.625 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 9 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.8 | 6.5 | 6.7 | 6.5 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43407-01C02 | CML-1 | 150-FH-43407-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7947 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-18 07:00 | 2015-01-18 08:00 |  |  | Administrator | 2015-09-08 13:26 | [32 empty] | 7.175 | CML-1 | CML: Reducer | 3 | 2081-11-01 | 2076-06-25 | 2015-01-18 07:00 | 2.5 | 0.06733 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 9 O'Clock | 150 | 7.11 | 150-FH-43407-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7.3 | 7.3 | 7 | 0.15
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20332 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.375 | CML-3 | CML: Pipe Length | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 6 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.3 | 7.5 | 7.2 | 7.5 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-13 | 80-FH-43007-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12574 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.575 | CML-13 | CML: Pipe Length | 3 | 2048-03-30 | 2043-10-19 | 2014-01-18 07:00 | 0.54 | 0.14203 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.7 | 5.4 | 5.5 | 5.7 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-15 | 400-WC-40024-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1084 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.525 | CML-15 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.5 | 9 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.5 | 8.5 | 8.6 | 8.5 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-17 | 150-FH-43026-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 5526 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 7.125 | CML-17 | CML: Fitting | 3 | 2068-09-10 | 2058-09-25 | 2014-06-01 07:00 | 1.03 | 0.10991 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 | 0 | 7.2 | 7.3 | 7 | 7 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-17 | 150-FH-43026-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12657 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.125 | CML-17 | CML: Fitting | 3 | 2049-01-08 | 2042-08-09 | 2014-01-22 07:00 | 1.03 | 0.17064 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 |  | 7.2 | 7.3 | 7 | 7 | 0.15
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-2 | 150-FL-43174-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22555 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [36 empty] | 3.725 | CML-2 | CML: Reducer | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 3.5 | 3 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.8 | 3.5 | 3.8 | 3.8 | 0.15
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-38 | 150-FL-43174-01C02 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 6916 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.575 | CML-38 | CML: type TBC | 0.5 | 2023-06-01 | 2020-11-30 | 2015-04-05 07:00 | 3.5 | 0 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4.5 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4.5 | 4.5 | 4.8 | 4.5 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43156-01C02 | CML-3 | 80-FH-43156-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10721 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 5.025 | CML-3 | CML: type TBC | 3 | 2015-06-12 | 2015-09-06 | 2013-11-19 | 2.5 | 1.4728 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 12 O'Clock | 80 | 5.49 | 80-FH-43156-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.1 | 5.1 | 5.1 | 0.15
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56117-01C02 | CML-4 | 50-DH-56117-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21017 | Rope Access | 2014-05-19 13:00 | 2014-05-19 14:00 | [36 empty] | 5.025 | CML-4 | CML: type TBC | 3 | 2017-05-19 | 2017-10-21 | 2014-05-19 13:00 | 2.5 | 0.76615 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 5.1 | 5.1 | 4.8 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40061-01C02 | CML-2 | 400-WC-40061-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1126 |  | 2014-03-21 08:30 | 2014-03-21 09:00 | [36 empty] | 9.925 | CML-2 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 08:30 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8.6 | 9 O'Clock | 400 | 7.92 | 400-WC-40061-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.8 | 10.4 | 10.9 | 8.6 | 0.99121
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56066-01C02 | CML-6 | 50-DH-56066-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3283 | Rope Access | 2014-05-09 14:00 | 2014-05-09 15:00 | [36 empty] | 4.975 | CML-6 | CML: type TBC | 3 | 2017-11-14 | 2018-05-07 | 2014-05-09 14:00 | 2.5 | 0.68188 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-DH-56066-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 4.9 | 4.9 | 4.9 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43019-01C02 | CML-2 | 80-FH-43019-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10621 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.125 | CML-2 | CML: type TBC | 3 | 2015-10-05 | 2016-01-13 | 2013-11-17 | 2.5 | 1.2743 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-FH-43019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.2 | 5.2 | 5.2 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43451-01C02 | CML-12 | 50-FH-43451-01C02 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 20031 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.125 | CML-12 | CML: type TBC | 3 | 2015-08-12 | 2015-11-06 | 2013-11-17 | 2.5 | 1.3822 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.2 | 5.2 | 5.2 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43142-01C02 | CML-3 | 100-FH-43142-01C02 CML-3 | Yes | FPSO 2013 | Pipe Wall Thickness | 10521 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.125 | CML-3 | CML: type TBC | 3 | 2014-11-07 | 2014-11-25 | 2013-11-15 | 2.5 | 2.4479 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 6 O'Clock | 100 | 6.02 | 100-FH-43142-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5.2 | 4.9 | 5.2 | 0.15
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-19 | 250-PG-23003-06C02-PA CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10547 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.375 | CML-19 | CML: type TBC | 3 | 2019-03-30 | 2019-03-16 | 2013-11-16 | 2.5 | 0.52143 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.6 | 5.3 | 5.3 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-12 | 50-FH-43137-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12864 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 5.525 | CML-12 | CML: Reducing Tee | 3 | 2021-08-11 | 2022-06-28 | 2014-01-23 08:00 | 2.5 | 0.37066 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.6 | 5.6 | 5.6 | 0.15
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-4 | 300-PW-44002-01X01-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22021 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 9.825 | CML-4 | CML: Reducing Tee | 6 | 2022-04-23 | 2021-04-12 | 2014-10-17 07:00 | 2.5 | 0.87752 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.1 | 12 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 10.1 | 10.5 | 9.6 | 0.60759
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44032-01C02-P | CML-1 | 80-PW-44032-01C02-P CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 23264 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 10.175 | CML-1 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 9.1 | 12 O'Clock | 80 | 5.49 | 80-PW-44032-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | 4.9463 | 9.1 | 9.7 | 10.4 | 11.5 | 1.0308
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56122-01C02 | CML-2 | 50-DH-56122-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1822 |  | 2014-04-29 14:00 | 2014-04-29 14:30 | [36 empty] | 6.125 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-29 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 5.9 | 6.2 | 6.2 | 0.15
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-23 | 50-FG-45301-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 5809 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.425 | CML-23 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 3 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.2 | 6.5 | 6.5 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-9 | 400-WC-40022-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1103 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.9 | CML-9 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.6 | 3 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.7 | 8.6 | 9.3 | 9 | 0.31623
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-6 | 300-FL-43080-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2385 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 6.775 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7 | 6.7 | 6.7 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-12 | 50-WC-40451-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 3074 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | [36 empty] | 8.925 | CML-12 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-03 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.5 | 6 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | -7.2861 | 9 | 9.2 | 8.5 | 9 | 0.29861
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43029-01C02 | CML-4 | 400-FH-43029-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10020 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.625 | CML-4 | CML: Elbow | 3 | 2017-11-19 | 2017-04-15 | 2013-11-04 | 2.48 | 1.2167 | A4: Left Quadrant |  | 4.92 | 2.48 | 3.205 | 7.4 | 9 O'Clock | 400 | 7.92 | 400-FH-43029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.92 |  | 7.7 | 7.7 | 7.7 | 7.4 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-13 | 150-FH-43518-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2713 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.275 | CML-13 | CML: Pipe Length | 3 | 2072-03-18 | 2062-04-04 | 2014-03-12 09:00 | 1.23 | 0 | A2: Right Quadrant |  | 4.11 | 1.23 | 2.2256 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 | 0 | 7.5 | 7.2 | 7.2 | 7.2 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-13 | 150-FH-43518-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 352 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.275 | CML-13 | CML: Pipe Length | 3 | 2072-03-18 | 2062-04-04 | 2014-03-12 | 1.23 | 0 | A2: Right Quadrant |  | 4.11 | 1.23 | 2.2256 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 |  | 7.5 | 7.2 | 7.2 | 7.2 | 0.15
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-12 | 50-FL-43454-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12652 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.375 | CML-12 | CML: Fitting | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.3 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.27 |  | 7.6 | 7.3 | 7.3 | 7.3 | 0.15
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-18 | 50-CG-38500-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 7890 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:45 | [32 empty] | 3.675 | CML-18 | CML: Elbow | 3 | 2015-10-31 | 2016-02-03 | 2015-01-14 10:30 | 2.5 | 1.2568 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.5 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.8 | 3.6 | 3.8 | 3.5 | 0.15
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-13 | 50-CG-38500-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7885 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:43 | [32 empty] | 3.725 | CML-13 | CML: Elbow | 3 | 2015-12-16 | 2016-03-24 | 2015-01-14 10:30 | 2.5 | 1.1952 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.6 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.9 | 3.6 | 3.8 | 0.15
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-13 | 80-PW-44001-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 22004 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 9.875 | CML-13 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 9.4 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.4 | 9.8 | 10.1 | 10.2 | 0.3594
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-21 | 50-FG-45020-03C02 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10593 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.025 | CML-21 | CML: type TBC | 3 | 2015-08-12 | 2015-08-07 | 2013-11-17 | 2.5 | 1.3822 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.1 | 5.2 | 4.9 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-5 | 80-FH-43158-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12886 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.525 | CML-5 | CML: type TBC | 3 | 2034-10-31 | 2037-04-29 | 2014-01-22 11:00 | 2.5 | 0.13952 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.6 | 5.4 | 5.4 | 0.15
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20681 | Rope Access | 2014-05-26 13:00 | 2014-05-26 14:00 | [36 empty] | 10.95 | CML-3 | CML: type TBC | 3 | 2030-05-12 | 2025-11-17 | 2014-05-26 13:00 | 4.7 | 0.37562 | A2: Right Quadrant |  | 8.07 | 4.7 | 6.385 | 10.7 | 3 O'Clock | 50 | 11.07 | 50-PG-23061-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10.9 | 10.7 | 11.3 | 10.9 | 0.25166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43138-01C02 | CML-3 | 50-FH-43138-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22689 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.525 | CML-3 | CML: Reducing Tee | 3 | 2054-10-01 | 2059-03-10 | 2015-04-27 07:00 | 2.5 | 0.07349 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-FH-43138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.15839 | 5.6 | 5.4 | 5.4 | 5.7 | 0.15
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-7 | 50-DH-56013-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1856 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 5.975 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0 | 5.9 | 6.1 | 5.8 | 6.1 | 0.15
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-7 | 50-DH-56013-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22336 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 5.975 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 6.1 | 5.8 | 6.1 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-7 | 400-WC-40025-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1267 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 8.875 | CML-7 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8.6 | 9 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.9 | 8.9 | 9.1 | 8.6 | 0.20616
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-8 | 250-WC-40017-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2071 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 8.725 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.5 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.7 | 8.8 | 8.9 | 8.5 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-5 | 400-WC-40024-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1074 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.825 | CML-5 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 8.6 | 9 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9 | 8.9 | 8.8 | 8.6 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43101-01C02 | CML-6 | 100-FH-43101-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12745 |  | 2014-01-24 07:00 | 2014-01-24 08:00 | [36 empty] | 5.975 | CML-6 | CML: Reducer | 3 | 2023-10-23 | 2024-02-26 | 2014-01-24 07:00 | 2.5 | 0.3384 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 6 O'Clock | 100 | 6.02 | 100-FH-43101-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 6.1 | 5.8 | 5.9 | 0.15
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-23 | 250-PW-44006-01X01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 23194 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 9.8 | CML-23 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.1 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | -9.5414 | 9.7 | 9.9 | 9.1 | 10.5 | 0.57735
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-14 | 150-FG-45505-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 22354 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.475 | CML-14 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.3 | 12 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.6 | 7.6 | 7.4 | 0.15
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57077-15C02 | CML-1 | 50-DC-57077-15C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10361 | Deck Level | 2013-11-11 | 2013-11-11 | [36 empty] | 11.2 | CML-1 | CML: type TBC | 3 | 2099-02-10 | 2078-03-07 | 2013-11-11 | 2.5 | 0 | A1: Outside Quadrant |  | 8.07 | 2.5 | 4.5931 | 11.2 | 9 O'Clock | 50 | 11.07 | 50-DC-57077-15C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.2 | 11.2 | 11.2 | 11.2 | 0
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-20 | 50-PL-23021-03C03 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10252 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.075 | CML-20 | CML: type TBC | 6 | 2016-09-01 | 2016-08-09 | 2013-11-08 | 2.5 | 1.9163 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 6 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.2 | 8 | 7.9 | 8.2 | 0.15
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-11 | 50-PL-23514-01C03 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8644 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:22 | [32 empty] | 8.525 | CML-11 | CML: Pipe Length | 6 | 2044-07-17 | 2043-12-11 | 2015-02-10 11:30 | 2.5 | 0.20033 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.7 | 8.6 | 8.4 | 0.15
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-3 | 50-PL-23516-03C03 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7791 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:03 | [32 empty] | 8.575 | CML-3 | CML: Pipe Length | 6 | 2043-02-15 | 2042-07-22 | 2015-01-13 07:00 | 2.5 | 0.20988 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 6 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.5 | 8.7 | 8.4 | 8.7 | 0.15
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-1 | 100-PG-23028-25C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 440 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 15.475 | CML-1 | CML: Pipe Length | 3 | 2016-09-19 | 2015-09-16 | 2014-03-12 09:00 | 9.4 | 2.336 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 15.3 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 15.6 | 15.3 | 15.4 | 15.6 | 0.15
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-1 | 100-PG-23028-25C02-P CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 20551 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 15.525 | CML-1 | CML: Pipe Length | 3 | 2017-11-18 | 2016-07-07 | 2014-05-30 09:30 | 9.4 | 1.7276 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 15.4 | 6 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | -0.4619 | 15.7 | 15.4 | 15.4 | 15.6 | 0.15
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43014-01C02 | CML-1 | 250-FL-43014-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23073 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 9.025 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.8 | 6 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 | 0 | 9.1 | 9.1 | 8.8 | 9.1 | 0.15
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-15 | 300-PW-44002-01X01-P CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 22861 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.5 | CML-15 | CML: Elbow | 6 | 2025-10-09 | 2024-05-04 | 2015-05-01 07:00 | 2.5 | 0.63157 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.1 | 6 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | 1.676 | 9.2 | 9.9 | 9.1 | 9.8 | 0.40825
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44027-01X01 | CML-2 | 50-PW-44027-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22744 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 9.55 | CML-2 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-04-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.1 | 3 O'Clock | 50 | 5.54 | 50-PW-44027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | -4.1989 | 9.9 | 9.1 | 9.5 | 9.7 | 0.34157
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-18 | 200-PL-20034-03C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21615 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 10.975 | CML-18 | CML: Elbow | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 10.7 | 9 O'Clock | 40 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.09 |  | 10.9 | 10.7 | 11.6 | 10.7 | 0.4272
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-3 | 250-PW-44010-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21920 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 9.975 | CML-3 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 9.8 | 9 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.9 | 10.1 | 10.1 | 9.8 | 0.15
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-3 | 250-PW-44010-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5822 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 9.975 | CML-3 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 9.8 | 9 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.9 | 10.1 | 10.1 | 9.8 | 0.15
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-9 | 50-PL-23300-09C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 13125 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.575 | CML-9 | CML: type TBC | 6 | 2021-10-18 | 2020-08-25 | 2014-02-04 07:00 | 2.81 | 0.98493 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.4 | 12 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.59 |  | 10.4 | 10.5 | 10.7 | 10.7 | 0.15
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-8 | 80-PG-23025-06C03 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20547 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 10.975 | CML-8 | CML: Pipe Length | 6 | 2049-02-22 | 2044-02-24 | 2014-05-27 08:00 | 2.8 | 0.23298 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 10.9 | 9 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | 0.33525 | 10.9 | 10.9 | 11.2 | 10.9 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-15 | 400-WC-40022-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1109 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.8 | CML-15 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.6 | 12 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.6 | 8.8 | 9 | 8.8 | 0.1633
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-7 | 400-WC-40024-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1076 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.675 | CML-7 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.6 | 9 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.6 | 8.8 | 8.7 | 8.6 | 0.095743
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-3 | 50-PG-44022-01C03-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22978 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 11.075 | CML-3 | CML: Reducer | 6 | 2075-10-24 | 2074-08-12 | 2015-05-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 10.9 | 12 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | 0.69968 | 10.9 | 11.2 | 11.2 | 11 | 0.15
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20060-01C02 | CML-7 | 50-PL-20060-01C02 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 21311 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 10.625 | CML-7 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.6 | 3 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.2 | 9.6 | 12.2 | 10.5 | 1.1147
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38455-01C02-H | CML-7 | 50-CG-38455-01C02-H CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 23691 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.3 | CML-7 | CML: Elbow | 3 | 2030-01-31 | 2031-11-16 | 2015-10-30 07:00 | 2.5 | 0.18223 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 80 | 5.54 | 50-CG-38455-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.1 | 5.3 | 5.4 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-1 | 400-WC-40022-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1095 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 8.65 | CML-1 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 8.6 | 6 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.7 | 8.6 | 8.6 | 8.7 | 0.057735
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-4 | 250-PW-44004-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5623 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 10.1 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-20 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.6 | 3 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.8 | 9.6 | 10.3 | 9.7 | 0.55976
PG06 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PG-23008-15S01-A | CML-1 | 200-PG-23008-15S01-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20291 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | Check Corrosion Rate of 0.319mm/ yr | [35 empty] | 5.2 | CML-1 | CML: Elbow | 3 | 2022-12-08 | 2023-12-16 | 2014-10-17 07:00 | 2.5 | 0.3191 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DC-57300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.1 | 5.1 | 5.2 | 0.14142
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-9 | 50-CG-38458-01C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23737 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.3 | CML-9 | CML: Elbow | 3 | 2030-01-31 | 2031-11-16 | 2015-10-30 07:00 | 2.5 | 0.18223 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 20 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.1 | 5.4 | 5.3 | 0.14142
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-3 | 250-PW-44006-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23174 | New Spool not painted | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 9.475 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.1 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | -10.8575 | 9.7 | 9.4 | 9.7 | 9.1 | 0.28723
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 20682 | Rope Access | 2014-05-26 13:00 | 2014-05-26 14:00 | [36 empty] | 12.275 | CML-4 | CML: type TBC | 3 | 2036-08-21 | 2030-06-30 | 2014-05-26 13:00 | 4.7 | 0.2741 | A4: Left Quadrant |  | 8.07 | 4.7 | 6.385 | 10.8 | 9 O'Clock | 50 | 11.07 | 50-PG-23061-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 13.3 | 12.6 | 12.4 | 10.8 | 1.0563
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38471-01C02-P | CML-2 | 50-CG-38471-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23621 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.8 | CML-2 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-CG-38471-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 5.8 | 5.9 | 5.6 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-6 | 100-FH-43104-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12757 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 6.2 | CML-6 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 9 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.4 | 6.1 | 6.1 | 0.14142
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-19 | 50-FG-45024-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1202 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.8 | CML-19 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.9 | 6.9 | 6.6 | 0.14142
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-7 | 100-PG-23503-03C03-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2723 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.8 | CML-7 | CML: Pipe Length | 6 | 2023-05-10 | 2023-11-02 | 2014-03-13 09:00 | 5.66 | 0.54998 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.7 | 3 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.04 |  | 10.7 | 10.7 | 11 | 10.8 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1643 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.7 | CML-2 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.6 | 9 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 10.3 | 10.2 | 9.7 | 8.6 | 0.77889
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-11 | 50-PL-23516-03C03 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 7799 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 15:57 | [32 empty] | 8.2 | CML-11 | CML: Pipe Length | 6 | 2027-01-25 | 2026-10-21 | 2015-01-13 07:00 | 2.5 | 0.4568 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 12 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.3 | 8.3 | 8.2 | 0.14142
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20683 | Rope Access | 2014-05-26 13:00 | 2014-05-26 14:00 | [36 empty] | 11.55 | CML-5 | CML: type TBC | 3 | 2036-08-21 | 2030-06-30 | 2014-05-26 13:00 | 4.7 | 0.2741 | A3: Inside Quadrant |  | 8.07 | 4.7 | 6.385 | 10.8 | 6 O'Clock | 50 | 11.07 | 50-PG-23061-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 11.6 | 12.4 | 10.8 | 11.4 | 0.66081
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45009-01C02-E | CML-5 | 150-FG-45009-01C02-E CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24299 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.7 | CML-5 | CML: Equal Tee | 3 | 2049-01-12 | 2042-08-13 | 2016-05-27 07:00 | 1.03 | 0.17058 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-FG-45009-01C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.57 |  | 6.6 | 6.7 | 6.6 | 6.9 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40011-01C02 | CML-6 | 50-WC-40011-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1891 | Rope Access | 2014-03-25 13:00 | 2014-03-25 14:00 | [36 empty] | 9.1 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.6 | 9 O'Clock | 50 | 5.54 | 50-WC-40011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  |  | 9.4 | 9.3 | 8.6 | 0.43589
PL01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-PL-20060-01C02 | CML-14 | 50-PL-20060-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20311 | Reviewed 24/11/14. FFS. CML to be checked in Oct.16 | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 1.024mm/ yr |  | Nestor | 2014-11-26 14:08 | [32 empty] | 10.3 | CML-14 | CML: Elbow | 6 | 2021-09-05 | 2020-06-22 | 2014-10-02 07:00 | 2.5 | 1.0241 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 9.6 | 3 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.5 | 9.6 | 10.3 | 10.8 | 0.5099
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-4 | 25-PW-44026-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5757 | Rope access | 2014-06-23 07:00 | 2014-06-23 08:00 | [36 empty] | 9.3 | CML-4 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.1 | 3 O'Clock | 50 | 5.54 | 50-PW-44026-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.4 | 9.1 | 9.3 | 9.4 | 0.14142
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-7 | 25-PW-44026-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22739 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 9.3 | CML-7 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-04-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 9 O'Clock | 50 | 6.35 | 25-PW-44026-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.3 | 9.5 | 9.2 | 9.2 | 0.14142
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-22 | 50-PL-23300-09C03 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 13138 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.4 | CML-22 | CML: type TBC | 6 | 2019-11-14 | 2018-12-26 | 2014-02-04 07:00 | 2.81 | 1.2789 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.2 | 12 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.39 |  | 10.2 | 10.4 | 10.5 | 10.5 | 0.14142
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-13 | 300-PG-20005-03C03-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22775 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 12.6 | CML-13 | CML: Reducing Tee | 6 | 2023-07-10 | 2021-09-14 | 2015-04-29 07:00 | 4.9 | 0.92651 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.5 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 | 0.12501 | 12.8 | 12.5 | 12.5 | 12.6 | 0.14142
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-10 | 50-PW-44013-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22729 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 9.325 | CML-10 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-04-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.1 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | 0.11784 | 9.1 | 9.7 | 9.2 | 9.3 | 0.263
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-16 | 150-PG-20507-01C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2860 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 11.2 | CML-16 | CML: type TBC | 6 | 2098-02-09 | 2085-10-05 | 2014-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 11 | 12 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11 | 11.2 | 11.3 | 11.3 | 0.14142
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-13 | 50-DH-56137-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5681 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [35 empty] | Low alarm breach | 18 | CML-13 | CML: Elbow | 3 | 2019-01-23 | 2016-09-07 | 2014-06-21 14:00 | 2.5 | 3.351 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.9 | 3 O'Clock | 250 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 |  | 17.9 | 17.9 | 18 | 18.2 | 0.14142
FH01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-FH-43141-01C02 | CML-8 | 150-FH-43141-01C02 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 5064 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.5 | CML-8 | CML: type TBC | 0 | 2036-10-14 | 2030-08-10 | 2015-03-06 07:00 | 2.5 | 0.037 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.3 | 12 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.5 | 3.6 | 3.6 | 0.14142
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-10 | 150-FL-43174-01C02 CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 8544 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 3.6 | CML-10 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-02-04 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 6 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.7 | 3.6 | 3.4 | 3.7 | 0.14142
FL01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FL-43174-01C02 | CML-4 | 150-FL-43174-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 7876 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:41 | [32 empty] | 3.6 | CML-4 | CML: Pipe Length | 3 | 2015-09-20 | 2015-12-19 | 2015-01-14 10:30 | 2.5 | 1.3184 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.7 | 3.6 | 3.4 | 3.7 | 0.14142
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-37 | 80-DH-56004-01C02 CML-37 | yes | FPSO 2015 | Pipe Wall Thickness | 6915 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.5 | CML-37 | CML: type TBC | 0.5 | 2022-08-19 | 2020-04-29 | 2015-04-05 07:00 | 3.5 | 0.10842 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4.3 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.6 | 4.6 | 4.5 | 4.3 | 0.14142
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-23 | 80-DH-56004-01C02 CML-23 | yes | FPSO 2015 | Pipe Wall Thickness | 6901 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.5 | CML-23 | CML: type TBC | 0.5 | 2022-08-19 | 2020-04-29 | 2015-04-05 07:00 | 3.5 | 0.10842 | A2: Right Quadrant |  | 4 | 3.5 | 3.75 | 4.3 | 3 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.5 | 4.3 | 4.6 | 4.6 | 0.14142
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-2 | 80-DH-56004-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 6880 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.5 | CML-2 | CML: type TBC | 0.5 | 2022-08-19 | 2020-04-29 | 2015-04-05 07:00 | 3.5 | 0.10842 | A2: Right Quadrant |  | 4 | 3.5 | 3.75 | 4.3 | 3 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.5 | 4.3 | 4.6 | 4.6 | 0.14142
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23302-01C02 | CML-9 | 80-VA-23302-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22525 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.7 | CML-9 | CML: Elbow | 3 | 2016-03-31 | 2016-07-29 | 2015-04-20 07:00 | 2.5 | 1.0553 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.5 | 6 O'Clock | 50 | 5.49 | 80-VA-23302-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.8 | 3.8 | 3.5 | 3.7 | 0.14142
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23301-01C02 | CML-8 | 80-VA-23301-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22515 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.8 | CML-8 | CML: Elbow | 3 | 2016-07-24 | 2016-12-05 | 2015-04-20 07:00 | 2.5 | 0.94923 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.7 | 3 O'Clock | 50 | 5.49 | 80-VA-23301-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.7 | 4 | 3.8 | 0.14142
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23301-01C02 | CML-7 | 80-VA-23301-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22514 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.9 | CML-7 | CML: Elbow | 3 | 2016-09-30 | 2017-02-19 | 2015-04-20 07:00 | 2.5 | 0.8962 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.8 | 9 O'Clock | 50 | 5.49 | 80-VA-23301-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.9 | 4.1 | 3.8 | 0.14142
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-2 | 300-PW-44002-01X01-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22848 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.45 | CML-2 | CML: Elbow | 6 | 2025-10-09 | 2024-05-04 | 2015-05-01 07:00 | 2.5 | 0.63157 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.1 | 6 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | 0.18622 | 9.6 | 9.6 | 9.1 | 9.5 | 0.23805
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43303-01C02 | CML-8 | 50-FL-43303-01C02 CML-8 | yes | FPSO 2014 | Pipe Wall Thickness | 20464 | Reviewed 24/11/14. FFS. Repeat on Oct.15. | 2014-10-05 07:00 | 2014-10-05 15:00 |  |  | Nestor | 2014-11-24 11:57 | [32 empty] | 5 | CML-8 | CML: Elbow | 3 | 2018-12-10 | 2019-07-14 | 2014-10-05 07:00 | 2.5 | 0.54978 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-FL-43303-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 4.8 | 5.1 | 5 | 0.14142
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-16 | 100-DH-56009-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 3439 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5 | CML-16 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 4.8 | 12 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.1 | 5 | 5.1 | 0.14142
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56057-01C02 | CML-3 | 50-DH-56057-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3171 | Rope Access | 2014-05-07 08:00 | 2014-05-07 09:00 | [36 empty] | 5.1 | CML-3 | CML: type TBC | 3 | 2017-11-03 | 2018-04-26 | 2014-05-07 08:00 | 2.5 | 0.68639 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56057-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.2 | 5.1 | 5.2 | 0.14142
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-3 | 50-DH-56056-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20123 | Rope Access | 2014-05-07 08:00 | 2014-05-07 09:00 | [36 empty] | 5.1 | CML-3 | CML: type TBC | 3 | 2017-11-03 | 2018-04-26 | 2014-05-07 08:00 | 2.5 | 0.68639 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 4379.9428 | 4.9 | 5.2 | 5.1 | 5.2 | 0.14142
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-8 | 300-PW-44002-01X01-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22854 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.5 | CML-8 | CML: Reducing Tee | 6 | 2026-11-20 | 2025-04-29 | 2015-05-01 07:00 | 2.5 | 0.57937 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 0.55867 | 11.1 | 9.2 | 10.4 | 11.3 | 0.94868
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-26 | 50-DH-56070-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 3242 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.2 | CML-26 | CML: type TBC | 3 | 2018-09-09 | 2019-04-04 | 2014-05-09 07:00 | 2.5 | 0.57582 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.3 | 5.3 | 5 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-17 | 50-FH-43450-01C02 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10684 | Deck Level | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-13 13:55 | [32 empty] | 5.1 | CML-17 | CML: Elbow | 3 | 2016-01-08 | 2016-04-19 | 2013-11-17 | 2.5 | 1.1663 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.3 | 5 | 5 | 0.14142
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38477-01C02-P | CML-2 | 50-CG-38477-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20896 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.2 | CML-2 | CML: type TBC | 3 | 2017-03-30 | 2017-03-20 | 2014-10-04 07:00 | 2.5 | 1.005 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 6 O'Clock | 25 | 6.35 | 25-CG-38484-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.3 | 5 | 5.3 | 0.14142
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-3 | 300-PW-44002-01X01-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22020 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 9.95 | CML-3 | CML: Elbow | 6 | 2023-02-10 | 2021-12-26 | 2014-10-17 07:00 | 2.5 | 0.805 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.4 | 9.2 | 9.4 | 10.8 | 0.77244
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-9 | 50-PG-23074-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20631 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.4 | CML-9 | CML: Elbow | 3 | 2023-09-14 | 2024-10-22 | 2014-07-26 07:00 | 2.5 | 0.29527 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.5 | 5.5 | 5.2 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-13 | 50-FH-43450-01C02 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10680 | Deck Level | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-13 13:13 | [32 empty] | 5.3 | CML-13 | CML: Pipe Length | 3 | 2017-07-21 | 2017-12-30 | 2013-11-17 | 2.5 | 0.73432 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.3 | 5.5 | 0.14142
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-29 | 250-PW-44006-01X01 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 1926 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 10.025 | CML-29 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.3 | 10.8 | 9.2 | 9.8 | 0.68496
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-4 | 80-FH-43111-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12802 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 5.4 | CML-4 | CML: type TBC | 3 | 2023-12-26 | 2025-03-19 | 2014-02-01 07:00 | 2.5 | 0.28272 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.3 | 5.6 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-18 | 400-WC-40024-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1087 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 9 | CML-18 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.7 | 12 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 9 | 8.8 | 9.5 | 0.3559
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-10 | 50-FH-43137-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12862 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 5.5 | CML-10 | CML: Pipe Length | 3 | 2021-08-11 | 2022-06-28 | 2014-01-23 08:00 | 2.5 | 0.37066 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.6 | 5.5 | 5.3 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-22 | 400-WC-40024-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 1091 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 8.8333 | CML-22 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.7 | 3 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.7 |  | 9.1 | 0.23094
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43302-01C02-E | CML-4 | 200-PL-43302-01C02-E CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8605 |  | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6.925 | CML-4 | CML: type TBC | 3 | 2063-07-07 | 2057-06-06 | 2015-02-09 07:30 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.8 | 12 O'Clock | 200 | 6.35 | 200-PL-43302-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.46 |  | 6.8 | 7 | 7 | 6.9 | 0.095743
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38007-01C02 | CML-4 | 50-CG-38007-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3111 | Rope Access | 2014-05-04 09:30 | 2014-05-04 10:00 | [36 empty] | 5.9 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-04 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 15 | 5.54 | 50-CG-38007-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6.1 | 5.9 | 0.14142
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45022-01C02 | CML-2 | 100-FG-45022-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22052 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 6.1 | CML-2 | CML: Elbow | 3 | 2054-01-28 | 2055-06-02 | 2014-10-20 07:00 | 2.5 | 0.08651 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-FG-45022-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.2 | 5.9 | 6.1 | 0.14142
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38005-01C02 | CML-1 | 50-CG-38005-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3101 | Rope Access | 2014-05-04 10:00 | 2014-05-04 10:30 | [36 empty] | 6 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-04 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 15 | 5.54 | 50-CG-38005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 5.9 | 6.2 | 0.14142
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23415-01C03 | CML-4 | 100-PG-23415-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20784 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 12.675 | CML-4 | CML: type TBC | 6 | 2098-02-09 | 2085-10-05 | 2014-10-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.4 | 12 O'Clock | 150 | 10.97 | 150-PG-23415-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.4 | 14.3 | 11.6 | 13.4 | 1.408
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23415-01C03 | CML-1 | 100-PG-23415-01C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20781 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 11.85 | CML-1 | CML: type TBC | 6 | 2098-02-09 | 2085-10-05 | 2014-10-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 11.4 | 9 O'Clock | 150 | 10.97 | 150-PG-23415-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.8 | 12.1 | 12.1 | 11.4 | 0.33166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43106-01C02 | CML-2 | 100-FH-43106-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12771 |  | 2014-01-25 10:00 | 2014-01-25 11:00 | [36 empty] | 6.1 | CML-2 | CML: type TBC | 3 | 2032-07-24 | 2033-03-12 | 2014-01-25 10:00 | 2.5 | 0.18371 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 12 O'Clock | 100 | 6.02 | 100-FH-43106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.1 | 6.2 | 6.2 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43102-01C02 | CML-5 | 100-FH-43102-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12750 |  | 2014-01-24 08:00 | 2014-01-24 09:00 | [36 empty] | 6.1 | CML-5 | CML: type TBC | 3 | 2032-06-22 | 2033-02-07 | 2014-01-24 08:00 | 2.5 | 0.18455 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-FH-43102-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 6.2 | 6.2 | 5.9 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-9 | 80-FH-43151-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2243 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 6.2 | CML-9 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 6 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.3 | 6 | 6.3 | 0.14142
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1888 | Rope Access | 2014-03-25 13:00 | 2014-03-25 14:00 | [36 empty] | 6.2 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-WC-40011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6 | 6.2 | 6.3 | 0.14142
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-8 | 25-FG-45455-01C02-E CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1242 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 6.1 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6 | 6.3 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-6 | 300-FH-43001-01C02 CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 12518 |  | 2014-01-24 13:00 | 2014-01-24 15:00 | [36 empty] | 6.1 | CML-6 | CML: type TBC | 3 | 2020-07-26 | 2020-07-07 | 2014-01-24 13:00 | 2.5 | 0.5378 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.3 | 6 | 6.1 | 0.14142
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-4 | 25-PW-44026-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22736 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 6.2 | CML-4 | CML: Pipe Length | 3 | 2034-05-21 | 2034-03-26 | 2015-04-28 07:00 | 2.5 | 0.18347 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 25 | 6.35 | 25-PW-44026-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6.3 | 6 | 6.2 | 0.14142
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20060-01C02 | CML-8 | 50-PL-20060-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21837 |  | 2014-10-12 07:00 | 2014-10-12 12:00 | [36 empty] | 10.1 | CML-8 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.6 | 12 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 | -5.9148 | 9.6 | 10.4 | 10.5 | 9.9 | 0.42426
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-2 | 300-PW-44002-01X01-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22019 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 9.9 | CML-2 | CML: Elbow | 6 | 2023-02-10 | 2021-12-26 | 2014-10-17 07:00 | 2.5 | 0.805 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 6 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.5 | 10 | 9.2 | 9.9 | 0.53541
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-VA-23058-01C02 | CML-4 | 200-VA-23058-01C02 CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 3144 | Rope Access | 2014-05-02 13:00 | 2014-05-02 14:00 | [36 empty] | 6.5 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-05-02 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-VA-23058-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.7 | 6.4 | 6.4 | 0.14142
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P |  | 50-CG-38452-09C02-P |  | FPSO 2016 | Pipe Wall Thickness | 9169 |  | 2016-02-23 07:00 | 2016-02-23 15:00 | [36 empty] | 6.5 | 200-FH-43304-01C02 | Piping | 3 | 2051-11-30 |  | 2016-02-23 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.4 | 9 O'Clock | 200 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.5 | 6.7 | 6.4 | 0.14142
PL01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-PL-20060-01C02 | CML-12 | 50-PL-20060-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20309 | Reviewed 24/11/14. FFS. CML to be checked in Oct.16 | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 1.024mm/ yr |  | Nestor | 2014-11-26 14:08 | [32 empty] | 10.1 | CML-12 | CML: Reducing Tee | 6 | 2021-09-05 | 2020-06-22 | 2014-10-02 07:00 | 2.5 | 1.0241 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 9.6 | 9 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.9 | 10.4 | 10.5 | 9.6 | 0.42426
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 20680 | Rope Access | 2014-05-26 13:00 | 2014-05-26 14:00 | [36 empty] | 12.675 | CML-2 | CML: type TBC | 3 | 2050-04-20 | 2040-07-17 | 2014-05-26 13:00 | 4.7 | 0.17258 | A4: Left Quadrant |  | 8.07 | 4.7 | 6.385 | 10.9 | 9 O'Clock | 50 | 11.07 | 50-PG-23061-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 12.4 | 13.5 | 13.9 | 10.9 | 1.3426
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-10 | 400-WC-40025-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1270 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 9.5 | CML-10 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.8 | 6 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 10.9 | 9.3 | 8.8 | 9 | 0.95568
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-4 | 150-FL-43174-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12902 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.3 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 6 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.5 | 7.2 | 7.3 | 0.14142
CG04 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2158 | Rope Access | 2014-03-30 08:00 | 2014-03-30 09:00 | [36 empty] | 7.3 | CML-1 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-03-30 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-VA-80003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 | 0 | 7.5 | 7.3 | 7.2 | 7.2 | 0.14142
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-9 | 50-CG-38452-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1124 |  | 2014-03-21 11:30 | 2014-03-21 12:00 | [36 empty] | 7.4 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-21 11:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 6 O'Clock | 300 | 6.35 | 300-WC-40044-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.5 | 7.5 | 7.2 | 7.4 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-27 | 400-FH-43508-01C02 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6576 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.5 | CML-27 | CML: Elbow | 3 | 2032-06-16 | 2029-12-11 | 2015-03-30 07:00 | 2.5 | 0.28443 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 6 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.5 | 7.4 | 7.4 | 7.7 | 0.14142
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43509-01C02 | CML-1 | 300-FL-43509-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2395 | Rope Access | 2014-03-19 09:30 | 2014-03-19 11:00 | [36 empty] | 7.5 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 6 O'Clock | 300 | 6.35 | 300-FL-43509-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.7 | 7.4 | 7.5 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-2 | 400-WC-40025-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1262 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 9.15 | CML-2 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.8 | 6 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.8 | 8.9 | 8.8 | 9.1 | 0.45092
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45009-01C02-E | CML-3 | 150-FG-45009-01C02-E CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24297 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.7 | CML-3 | CML: Fitting | 3 | 2043-03-13 | 2037-10-30 | 2016-05-27 07:00 | 1.03 | 0.20402 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.5 | 6 O'Clock | 40 | 7.11 | 150-FG-45009-01C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.47 |  | 6.7 | 6.8 | 6.5 | 6.8 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-15 | 150-FH-43026-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12655 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.1 | CML-15 | CML: Pipe Length | 3 | 2032-01-25 | 2028-09-14 | 2014-01-22 07:00 | 1.03 | 0.32577 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.9 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.87 |  | 7.2 | 6.9 | 7.1 | 7.2 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-7 | 150-FH-43026-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12647 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.2 | CML-7 | CML: Pipe Length | 3 | 2049-01-08 | 2042-08-09 | 2014-01-22 07:00 | 1.03 | 0.17064 | A4: Left Quadrant |  | 4.11 | 1.03 | 2.1256 | 7 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 |  | 7.2 | 7.3 | 7.3 | 7 | 0.14142
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23420 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 10.1 | CML-6 | CML: Pipe Length | 6 | 2039-12-21 | 2042-05-06 | 2015-07-22 07:00 | 5.22 | 0.19154 | A4: Left Quadrant |  | 4.31 | 5.22 | 4.765 | 9.9 | 9 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.68 | 0.44161 | 10.2 | 10.2 | 10.1 | 9.9 | 0.14142
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-4 | 50-CG-38487-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20843 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.5 | CML-4 | CML: Pipe Length | 3 | 2037-12-13 | 2031-08-01 | 2014-10-02 07:00 | 2.5 | 0.25415 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 0.96264 | 8.4 | 8.5 | 8.7 | 8.4 | 0.14142
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62004-01S01 | CML-10 | 50-DO-62004-01S01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1459 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [36 empty] | 11.9 | CML-10 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2014-04-25 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 11.4 | 6 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 12 | 12.3 | 11.4 | 11.9 | 0.37417
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20060-01C02 | CML-7 | 50-PL-20060-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 23894 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 9.9 | CML-7 | CML: Pipe Length | 6 | 2027-12-10 | 2026-04-04 | 2014-09-26 07:00 | 2.5 | 0.53733 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.6 | 3 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10 | 9.6 | 10 | 10 | 0.2
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-1 | 300-PW-44002-01X01-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22847 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.775 | CML-1 | CML: Pipe Length | 6 | 2026-11-20 | 2025-04-29 | 2015-05-01 07:00 | 2.5 | 0.57937 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 9 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 0.37245 | 9.8 | 9.9 | 10.2 | 9.2 | 0.41932
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-10 | 50-PW-44013-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5734 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 9.4 | CML-10 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-22 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | -7.1523 | 9.3 | 9.8 | 9.2 | 9.3 | 0.2708
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-10 | 50-PL-23300-09C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 13126 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.5 | CML-10 | CML: type TBC | 6 | 2021-10-18 | 2020-08-25 | 2014-02-04 07:00 | 2.81 | 0.98493 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 10.4 | 6 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.59 |  | 10.5 | 10.4 | 10.4 | 10.7 | 0.14142
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-14 | 50-PL-23042-09C03 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10079 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.6 | CML-14 | CML: type TBC | 6 | 2018-12-25 | 2018-02-23 | 2013-11-07 | 2.5 | 1.538 | A2: Right Quadrant |  | 5.07 | 2.5 | 3.785 | 10.4 | 3 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.7 | 10.4 | 10.6 | 10.7 | 0.14142
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80001-01C02 | CML-1 | 50-VA-80001-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3134 | Rope Access | 2014-05-02 10:30 | 2014-05-02 11:30 | [36 empty] | 11 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-02 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.8 | 9 O'Clock | 50 | 5.54 | 50-VA-80001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.1 | 11 | 11.1 | 10.8 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-11 | 150-WC-40006-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1652 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.025 | CML-11 | CML: Fitting | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.7 | 9 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.2 | 9.5 | 8.7 | 8.7 | 0.39476
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20044-03C03-P | CML-6 | 80-PG-20044-03C03-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23335 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-19 07:00 | 2015-07-19 15:00 | [36 empty] | 11 | CML-6 | CML: Reducer | 6 | 2093-05-14 | 2081-03-09 | 2015-07-19 07:00 | 2.5 | 0.10786 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 9 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | 8.4399 | 11 | 10.9 | 11.2 | 10.9 | 0.14142
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20031-01C03-P | CML-8 | 150-PG-20031-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 23870 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 11.1 | CML-8 | CML: Fitting | 6 | 2173-03-11 | 2149-11-23 | 2014-09-26 07:00 | 2.5 | 0.05298 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 10.9 | 3 O'Clock | 150 | 10.97 | 150-PG-20031-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.1 | 10.9 | 11.2 | 11.2 | 0.14142
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-17 | 50-PL-23041-06C03 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10230 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.6 | CML-17 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 1.5284 | A2: Right Quadrant |  | 5.07 |  |  | 10.4 | 3 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.7 | 10.4 | 10.7 | 10.6 | 0.14142
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-31 | 200-PL-20008-01C02-H CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 8828 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 7.2 | CML-31 | CML: Reducer | 3 | 2065-11-29 | 2058-08-19 | 2015-02-21 07:00 | 1.1 | 0 | A4: Left Quadrant |  | 3.35 | 1.1 | 1.8281 | 7.1 | 9 O'Clock | 300 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 7.2 | 7.2 | 7.3 | 7.1 | 0.08165
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-10 | 50-PG-23024-03C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10042 | Rope Access | 2014-01-06 | 2014-01-06 | [36 empty] | 8.75 | CML-10 | CML: Pipe Length | 6 | 2046-09-10 | 2042-11-26 | 2014-01-06 | 0.97 | 0.23333 | A3: Inside Quadrant |  | 2.74 | 0.97 | 1.855 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.63 |  | 8.9 | 8.7 | 8.6 | 8.8 | 0.1291
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-5 | 250-PW-20022-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2048 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 12.7 | CML-5 | CML: Equal Tee | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 12.5 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 13.1 | 12.6 | 12.6 | 12.5 | 0.2708
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-31 | 50-CG-38001-09C02 CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 10946 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.75 | CML-31 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0.23122 | A1: Outside Quadrant |  | 5.74 |  |  | 8.6 | 12 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.6 | 8.6 | 8.8 | 8.7 | 8.9 | 0.1291
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44029-01C02 | CML-5 | 250-PW-44029-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21909 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 10.25 | CML-5 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 6 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 11.1 | 10.4 | 9.7 | 9.8 | 0.6455
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-45 | 200-PG-23008-15S01-A CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 9132 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.25 | CML-45 | CML: type TBC | 3 | 2025-07-04 | 2026-10-21 | 2015-03-02 07:00 | 2.5 | 0.25122 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.1 | 5.2 | 5.3 | 0.1291
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3397 | Rope Access | 2014-05-10 13:00 | 2014-05-10 14:00 | [36 empty] | 5.25 | CML-2 | CML: type TBC | 3 | 2019-11-30 | 2020-08-11 | 2014-05-10 13:00 | 2.5 | 0.46748 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56069-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.2 | 5.4 | 5.1 | 0.1291
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38472-01C02 | CML-3 | 50-CG-38472-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23658 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.25 | CML-3 | CML: Elbow | 3 | 2030-01-31 | 2031-11-16 | 2015-10-30 07:00 | 2.5 | 0.18223 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-CG-38472-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.1 | 5.3 | 5.2 | 0.1291
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44027-01X01 | CML-1 | 50-PW-44027-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21903 |  | 2014-06-19 08:30 | 2014-06-19 09:00 | [36 empty] | 9.25 | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-06-19 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.3 | 9.3 | 9.2 | 0.057735
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-5 | 50-FG-45024-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1188 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.25 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.4 | 6.1 | 6.3 | 0.1291
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-6 | 50-WC-40451-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3068 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | [36 empty] | 8.975 | CML-6 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-03 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.7 | 3 O'Clock | 100 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 | -1.4572 | 8.9 | 8.7 | 9.5 | 8.8 | 0.3594
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-6 | 150-FL-43453-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2250 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.75 | CML-6 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.6 | 6 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.9 | 6.6 | 6.7 | 0.1291
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-13 | 100-PG-23503-03C03-A CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2729 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.85 | CML-13 | CML: Pipe Length | 6 | 2023-05-10 | 2023-11-02 | 2014-03-13 09:00 | 5.66 | 0.54998 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.7 | 12 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.04 |  | 10.7 | 11 | 10.8 | 10.9 | 0.1291
PL01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-20060-01C02 | CML-7 | 50-PL-20060-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20754 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 9.9 | CML-7 | CML: type TBC | 6 | 2027-12-10 | 2026-04-04 | 2014-09-26 07:00 | 2.5 | 0.53733 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.6 | 3 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10 | 9.6 | 10 | 10 | 0.2
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40500-1CG | CML-9 | 400-WC-40500-1CG CML-9 |  | FPSO 2016 | Pipe Wall Thickness | 24427 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.92mm/ yr | [35 empty] | 19.125 | CML-9 | CML: Reducing Tee | 3 | 2033-12-30 | 2025-05-03 | 2016-07-02 07:00 | 2.5 | 0.91955 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 18.6 | 12 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.1 | 1.058 | 18.6 | 19.6 | 19.2 | 19.1 | 0.4113
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-7 | 50-PL-23514-01C03 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8640 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:20 | [32 empty] | 8.15 | CML-7 | CML: Pipe Length | 6 | 2027-09-19 | 2027-06-11 | 2015-02-10 11:30 | 2.5 | 0.43601 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.1 | 8.2 | 8.3 | 8 | 0.1291
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-7 | 50-PL-23020-01C03 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10121 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-7 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 6 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.1 | 8.3 | 8 | 8.2 | 0.1291
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-4 | 50-PL-23021-03C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10236 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-4 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 6 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8.2 | 8 | 8.1 | 0.1291
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-1 | 50-PL-23023-03C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10201 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-1 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 6 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.1 | 8.3 | 8 | 8.2 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-11 | 80-FH-43005-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12561 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 8.35 | CML-11 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-20 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.2 | 3 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.3 | 8.2 | 8.4 | 8.5 | 0.1291
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-10 | 250-WC-40017-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2073 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 8.95 | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 9 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.2 | 9 | 8.9 | 8.7 | 0.20817
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-6 | 150-WC-40006-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1647 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 8.845 | CML-6 | CML: Fitting | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.7 | 6 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.78 | 8.8 | 8.7 | 9.1 | 0.1754
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43109-01C02 | CML-5 | 200-FH-43109-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12789 |  | 2014-01-18 14:30 | 2014-01-18 15:30 | [36 empty] | 7.75 | CML-5 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 14:30 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.6 | 6 O'Clock | 200 | 6.35 | 200-FH-43109-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.26 |  | 7.8 | 7.7 | 7.6 | 7.9 | 0.1291
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-4 | 50-PL-23022-03C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1860 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.15 | CML-4 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 3 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.3 | 9 | 9.1 | 9.2 | 0.1291
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-2 | 100-PG-23406-03C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20728 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 12.25 | CML-2 | CML: Elbow | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 11.5 | 12 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 11.5 | 12 | 13.7 | 11.8 | 0.98826
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-8 | 100-PG-23406-03C03 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20734 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 12 | CML-8 | CML: Elbow | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 11.5 | 9 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 12.3 | 12.5 | 11.7 | 11.5 | 0.4761
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23033-03C03 | CML-13 | 50-PL-23033-03C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1885 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.15 | CML-13 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 6 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.3 | 9.2 | 9 | 9.1 | 0.1291
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-6 | 50-FL-43454-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22991 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.35 | CML-6 | CML: Reducing Tee | 6 | 2199-08-23 | 2189-01-19 | 2015-05-05 07:00 | 2.5 | 0.03633 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.2 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 0 | 9.5 | 9.3 | 9.2 | 9.4 | 0.1291
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-8 | 300-PF-20001-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21146 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.85 | CML-8 | CML: Elbow | 6 | 2016-04-22 | 2015-08-07 | 2014-07-16 07:30 | 2.5 | 4.0653 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 9.7 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10 | 9.8 | 9.9 | 9.7 | 0.1291
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40511-1CG | CML-1 | 300-WC-40511-1CG CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 5654 | Material class 1CG | 2014-06-21 10:00 | 2014-06-21 11:00 | [36 empty] | 20.8 | CML-1 | CML: type TBC | 3 | 2163-03-18 | 2103-04-25 | 2014-06-21 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 14.48 | 2.5 | 8.49 | 19.4 | 3 O'Clock | 300 | 17.48 | 300-WC-40511-1CG-S1 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.9 |  | 21 | 19.4 | 21 | 21.8 | 1.0066
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44027-01X01 | CML-1 | 50-PW-44027-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5574 |  | 2014-06-19 08:30 | 2014-06-19 09:00 | [36 empty] | 9.25 | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-06-19 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | -6.957 | 9.2 | 9.3 | 9.3 | 9.2 | 0.057735
CG03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-CG-38459-09C02-P | CML-23 | 80-CG-38459-09C02-P CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 22888 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 15.15 | CML-23 | CML: Pipe Length | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 15 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.5 | -1.5052 | 15.3 | 15.2 | 15 | 15.1 | 0.1291
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-5 | 250-PW-44004-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22749 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 10.025 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-04-29 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 | -4.3181 | 10 | 9.8 | 9.7 | 10.6 | 0.40311
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-3 | 250-PW-44004-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5622 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 11 | CML-3 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2014-06-20 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 10 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 11.2 | 12.2 | 10.6 | 10 | 0.93808
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38301-01C02-P |  | 50-CG-38301-01C02-P | yes | FPSO 2014 | Pipe Wall Thickness | 22093 | Rope access | 2014-06-02 07:00 | 2014-06-02 08:00 | [36 empty] | 5.15 | 50-CG-38301-01C02-P | Piping | 3 | 2019-01-23 |  | 2014-06-02 07:00 |  | 0.5381 | A2: Right Quadrant |  |  | 2.5 |  | 5 | 3 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 5 | 5.2 | 5 | 5.1 | 5.3 | 0.1291
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56113-01C02 | CML-6 | 50-DH-56113-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5245 | Rope Access | 2014-05-20 14:00 | 2014-05-20 15:00 | [36 empty] | 5.15 | CML-6 | CML: Elbow | 3 | 2018-11-12 | 2019-06-14 | 2014-05-20 14:00 | 2.5 | 0.55744 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DH-56113-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.1 | 5.3 | 0.1291
FH01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FH-43507-01C02 | CML-2 | 100-FH-43507-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2579 |  | 2014-04-26 14:00 | 2014-04-26 15:00 | [36 empty] | 5.15 | CML-2 | CML: type TBC | 3 | 2018-06-30 | 2018-06-18 | 2014-04-26 14:00 | 2.5 | 0.59803 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45035-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.2 | 5.3 | 5 | 0.1291
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-12 | 300-PW-44002-01X01-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22858 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.95 | CML-12 | CML: Reducing Tee | 6 | 2028-03-21 | 2026-07-03 | 2015-05-01 07:00 | 2.5 | 0.52718 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.3 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | 0.7449 | 10.1 | 9.3 | 9.7 | 10.7 | 0.59722
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-29 | 250-PW-44006-01X01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 8021 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 9.75 | CML-29 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | -0.12164 | 9.6 | 10 | 10.1 | 9.3 | 0.36968
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23403-01C03-A | CML-3 | 150-PG-23403-01C03-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5604 |  | 2014-06-20 08:00 | 2014-06-20 09:00 | [36 empty] | 11.75 | CML-3 | CML: Elbow | 6 | 2098-02-09 | 2085-10-05 | 2014-06-20 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.5 | 12 O'Clock | 150 | 10.97 | 150-PG-23403-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 11.5 | 12.2 | 11.6 | 11.7 | 0.31091
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-30 | 100-DC-57036-01C02 CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 1436 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 12.3 | CML-30 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 11.5 | 3 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  |  | 11.5 | 12.8 | 12.6 | 0.7
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44025-01X01 | CML-2 | 50-PW-44025-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22742 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 9.45 | CML-2 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-04-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.3 | 9 O'Clock | 50 | 5.54 | 50-PW-44025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | -4.8984 | 9.6 | 9.5 | 9.4 | 9.3 | 0.1291
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43171-01C02 | CML-3 | 80-FL-43171-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20525 |  | 2014-10-06 07:00 | 2014-10-06 15:00 | [36 empty] | 5.35 | CML-3 | CML: Elbow | 3 | 2027-04-24 | 2028-12-05 | 2014-10-06 07:00 | 2.5 | 0.21501 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-FL-43171-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 5.5 | 5.4 | 0.1291
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80002-01C02 | CML-6 | 100-VA-80002-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2166 | Rope Access | 2014-03-30 09:30 | 2014-03-30 11:00 | [36 empty] | 5.35 | CML-6 | CML: type TBC | 3 | 2016-12-20 | 2017-01-31 | 2014-03-30 09:30 | 2.5 | 0.98976 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-VA-80002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.2 | 5.3 | 5.4 | 0.1291
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-19 | 80-PW-44001-01C02-P CML-19 | Yes | FPSO 2015 | Pipe Wall Thickness | 23228 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 12.3 | CML-19 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 10.6 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | 4.0167 | 13.8 | 13 | 10.6 | 11.8 | 1.4
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-11 | 200-PL-20018-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 23883 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.375 | CML-11 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 9 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 | 0 | 11.8 | 10 | 10 | 9.7 | 0.96047
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56008-01C02 | CML-1 | 80-DH-56008-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3446 | Rope Access | 2014-05-12 11:30 | 2014-05-12 12:00 | [36 empty] | 5.65 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-12 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-DH-56008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.8 | 5.6 | 5.7 | 0.1291
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21833 |  | 2014-10-12 07:00 | 2014-10-12 12:00 | [36 empty] | 6.15 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | -1.3917 | 6.1 | 6.2 | 6 | 6.3 | 0.1291
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1047 |  | 2014-03-20 13:00 | 2014-03-20 14:00 | Check Corrosion Rate of 0.437mm/ yr | [35 empty] | 6.15 | CML-6 | CML: type TBC | 3 | 2022-03-23 | 2022-02-28 | 2014-03-20 13:00 | 2.5 | 0.43669 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 300 | 6.35 | 300-WC-40043-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6.2 | 6 | 6.3 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43035-01C02 | CML-3 | 100-FH-43035-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12662 |  | 2014-01-22 10:00 | 2014-01-22 11:00 | [36 empty] | 6.15 | CML-3 | CML: type TBC | 3 | 2126-11-09 | 2130-08-08 | 2014-01-22 10:00 | 2.5 | 0.03101 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 9 O'Clock | 100 | 6.02 | 100-FH-43035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.1 | 6.3 | 6 | 0.1291
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43176-01C02 | CML-4 | 300-FL-43176-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20434 | Protective mesh removed/Rope access | 2014-06-27 10:30 | 2014-06-27 12:00 | [36 empty] | 6.35 | CML-4 | CML: Fitting | 3 | 2040-12-02 | 2040-09-20 | 2014-06-27 10:30 | 2.5 | 0.13987 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 300 | 6.35 | 300-FL-43176-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.4 | 6.3 | 6.2 | 0.1291
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-8 | 50-FG-45024-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1212 | Rope Access | 2014-03-22 13:00 | 2014-03-22 14:30 | [36 empty] | 6.35 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 3 O'Clock | 50 | 5.54 | 50-FL-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.2 | 6.5 | 6.4 | 0.1291
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44025-01X01 | CML-1 | 50-PW-44025-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5576 |  | 2014-06-19 08:00 | 2014-06-19 08:30 | [36 empty] | 9.425 | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-06-19 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.3 | 12 O'Clock | 50 | 5.54 | 50-PW-44025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.3 | 9.6 | 9.4 | 9.4 | 0.12583
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-4 | 50-FG-45024-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1187 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.65 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.8 | 6.7 | 6.5 | 6.6 | 0.1291
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8034 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:31 | [32 empty] | 7.35 | CML-4 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-20 14:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 12 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.5 | 7.3 | 7.4 | 0.1291
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 901 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 7.35 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 9 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.5 | 7.4 | 7.3 | 7.2 | 0.1291
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1565 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 7.35 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 9 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.5 | 7.4 | 7.3 | 7.2 | 0.1291
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-20 | 400-WC-40024-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 1089 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 9.05 | CML-20 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.8 | 12 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.8 | 9.1 | 9.2 | 9.1 | 0.17321
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PL-57403-01C03 |  | 50-PL-57403-01C03 |  | FPSO 2015 | Pipe Wall Thickness | 8372 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 11.7 | 50-PL-57403-01C03 | Piping | 6 | 2075-10-24 |  | 2015-01-29 07:30 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 11.6 | 6 O'Clock | 50 | 8.74 | Pipework | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 11.6 | 11.9 | 11.6 | 11.7 | 0.14142
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PL-57403-01C03 |  | 50-PL-57403-01C03 |  | FPSO 2015 | Pipe Wall Thickness | 8371 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 11.7 | 50-PL-57403-01C03 | Piping | 6 | 2075-10-24 |  | 2015-01-29 07:30 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 11.6 | 12 O'Clock | 50 | 8.74 | Pipework | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 11.6 | 11.8 | 11.7 | 11.7 | 0.08165
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57402-01C03 | CML-6 | 50-DC-57402-01C03 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8363 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 12.175 | CML-6 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 11.6 | 12 O'Clock | 50 | 8.74 | 50-DC-57402-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 11.6 | 12.3 | 12.2 | 12.6 | 0.41932
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 150-DH-56080-01C02 | CML-8 | 150-DH-56080-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3331 | Rope Access | 2014-05-08 07:00 | 2014-05-08 09:00 | [36 empty] | 7.85 | CML-8 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-05-08 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.7 | 3 O'Clock | 150 | 7.11 | 150-DH-56080-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8 | 7.7 | 7.9 | 7.8 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-13 | 150-FH-43026-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23512 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 7.15 | CML-13 | CML: Pipe Length | 3 | 2132-07-22 | 2111-02-02 | 2015-07-28 07:00 | 1.03 | 0.051 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 | 0.26449 | 7.2 | 7 | 7.3 | 7.1 | 0.1291
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-16 | 50-CG-38500-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 7888 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:44 | [32 empty] | 3.65 | CML-16 | CML: Pipe Length | 3 | 2015-10-31 | 2016-02-03 | 2015-01-14 10:30 | 2.5 | 1.2568 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.5 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.7 | 3.5 | 3.6 | 3.8 | 0.1291
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43514-01C02 | CML-45 | 150-FL-43514-01C02 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 5290 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.75 | CML-45 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.9 | 3.8 | 3.7 | 3.6 | 0.1291
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-1 | 50-FG-45018-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2583 | Rope Access | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 5.05 | CML-1 | CML: type TBC | 3 | 2017-09-12 | 2017-09-01 | 2014-04-26 07:00 | 2.5 | 0.7094 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.89962 | 5 | 5.2 | 4.9 | 5.1 | 0.1291
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-2 | 50-FG-45018-03C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2584 | Rope Access | 2014-04-26 07:00 | 2014-04-26 08:00 | [36 empty] | 5.05 | CML-2 | CML: type TBC | 3 | 2017-09-12 | 2017-09-01 | 2014-04-26 07:00 | 2.5 | 0.7094 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0 | 5 | 5.2 | 4.9 | 5.1 | 0.1291
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45048-03C02 | CML-2 | 50-FG-45048-03C02 CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 2277 |  | 2014-03-16 14:00 | 2014-03-16 14:30 | [36 empty] | 5.05 | CML-2 | CML: type TBC | 3 |  |  | 2014-03-16 14:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 4.9 | 9 O'Clock | 50 |  | 50-PG-45048-03C02 | 80XS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5.1 | 5 | 4.9 | 0.1291
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-1 | 80-FL-43015-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20406 | Reviewed on 20/11/14. Line is FFS. Repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-20 11:11 | [32 empty] | 5.45 | CML-1 | CML: Reducing Tee | 3 | 2034-08-17 | 2037-02-04 | 2014-10-06 07:00 | 2.5 | 0.14087 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.5 | 5.6 | 0.1291
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-1 | 50-WC-40451-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3063 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | [36 empty] | 8.85 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-03 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.7 | 9 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 | -8.7433 | 8.9 | 9 | 8.8 | 8.7 | 0.1291
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-6 | 150-WC-40006-01C02 CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 20684 | Rope Access | 2014-05-26 13:00 | 2014-05-26 14:00 | [36 empty] | 12.4 | CML-6 | CML: type TBC | 3 | 2102-12-30 | 2079-04-19 | 2014-05-26 13:00 | 4.7 | 0.07106 | A4: Left Quadrant |  | 8.07 | 4.7 | 6.385 | 11 | 9 O'Clock | 50 | 11.07 | 50-PG-23061-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 12.7 | 12.5 | 13.4 | 11 | 1.01
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-8 | 50-FH-43137-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12860 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 5.55 | CML-8 | CML: Pipe Length | 3 | 2027-06-19 | 2028-12-21 | 2014-01-23 08:00 | 2.5 | 0.21622 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.7 | 5.5 | 5.4 | 0.1291
PG05 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21323 | Protective mesh removed | 2014-06-27 07:00 | 2014-06-27 08:00 | [36 empty] | 6.95 | CML-3 | CML: Elbow | 1 | 2038-04-25 | 2030-11-12 | 2014-06-27 07:00 | 3.86 | 0 | A3: Inside Quadrant |  | 5.35 | 3.86 | 4.605 | 6.8 | 6 O'Clock | 300 | 6.35 | 300-PG-20025-03D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.94 |  | 7.1 | 6.9 | 6.8 | 7 | 0.1291
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-7 | 50-FG-45023-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1155 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.45 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | -0.59734 | 6.4 | 6.6 | 6.3 | 6.5 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-2 | 100-FH-43507-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7981 |  | 2015-01-18 14:00 | 2015-01-18 15:00 | [36 empty] | 6.45 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-18 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-FH-43507-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | -80.5517 | 6.4 | 6.3 | 6.5 | 6.6 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43120-01C02 | CML-7 | 200-FH-43120-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12841 |  | 2014-02-06 07:00 | 2014-02-06 09:00 | [36 empty] | 6.55 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-FH-43120-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.5 | 6.6 | 6.4 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43127-01C02 | CML-5 | 150-FH-43127-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1798 | Rope access | 2014-04-28 10:30 | 2014-04-28 12:00 | [36 empty] | 6.55 | CML-5 | CML: Elbow | 3 | 2019-04-23 | 2018-11-05 | 2014-04-28 10:30 | 2.5 | 0.7819 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43127-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.7 | 6.4 | 6.5 | 0.1291
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23403-01C03-A | CML-4 | 150-PG-23403-01C03-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5605 |  | 2014-06-20 08:00 | 2014-06-20 09:00 | [36 empty] | 13.025 | CML-4 | CML: Equal Tee | 6 | 2098-02-09 | 2085-10-05 | 2014-06-20 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.6 | 12 O'Clock | 150 | 10.97 | 150-PG-23403-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 11.6 | 12.7 | 13.8 | 14 | 1.1087
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-20 | 100-DC-57036-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 1426 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 11.9333 | CML-20 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 11.6 | 3 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  |  | 11.6 | 11.9 | 12.3 | 0.35119
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-6 | 80-FH-43007-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12567 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.45 | CML-6 | CML: Pipe Length | 3 | 2029-11-29 | 2027-10-22 | 2014-01-18 07:00 | 0.54 | 0.29984 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 12 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.3 | 5.5 | 5.4 | 5.6 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43019-01C02 | CML-3 | 80-FH-43019-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10622 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.95 | CML-3 | CML: type TBC | 3 | 2015-06-03 | 2015-08-27 | 2013-11-17 | 2.5 | 1.4902 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 9 O'Clock | 80 | 5.49 | 80-FH-43019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 5.1 | 5 | 4.8 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43019-01C02 | CML-4 | 80-FH-43019-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10623 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.05 | CML-4 | CML: type TBC | 3 | 2015-10-05 | 2016-01-13 | 2013-11-17 | 2.5 | 1.2743 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-FH-43019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.2 | 5.1 | 5 | 0.1291
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-5 | 50-FG-45302-01C02 CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 5773 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 5.45 | CML-5 | CML: Elbow | 3 | 2026-11-07 | 2028-04-17 | 2014-06-23 11:00 | 2.5 | 0.22609 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.5 | 5.3 | 5.6 | 0.1291
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-8 | 80-CG-38459-09C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23705 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.45 | CML-8 | CML: Elbow | 3 | 2051-05-21 | 2055-10-22 | 2015-10-30 07:00 | 2.5 | 0.07869 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 5.6 | 5.4 | 0.1291
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1644 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.375 | CML-3 | CML: Fitting | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.8 | 12 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 8.9 | 9.2 | 10.6 | 0.83417
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-11 | 50-WC-40028-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1691 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 9.875 | CML-11 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 10.6 | 10.2 | 9.9 | 0.7719
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2042 |  | 2014-03-27 14:00 | 2014-03-27 14:30 | [36 empty] | 5.55 | CML-3 | CML: type TBC | 3 | 2040-08-30 | 2043-11-02 | 2014-03-27 14:00 | 2.5 | 0.10965 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-DH-56107-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 5.6 | 5.5 | 0.1291
PG05 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-23003-06C02-PA | CML-11 | 250-PG-23003-06C02-PA CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2275 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 5.55 | CML-11 | CML: type TBC | 3 | 2030-07-26 | 2032-05-28 | 2014-03-16 11:30 | 2.5 | 0.17714 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 5.6 | 5.5 | 0.1291
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44029-01C02 | CML-3 | 250-PW-44029-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22900 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 11.15 | CML-3 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.6 | 6 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | 3.2525 | 12 | 11.1 | 10.6 | 10.9 | 0.60277
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P |  | 50-CG-38452-09C02-P |  | FPSO 2016 | Pipe Wall Thickness | 9170 |  | 2016-02-23 07:00 | 2016-02-23 15:00 | [36 empty] | 6.55 | 200-FH-43304-01C02 | Piping | 3 | 2051-11-30 |  | 2016-02-23 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.4 | 12 O'Clock | 200 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.7 | 6.5 | 6.6 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-3 | 100-FH-43507-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1773 | Rope access | 2014-04-27 13:00 | 2014-04-27 14:00 | [36 empty] | 6.55 | CML-3 | CML: Elbow | 3 | 2019-04-17 | 2018-10-31 | 2014-04-27 13:00 | 2.5 | 0.78402 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 9 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.5 | 6.7 | 6.4 | 0.1291
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43300-01C02-E | CML-2 | 200-PL-43300-01C02-E CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8588 | Line is FFS. Current RBI frequency is 36m. Action: CML’s to Inspect in 48m. RBI to be updated | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-08 14:57 | [32 empty] | 7.75 | CML-2 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2015-02-08 11:00 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.7 | 9 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.36 |  | 7.7 | 7.7 | 7.9 | 7.7 | 0.1
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-5 | 400-WC-40025-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1265 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 9.25 | CML-5 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.9 | 9 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 10.2 | 9 | 8.9 | 8.9 | 0.63509
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-WC-40059-01C02 | CML-1 | 80-WC-40059-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3150 |  | 2014-05-02 11:30 | 2014-05-02 12:00 | [36 empty] | 9.275 | CML-1 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-05-02 11:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.8 | 9 O'Clock | 80 | 5.49 | 80-WC-40059-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 10 | 9.3 | 9 | 8.8 | 0.5252
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-3 | 400-WC-40060-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1051 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 9.35 | CML-3 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-20 14:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 8.9 | 12 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.9 | 9.5 | 9 | 10 | 0.50662
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-13 | 250-PW-44004-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22757 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 11.875 | CML-13 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-04-29 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.1 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 | -3.2678 | 11.8 | 11.5 | 11.1 | 13.1 | 0.86554
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57303-03C03 | CML-5 | 20-DC-57303-03C03 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7930 |  | 2015-01-17 10:30 | 2015-01-17 12:00 | [36 empty] | 11.875 | CML-5 | CML: type TBC | 6 | 2044-01-06 | 2058-09-17 | 2015-01-17 10:30 | 2.5 | 0 | A4: Left Quadrant |  | -0.44 | 2.5 | 1.03 | 11.7 | 9 O'Clock | 20 | 5.56 | 20-DC-57303-03C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 12 | 12 | 11.8 | 11.7 | 0.15
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45028-03C02-E | CML-3 | 80-FG-45028-03C02-E CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24327 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.55 | CML-3 | CML: Elbow | 3 | 2053-09-17 | 2048-07-24 | 2016-06-01 07:00 | 1.46 | 0 | A2: Right Quadrant |  | 2.49 | 1.46 | 1.975 | 6.4 | 3 O'Clock | 80 | 5.49 | 80-FG-45028-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.94 |  | 6.5 | 6.4 | 6.7 | 6.6 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-5 | 150-FH-43136-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2766 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 6.45 | CML-5 | CML: Elbow | 3 | 2019-04-13 | 2018-03-23 | 2014-03-13 09:00 | 1.03 | 1.036 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.3 | 6 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.27 |  | 6.4 | 6.5 | 6.3 | 6.6 | 0.1291
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-3 | 50-CG-38458-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23731 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 7.95 | CML-3 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.8 | 3 O'Clock | 100 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.1 | 7.8 | 8 | 7.9 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-15 | 400-FH-43500-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 5651 | Readings taking at weld | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 8.05 | CML-15 | CML: type TBC | 3 | 2299-04-17 | 2261-07-30 | 2014-06-21 07:00 | 2.5 | 0.01895 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 3 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.1 | 7.9 | 8.2 | 8 | 0.1291
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-1 | 100-PW-20021-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21804 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 11.225 | CML-1 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2014-10-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 11.1 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.1 | 11.2 | 11.4 | 11.2 | 0.12583
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-10 | 50-PL-23516-03C03 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7798 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 15:57 | [32 empty] | 8.45 | CML-10 | CML: Pipe Length | 6 | 2036-05-16 | 2035-12-07 | 2015-01-13 07:00 | 2.5 | 0.27161 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 6 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.5 | 8.6 | 8.3 | 8.4 | 0.1291
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-15 | 200-WC-40008-01C02-P CML-15 | yes | FPSO 2015 | Pipe Wall Thickness | 7821 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 10 | CML-15 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.9 | 12 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9 | 11.9 | 10.2 | 1.3976
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45044-03C02 | CML-1 | 50-FG-45044-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 24267 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 10.95 | CML-1 | CML: Pipe Length | 3 | 2061-11-30 | 2054-07-28 | 2014-09-24 07:00 | 4.7 | 0.12919 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 10.8 | 3 O'Clock | 150 | 10.97 | 150-PG-23045-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 11.1 | 10.8 | 10.9 | 11 | 0.1291
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-10 | 50-PF-20300-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21576 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 8.95 | CML-10 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.8 | 3 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.9 | 8.8 | 9.1 | 9 | 0.1291
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-27 | 50-PF-20300-03C03-P CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 21593 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.05 | CML-27 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.1 | 9.2 | 9 | 8.9 | 0.1291
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-11 | 250-PW-44006-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8003 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 10.975 | CML-11 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | 2.4328 | 11.2 | 11.6 | 11.7 | 9.4 | 1.072
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40021-01C02 | CML-9 | 50-WC-40021-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2104 | Rope Access | 2014-03-28 13:00 | 2014-03-28 14:00 | [36 empty] | 9.35 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-28 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.9 | 3 O'Clock | 50 | 5.54 | 50-WC-40021-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.4 | 8.9 | 10 | 9.1 | 0.47958
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-11 | 400-WC-40024-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1080 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 9.25 | CML-11 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 9 | 3 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.1 | 9 | 9.1 | 9.8 | 0.36968
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-3 | 80-PG-23025-06C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13074 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 10.95 | CML-3 | CML: Pipe Length | 6 | 2030-10-17 | 2028-05-12 | 2014-02-07 11:00 | 2.8 | 0.47901 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 10.8 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.8 | 11.1 | 11 | 10.9 | 0.1291
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-16 | 80-PG-23025-06C03 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 13087 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 11.05 | CML-16 | CML: Elbow | 6 | 2038-05-08 | 2034-11-11 | 2014-02-07 11:00 | 2.8 | 0.33385 | A2: Right Quadrant |  | 5.13 | 2.8 | 3.965 | 10.9 | 3 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 11 | 10.9 | 11.1 | 11.2 | 0.1291
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23403-01C03-A | CML-1 | 150-PG-23403-01C03-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5602 |  | 2014-06-20 08:00 | 2014-06-20 09:00 | [36 empty] | 13.225 | CML-1 | CML: Equal Tee | 6 | 2098-02-09 | 2085-10-05 | 2014-06-20 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.7 | 6 O'Clock | 150 | 10.97 | 150-PG-23403-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 14.1 | 13.7 | 11.7 | 13.4 | 1.0563
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-10 | 80-PG-23025-06C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 13081 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 11.05 | CML-10 | CML: Pipe Length | 6 | 2038-05-08 | 2034-11-11 | 2014-02-07 11:00 | 2.8 | 0.33385 | A4: Left Quadrant |  | 5.13 | 2.8 | 3.965 | 10.9 | 9 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 11 | 11.2 | 11.1 | 10.9 | 0.1291
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20061-01C03-P | CML-1 | 80-PG-20061-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21673 | Protective mesh removed | 2014-06-26 11:00 | 2014-06-26 12:00 | [36 empty] | 11.05 | CML-1 | CML: Fitting | 6 | 2053-07-11 | 2047-06-01 | 2014-06-26 11:00 | 2.5 | 0.215 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 3 O'Clock | 80 | 11.13 | 80-PG-20061-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.2 | 10.9 | 11 | 11.1 | 0.1291
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-1 | 25-VA-23054-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13103 |  | 2014-02-07 07:00 | 2014-02-07 08:00 | [36 empty] | 11.45 | CML-1 | CML: type TBC | 6 | 2091-02-10 | 2082-04-06 | 2014-02-07 07:00 | 0.97 | 0 | A4: Left Quadrant |  | 2.74 | 0.97 | 1.855 | 11.3 | 9 O'Clock | 50 | 8.74 | 50-PG-23044-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.33 |  | 11.4 | 11.5 | 11.6 | 11.3 | 0.1291
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-21 | 50-PL-23052-09C03 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10185 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 8.775 | CML-21 | CML: type TBC | 6 | 2014-11-21 | 2014-09-08 | 2013-11-09 | 2.81 | 5.5997 | A4: Left Quadrant |  | 5.07 | 2.81 | 3.94 | 8.6 | 9 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.79 |  | 8.8 | 8.9 | 8.8 | 8.6 | 0.12583
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-2 | 50-CG-38488-09C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23591 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 8.625 | CML-2 | CML: Fitting | 3 | 2072-12-20 | 2057-07-05 | 2015-09-15 15:30 | 2.5 | 0.1047 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 3 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 0.17209 | 8.6 | 8.5 | 8.6 | 8.8 | 0.12583
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45044-03C02 | CML-4 | 50-FG-45044-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20804 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 8.725 | CML-4 | CML: Pipe Length | 3 | 2063-09-30 | 2050-09-06 | 2014-07-18 11:00 | 2.5 | 0.12389 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.9 | 8.6 | 8.7 | 0.12583
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45044-03C02 | CML-24 | 50-FG-45044-03C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21162 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 8.775 | CML-24 | CML: Pipe Length | 6 | 2015-09-30 | 2015-03-05 | 2014-07-16 07:30 | 2.5 | 5.0438 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.6 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.9 | 8.8 | 8.8 | 8.6 | 0.12583
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-7 | 50-PF-20300-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21573 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 8.725 | CML-7 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.7 | 8.7 | 8.9 | 0.12583
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-4 | 50-PL-23300-09C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13120 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.625 | CML-4 | CML: type TBC | 6 | 2023-04-08 | 2021-12-01 | 2014-02-04 07:00 | 2.81 | 0.83793 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.5 | 12 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.69 |  | 10.5 | 10.6 | 10.6 | 10.8 | 0.12583
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-17 | 80-PW-44016-01C02-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 22919 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 12.2 | CML-17 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.4 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 | 0 | 12.9 | 12.3 | 11.4 | 12.2 | 0.61644
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-9 | 300-PF-20501-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21685 | Protective mesh removed | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 13.775 | CML-9 | CML: Pipe Length | 6 | 2031-12-16 | 2028-08-15 | 2014-09-28 07:00 | 4.9 | 0.50496 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 13.8 | 13.9 | 13.6 | 13.8 | 0.12583
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20303-03C03-P | CML-3 | 200-PG-20303-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5878 |  | 2014-06-25 13:00 | 2014-06-25 14:00 | [36 empty] | 12.625 | CML-3 | CML: Fitting | 6 | 2063-07-17 | 2054-06-23 | 2014-06-25 13:00 | 3.3 | 0.1874 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 12.5 | 12 O'Clock | 200 | 12.7 | 200-PG-20303-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 12.5 | 12.6 | 12.8 | 12.6 | 0.12583
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-21 | 300-PF-20001-03C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21159 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 15.225 | CML-21 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 15.1 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 15.1 | 15.2 | 15.2 | 15.4 | 0.12583
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-1 | 150-PG-23043-06C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23457 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 8.875 | CML-1 | CML: Elbow | 3 | 2019-05-04 | 2018-06-10 | 2015-07-24 07:00 | 4.7 | 1.0578 | A1: Outside Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.7 | 12 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | 0.84323 | 8.7 | 8.9 | 8.9 | 9 | 0.12583
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-1 | 25-VA-23054-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1470 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 9.375 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-29 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.2 | 12 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.5 | 9.4 | 9.4 | 0.12583
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-9 | 300-PG-20502-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 23896 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.375 | CML-9 | CML: Pipe Length | 6 | 2107-03-03 | 2096-04-20 | 2014-09-26 07:00 | 2.5 | 0.08325 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.2 | 6 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.4 | 10.5 | 10.2 | 10.4 | 0.12583
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-9 | 300-PG-20502-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20756 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.375 | CML-9 | CML: type TBC | 6 | 2107-03-03 | 2096-04-20 | 2014-09-26 07:00 | 2.5 | 0.08325 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.2 | 6 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.4 | 10.5 | 10.2 | 10.4 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-11 | 200-PL-20018-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21247 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.375 | CML-11 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 9 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 11.8 | 10 | 10 | 9.7 | 0.96047
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-4 | 100-FL-43455-01C02-P CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 20487 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 5.275 | CML-4 | CML: Elbow | 3 | 2018-07-17 | 2018-09-16 | 2014-10-03 07:00 | 2.5 | 0.6863 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 3 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.1 | 5.4 | 5.3 | 0.12583
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-17 | 80-PW-44016-01C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21949 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 12.025 | CML-17 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.4 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 12.8 | 11.9 | 11.4 | 12 | 0.57951
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57402-01C03 | CML-7 | 50-DC-57402-01C03 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8364 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 12.025 | CML-7 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 11.8 | 12 O'Clock | 50 | 8.74 | 50-DC-57402-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 11.8 | 11.9 | 12.4 | 12 | 0.263
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-8 | 50-PL-23514-01C03 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 8641 | This CML is on a straight piping section. It appears that CML-10 together with CML-8 & 9 below are located in the same spool. This spool was confirmed to have being wrongly fabricated with Sched. Extra strong (NWT: 5.54 mm) instead of sched. 160 (NWT: 8.74). | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:21 | [32 empty] | 5.225 | CML-8 | CML: Pipe Length | 6 | 2016-04-27 | 2016-04-07 | 2015-02-10 11:30 | 2.5 | 2.1447 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 5.1 | 12 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.2 | 5.2 | 5.4 | 0.12583
PG06 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PG-23008-15S01-A | CML-7 | 200-PG-23008-15S01-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5667 | Rope access | 2014-06-21 13:00 | 2014-06-21 14:00 | Check Corrosion Rate of 0.417mm/ yr | [35 empty] | 5.225 | CML-7 | CML: Pipe Length | 3 | 2020-09-15 | 2021-06-28 | 2014-06-21 13:00 | 2.5 | 0.41656 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DC-57301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.2 | 5.1 | 5.4 | 0.12583
PG06 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 200-PG-23008-15S01-A |  | 200-PG-23008-15S01-A | yes | FPSO 2014 | Pipe Wall Thickness | 22100 | Rope access | 2014-06-02 09:30 | 2014-06-02 11:00 | [36 empty] | 5.275 | 50-CG-38302-01C02-P | Piping | 3 | 2020-05-06 |  | 2014-06-02 09:30 |  | 0.43832 | A2: Right Quadrant |  |  | 2.5 |  | 5.1 | 3 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 5.1 | 5.4 | 5.1 | 5.3 | 5.3 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-1 | 80-FH-43158-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12882 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.725 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-22 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.7 | 5.6 | 5.9 | 0.12583
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-1 | 100-VA-80006-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2170 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 5.775 | CML-1 | CML: type TBC | 3 | 2020-05-10 | 2020-08-02 | 2014-03-30 13:00 | 2.5 | 0.50671 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.9 | 5.8 | 5.6 | 0.12583
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-1 | 400-WC-40025-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1261 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 9.275 | CML-1 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 9 | 3 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.5 | 9 | 9.1 | 9.5 | 0.263
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-8 | 100-VA-80006-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2177 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 6.225 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 12 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.4 | 6.2 | 6.2 | 0.12583
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-17 | 50-FG-45023-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1165 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.275 | CML-17 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.3 | 6.3 | 6.1 | 6.4 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43116-01C02 | CML-3 | 150-FH-43116-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7867 | Line is FFS. It has been check twice. The higher values reported here are from the data collected in Apr. 2014. The rechecked CR’s from data from Jan. 2015 are lower. Current RBI frequency is 48m. Action: to recheck line in a 24m (Jan. 2017) to confirm CR. | 2015-01-14 09:30 | 2015-01-14 10:30 |  |  | Administrator | 2015-09-07 17:03 | [32 empty] | 6.275 | CML-3 | CML: Elbow | 3 | 2020-10-25 | 2020-03-28 | 2015-01-14 09:30 | 2.5 | 0.6223 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.1 | 6 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 | 0.41817 | 6.3 | 6.4 | 6.1 | 6.3 | 0.12583
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-1 | 100-PG-23406-03C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20727 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 12.9 | CML-1 | CML: Elbow | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 11.8 | 9 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.7 | 13.6 | 13.5 | 11.8 | 0.83666
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-14 | 100-PG-23406-03C03 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20740 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 12.1 | CML-14 | CML: Elbow | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 11.8 | 12 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 11.8 | 12 | 12.4 | 12.2 | 0.2582
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43105-01C02 | CML-3 | 100-FH-43105-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12766 |  | 2014-01-25 09:00 | 2014-01-25 10:00 | [36 empty] | 6.225 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-25 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 9 O'Clock | 100 | 6.02 | 100-FH-43105-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.2 | 6.2 | 6.1 | 0.12583
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-3 | 150-FL-43514-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20496 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.225 | CML-3 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 7.1 | 9 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.2 | 7.2 | 7.4 | 7.1 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20013-01C02-P | CML-4 | 200-PL-20013-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21214 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 9.95 | CML-4 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 12 O'Clock | 150 | 6.35 | 200-PL-20013-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 9.9 | 10.1 | 10.1 | 0.19149
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56107-01C02 | CML-1 | 80-DH-56107-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2040 |  | 2014-03-27 14:00 | 2014-03-27 14:30 | [36 empty] | 7.775 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-27 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.6 | 6 O'Clock | 80 | 5.49 | 80-DH-56107-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.8 | 7.9 | 7.6 | 7.8 | 0.12583
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-2 | 100-PG-23503-03C03-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2718 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.825 | CML-2 | CML: Pipe Length | 6 | 2023-05-10 | 2023-11-02 | 2014-03-13 09:00 | 5.66 | 0.54998 | A4: Left Quadrant |  | 5.13 | 5.66 | 5.395 | 10.7 | 9 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.04 |  | 10.8 | 11 | 10.8 | 10.7 | 0.12583
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-18 | 50-PL-23020-01C03 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10132 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.175 | CML-18 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.3 | 8.2 | 8.2 | 8 | 0.12583
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-6 | 150-WC-40002-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20345 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 9.125 | CML-6 | CML: Equal Tee | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.9 | 12 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9 | 9.3 | 9.3 | 0.20616
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-11 | 50-CG-38487-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20850 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.675 | CML-11 | CML: Reducing Tee | 3 | 2048-03-04 | 2039-02-24 | 2014-10-02 07:00 | 2.5 | 0.1794 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 10.589 | 8.7 | 8.8 | 8.7 | 8.5 | 0.12583
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-6 | 300-PW-44002-01X01-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22023 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 10.525 | CML-6 | CML: Reducing Tee | 6 | 2025-03-29 | 2023-11-14 | 2014-10-17 07:00 | 2.5 | 0.65996 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.4 | 6 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 11.5 | 10.9 | 9.4 | 10.3 | 0.89582
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-7 | 300-PW-44002-01X01-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22024 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 10.325 | CML-7 | CML: Reducing Tee | 6 | 2025-03-29 | 2023-11-14 | 2014-10-17 07:00 | 2.5 | 0.65996 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.4 | 6 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 11.5 | 10.1 | 9.4 | 10.3 | 0.87321
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23033-03C03 | CML-7 | 50-PL-23033-03C03 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1879 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.175 | CML-7 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 12 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.2 | 9.3 | 9.2 | 0.12583
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23033-03C03 | CML-5 | 50-PL-23033-03C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1877 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.175 | CML-5 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 6 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.3 | 9.2 | 9 | 9.2 | 0.12583
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-6 | 150-PG-23043-06C02-P CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 23768 | re-check line | 2016-02-13 07:00 | 2016-02-13 15:00 | [36 empty] | 11.825 | CML-6 | CML: Reducer | 3 | 2076-02-10 | 2066-08-14 | 2016-02-13 07:00 | 4.7 | 0 | A1: Outside Quadrant |  | 7.97 | 4.7 | 5.6494 | 11.7 | 12 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 0 | 11.7 | 11.8 | 11.8 | 12 | 0.12583
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-6 | 150-PG-23043-06C02-P CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24157 | re-check line | 2016-02-13 | 2016-02-13 | [36 empty] | 11.825 | CML-6 | CML: Reducer | 3 | 2076-02-10 | 2066-08-14 | 2016-02-13 | 4.7 | 0 | A1: Outside Quadrant |  | 7.97 | 4.7 | 5.6494 | 11.7 | 12 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | -0.2161 | 11.7 | 11.8 | 11.8 | 12 | 0.12583
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-42 | 300-PF-20500-03C03-P CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 23499 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 12.325 | CML-42 | CML: Fitting | 6 | 2023-02-28 | 2021-05-29 | 2015-07-27 07:00 | 4.9 | 0.9609 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.2 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 | 0 | 12.2 | 12.3 | 12.3 | 12.5 | 0.12583
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-1 | 300-PW-44002-01X01-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22018 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 10.075 | CML-1 | CML: Pipe Length | 6 | 2025-03-29 | 2023-11-14 | 2014-10-17 07:00 | 2.5 | 0.65996 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.4 | 12 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.4 | 10.2 | 11.1 | 9.6 | 0.76322
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23301-01C02 | CML-4 | 80-VA-23301-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22511 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 4.025 | CML-4 | CML: Elbow | 3 | 2016-12-16 | 2017-05-16 | 2015-04-20 07:00 | 2.5 | 0.84317 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.9 | 12 O'Clock | 50 | 5.49 | 80-VA-23301-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4 | 4.2 | 4 | 0.12583
DH01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 80-DH-56004-01C02 | CML-10 | 80-DH-56004-01C02 CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 5009 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [35 empty] | Low alarm breach | 3.325 | CML-10 | CML: type TBC | 0 | 2023-07-17 | 2020-10-20 | 2015-03-03 07:00 | 2.5 | 0.08356 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.2 | 9 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.3 | 3.5 | 3.3 | 3.2 | 0.12583
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-26 | 80-DH-56004-01C02 CML-26 | yes | FPSO 2015 | Pipe Wall Thickness | 6904 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.475 | CML-26 | CML: type TBC | 0.5 | 2022-08-19 | 2020-04-29 | 2015-04-05 07:00 | 3.5 | 0.10842 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4.3 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.3 | 4.5 | 4.5 | 4.6 | 0.12583
FL01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FL-43174-01C02 | CML-18 | 150-FL-43174-01C02 CML-18 | Yes | FPSO 2016 | Pipe Wall Thickness | 24503 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.675 | CML-18 | CML: Elbow | 3 | 2018-01-16 | 2018-07-16 | 2016-07-09 07:00 | 2.5 | 0.65644 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.5 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 | 0.09841 | 3.7 | 3.5 | 3.7 | 3.8 | 0.12583
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-6 | 150-FL-43174-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6377 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.675 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 9 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.7 | 3.7 | 3.8 | 3.5 | 0.12583
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-16 | 50-FG-45020-03C02 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10588 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.975 | CML-16 | CML: type TBC | 3 | 2015-04-26 | 2015-04-21 | 2013-11-17 | 2.5 | 1.5982 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 5.1 | 4.8 | 5 | 0.12583
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-27 | 250-PW-44006-01X01 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 1924 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 10.1 | CML-27 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.6 | 10.6 | 9.4 | 9.8 | 0.6
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-24 | 50-FG-45020-03C02 CML-24 |  | FPSO 2013 | Pipe Wall Thickness | 10596 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.025 | CML-24 | CML: type TBC | 3 | 2015-08-12 | 2015-08-07 | 2013-11-17 | 2.5 | 1.3822 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.2 | 5 | 4.9 | 0.12583
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-4 | 250-PW-44007-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23137 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 10.075 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 12 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | 0.35626 | 9.4 | 10.1 | 10.8 | 10 | 0.57373
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-15 | 50-FG-45019-03C02 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10497 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.175 | CML-15 | CML: type TBC | 3 | 2015-12-28 | 2015-12-21 | 2013-11-15 | 2.5 | 1.1802 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5.2 | 5 | 5.2 | 0.12583
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44033-01C02-P | CML-1 | 80-PW-44033-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21932 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 11.95 | CML-1 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.6 | 9 O'Clock | 80 | 5.49 | 80-PW-44033-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 12 | 12.4 | 11.8 | 11.6 | 0.34157
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-11 | 100-DH-56086-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20970 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 5.175 | CML-11 | CML: type TBC | 3 | 2016-09-19 | 2016-10-29 | 2014-05-16 13:00 | 2.5 | 1.0651 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.3 | 5.2 | 0.12583
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-14 | 300-PW-44002-01X01-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 22860 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.775 | CML-14 | CML: Elbow | 6 | 2029-11-05 | 2027-12-11 | 2015-05-01 07:00 | 2.5 | 0.47498 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.4 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | -2.0485 | 10 | 9.4 | 9.7 | 10 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-8 | 300-PW-44002-01X01-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 22025 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 10.3 | CML-8 | CML: Reducing Tee | 6 | 2026-09-13 | 2025-02-28 | 2014-10-17 07:00 | 2.5 | 0.58743 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 6 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 11.3 | 10.1 | 9.5 | 10.3 | 0.74833
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-8 | 250-PW-44007-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23141 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 10.2 | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-10 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 3 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 0.35626 | 10 | 9.5 | 10.1 | 11.2 | 0.71647
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56119-01C02 | CML-1 | 50-DH-56119-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21027 | Rope Access | 2014-05-19 09:30 | 2014-05-19 11:00 | [36 empty] | 5.375 | CML-1 | CML: type TBC | 3 | 2022-01-15 | 2022-12-19 | 2014-05-19 09:30 | 2.5 | 0.35216 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DH-56119-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.5 | 5.4 | 0.12583
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2614 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.375 | CML-2 | CML: type TBC | 3 | 2021-06-24 | 2021-06-05 | 2014-04-26 10:45 | 2.5 | 0.37669 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.45216 | 5.4 | 5.2 | 5.4 | 5.5 | 0.12583
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38472-01C02 | CML-1 | 50-CG-38472-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23656 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.475 | CML-1 | CML: Pipe Length | 3 | 2043-12-24 | 2047-04-05 | 2015-10-30 07:00 | 2.5 | 0.0994 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-CG-38472-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.5 | 5.3 | 5.5 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-11 | 200-PL-20019-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21262 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 9.85 | CML-11 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10 | 9.7 | 9.7 | 10 | 0.17321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43140-01C02 | CML-3 | 50-FH-43140-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22692 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.525 | CML-3 | CML: Reducing Tee | 3 | 2054-10-01 | 2059-03-10 | 2015-04-27 07:00 | 2.5 | 0.07349 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43140-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.47518 | 5.7 | 5.5 | 5.5 | 5.4 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-6 | 80-FH-43111-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12804 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 5.625 | CML-6 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-02-01 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 3 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.5 | 5.6 | 5.8 | 0.12583
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56083-01C02 | CML-4 | 100-DH-56083-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22529 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.875 | CML-4 | CML: Pipe Length | 3 | 2034-02-22 | 2034-10-30 | 2015-04-20 07:00 | 2.5 | 0.1697 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-DH-56083-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 6 | 5.9 | 5.7 | 0.12583
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-1 | 50-CG-38470-01C02-P CML-1 | Yes | FPSO 2015 | Pipe Wall Thickness | 23607 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.825 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 80 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.8 | 6 | 5.7 | 0.12583
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-8 | 50-CG-38476-01C02-H CML-8 | Yes | FPSO 2015 | Pipe Wall Thickness | 23640 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 6.025 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6.2 | 5.9 | 6 | 0.12583
RP01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57402-01C03 | CML-4 | 50-DC-57402-01C03 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8361 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 13.75 | CML-4 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2015-01-29 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 11.9 | 9 O'Clock | 50 | 8.74 | 50-DC-57402-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 16.2 | 14.4 | 12.5 | 11.9 | 1.9502
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-10 | 150-DC-57308-01C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20307 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 12.375 | CML-10 | CML: Reducing Tee | 6 | 2098-02-09 | 2085-10-05 | 2014-10-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.9 | 6 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 12.8 | 12.5 | 11.9 | 12.3 | 0.37749
FG02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20944 | Rope Access | 2014-05-17 08:00 | 2014-05-17 09:00 | [36 empty] | 6.125 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-17 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 6 O'Clock | 80 | 5.49 | 80-DH-56054-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6.1 | 6 | 6.3 | 0.12583
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-10 | 50-FG-45301-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5796 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.375 | CML-10 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.4 | 6.5 | 6.4 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-22 | 250-PL-20006-01C02-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 13192 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 11.0667 | CML-22 | CML: Tee | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A2: Right Quadrant |  | 3.35 | 3.61 | 3.0831 | 10.9 | 3 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.29 |  | 11.2 | 10.9 | 11.1 |  | 0.15275
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-10 | 400-WC-40024-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1079 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 9.05 | CML-10 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 9 | 6 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.1 | 9 | 9 | 9.1 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-6 | 250-FH-43303-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12944 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.625 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 9 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.8 | 6.6 | 6.5 | 0.12583
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2500 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.125 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7 | 7.1 | 7.3 | 0.12583
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-18 | 80-PW-44001-01C02-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23227 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 12.425 | CML-18 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.7 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 | 1.5718 | 12.8 | 12.7 | 11.7 | 12.5 | 0.49917
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43460-01C02 | CML-1 | 80-FL-43460-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2966 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.525 | CML-1 | CML: Fitting | 3 | 2063-10-19 | 2057-05-14 | 2014-05-01 14:00 | 0.54 | 0.09818 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.5 | 5.7 | 5.5 | 5.4 | 0.12583
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43460-01C02 | CML-1 | 80-FL-43460-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22245 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.525 | CML-1 | CML: Fitting | 3 | 2063-10-19 | 2057-05-14 | 2014-05-01 14:00 | 0.54 | 0.09818 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.5 | 5.7 | 5.5 | 5.4 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-25 | 100-DC-57036-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 1431 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 12.2 | CML-25 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 11.9 | 6 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  |  | 12.6 | 11.9 | 12.1 | 0.36056
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-14 | 50-FH-43011-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7964 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 7.525 | CML-14 | CML: type TBC | 3 | 2030-06-07 | 2028-03-09 | 2015-01-18 08:00 | 2.5 | 0.31828 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 9 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.5 | 7.7 | 7.5 | 7.4 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43124-01C02 | CML-7 | 80-FH-43124-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12849 |  | 2014-02-05 11:00 | 2014-02-05 13:00 | [36 empty] | 5.625 | CML-7 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-02-05 11:00 | 0.54 | 0 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.5 | 3 O'Clock | 80 | 5.49 | 80-FH-43124-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 5.6 | 5.5 | 5.6 | 5.8 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-10 | 200-PL-20010-01C02-P CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 23810 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 10.575 | CML-10 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.8 | 6 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10 | 10.2 | 9.8 | 12.3 | 1.1615
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43125-01C02 | CML-3 | 200-FH-43125-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2757 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 6.525 | CML-3 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-13 09:00 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.4 | 3 O'Clock | 200 | 6.35 | 200-FH-43125-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.06 |  | 6.5 | 6.4 | 6.7 | 6.5 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43110-01C02 | CML-1 | 200-FH-43110-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12792 |  | 2014-01-18 13:30 | 2014-01-18 14:30 | [36 empty] | 6.525 | CML-1 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 13:30 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-FH-43110-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.06 |  | 6.7 | 6.5 | 6.5 | 6.4 | 0.12583
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1642 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.425 | CML-1 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 9 | 3 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.1 | 9 | 9.7 | 9.9 | 0.44253
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-17 | 80-FH-43007-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12578 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.975 | CML-17 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-01-18 07:00 | 0.54 | 0 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.8 | 9 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.26 |  | 6 | 6 | 6.1 | 5.8 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-18 | 150-FH-43026-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 5527 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 7.125 | CML-18 | CML: Fitting | 3 | 2068-09-10 | 2058-09-25 | 2014-06-01 07:00 | 1.03 | 0.10991 | A4: Left Quadrant |  | 4.11 | 1.03 | 2.1256 | 7 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 | 4.2115 | 7.3 | 7.1 | 7.1 | 7 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-13 | 150-FH-43026-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12653 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.525 | CML-13 | CML: Pipe Length | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.4 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.37 |  | 7.5 | 7.4 | 7.5 | 7.7 | 0.12583
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-2 | 50-CG-38500-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23289 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 4.125 | CML-2 | CML: Elbow | 3 | 2017-07-16 | 2017-12-25 | 2015-07-04 09:30 | 2.5 | 0.73632 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | -0.64051 | 4.3 | 4 | 4.1 | 4.1 | 0.12583
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-12 | 50-FG-45300-01C02 CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 7835 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:38 | [32 empty] | 4.875 | CML-12 | CML: Elbow | 3 | 2019-04-11 | 2019-11-27 | 2015-01-13 13:00 | 2.5 | 0.51831 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5 | 4.9 | 4.9 | 0.12583
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56071-01C02 | CML-2 | 50-DH-56071-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3417 | Rope Access | 2014-05-11 13:00 | 2014-05-11 14:00 | [36 empty] | 5.025 | CML-2 | CML: type TBC | 3 | 2017-11-23 | 2018-05-18 | 2014-05-11 13:00 | 2.5 | 0.678 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.2 | 5 | 5 | 0.12583
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40061-01C02 | CML-7 | 400-WC-40061-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1131 |  | 2014-03-21 08:30 | 2014-03-21 09:00 | [36 empty] | 9.3 | CML-7 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 08:30 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 9.1 | 3 O'Clock | 400 | 7.92 | 400-WC-40061-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.1 | 9.1 | 9.8 | 9.2 | 0.33665
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-29 | 250-PW-44006-01X01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 23200 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 9.9 | CML-29 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | -0.65803 | 10.1 | 10.3 | 9.5 | 9.7 | 0.36515
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-8 | 25-PW-44026-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22740 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.675 | CML-8 | CML: Pipe Length | 3 | 2022-01-18 | 2021-12-26 | 2015-04-28 07:00 | 2.5 | 0.44557 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 3 O'Clock | 50 | 6.35 | 25-PW-44026-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 5.5 | 5.7 | 5.7 | 0.12583
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-10 | 50-FG-45024-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1193 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.675 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.8 | 6.5 | 6.7 | 6.7 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43120-01C02 | CML-5 | 200-FH-43120-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12839 |  | 2014-02-06 07:00 | 2014-02-06 09:00 | [36 empty] | 6.625 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 12 O'Clock | 200 | 6.35 | 200-FH-43120-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.8 | 6.6 | 6.6 | 0.12583
CG04 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 50-CG-38452-09C02-P | CML-5 | 50-CG-38452-09C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22489 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 7.375 | CML-5 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-04-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 3 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.5 | 7.2 | 7.4 | 7.4 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-7 | 250-PL-20006-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13177 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 10.025 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-01-21 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.8 | 3 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.8 | 9.8 | 10.3 | 10.2 | 0.263
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 0200-DN-56L9004-AC21M-00 | CML-2 | 0200-DN-56L9004-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5069 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 12.35 | CML-2 | CML: type TBC | 3 | 2075-05-31 | 2064-09-03 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 12 | 6 O'Clock | 50 | 8.74 | 0200-DN-56L9004-AC21M-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12 | 12 | 12 | 13.4 | 0.7
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-22 | 150-FL-43174-01C02 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6301 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.625 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.6 | 3.5 | 3.6 | 3.8 | 0.12583
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-6 | 50-CG-38500-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23293 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.775 | CML-6 | CML: Pipe Length | 3 | 2016-09-09 | 2017-01-15 | 2015-07-04 09:30 | 2.5 | 0.92757 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.6 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 | 0.2135 | 3.8 | 3.9 | 3.8 | 3.6 | 0.12583
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-8 | 50-CG-38500-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23295 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.725 | CML-8 | CML: Pipe Length | 3 | 2016-09-09 | 2017-01-15 | 2015-07-04 09:30 | 2.5 | 0.92757 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.6 | 12 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 | -0.427 | 3.6 | 3.7 | 3.9 | 3.7 | 0.12583
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45032-03C02 | CML-4 | 100-FG-45032-03C02 CML-4 | yes | FPSO 2013 | Pipe Wall Thickness | 10645 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.425 | CML-4 | CML: type TBC | 3 |  |  | 2013-11-18 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.3 | 12 O'Clock | 100 |  | 100-FG-45032-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.6 | 5.4 | 5.4 | 0.12583
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-8 | 150-WC-40006-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1649 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.275 | CML-8 | CML: Pipe Length | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 9 | 6 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.4 | 9.6 | 9 | 9.1 | 0.27538
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-22 | 50-WC-40452-01C02 CML-22 |  | FPSO 2013 | Pipe Wall Thickness | 10619 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 9.05 | CML-22 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2013-11-17 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9 | 6 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9 | 9 | 9.2 | 0.1
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1972 |  | 2014-03-26 13:00 | 2014-03-26 14:00 | [36 empty] | 5.575 | CML-3 | CML: type TBC | 3 | 2031-03-01 | 2033-01-25 | 2014-03-26 13:00 | 2.5 | 0.17117 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56105-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.6 | 5.7 | 5.4 | 0.12583
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1311 |  | 2014-03-31 09:30 | 2014-03-31 10:00 | [36 empty] | 5.575 | CML-2 | CML: type TBC | 3 | 2031-06-15 | 2033-05-22 | 2014-03-31 09:30 | 2.5 | 0.16843 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DN-56096-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.6 | 5.4 | 5.6 | 0.12583
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-15 | 80-PW-44001-01C02-P CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23224 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 12.075 | CML-15 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.7 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 | 2.0957 | 12.6 | 12.1 | 11.9 | 11.7 | 0.38622
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-VA-23057-01C02 | CML-3 | 200-VA-23057-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3147 | Rope Access | 2014-05-02 14:00 | 2014-05-02 15:00 | [36 empty] | 7.575 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-05-02 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 9 O'Clock | 200 | 6.35 | 200-VA-23057-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.6 | 7.6 | 7.7 | 7.4 | 0.12583
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-7 | 250-PW-44006-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23178 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 9.925 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | -5.2642 | 10.1 | 9.9 | 9.5 | 10.2 | 0.30957
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-11 | 50-FH-43137-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22685 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.075 | CML-11 | CML: Elbow | 3 | 2022-06-16 | 2023-06-06 | 2015-04-27 07:00 | 2.5 | 0.33597 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0 | 4.9 | 5.1 | 5.1 | 5.2 | 0.12583
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43072-01C02 | CML-4 | 50-FL-43072-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22256 | Deck Level | 2014-05-01 13:00 | 2014-05-01 14:00 | [36 empty] | 5.075 | CML-4 | CML: Elbow | 3 | 2017-10-17 | 2018-03-31 | 2014-05-01 13:00 | 2.48 | 0.69827 | A3: Inside Quadrant |  | 2.54 | 2.48 | 2.1637 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FL-43072-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.42 |  | 5.1 | 5.1 | 4.9 | 5.2 | 0.12583
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43072-01C02 | CML-4 | 50-FL-43072-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2977 | Deck Level | 2014-05-01 13:00 | 2014-05-01 14:00 | [36 empty] | 5.075 | CML-4 | CML: Elbow | 3 | 2017-10-17 | 2018-03-31 | 2014-05-01 13:00 | 2.48 | 0.69827 | A3: Inside Quadrant |  | 2.54 | 2.48 | 2.1637 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FL-43072-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.42 |  | 5.1 | 5.1 | 4.9 | 5.2 | 0.12583
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2029 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 5.575 | CML-3 | CML: type TBC | 3 | 2040-08-31 | 2043-11-03 | 2014-03-27 14:30 | 2.5 | 0.10964 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.6 | 5.4 | 5.7 | 0.12583
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-14 | 250-PG-23003-06C02-PA CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 854 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.575 | CML-14 | CML: Pipe Length | 3 | 2031-08-01 | 2033-07-13 | 2014-04-02 14:00 | 2.5 | 0.16722 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.6 | 5.4 | 5.7 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-36 | 100-DC-57036-01C02 CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 1442 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 12.1667 | CML-36 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 12 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  |  | 12.3 | 12.2 | 12 | 0.15275
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-22 | 50-FG-45301-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 5808 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.925 | CML-22 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 5.9 | 5.8 | 5.9 | 0.12583
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45028-03C02-E | CML-5 | 80-FG-45028-03C02-E CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24329 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.075 | CML-5 | CML: Reducer | 3 | 2033-12-01 | 2031-04-19 | 2016-06-01 07:00 | 1.46 | 0.19643 | A4: Left Quadrant |  | 2.49 | 1.46 | 1.975 | 4.9 | 9 O'Clock | 50 | 5.49 | 80-FG-45028-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.44 |  | 5.2 | 5.1 | 5.1 | 4.9 | 0.12583
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-6 | 50-FG-45024-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1189 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.575 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.6 | 6.4 | 6.7 | 0.12583
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-26 | 200-PL-20008-01C02-H CML-26 | yes | FPSO 2015 | Pipe Wall Thickness | 8823 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 8.025 | CML-26 | CML: Fitting | 3 | 2065-11-29 | 2058-08-19 | 2015-02-21 07:00 | 1.1 | 0 | A3: Inside Quadrant |  | 3.35 | 1.1 | 1.8281 | 7.6 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 8.1 | 8.4 | 7.6 | 8 | 0.3304
PG06 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PG-23008-15S01-A | CML-13 | 200-PG-23008-15S01-A CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12591 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.575 | CML-13 | CML: Elbow | 3 | 2050-12-17 | 2046-03-02 | 2014-02-05 08:00 | 0.54 | 0.13175 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.6 | 5.4 | 5.6 | 5.7 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-18 | 250-PL-20006-01C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 13188 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 11.2333 | CML-18 | CML: Tee | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A1: Outside Quadrant |  | 3.35 | 3.61 | 3.0831 | 11 | 12 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.39 |  | 11 | 11.2 | 11.5 |  | 0.25166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-50 | 400-FH-43508-01C02 CML-50 |  | FPSO 2015 | Pipe Wall Thickness | 23569 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 8.025 | CML-50 | CML: Pipe Length | 3 | 258310 | 229699 | 2015-08-10 07:30 | 2.5 | 0.00912 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8 | 8 | 8.2 | 7.9 | 0.12583
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-11 | 400-WC-40025-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1271 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 9.225 | CML-11 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 9.1 | 12 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.1 | 9.2 | 9.3 | 9.3 | 0.095743
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-22 | 300-PW-44003-01C03 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21864 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 17:07 | [32 empty] | 12.75 | CML-22 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 12.5 | 12 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 12.5 | 12.8 | 13 | 12.7 | 0.20817
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12579 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 7.975 | CML-1 | CML: Reducer | 3 | 2062-11-29 | 2056-08-05 | 2014-02-05 08:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 7.6 | 12 O'Clock | 50 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.06 |  | 7.6 | 8.2 | 8 | 8.1 | 0.263
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-1 | 50-PL-23042-09C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10066 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 9.975 | CML-1 | CML: type TBC | 6 | 2016-05-08 | 2015-11-30 | 2013-11-07 | 2.5 | 2.9154 | A4: Left Quadrant |  | 5.07 | 2.5 | 3.785 | 9.8 | 9 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10 | 10 | 10.1 | 9.8 | 0.12583
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-2 | 80-PG-23025-06C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13073 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 11.075 | CML-2 | CML: Pipe Length | 6 | 2038-05-08 | 2034-11-11 | 2014-02-07 11:00 | 2.8 | 0.33385 | A3: Inside Quadrant |  | 5.13 | 2.8 | 3.965 | 10.9 | 6 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 11.2 | 11.1 | 10.9 | 11.1 | 0.12583
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20026-03C03-P | CML-3 | 80-PG-20026-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21667 | Protective mesh removed | 2014-06-26 08:00 | 2014-06-26 09:00 | [36 empty] | 11.025 | CML-3 | CML: Fitting | 6 | 2053-07-06 | 2047-05-28 | 2014-06-26 08:00 | 2.5 | 0.21507 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 9 O'Clock | 80 | 11.13 | 80-PG-20026-03C03-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11 | 11.2 | 11 | 10.9 | 0.12583
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-27 | 350-FL-43511-01C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 2308 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 11.525 | CML-27 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 11.4 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.7 | 11.5 | 11.5 | 11.4 | 0.12583
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-18 | 50-CG-38001-09C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 10932 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.075 | CML-18 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.3873 | A3: Inside Quadrant |  | 5.74 |  |  | 7.9 | 6 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.9 | 8.1 | 8.1 | 7.9 | 8.2 | 0.12583
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43301-01C02-E | CML-4 | 200-PL-43301-01C02-E CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8601 | Line is FFS. Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-02-09 07:30 | 2015-02-09 15:00 |  |  | Administrator | 2015-09-07 16:33 | [32 empty] | 8.025 | CML-4 | CML: Reducer | 3 | 2063-07-07 | 2057-06-06 | 2015-02-09 07:30 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.9 | 12 O'Clock | 200 | 6.35 | 200-PL-43301-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.56 |  | 7.9 | 8.2 | 8 | 8 | 0.12583
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-15 | 300-PG-20506-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 13229 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.025 | CML-15 | CML: type TBC | 6 | 2030-08-27 | 2027-07-22 | 2014-02-04 15:00 | 4.9 | 0.54319 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 12 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 13.9 | 14.2 | 14 | 14 | 0.12583
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-14 | 50-DH-56137-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 5682 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [35 empty] | Low alarm breach | 17.775 | CML-14 | CML: Elbow | 3 | 2018-08-15 | 2016-06-06 | 2014-06-21 14:00 | 2.5 | 3.635 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.6 | 6 O'Clock | 150 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.1 |  | 17.8 | 17.9 | 17.6 | 17.8 | 0.12583
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-6 | 50-PL-23514-01C03 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8639 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:19 | [32 empty] | 8.3 | CML-6 | CML: Pipe Length | 6 | 2033-01-05 | 2032-08-20 | 2015-02-10 11:30 | 2.5 | 0.31817 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 6 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.4 | 8.2 | 8.2 | 8.4 | 0.11547
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-1 | 150-FH-43141-01C02 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 6385 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.5 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 6 O'Clock | 40 | 2.5 | 40-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.6 | 3.4 | 3.4 | 3.6 | 0.11547
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-8 | 250-PG-23003-06C02-PA CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7687 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:57 | [32 empty] | 4.9 | CML-8 | CML: Elbow | 3 | 2020-01-05 | 2020-09-20 | 2015-01-08 13:00 | 2.5 | 0.4605 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.43708 | 5 | 4.8 | 5 | 4.8 | 0.11547
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-18 | 50-FG-45300-01C02 CML-18 | yes | FPSO 2015 | Pipe Wall Thickness | 7841 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:40 | [32 empty] | 5.1 | CML-18 | CML: Pipe Length | 3 | 2022-07-14 | 2023-07-06 | 2015-01-13 13:00 | 2.5 | 0.3332 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5.2 | 5 | 0.11547
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-32 | 50-DH-56062-01C02 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 9119 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.1 | CML-32 | CML: type TBC | 3 | 2023-04-08 | 2024-04-29 | 2015-03-02 07:00 | 2.5 | 0.30831 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5 | 5.2 | 0.11547
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-23 | 250-PW-44006-01X01 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 1920 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 10.6 | CML-23 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.6 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.5 | 10.4 | 9.6 | 11.9 | 0.95568
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-16 | 300-PW-44002-01X01-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 22033 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 10.55 | CML-16 | CML: Elbow | 6 | 2028-07-28 | 2026-10-25 | 2014-10-17 07:00 | 2.5 | 0.51491 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.6 | 12 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.6 | 10.8 | 11.1 | 10.7 | 0.65574
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-1 | 250-DC-57064-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20281 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 12.3 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 12.1 | 6 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 12.1 | 12.7 | 12.1 | 12.3 | 0.28284
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-5 | 300-PW-44002-01X01-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22022 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 9.825 | CML-5 | CML: Elbow | 6 | 2028-07-28 | 2026-10-25 | 2014-10-17 07:00 | 2.5 | 0.51491 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.6 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.8 | 9.6 | 9.7 | 10.2 | 0.263
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-18 | 50-FG-45018-03C02 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10517 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.3 | CML-18 | CML: type TBC | 3 | 2017-07-03 | 2017-06-23 | 2013-11-15 | 2.5 | 0.74311 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.4 | 5.2 | 5.2 | 0.11547
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-6 | 300-PW-44002-01X01-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22852 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.375 | CML-6 | CML: Reducing Tee | 6 | 2037-12-05 | 2035-02-01 | 2015-05-01 07:00 | 2.5 | 0.31839 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 6 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 | -0.55867 | 11.3 | 10.1 | 9.7 | 10.4 | 0.68007
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-12 | 300-PW-44002-01X01-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 22029 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 10.15 | CML-12 | CML: Reducing Tee | 6 | 2031-01-21 | 2029-01-05 | 2014-10-17 07:00 | 2.5 | 0.44239 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 12 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 9.8 | 10 | 11.1 | 0.6455
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-27 | 250-PW-44006-01X01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 8019 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 10.05 | CML-27 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 3 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 | -0.36492 | 10.5 | 9.7 | 10.1 | 9.9 | 0.34157
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-12 | 400-WC-40025-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1272 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 9.2 | CML-12 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 9.1 | 9 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.2 | 9.2 | 9.3 | 9.1 | 0.08165
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-13 | 100-DC-57036-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1419 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 12.4333 | CML-13 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 12.1 | 6 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  |  | 12.8 | 12.1 | 12.4 | 0.35119
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38494-01C02 | CML-1 | 25-CG-38494-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10384 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.7 | CML-1 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 3 O'Clock | 25 | 6.35 | 25-CG-38494-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.6 | 5.6 | 5.8 | 5.8 | 0.11547
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-14 | 80-PW-44001-01C02-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23223 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 12 | CML-14 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.7 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 | 2.6196 | 12.4 | 11.8 | 11.7 | 12.1 | 0.31623
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43105-01C02 | CML-6 | 100-FH-43105-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12769 |  | 2014-01-25 09:00 | 2014-01-25 10:00 | [36 empty] | 6.1 | CML-6 | CML: type TBC | 3 | 2128-04-13 | 2132-01-28 | 2014-01-25 09:00 | 2.5 | 0.03062 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-FH-43105-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.2 | 6.2 | 0.11547
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-7 | 50-FG-45023-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12993 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 6.2667 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-01-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.4 | 6.2 |  | 0.11547
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43120-01C02 | CML-2 | 200-FH-43120-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12836 |  | 2014-02-06 07:00 | 2014-02-06 09:00 | [36 empty] | 6.5667 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 9 O'Clock | 200 | 6.35 | 200-FH-43120-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.5 |  | 6.5 | 0.11547
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43017-01C02 | CML-2 | 150-FH-43017-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10648 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.6667 | CML-2 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-18 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 9 O'Clock | 100 | 6.02 | 100-FH-43017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.8 |  | 6.6 | 0.11547
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-8 | 150-FL-43453-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2252 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.8 | CML-8 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.7 | 6 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.9 | 6.7 | 6.7 | 6.9 | 0.11547
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-29 | 200-PL-20008-01C02-H CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 8826 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 8.175 | CML-29 | CML: Fitting | 3 | 2065-11-29 | 2058-08-19 | 2015-02-21 07:00 | 1.1 | 0 | A3: Inside Quadrant |  | 3.35 | 1.1 | 1.8281 | 7.8 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 8 | 8.5 | 7.8 | 8.4 | 0.3304
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2507 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.1 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7.2 | 7 | 7 | 0.11547
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-4 | 50-CG-38457-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23722 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 7.3 | CML-4 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 3 O'Clock | 100 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.2 | 7.4 | 7.4 | 0.11547
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-5 | 80-FH-43009-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12583 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.4 | CML-5 | CML: Pipe Length | 3 | 2031-03-14 | 2028-12-05 | 2014-02-05 08:00 | 0.54 | 0.27814 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.5 | 5.3 | 5.5 | 5.3 | 0.11547
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-1 | 200-PL-20008-01C02-H CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 8798 | LAGGING REMOVAL REQUIRED, Reducer 200-400Ø | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 9.75 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 9 O'Clock | 300 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.8 | 10.2 | 9.7 | 9.3 | 0.36968
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-9 | 50-CG-38452-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2508 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.7 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 9 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.8 | 7.6 | 7.8 | 7.6 | 0.11547
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40052-01C02 | CML-1 | 50-WC-40052-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1524 |  | 2014-04-03 11:00 | 2014-04-03 12:00 | [36 empty] | 9.025 | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-04-03 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9 | 6 O'Clock | 50 | 5.54 | 50-WC-40052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9 | 9 | 9.1 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1667 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 9.875 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 3 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.8 | 9.2 | 9.6 | 10.9 | 0.72744
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43029-01C02 | CML-5 | 400-FH-43029-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10021 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.7 | CML-5 | CML: Elbow | 3 | 2020-09-04 | 2019-09-16 | 2013-11-04 | 2.48 | 0.74872 | A1: Outside Quadrant |  | 4.92 | 2.48 | 3.205 | 7.6 | 9 O'Clock | 400 | 7.92 | 400-FH-43029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.12 |  | 7.6 | 7.8 | 7.8 | 7.6 | 0.11547
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20013-01C02-P | CML-8 | 200-PL-20013-01C02-P CML-8 | yes | FPSO 2014 | Pipe Wall Thickness | 21218 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 11.075 | CML-8 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 3 O'Clock | 200 | 6.35 | 200-PL-20013-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.2 | 9.9 | 10.5 | 13.7 | 1.7671
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-7 | 50-CG-38500-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23294 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.7 | CML-7 | CML: Pipe Length | 3 | 2016-09-09 | 2017-01-15 | 2015-07-04 09:30 | 2.5 | 0.92757 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.6 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 | 0 | 3.6 | 3.6 | 3.8 | 3.8 | 0.11547
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-6 | 50-FG-45020-03C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10578 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5 | CML-6 | CML: type TBC | 3 | 2015-08-12 | 2015-08-07 | 2013-11-17 | 2.5 | 1.3822 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 4.9 | 4.9 | 5.1 | 0.11547
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-7 | 50-CG-38458-01C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23735 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5 | CML-7 | CML: Elbow | 3 | 2024-11-16 | 2026-02-08 | 2015-10-30 07:00 | 2.5 | 0.26507 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 4.9 | 5.1 | 4.9 | 0.11547
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-11 | 150-WC-40006-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20633 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 9.375 | CML-11 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-07-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.3 | 6 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.4 | 9.4 | 9.3 | 9.4 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43516-01C02 | CML-11 | 200-FH-43516-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12974 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.5 | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.6 | 6.4 | 6.4 | 0.11547
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-1 | 50-PW-44041-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23001 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 4.5 | CML-1 | CML: Elbow | 3 | 2017-03-20 | 2017-08-16 | 2015-05-05 07:00 | 2.5 | 0.79924 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4 | 6 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 0.18161 | 5 | 4.5 | 4 | 4.5 | 0.40825
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12965 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.5 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 6 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.4 | 6.4 | 6.6 | 0.11547
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-1 | 200-PL-20020-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21305 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 10.525 | CML-1 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 11 | 10.9 | 10.3 | 9.9 | 0.51881
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40060-01C02 | CML-6 | 400-WC-40060-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1054 |  | 2014-03-20 14:00 | 2014-03-20 14:30 | [36 empty] | 10.225 | CML-6 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-20 14:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 9.5 | 12 O'Clock | 400 | 7.92 | 400-WC-40060-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.5 | 10.5 | 10.6 | 10.3 | 0.49917
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-7 | 100-PG-23406-03C03 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20733 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 12.4 | CML-7 | CML: Elbow | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 12.2 | 6 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 12.6 | 12.2 | 12.2 | 12.6 | 0.23094
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-13 | 300-PW-44002-01X01-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22859 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.8 | CML-13 | CML: Elbow | 6 | 2037-12-05 | 2035-02-01 | 2015-05-01 07:00 | 2.5 | 0.31839 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 12 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 | -2.4209 | 9.7 | 9.8 | 9.9 | 9.8 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-2 | 150-FH-43136-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5516 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 6.5 | CML-2 | CML: Elbow | 3 | 2021-12-24 | 2020-06-08 | 2014-06-01 07:00 | 1.03 | 0.70943 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 | 0 | 6.4 | 6.6 | 6.4 | 6.6 | 0.11547
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-2 | 150-FH-43136-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2763 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 6.5 | CML-2 | CML: Elbow | 3 | 2020-02-08 | 2018-11-25 | 2014-03-13 09:00 | 1.03 | 0.9081 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 |  | 6.4 | 6.6 | 6.4 | 6.6 | 0.11547
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-1 | 50-PW-44041-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2124 |  | 2014-03-29 08:00 | 2014-03-29 09:00 | [36 empty] | 4.65 | CML-1 | CML: Elbow | 3 | 2015-04-15 | 2015-06-27 | 2014-03-29 08:00 | 2.5 | 1.6231 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.3 | 5.1 | 4.2 | 5 | 0.46547
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-4 | 50-PW-44041-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23004 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 5.075 | CML-4 | CML: Elbow | 3 | 2021-04-29 | 2022-03-05 | 2015-05-05 07:00 | 2.5 | 0.38405 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.36322 | 4.9 | 5.2 | 4.8 | 5.4 | 0.27538
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-14 | 50-WC-40028-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1694 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 9.875 | CML-14 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.4 | 3 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.7 | 9.4 | 10.2 | 10.2 | 0.39476
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23034-01C03 | CML-1 | 50-PL-23034-01C03 CML-1 | no | FPSO 2014 | Pipe Wall Thickness | 20569 | Reviewed on 26/11/14.FFS. Repeat Oct.19 | 2014-10-12 07:00 | 2014-10-12 12:00 |  |  | Nestor | 2014-11-20 15:17 | [32 empty] | 8.6 | CML-1 | CML: Pipe Length | 6 | 2048-11-19 | 2048-03-15 | 2014-10-12 07:00 | 2.5 | 0.1758 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-PL-23034-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.7 | 8.7 | 8.5 | 0.11547
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20023-01C03-P | CML-1 | 250-PW-20023-01C03-P CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 5598 |  | 2014-06-20 07:00 | 2014-06-20 08:00 | [36 empty] | 12.8 | CML-1 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2014-06-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 12.6 | 9 O'Clock | 250 | 9.27 | 250-PW-20023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.1 |  | 12.8 | 13.2 | 12.6 | 12.6 | 0.28284
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-16 | 50-PL-23300-09C03 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 13132 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.4 | CML-16 | CML: type TBC | 6 | 2020-09-15 | 2019-09-17 | 2014-02-04 07:00 | 2.81 | 1.1319 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.3 | 9 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.49 |  | 10.3 | 10.5 | 10.5 | 10.3 | 0.11547
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-4 | 50-CG-38488-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20822 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 10.6 | CML-4 | CML: Reducer | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.5 | 3 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.5 | 10.5 | 10.7 | 10.7 | 0.11547
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-19 | 50-PL-23052-09C03 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10183 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 12.5667 | CML-19 | CML: type TBC | 6 | 2096-01-05 | 2084-09-16 | 2013-11-09 | 2.81 | 0 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 12.5 | 9 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.69 |  | 12.5 | 12.7 |  | 12.5 | 0.11547
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-13 | 300-PG-20049-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21499 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | [36 empty] | 17.7 | CML-13 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-06-28 10:45 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.6 | 9 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.7 |  | 17.8 | 17.8 | 17.6 | 17.6 | 0.11547
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-10 | 50-PL-23041-06C03 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10223 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.6 | CML-10 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 1.3003 | A1: Outside Quadrant |  | 5.07 |  |  | 10.5 | 3 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.5 | 10.5 | 10.7 | 10.7 | 0.11547
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57308-01C03 | CML-16 | 150-DC-57308-01C03 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20313 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 13.3 | CML-16 | CML: type TBC | 6 | 2098-02-09 | 2085-10-05 | 2014-10-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 12.3 | 6 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 13.6 | 14 | 12.3 | 13.3 | 0.72572
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56004-01C02 | CML-3 | 80-DH-56004-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3406 | Rope Access | 2014-05-11 07:00 | 2014-05-11 09:00 | [36 empty] | 8.15 | CML-3 | CML: type TBC | 3 |  |  | 2014-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 8.1 | 9 O'Clock | 100 |  | 100-DH-56004-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.3 | 8.1 | 0.1
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-3 | 50-CG-38487-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20803 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 8.75 | CML-3 | CML: Pipe Length | 3 | 2189-07-31 | 2143-11-05 | 2014-07-18 11:00 | 2.5 | 0.0354 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 8.7 | 8.7 | 8.9 | 0.1
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-32 | 300-PG-20004-03C03-P CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 6155 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 8.75 | CML-32 | CML: Pipe Length | 6 | 2015-10-05 | 2015-03-09 | 2014-07-11 07:30 | 2.5 | 5.016 | A1: Outside Quadrant |  | 8.27 | 2.5 | 5.385 | 8.7 | 9 O'Clock | 50 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 8.7 | 8.9 | 8.7 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-7 | 200-FH-43038-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12688 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 9.3 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 9 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  |  | 9.3 | 9.4 | 9.2 | 0.1
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-24 | 50-FG-45023-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 1172 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 10.75 | CML-24 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.6 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.8 | 10.8 | 10.6 | 10.8 | 0.1
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-3 | 50-CG-24002-09C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2549 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 10.75 | CML-3 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.7 | 6 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.7 | 10.7 | 10.7 | 10.9 | 0.1
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-4 | 50-PG-44022-01C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22979 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 11.35 | CML-4 | CML: Reducer | 6 | 2075-10-24 | 2074-08-12 | 2015-05-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 11.2 | 3 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 | 1.2827 | 11.4 | 11.2 | 11.4 | 11.4 | 0.1
FL01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FL-43174-01C02 | CML-9 | 150-FL-43174-01C02 CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 7881 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:42 | [32 empty] | 3.55 | CML-9 | CML: Pipe Length | 3 | 2015-09-20 | 2015-12-19 | 2015-01-14 10:30 | 2.5 | 1.3184 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.6 | 3.4 | 3.6 | 3.6 | 0.1
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML86 | 150-FL-43174-01C02 CML86 |  | FPSO 2015 | Pipe Wall Thickness | 7331 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 3.55 | CML86 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.5 | 3.5 | 3.7 | 3.5 | 0.1
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-18 | 50-FG-45020-03C02 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10590 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.85 | CML-18 | CML: type TBC | 3 | 2015-02-02 | 2015-01-29 | 2013-11-17 | 2.5 | 1.8142 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 4.9 | 4.9 | 4.9 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43155-01C02 | CML-2 | 80-FH-43155-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10715 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 4.95 | CML-2 | CML: type TBC | 3 | 2015-06-07 | 2015-09-01 | 2013-11-18 | 2.5 | 1.4815 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 9 O'Clock | 80 | 5.49 | 80-FH-43155-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 5 | 5 | 4.8 | 0.1
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38302-01C02-P |  | 50-CG-38302-01C02-P | yes | FPSO 2014 | Pipe Wall Thickness | 22106 | Rope access | 2014-06-02 09:30 | 2014-06-02 11:00 | [36 empty] | 5.05 | 50-CG-38302-01C02-P | Piping | 3 | 2019-01-23 |  | 2014-06-02 09:30 |  | 0.53794 | A1: Outside Quadrant |  |  | 2.5 |  | 5 | 9 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 5 | 5 | 5 | 5.2 | 5 | 0.1
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-4 | 250-PW-44007-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1961 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 10.475 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.8 | 12 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.8 | 10.2 | 11.4 | 10.5 | 0.68007
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-7 | 250-PW-44006-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1904 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 10.7 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.5 | 10.4 | 12 | 9.9 | 0.90554
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-16 | 80-PW-44016-01C02-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 22918 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 12.125 | CML-16 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.7 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 | 0.17892 | 12.4 | 12.2 | 11.7 | 12.2 | 0.29861
PG06 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PG-23008-15S01-A | CML-4 | 200-PG-23008-15S01-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20294 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | Check Corrosion Rate of 0.319mm/ yr | [35 empty] | 5.25 | CML-4 | CML: Elbow | 3 | 2022-12-08 | 2023-12-16 | 2014-10-17 07:00 | 2.5 | 0.3191 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.3 | 5.3 | 5.1 | 0.1
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-1 | 200-PG-23008-15S01-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21127 | Reviewed on 20/11/14. FFS. Recheck in Oct. 19. It appears wrong schedule was used. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. Action: Update RBI study to include this line. While RBI is updated rest of CMLs to be inspected in 48m. CML-2 avg. WT is 5.0 mm. | 2014-10-08 07:00 | 2014-10-08 15:00 | [36 empty] | 5.25 | CML-1 | CML: Elbow | 3 | 2022-10-07 | 2023-10-08 | 2014-10-08 07:00 | 2.5 | 0.32491 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 25 | 5.54 | 50-DH-56556-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.3 | 5.3 | 5.1 | 0.1
PG06 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PG-23008-15S01-A | CML-8 | 200-PG-23008-15S01-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3051 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 5.25 | CML-8 | CML: type TBC | 3 | 2019-10-11 | 2020-06-16 | 2014-05-03 07:00 | 2.5 | 0.47756 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 5.3 | 5.3 | 0.1
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-8 | 250-PW-44007-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1965 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 10.725 | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 11:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 9 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.7 | 11.7 | 10.6 | 9.9 | 0.74106
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-17 | 300-PW-44002-01X01-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 22034 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 10.7 | CML-17 | CML: Elbow | 6 | 2039-08-31 | 2036-08-15 | 2014-10-17 07:00 | 2.5 | 0.29734 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.9 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.9 | 9.9 | 11.1 | 10.9 | 0.5416
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-18 | 150-WC-40006-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1659 | Rope Access | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.725 | CML-18 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.4 | 3 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.7 | 9.4 | 9.7 | 10.1 | 0.28723
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-20 | 50-FG-45021-03C02 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10548 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.35 | CML-20 | CML: type TBC | 3 | 2017-07-12 | 2017-07-02 | 2013-11-16 | 2.5 | 0.73869 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.4 | 5.4 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-5 | 50-FH-43450-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10672 | Deck Level. High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.585 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 17:46 | [32 empty] | 5.35 | CML-5 | CML: Elbow | 3 | 2017-07-21 | 2017-12-30 | 2013-11-17 | 2.5 | 0.73432 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.4 | 5.2 | 5.4 | 0.1
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-24 | 100-DC-57036-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 1430 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 12.5333 | CML-24 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 12.4 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  |  | 12.5 | 12.7 | 12.4 | 0.15275
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-11 | 50-DH-56137-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21095 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 5.35 | CML-11 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.2 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.4 | 5.4 | 5.2 | 0.1
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-2 | 50-PW-44041-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23002 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 5.075 | CML-2 | CML: Elbow | 3 | 2021-04-29 | 2022-03-05 | 2015-05-05 07:00 | 2.5 | 0.38405 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0 | 4.8 | 5.1 | 5.1 | 5.3 | 0.20616
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-2 | 50-PW-44041-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2125 |  | 2014-03-29 08:00 | 2014-03-29 09:00 | [36 empty] | 5.025 | CML-2 | CML: Elbow | 3 | 2016-10-20 | 2017-03-02 | 2014-03-29 08:00 | 2.5 | 0.89635 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.9 | 5.2 | 5.2 | 0.20616
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-4 | 50-PW-44041-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2127 |  | 2014-03-29 08:00 | 2014-03-29 09:00 | [36 empty] | 5.375 | CML-4 | CML: Elbow | 3 | 2020-10-16 | 2021-08-01 | 2014-03-29 08:00 | 2.5 | 0.41184 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.4 | 5.5 | 0.12583
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-2 | 50-FG-45020-03C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2601 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.35 | CML-2 | CML: type TBC | 3 | 2024-11-02 | 2024-10-05 | 2014-04-26 09:30 | 2.5 | 0.26594 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | -0.68269 | 5.5 | 5.3 | 5.3 | 5.3 | 0.1
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-5 | 50-FG-45300-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 7828 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:45 | [32 empty] | 5.45 | CML-5 | CML: Reducer | 3 | 2033-12-05 | 2036-02-17 | 2015-01-13 13:00 | 2.5 | 0.14809 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 5.5 | 5.5 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-8 | 50-FH-43450-01C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10675 | Deck Level. High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.461 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 17:44 | [32 empty] | 5.35 | CML-8 | CML: Elbow | 3 | 2019-04-11 | 2019-11-27 | 2013-11-17 | 2.5 | 0.51834 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.5 | 5.3 | 5.3 | 0.1
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45017-03C02 | CML-13 | 100-FG-45017-03C02 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10637 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.55 | CML-13 | CML: type TBC | 3 | 2016-07-25 | 2016-05-01 | 2013-11-18 | 2.5 | 1.1165 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.5 | 6 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.5 | 5.5 | 5.7 | 0.1
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38483-01C02 | CML-1 | 25-CG-38483-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10390 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.65 | CML-1 | CML: type TBC | 3 | 2015-06-13 | 2015-06-08 | 2013-11-12 | 2.5 | 1.8918 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 25 | 6.35 | 25-CG-38483-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 5.5 | 5.7 | 5.7 | 5.5 | 5.7 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43115-01C02 | CML-4 | 80-FH-43115-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12824 |  | 2014-01-20 09:00 | 2014-01-20 10:00 | [36 empty] | 5.85 | CML-4 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-20 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 9 O'Clock | 80 | 5.49 | 80-FH-43115-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 5.9 | 5.9 | 5.7 | 0.1
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56083-01C02 | CML-5 | 100-DH-56083-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22530 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.85 | CML-5 | CML: Pipe Length | 3 | 2043-07-26 | 2044-07-24 | 2015-04-20 07:00 | 2.5 | 0.11667 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-DH-56083-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6 | 5.8 | 0.1
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-17 | 150-WC-40006-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1658 | Rope Access | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.675 | CML-17 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.4 | 3 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.8 | 9.4 | 9.6 | 9.9 | 0.22174
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-11 | 25-FG-45455-01C02-E CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21444 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 6.05 | CML-11 | CML: Reducing Tee | 1 | 2025-09-06 | 2021-02-21 | 2014-07-13 07:30 | 2.5 | 0.31364 | A1: Outside Quadrant |  | 5.35 | 2.5 | 3.925 | 6 | 9 O'Clock | 250 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.2 | 6 | 0.1
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2412 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 6.05 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6 | 6.2 | 0.1
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-3 | 50-PW-44041-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23003 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 5.675 | CML-3 | CML: Elbow | 3 | 2037-10-21 | 2040-06-03 | 2015-05-05 07:00 | 2.5 | 0.12456 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0.27242 | 5.8 | 6.2 | 5.4 | 5.3 | 0.4113
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43105-01C02 | CML-1 | 100-FH-43105-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12764 |  | 2014-01-25 09:00 | 2014-01-25 10:00 | [36 empty] | 6.15 | CML-1 | CML: type TBC | 3 | 2128-04-13 | 2132-01-28 | 2014-01-25 09:00 | 2.5 | 0.03062 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-FH-43105-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.2 | 6.2 | 0.1
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-22 | 50-FG-45023-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 1170 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.65 | CML-22 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.7 | 6.7 | 6.7 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-15 | 250-FH-43303-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12953 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.65 | CML-15 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 9 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.7 | 6.7 | 6.5 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-1 | 250-FH-43303-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12939 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.65 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.5 | 6.7 | 6.7 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-6 | 100-FH-43507-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1776 | Rope access | 2014-04-27 13:00 | 2014-04-27 14:00 | [36 empty] | 6.55 | CML-6 | CML: Pipe Length | 3 | 2020-04-03 | 2019-09-20 | 2014-04-27 13:00 | 2.5 | 0.67359 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.5 | 9 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.5 | 6.7 | 6.5 | 0.1
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1808 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 7.15 | CML-6 | CML: Fitting | 3 | 2433-01-13 | 2400-03-18 | 2014-04-29 11:00 | 2.5 | 0.01098 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.1 | 9 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.3 | 7.1 | 7.1 | 0.1
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-VA-23058-01C02 | CML-3 | 200-VA-23058-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3143 | Rope Access | 2014-05-02 13:00 | 2014-05-02 14:00 | [36 empty] | 7.75 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-05-02 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 6 O'Clock | 200 | 6.35 | 200-VA-23058-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.8 | 7.8 | 7.6 | 7.8 | 0.1
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43175-01C02 | CML-5 | 150-FL-43175-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12916 |  | 2014-02-03 07:00 | 2014-02-03 08:00 | [36 empty] | 7.95 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.8 | 3 O'Clock | 100 | 6.02 | 100-FL-43175-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8 | 7.8 | 8 | 8 | 0.1
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-15 | 200-PL-20010-01C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 23815 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 10.6 | CML-15 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 10 | 3 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.3 | 10 | 10.4 | 11.7 | 0.75277
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43300-01C02-E | CML-11 | 200-PL-43300-01C02-E CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8597 | Line is FFS. Current RBI frequency is 36m. Action: CML’s to Inspect in 48m. RBI to be updated | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-08 14:59 | [32 empty] | 8.475 | CML-11 | CML: Cap End | 3 | 2063-07-07 | 2057-06-06 | 2015-02-08 11:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 8.3 | 9 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.96 |  | 8.5 | 8.8 | 8.3 | 8.3 | 0.23629
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-19 | 150-WC-40006-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1660 | Rope Access | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.475 | CML-19 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.4 | 3 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.5 | 9.4 | 9.5 | 9.5 | 0.05
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23403-01C03-A | CML-2 | 150-PG-23403-01C03-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5603 |  | 2014-06-20 08:00 | 2014-06-20 09:00 | [36 empty] | 13.1 | CML-2 | CML: Equal Tee | 6 | 2098-02-09 | 2085-10-05 | 2014-06-20 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 12.5 | 12 O'Clock | 150 | 10.97 | 150-PG-23403-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 12.5 | 13.5 | 13.5 | 12.9 | 0.4899
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-3 | 50-FH-43016-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12602 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.55 | CML-3 | CML: Pipe Length | 3 | 2027-06-24 | 2028-12-26 | 2014-01-23 13:00 | 2.5 | 0.21603 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.4 | 5.6 | 5.6 | 0.1
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-5 | 50-PW-44041-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2128 |  | 2014-03-29 08:00 | 2014-03-29 09:00 | [36 empty] | 5.625 | CML-5 | CML: Reducer | 3 | 2023-11-12 | 2024-12-26 | 2014-03-29 08:00 | 2.5 | 0.29071 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.8 | 5.4 | 6 | 0.3304
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-6 | 50-PW-44041-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23006 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 6.05 | CML-6 | CML: Elbow | 3 | 2159-10-04 | 2175-06-18 | 2015-05-05 07:00 | 2.5 | 0.02076 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 25 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 3.269 | 5.9 | 5.5 | 6.6 | 6.2 | 0.46547
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-11 | 350-FL-43511-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2292 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 27.575 | CML-11 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 8 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.1 | . | 8.2 | 8 | 0.1
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-9 | 150-WC-40006-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1650 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 10.325 | CML-9 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.5 | 3 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.1 | 9.5 | 11.4 | 10.3 | 0.7932
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40002-01C02 | CML-16 | 150-WC-40002-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20355 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 10.25 | CML-16 | CML: Equal Tee | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.5 | 12 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.5 | 10.3 | 10.6 | 10.6 | 0.51962
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1645 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.875 | CML-4 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.5 | 3 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.6 | 9.5 | 9.7 | 9.7 | 0.49244
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40401-01C02 | CML-7 | 200-WC-40401-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7923 |  | 2015-01-17 08:00 | 2015-01-17 09:00 |  |  | Administrator | 2015-09-08 11:22 | [32 empty] | 9.8 | CML-7 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-01-17 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 3 O'Clock | 200 | 6.35 | 200-WC-40401-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.5 | 9.5 | 10.4 | 9.8 | 0.42426
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45003-03C02 | CML-1 | 150-FG-45003-03C02 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24367 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.05 | CML-1 | CML: Elbow | 3 | 2079-08-09 | 2068-01-18 | 2016-06-06 07:00 | 2.5 | 0.0696 | A3: Inside Quadrant |  | 4.11 | 2.5 | 3.305 | 6.9 | 6 O'Clock | 150 | 7.11 | 150-FG-45003-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.1 | 7.1 | 6.9 | 7.1 | 0.1
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-5 | 100-PG-23503-03C03-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2721 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.9 | CML-5 | CML: Pipe Length | 6 | 2026-05-14 | 2026-12-29 | 2014-03-13 09:00 | 5.66 | 0.42208 | A2: Right Quadrant |  | 5.13 | 5.66 | 5.395 | 10.8 | 3 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.14 |  | 10.9 | 10.8 |  | 11 | 0.1
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-3 | 150-FG-45505-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22339 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 8.05 | CML-3 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8 | 9 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.2 | 8 | 8 | 0.1
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-3 | 50-PW-44041-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2126 |  | 2014-03-29 08:00 | 2014-03-29 09:00 | [36 empty] | 6.15 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-29 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.1 | 5.6 | 5.9 | 7 | 0.60277
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-19 | 50-PL-23020-01C03 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10133 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-19 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 6 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.2 | 8 | 8.2 | 0.1
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40008-01C02-P | CML-7 | 200-WC-40008-01C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7813 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 9.625 | CML-7 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 6 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.8 | 9.5 | 9.5 | 9.7 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-6 | 50-FH-43016-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12605 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 8.5 | CML-6 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-01-23 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 6 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.5 | 8.6 | 8.4 |  | 0.1
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-16 | 50-PL-23022-03C03 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1872 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.15 | CML-16 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 3 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.2 | 9 | 9.2 | 9.2 | 0.1
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-23 | 50-PL-45016-03C03 CML-23 |  | FPSO 2013 | Pipe Wall Thickness | 10463 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.15 | CML-23 | CML: type TBC | 6 | 2018-02-23 | 2017-08-11 | 2013-11-13 | 0.99 | 1.637 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 8 | 3 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.01 |  | 8.2 | 8 | 8.2 | 8.2 | 0.1
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-9 | 250-PW-44007-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23142 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 10.25 | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 12 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 | 0.44533 | 9.9 | 10.5 | 10.2 | 10.4 | 0.26458
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40500-1CG | CML-22 | 400-WC-40500-1CG CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 5690 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [36 empty] | 21.05 | CML-22 | CML: Pipe Length | 3 | 2030-12-15 | 2023-07-29 | 2014-06-21 14:00 | 2.5 | 1.0791 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 20.3 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.8 |  | 21.9 | 21 | 21 | 20.3 | 0.65574
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-5 | 50-PW-44041-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23005 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 6.025 | CML-5 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-05-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | -0.54483 | 5.9 | 6 | 6.1 | 6.1 | 0.095743
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20026-03C03-P | CML-1 | 80-PG-20026-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21665 | Protective mesh removed | 2014-06-26 08:00 | 2014-06-26 09:00 | [36 empty] | 10.95 | CML-1 | CML: Pipe Length | 6 | 2053-07-06 | 2047-05-28 | 2014-06-26 08:00 | 2.5 | 0.21507 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 9 O'Clock | 80 | 11.13 | 80-PG-20026-03C03-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 10.9 | 10.9 | 11.1 | 10.9 | 0.1
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-21 | 300-PW-44003-01C03 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21863 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 17:07 | [32 empty] | 12.85 | CML-21 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 12.7 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 12.7 | 12.7 | 13 | 13 | 0.17321
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-20 | 300-PG-23001-03C03 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 10970 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 16.7 | CML-20 | CML: Pipe Length | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A2: Right Quadrant |  | 8.27 | 5.22 | 6.745 | 16.6 | 3 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.38 |  | 16.8 | 16.6 | 16.7 |  | 0.1
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-10 | 50-DH-56137-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5678 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 4.203mm/ yr | [34 empty] | Low alarm breach | 17.15 | CML-10 | CML: Reducer | 3 | 2017-12-01 | 2016-01-09 | 2014-06-21 14:00 | 2.5 | 4.203 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 17 | 6 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.5 |  | 17.2 | 17.2 | 17 | 17.2 | 0.1
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-16 | 50-FH-43450-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 7695 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-13 13:51 | [32 empty] | 5.05 | CML-16 | CML: Pipe Length | 3 | 2021-01-16 | 2021-11-11 | 2015-01-08 13:00 | 2.5 | 0.39827 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.26225 | 5.1 | 5.1 | 4.9 | 5.1 | 0.1
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-16 | 150-WC-40006-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1657 | Rope Access | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.6 | CML-16 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.5 | 12 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.5 | 9.6 | 9.6 | 9.7 | 0.08165
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-6 | 250-PW-44007-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23139 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 10.25 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 12 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 | 0.2672 | 9.9 | 10.4 | 10.2 | 10.5 | 0.26458
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43085-01C02 | CML-4 | 350-FL-43085-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10014 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.95 | CML-4 | CML: type TBC | 3 | 2129-03-01 | 2113-11-23 | 2013-11-04 | 2.5 | 0.04679 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 6 O'Clock | 350 | 7.92 | 350-FL-43085-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 7.9 | 7.9 | 8.1 | 0.1
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-7 | 50-PW-44041-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2130 |  | 2014-03-29 08:00 | 2014-03-29 09:00 | [36 empty] | 6.25 | CML-7 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-03-29 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 20 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.3 | 6.1 | 6.4 | 0.1291
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-12 | 50-PL-23021-03C03 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10244 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-12 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.2 | 8.2 | 8 | 0.1
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-6 | 50-PW-44041-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2129 |  | 2014-03-29 08:00 | 2014-03-29 09:00 | [36 empty] | 9.5 | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-29 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.1 | 6 O'Clock | 25 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.7 | 9.5 | 9.1 | 9.7 | 0.28284
RP01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-PW-44041-01C02 | CML-7 | 50-PW-44041-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23007 | No Reducer @ CML | 2015-05-05 07:00 | 2015-05-05 15:00 | [37 empty] | CML-7 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-05-05 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 20 | 5.54 | 50-PW-44041-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-3 | 50-PL-23023-03C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10203 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-3 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.2 | 8.2 | 8 | 0.1
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-10 | 150-WC-40006-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1651 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.975 | CML-10 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.6 | 6 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.7 | 9.7 | 9.6 | 10.9 | 0.61847
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-2 | 50-PL-45016-03C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10442 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.45 | CML-2 | CML: type TBC | 6 | 2023-09-18 | 2022-07-20 | 2013-11-13 | 0.99 | 0.75212 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 8.4 | 6 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.41 |  | 8.4 | 8.4 | 8.4 | 8.6 | 0.1
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-13 | 300-PW-44003-01C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21855 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 12.85 | CML-13 | CML: Reducer | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 12.7 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 12.8 | 12.8 | 12.7 | 13.1 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1663 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 10.45 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.6 | 9 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.9 | 10.9 | 10.4 | 9.6 | 0.61373
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-15 | 300-PW-44002-01X01-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 22032 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 10.05 | CML-15 | CML: Elbow | 6 | 2048-02-17 | 2044-02-09 | 2014-10-17 07:00 | 2.5 | 0.22482 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 10 | 9 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.2 | 10 | 10 | 10 | 0.1
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40401-01C02 | CML-4 | 200-WC-40401-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7920 |  | 2015-01-17 08:00 | 2015-01-17 09:00 |  |  | Administrator | 2015-09-08 11:21 | [32 empty] | 10.225 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-17 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.6 | 9 O'Clock | 200 | 6.35 | 200-WC-40401-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.7 | 10.5 | 10.1 | 9.6 | 0.48563
FL02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-FL-43454-01C02-P | CML-9 | 50-FL-43454-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20389 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 9.225 | CML-9 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.1 | 12 O'Clock | 100 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.3 | 9.3 | 9.2 | 0.095743
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-14 | 50-PG-23024-03C03 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 10046 | Rope Access | 2014-01-06 | 2014-01-06 | [36 empty] | 8.725 | CML-14 | CML: Pipe Length | 6 | 2046-09-10 | 2042-11-26 | 2014-01-06 | 0.97 | 0.23333 | A2: Right Quadrant |  | 2.74 | 0.97 | 1.855 | 8.6 | 3 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.63 |  | 8.8 | 8.6 | 8.7 | 8.8 | 0.095743
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-19 | 50-PL-23042-09C03 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10084 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.725 | CML-19 | CML: type TBC | 6 | 2021-05-09 | 2020-02-29 | 2013-11-07 | 2.5 | 1.0789 | A4: Left Quadrant |  | 5.07 | 2.5 | 3.785 | 10.6 | 9 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.7 | 10.8 | 10.8 | 10.6 | 0.095743
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-9 | 50-PL-23042-09C03 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10074 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.725 | CML-9 | CML: type TBC | 6 | 2021-05-09 | 2020-02-29 | 2013-11-07 | 2.5 | 1.0789 | A3: Inside Quadrant |  | 5.07 | 2.5 | 3.785 | 10.6 | 6 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.8 | 10.7 | 10.6 | 10.8 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-12 | 150-WC-40006-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1672 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 9.75 | CML-12 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.6 | 12 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.6 | 9.7 | 9.7 | 10 | 0.17321
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-6 | 250-PW-44007-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1963 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 11 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 11:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.2 | 9 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.7 | 12.4 | 10.7 | 10.2 | 0.96264
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-11 | 50-FL-43454-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1883 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.175 | CML-11 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.1 | 9.2 | 9.3 | 0.095743
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-10 | 250-PW-44509-01C03-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22995 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 13.075 | CML-10 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2015-05-05 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 12.8 | 9 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.3 | 0.18528 | 13.3 | 13.4 | 12.8 | 12.8 | 0.32016
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-21 | 50-PL-23300-09C03 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 13137 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.325 | CML-21 | CML: type TBC | 6 | 2019-11-14 | 2018-12-26 | 2014-02-04 07:00 | 2.81 | 1.2789 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.2 | 6 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.39 |  | 10.4 | 10.4 | 10.2 | 10.3 | 0.095743
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-20 | 50-PL-23300-09C03 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 13136 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.675 | CML-20 | CML: type TBC | 6 | 2025-05-12 | 2023-09-23 | 2014-02-04 07:00 | 2.81 | 0.69092 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.6 | 6 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.79 |  | 10.6 | 10.7 | 10.6 | 10.8 | 0.095743
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-34 | 300-PF-20500-03C03-P CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 21654 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.325 | CML-34 | CML: Pipe Length | 6 | 2190-07-15 | 2158-09-07 | 2014-09-27 07:00 | 4.9 | 0.05287 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.4 | 14.4 | 14.2 | 14.3 | 0.095743
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-24 | 300-PG-20005-03C03-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 6180 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.325 | CML-24 | CML: Reducing Tee | 6 | 2161-12-15 | 2135-03-31 | 2014-07-11 07:30 | 4.9 | 0.06304 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.3 | 14.2 | 14.4 | 14.4 | 0.095743
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44033-01C02-P | CML-1 | 80-PW-44033-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23263 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 11.775 | CML-1 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.7 | 6 O'Clock | 80 | 5.49 | 80-PW-44033-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 | -0.16977 | 11.7 | 11.7 | 11.7 | 12 | 0.15
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80005-01C02 | CML-4 | 50-VA-80005-01C02 CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 3130 | Rope Access | 2014-05-02 10:30 | 2014-05-02 11:30 | [36 empty] | 4.825 | CML-4 | CML: type TBC | 3 | 2016-09-26 | 2017-02-04 | 2014-05-02 10:30 | 2.5 | 0.91403 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-VA-80005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.8 | 4.9 | 4.7 | 4.9 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-9 | 150-WC-40006-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1669 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 10.25 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 9 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10.8 | 10.4 | 10.1 | 9.7 | 0.46547
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38300-01C02-P |  | 50-CG-38300-01C02-P | yes | FPSO 2014 | Pipe Wall Thickness | 22094 | Rope access | 2014-06-02 08:00 | 2014-06-02 09:00 |  |  | Administrator | 2015-09-07 10:57 | [32 empty] | 5.125 | 50-CG-38300-01C02-P | Piping | 3 | 2019-01-23 |  | 2014-06-02 08:00 |  | 0.53803 | A4: Left Quadrant |  |  | 2.5 |  | 5 | 9 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 5 | 5.1 | 5.2 | 5.2 | 5 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-18 | 300-PW-44002-01X01-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 22864 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.575 | CML-18 | CML: Reducer | 6 | 587572 | 524286 | 2015-05-01 07:00 | 2.5 | 0.00522 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 10.3 | 9 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 | 0.37245 | 10.4 | 11 | 10.6 | 10.3 | 0.30957
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-22 | 250-PW-44006-01X01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 8014 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 11 | CML-22 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-01-20 08:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.4 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 | 0.85149 | 11.6 | 11.2 | 10.8 | 10.4 | 0.5164
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-9 | 250-PW-44007-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1966 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 10.925 | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.4 | 12 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 11 | 11.1 | 11.2 | 0.3594
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-17 | 300-PW-44002-01X01-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 22863 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.95 | CML-17 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 10.5 | 9 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | -1.1173 | 10.8 | 10.9 | 11.6 | 10.5 | 0.46547
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-18 | 300-PW-44002-01X01-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 22035 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 11.05 | CML-18 | CML: Reducer | 6 | 2091-07-06 | 2082-06-18 | 2014-10-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 10.5 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11.1 | 10.5 | 11 | 11.6 | 0.45092
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38482-01C02 | CML-7 | 25-CG-38482-01C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10382 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.625 | CML-7 | CML: type TBC | 3 | 2015-06-13 | 2015-06-08 | 2013-11-12 | 2.5 | 1.8918 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 9 O'Clock | 25 | 6.35 | 25-CG-38482-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 5.5 | 5.6 | 5.7 | 5.7 | 5.5 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-10 | 80-FH-43005-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12560 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 5.675 | CML-10 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-20 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 9 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.8 | 5.6 | 5.6 | 0.095743
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38494-01C02 | CML-3 | 25-CG-38494-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10386 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.675 | CML-3 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 9 O'Clock | 25 | 6.35 | 25-CG-38494-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.7 | 5.8 | 5.6 | 5.6 | 0.095743
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38482-01C02 | CML-3 | 25-CG-38482-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10378 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.675 | CML-3 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 9 O'Clock | 25 | 6.35 | 25-CG-38482-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.7 | 5.8 | 5.6 | 5.6 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56014-01C02 | CML-5 | 50-DH-56014-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22327 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 5.825 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.9 | 5.7 | 5.9 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56014-01C02 | CML-5 | 50-DH-56014-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1847 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 5.825 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.9 | 5.7 | 5.9 | 0.095743
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-22 | 80-PW-44016-01C02-P CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 22924 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 12.2 | CML-22 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.8 | 3 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.5 | 11.8 | 12 | 12.5 | 0.3559
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-8 | 100-FH-43104-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12759 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 6.175 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 9 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.3 | 6.2 | 6.1 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-16 | 300-PW-44002-01X01-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 22862 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.6 | CML-16 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.5 | 9 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | -1.676 | 10.6 | 10.8 | 10.5 | 10.5 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-6 | 400-WC-40022-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1100 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 10.275 | CML-6 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 9.8 | 12 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.8 | 10.8 | 10.4 | 10.1 | 0.4272
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-1 | 300-PL-20011-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 23786 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 10.375 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 10 | 9 O'Clock | 350 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.3 | 10 | 11.2 | 10 | 0.56789
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-2 | 80-PW-44011-01X01-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22800 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 10.9 | CML-2 | CML: Pipe Length | 6 | 2051-10-14 | 2045-12-09 | 2015-04-30 07:00 | 2.5 | 0.22476 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.7 | 12 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 | 0.39388 | 10.7 | 10.8 | 11.2 | 10.9 | 0.21602
CG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12510 |  | 2014-02-04 16:00 | 2014-02-04 17:00 | Check Corrosion Rate of 0.426mm/ yr | [35 empty] | 5.325 | CML-8 | CML: Pipe Length | 3 | 2025-01-13 | 2023-07-21 | 2014-02-04 16:00 | 0.54 | 0.42567 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 9 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 5.4 | 5.4 | 5.3 | 5.2 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-16 | 80-FH-43007-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12577 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.875 | CML-16 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-01-18 07:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.8 | 9 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.26 |  | 5.8 | 6 | 5.9 | 5.8 | 0.095743
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-11 | 50-FG-45020-03C02 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10583 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.125 | CML-11 | CML: type TBC | 3 | 2016-01-08 | 2016-01-02 | 2013-11-17 | 2.5 | 1.1663 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.2 | 5.1 | 0.095743
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-13 | 50-FG-45020-03C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2612 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.125 | CML-13 | CML: type TBC | 3 | 2018-06-29 | 2018-06-17 | 2014-04-26 09:30 | 2.5 | 0.59837 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -1.1378 | 5.1 | 5.2 | 5 | 5.2 | 0.095743
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38477-01C02-P | CML-2 | 50-CG-38477-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20894 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.125 | CML-2 | CML: type TBC | 3 | 2017-03-30 | 2017-03-20 | 2014-10-04 07:00 | 2.5 | 1.005 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 6 O'Clock | 25 | 6.35 | 25-CG-38477-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.2 | 5 | 5.1 | 0.095743
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H |  | 50-CG-38454-01C02-H |  | FPSO 2015 | Pipe Wall Thickness | 23682 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.175 | 50-CG-38454-01C02-H | Piping | 3 | 2030-01-31 |  | 2015-10-30 07:00 |  | 0.18223 | A1: Outside Quadrant |  |  | 2.5 |  | 5.1 | 6 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 5.1 | 5.2 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-8 | 80-PW-44011-01X01-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22806 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 11.075 | CML-8 | CML: Equal Tee | 6 | 2085-02-24 | 2074-03-21 | 2015-04-30 07:00 | 2.5 | 0.12022 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 9 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | 0.39388 | 10.9 | 11.3 | 11.2 | 10.9 | 0.20616
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-30 | 50-FG-45501-01C02 CML-30 | Yes | FPSO 2015 | Pipe Wall Thickness | 23549 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 5.375 | CML-30 | CML: Elbow | 3 | 2041-03-03 | 2044-02-24 | 2015-08-10 07:30 | 2.5 | 0.10946 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 5.3 | 5.4 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1648 |  | 2014-04-12 07:30 | 2014-04-12 08:45 | [36 empty] | 9.7667 | CML-7 | CML: Equal Tee | 3 | 2059-07-07 | 2055-11-27 | 2014-04-12 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.7 | 3 O'Clock | 150 | 7.11 | 150-WC-40006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.8 | 9.7 | 9.8 |  | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43123-01C02 | CML-3 | 50-FH-43123-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1779 |  | 2014-04-28 14:30 | 2014-04-28 15:00 | [36 empty] | 5.375 | CML-3 | CML: Pipe Length | 3 | 2024-11-30 | 2026-02-24 | 2014-04-28 14:30 | 2.5 | 0.26417 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-FH-43123-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 5.3 | 5.4 | 0.095743
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-17 | 50-FG-45501-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6600 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.625 | CML-17 | CML: Pipe Length | 3 | 2152-04-07 | 2167-03-02 | 2015-03-30 07:00 | 2.5 | 0.02188 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.7 | 5.5 | 5.7 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-7 | 50-FH-43016-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12606 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.625 | CML-7 | CML: Pipe Length | 3 | 2062-08-20 | 2067-12-01 | 2014-01-23 13:00 | 2.5 | 0.06172 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.7 | 5.5 | 5.7 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44024-01X01-P | CML-1 | 80-PW-44024-01X01-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22896 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 11.225 | CML-1 | CML: Reducer | 6 | 2140-07-07 | 2121-02-23 | 2015-05-01 07:00 | 2.5 | 0.06785 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 11 | 9 O'Clock | 80 | 11.13 | 80-PW-44024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 | 0.65412 | 11.8 | 11 | 11.1 | 11 | 0.38622
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-4 | 50-CG-38458-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23732 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.675 | CML-4 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 100 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.6 | 5.6 | 5.7 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56083-01C02 | CML-7 | 100-DH-56083-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22532 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.875 | CML-7 | CML: Pipe Length | 3 | 2043-07-26 | 2044-07-24 | 2015-04-20 07:00 | 2.5 | 0.11667 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 6 O'Clock | 100 | 6.02 | 100-DH-56083-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.8 | 5.8 | 5.9 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43179-01C02 | CML-1 | 80-FH-43179-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2345 | Rope Access | 2014-03-17 11:30 | 2014-03-17 12:00 | [36 empty] | 6.125 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-17 11:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 3 O'Clock | 80 | 5.49 | 80-FH-43179-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.2 | 6.1 | 0.095743
FG02 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8528 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.125 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.2 | 6.2 | 6.1 | 0.095743
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-3 | 25-PW-44026-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22735 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 6.125 | CML-3 | CML: Equal Tee | 3 | 2034-05-21 | 2034-03-26 | 2015-04-28 07:00 | 2.5 | 0.18347 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 25 | 6.35 | 25-PW-44026-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6.2 | 6.2 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43101-01C02 | CML-5 | 100-FH-43101-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12744 |  | 2014-01-24 07:00 | 2014-01-24 08:00 | [36 empty] | 6.175 | CML-5 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2014-01-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 6 O'Clock | 100 | 6.02 | 100-FH-43101-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.3 | 6.1 | 6.1 | 6.2 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40063-01C02-P | CML-7 | 50-WC-40063-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2111 | Rope Access | 2014-03-28 14:00 | 2014-03-28 15:00 | Check Corrosion Rate of 0.899mm/ yr | [35 empty] | 5.25 | CML-7 | CML: type TBC | 3 | 2016-10-17 | 2017-02-27 | 2014-03-28 14:00 | 2.5 | 0.89859 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.4 | 5.5 | 5.3 | 0.31091
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40063-01C02-P | CML-3 | 50-WC-40063-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2107 | Rope Access | 2014-03-28 14:00 | 2014-03-28 15:00 | Check Corrosion Rate of 0.777mm/ yr | [35 empty] | 5.325 | CML-3 | CML: type TBC | 3 | 2017-04-28 | 2017-09-28 | 2014-03-28 14:00 | 2.5 | 0.77716 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-WC-40063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 5.7 | 4.9 | 5.3 | 0.3304
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-13 | 50-WC-40063-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 13013 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 20.25 | CML-13 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 19.3 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.75 |  | 20.4 | 21.2 | 20.1 | 19.3 | 0.78528
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-14 | 50-WC-40063-01C02-P CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10110 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 16.65 | CML-14 | CML: Pipe Length | 6 | 2103-11-30 | 2088-08-29 | 2013-11-07 | 5.22 | 0 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 16 | 12 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 16 | 16.8 | 17.1 | 16.7 | 0.46547
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-9 | 50-WC-40063-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20696 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21.025 | CML-9 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A2: Right Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21.1 | 21 | 21 | 21 | 0.05
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-8 | 50-WC-40063-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20695 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-8 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-7 | 50-WC-40063-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20694 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-7 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-6 | 50-WC-40063-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20693 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-6 | CML: Equal Tee | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-2 | 50-WC-40063-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20689 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-2 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-1 | 50-WC-40063-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20688 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-1 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-11 | 50-WC-40063-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20698 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-11 | CML: Equal Tee | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-10 | 50-WC-40063-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20697 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-10 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-27 | 50-WC-40063-01C02-P CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 20714 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-27 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-26 | 50-WC-40063-01C02-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 20713 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-26 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-25 | 50-WC-40063-01C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 20712 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-25 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-24 | 50-WC-40063-01C02-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 20711 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-24 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-23 | 50-WC-40063-01C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 20710 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-23 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-21 | 50-WC-40063-01C02-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 20708 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-21 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-18 | 50-WC-40063-01C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 20705 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-18 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-28 | 50-WC-40063-01C02-P CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 20715 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 21 | CML-28 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 13:00 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-2 | 50-WC-40063-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20721 | Protective mesh removed | 2014-06-30 10:30 | 2014-06-30 12:00 | [36 empty] | 21 | CML-2 | CML: Reducer | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 10:30 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 100 | 20.62 | 200-PG-23014-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-1 | 50-WC-40063-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20720 | Protective mesh removed | 2014-06-30 10:30 | 2014-06-30 12:00 | [36 empty] | 21 | CML-1 | CML: Reducing Tee | 6 | 2117-05-30 | 2095-05-30 | 2014-06-30 10:30 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21 | 9 O'Clock | 200 | 20.62 | 200-PG-23014-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.78 |  | 21 | 21 | 21 | 21 | 0
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-1 | 50-WC-40063-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6507 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 17.375 | CML-1 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-24 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 17 | 3 O'Clock | 300 | 14.27 | 300-PF-20509-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.1 |  | 17.7 | 17 | 17.1 | 17.7 | 0.37749
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-5 | 50-WC-40063-01C02-P CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 23838 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 21.075 | CML-5 | CML: Elbow | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A4: Left Quadrant |  | 15.26 | 9.3 | 12.28 | 20.1 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.8 |  | 20.9 | 20.9 | 22.4 | 20.1 | 0.96047
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40063-01C02-P | CML-2 | 50-WC-40063-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2106 | Rope Access | 2014-03-28 14:00 | 2014-03-28 15:00 | Check Corrosion Rate of 0.656mm/ yr | [35 empty] | 5.175 | CML-2 | CML: type TBC | 3 | 2018-01-18 | 2018-07-18 | 2014-03-28 14:00 | 2.5 | 0.65572 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-WC-40063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5.1 | 5.5 | 0.22174
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-27 | 50-WC-40063-01C02-P CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 20011 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 21.25 | CML-27 | CML: type TBC | 6 | 2117-05-30 | 2095-05-30 | 2014-01-10 | 10.22 | 0 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 21.1 | 9 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.88 |  | 21.2 | 21.5 | 21.2 | 21.1 | 0.17321
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40063-01C02-P | CML-4 | 50-WC-40063-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2108 | Rope Access | 2014-03-28 14:00 | 2014-03-28 15:00 | Check Corrosion Rate of 0.534mm/ yr | [35 empty] | 5.55 | CML-4 | CML: type TBC | 3 | 2019-02-06 | 2019-09-17 | 2014-03-28 14:00 | 2.5 | 0.53429 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-WC-40063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.5 | 5.7 | 5.1 | 5.9 | 0.34157
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40063-01C02-P | CML-3 | 50-WC-40063-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8668 | Material Class Not Selectable.Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Feb. 2020). RBI to be updated | 2015-02-12 13:00 | 2015-02-12 14:00 |  |  | Administrator | 2015-09-08 10:33 | [32 empty] | 13.725 | CML-3 | CML: Elbow | 3 | 2115-05-31 | 2079-05-31 | 2015-02-12 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 9.7 | 2.5 | 6.1 | 13.4 | 6 O'Clock | 200 | 12.7 | 200-WC-40508-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 13.8 | 13.5 | 13.4 | 14.2 | 0.3594
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40063-01C02-P | CML-2 | 50-WC-40063-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8625 | Rope Access / Material Class Not Selectable. Line is FFS. Action: to recheck in a year(Feb. 2016) to confirm CR. | 2015-02-10 07:00 | 2015-02-10 08:00 | Check Corrosion Rate of 0.996mm/ yr |  | Administrator | 2015-09-08 10:06 | [32 empty] | 15.375 | CML-2 | CML: Elbow | 3 | 2026-01-17 | 2021-03-27 | 2015-02-10 07:00 | 2.5 | 0.99606 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 13.4 | 12 O'Clock | 250 | 15.09 | 250-WC-40506-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 13.4 | 16.5 | 16.4 | 15.2 | 1.4431
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-3 | 50-WC-40063-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21569 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9 | CML-3 | CML: type TBC | 6 | 2038-12-31 | 2038-07-04 | 2014-05-26 09:30 | 2.5 | 0.24374 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 9.1 | 9 | 9.4 | 0.37417
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-2 | 50-WC-40063-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7747 |  | 2015-01-10 13:00 | 2015-01-10 16:00 | [36 empty] | 8.55 | CML-2 | CML: Elbow | 6 | 2027-01-01 | 2026-09-28 | 2015-01-10 13:00 | 2.5 | 0.45893 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 12 O'Clock | 50 | 8.74 | 50-PF-20504-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.7 | 8.7 | 8.8 | 0.36968
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-17 | 50-WC-40063-01C02-P CML-17 | Yes | FPSO 2014 | Pipe Wall Thickness | 23850 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 21 | CML-17 | CML: Fitting | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A2: Right Quadrant |  | 15.26 | 9.3 | 12.28 | 20.2 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 21.8 | 20.2 | 21.8 | 20.2 | 0.92376
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-15 | 50-WC-40063-01C02-P CML-15 | Yes | FPSO 2014 | Pipe Wall Thickness | 23848 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 20.725 | CML-15 | CML: Equal Tee | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A4: Left Quadrant |  | 15.26 | 9.3 | 12.28 | 20.2 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 20.9 | 20.9 | 20.9 | 20.2 | 0.35
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-13 | 50-WC-40063-01C02-P CML-13 | Yes | FPSO 2014 | Pipe Wall Thickness | 23846 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 20.525 | CML-13 | CML: Elbow | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 20.2 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 20.2 | 20.8 | 20.9 | 20.2 | 0.37749
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-11 | 50-WC-40063-01C02-P CML-11 | Yes | FPSO 2014 | Pipe Wall Thickness | 23844 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 21.075 | CML-11 | CML: Elbow | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A3: Inside Quadrant |  | 15.26 | 9.3 | 12.28 | 20.2 | 6 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 20.8 | 22.4 | 20.2 | 20.9 | 0.93586
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-1 | 50-WC-40063-01C02-P CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 23834 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 20.7 | CML-1 | CML: Reducer | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 20.2 | 12 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 20.2 | 20.8 | 20.9 | 20.9 | 0.33665
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-43 | 50-WC-40063-01C02-P CML-43 |  | FPSO 2014 | Pipe Wall Thickness | 21781 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.35 | CML-43 | CML: Fitting | 6 | 2047-03-15 | 2041-02-15 | 2014-10-01 07:00 | 4.9 | 0.27714 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.7 | 14.6 | 14.2 | 13.9 | 0.36968
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40063-01C02-P | CML-1 | 50-WC-40063-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2105 | Rope Access | 2014-03-28 14:00 | 2014-03-28 15:00 | [36 empty] | 5.725 | CML-1 | CML: type TBC | 3 | 2023-11-03 | 2024-12-15 | 2014-03-28 14:00 | 2.5 | 0.29143 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 6 | 5.8 | 5.3 | 0.29861
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-23 | 50-WC-40063-01C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 6179 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 16.975 | CML-23 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 15.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 17.8 | 16.7 | 17.6 | 15.8 | 0.91788
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-9 | 50-WC-40063-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5863 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 14.75 | CML-9 | CML: Cap End | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 10:30 | 3.3 | 0 | A2: Right Quadrant |  | 6.7 | 3.3 | 5 | 14.2 | 3 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 14.3 | 14.2 | 14.9 | 15.6 | 0.6455
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-25 | 50-WC-40063-01C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 13239 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 17.775 | CML-25 | CML: type TBC | 6 | 2107-02-11 | 2090-04-05 | 2014-02-04 15:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 15.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 16.3 | 17 | 22 | 15.8 | 2.8593
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40063-01C02-P | CML-6 | 50-WC-40063-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2110 | Rope Access | 2014-03-28 14:00 | 2014-03-28 15:00 | [36 empty] | 5.65 | CML-6 | CML: type TBC | 3 | 2031-04-14 | 2033-03-15 | 2014-03-28 14:00 | 2.5 | 0.17 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.9 | 5.9 | 5.4 | 0.28868
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-6 | 50-WC-40063-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21381 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | [36 empty] | 17.15 | CML-6 | CML: Elbow | 6 | 2102-10-24 | 2088-02-10 | 2014-06-29 13:00 | 5.33 | 0 | A3: Inside Quadrant |  | 8.27 | 5.33 | 6.8 | 16.3 | 6 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.97 |  | 17.9 | 17.5 | 16.3 | 16.9 | 0.7
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-21 | 50-WC-40063-01C02-P CML-21 | yes | FPSO 2014 | Pipe Wall Thickness | 20005 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 23.1 | CML-21 | CML: type TBC | 6 | 2117-05-30 | 2095-05-30 | 2014-01-10 | 10.22 | 0 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 21.2 | 9 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.98 |  | 22.7 | 24 | 24.5 | 21.2 | 1.4765
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-4 | 50-WC-40063-01C02-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 10988 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 22.75 | CML-4 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-01-10 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 21.2 | 12 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.98 |  | 21.2 | 24.4 | 22.7 | 22.7 | 1.3077
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-6 | 50-WC-40063-01C02-P CML-6 | yes | FPSO 2013 | Pipe Wall Thickness | 10102 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 17.1 | CML-6 | CML: Pipe Length | 6 | 2103-11-30 | 2088-08-29 | 2013-11-07 | 5.22 | 0 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 16.2 | 6 O'Clock | 40 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.98 |  | 16.6 | 16.9 | 16.2 | 18.7 | 1.1045
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-WC-40063-01C02-P | CML-3 | 50-WC-40063-01C02-P CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10099 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 16.825 | CML-3 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2013-11-07 | 5.22 | 0 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 16.2 | 6 O'Clock | 40 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.98 |  | 16.9 | 17 | 16.2 | 17.2 | 0.43493
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-47 | 50-WC-40063-01C02-P CML-47 |  | FPSO 2014 | Pipe Wall Thickness | 21785 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 20.9 | CML-47 | CML: Reducer | 6 | 2057-02-10 | 2065-04-06 | 2014-10-01 07:00 | 9.9 | 0 | A1: Outside Quadrant |  | 8.27 | 9.9 | 9.085 | 20.9 | 9 O'Clock | 600 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11 |  | 20.9 | 20.9 | 20.9 | 20.9 | 0
RP01 | Montara_Topside | No | Separation (20) | Pipework | 50-WC-40063-01C02-P | CML-37 | 50-WC-40063-01C02-P CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 23497 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 14 | CML-37 | CML: Pipe Length | 6 | 2048-10-20 | 2042-06-10 | 2015-07-27 07:00 | 4.9 | 0.2646 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | -0.60231 | 14.4 | 13.7 | 13.7 | 14.2 | 0.3559
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40063-01C02-P | CML-5 | 50-WC-40063-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2109 | Rope Access | 2014-03-28 14:00 | 2014-03-28 15:00 | [36 empty] | 5.825 | CML-5 | CML: type TBC | 3 | 2031-04-14 | 2033-03-15 | 2014-03-28 14:00 | 2.5 | 0.17 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-WC-40063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 5.8 | 6.3 | 0.36856
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-12 | 50-WC-40081-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1228 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.6 | CML-12 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A3: Inside Quadrant |  | 2.54 |  |  | 6.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.7 | 6.6 | 6.3 | 6.8 | 0.21602
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-25 | 50-FG-45023-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 1173 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.625 | CML-25 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.7 | 6.7 | 6.6 | 0.095743
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-1 | 50-FG-45024-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1184 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.625 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.7 | 6.5 | 6.6 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43407-01C02 | CML-4 | 150-FH-43407-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7950 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-18 07:00 | 2015-01-18 08:00 |  |  | Administrator | 2015-09-08 13:27 | [32 empty] | 7.325 | CML-4 | CML: Pipe Length | 3 | 2059-07-07 | 2055-11-27 | 2015-01-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 6 O'Clock | 150 | 7.11 | 150-FH-43407-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.4 | 7.4 | 7.2 | 7.3 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-11 | 50-WC-40081-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1227 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.2 | CML-11 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A3: Inside Quadrant |  | 2.54 |  |  | 5.6 | 6 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.2 | 6.4 | 5.6 | 6.6 | 0.43205
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-47 | 350-FL-43512-01C02 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 23558 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.825 | CML-47 | CML: Pipe Length | 3 | 2067-05-25 | 2060-04-10 | 2015-08-10 07:30 | 2.5 | 0.10034 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.7 | 3 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.9 | 7.7 | 7.9 | 7.8 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43460-01C02 | CML-2 | 80-FL-43460-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2967 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.875 | CML-2 | CML: Elbow | 3 | 2062-11-29 | 2056-08-05 | 2014-05-01 14:00 | 0.54 | 0 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.8 | 9 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.26 | 0 | 5.9 | 5.8 | 6 | 5.8 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43460-01C02 | CML-2 | 80-FL-43460-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22246 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.875 | CML-2 | CML: Elbow | 3 | 2062-11-29 | 2056-08-05 | 2014-05-01 14:00 | 0.54 | 0 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.8 | 9 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.26 |  | 5.9 | 5.8 | 6 | 5.8 | 0.095743
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-48 | 150-FH-43141-01C02 CML-48 | yes | FPSO 2015 | Pipe Wall Thickness | 6034 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.525 | CML-48 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.6 | 3.6 | 3.4 | 3.5 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-10 | 50-WC-40081-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1226 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.475 | CML-10 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A3: Inside Quadrant |  | 2.54 |  |  | 6.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.4 | 6.5 | 6.3 | 6.7 | 0.17078
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-9 | 50-WC-40081-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1225 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 8.3333 | CML-9 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A1: Outside Quadrant |  | 2.54 |  |  | 7.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 7.8 |  | 8 | 9.2 | 0.75719
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-13 | 50-WC-40081-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1229 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 9.8 | CML-13 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A4: Left Quadrant |  | 2.54 |  |  | 9.7 | 9 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 9.8 | 9.8 | 9.9 | 9.7 | 0.08165
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-1 | 50-WC-40081-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1217 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.575 | CML-1 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A3: Inside Quadrant |  | 2.54 |  |  | 6.5 | 9 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.6 | 6.7 | 6.5 | 6.5 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-8 | 50-WC-40081-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1224 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.575 | CML-8 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A2: Right Quadrant |  | 2.54 |  |  | 6.5 | 3 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.6 | 6.5 | 6.6 | 6.6 | 0.05
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-29 | 150-FH-43141-01C02 CML-29 | yes | FPSO 2015 | Pipe Wall Thickness | 6104 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.475 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.6 | 3.4 | 3.4 | 3.5 | 0.095743
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-26 | 150-FH-43141-01C02 CML-26 | yes | FPSO 2015 | Pipe Wall Thickness | 6101 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.475 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.6 | 3.4 | 3.5 | 0.095743
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-13 | 150-FH-43141-01C02 CML-13 | yes | FPSO 2015 | Pipe Wall Thickness | 5930 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.475 | CML-13 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.5 | 3.6 | 3.4 | 0.095743
FL01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FL-43174-01C02 | CML-12 | 150-FL-43174-01C02 CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 7884 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:43 | [32 empty] | 3.525 | CML-12 | CML: Elbow | 3 | 2015-09-20 | 2015-12-19 | 2015-01-14 10:30 | 2.5 | 1.3184 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 12 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.6 | 3.5 | 3.6 | 0.095743
FL01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FL-43174-01C02 | CML-9 | 150-FL-43174-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23296 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.575 | CML-9 | CML: Pipe Length | 3 | 2016-07-12 | 2016-11-11 | 2015-07-04 09:30 | 2.5 | 0.97538 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.5 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 | -0.2135 | 3.7 | 3.6 | 3.5 | 3.5 | 0.095743
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-2 | 150-FG-45505-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22338 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 25.925 | CML-2 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.8 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8 | 8 | 7.8 | 7.9 | 0.095743
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-16 | 80-DH-56004-01C02 CML-16 | yes | FPSO 2015 | Pipe Wall Thickness | 6894 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.425 | CML-16 | CML: type TBC | 0.5 | 2022-08-19 | 2020-04-29 | 2015-04-05 07:00 | 3.5 | 0.10842 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4.3 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.3 | 4.5 | 4.4 | 4.5 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-7 | 50-WC-40081-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1223 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.45 | CML-7 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A2: Right Quadrant |  | 2.54 |  |  | 6.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.5 | 6.4 | 6.5 | 6.4 | 0.057735
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23409-01C03 | CML-4 | 100-PG-23409-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20769 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 14.35 | CML-4 | CML: Pipe Length | 6 | 2098-02-09 | 2085-10-05 | 2014-10-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 13.8 | 9 O'Clock | 150 | 10.97 | 100-PG-23409-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 13.9 | 14 | 15.7 | 13.8 | 0.9037
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-15 | 80-DH-56004-01C02 CML-15 | yes | FPSO 2015 | Pipe Wall Thickness | 6893 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.425 | CML-15 | CML: type TBC | 0.5 | 2022-08-19 | 2020-04-29 | 2015-04-05 07:00 | 3.5 | 0.10842 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4.3 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.5 | 4.4 | 4.5 | 4.3 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-2 | 80-PW-44011-01X01-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21873 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 11.15 | CML-2 | CML: Pipe Length | 6 | 2089-10-20 | 2078-03-01 | 2014-07-26 07:00 | 2.5 | 0.1129 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 11 | 12 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11 | 11.3 | 11.2 | 11.1 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43450-01C02 | CML-1 | 50-FH-43450-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10668 | Deck Level.High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.9583 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 16:18 | [32 empty] | 4.925 | CML-1 | CML: Elbow | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 5 | 5 | 4.8 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40403-01C02 | CML-8 | 100-WC-40403-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20388 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 10.2 | CML-8 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.8 | 6 O'Clock | 100 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.5 | 10.2 | 9.8 | 10.3 | 0.29439
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-13 | 100-DH-56086-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20972 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 5.075 | CML-13 | CML: type TBC | 3 | 2016-09-19 | 2016-10-29 | 2014-05-16 13:00 | 2.5 | 1.0651 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5.2 | 5 | 0.095743
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38455-01C02-H | CML-2 | 50-CG-38455-01C02-H CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 23686 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.225 | CML-2 | CML: Reducing Tee | 3 | 2030-01-31 | 2031-11-16 | 2015-10-30 07:00 | 2.5 | 0.18223 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-CG-38455-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 5.2 | 5.3 | 0.095743
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-9 | 50-CG-38457-01C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23727 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.225 | CML-9 | CML: Fitting | 3 | 2030-01-31 | 2031-11-16 | 2015-10-30 07:00 | 2.5 | 0.18223 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.1 | 5.3 | 5.3 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-6 | 50-WC-40081-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1222 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.725 | CML-6 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A3: Inside Quadrant |  | 2.54 |  |  | 6.5 | 6 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 7.1 | 6.6 | 6.5 | 6.7 | 0.263
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-22 | 250-PW-44006-01X01 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 1919 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 11.875 | CML-22 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.1 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 12.2 | 12.8 | 11.4 | 11.1 | 0.7719
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-8 | 80-PW-44011-01X01-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21879 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 11.525 | CML-8 | CML: Equal Tee | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 11.2 | 9 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.4 | 11.8 | 11.7 | 11.2 | 0.27538
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44002-01X01-P | CML-9 | 300-PW-44002-01X01-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 22026 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 11.425 | CML-9 | CML: Equal Tee | 6 | 2091-07-06 | 2082-06-18 | 2014-10-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 11.2 | 3 O'Clock | 300 | 10.31 | 300-PW-44002-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.7 | 11.2 | 11.3 | 11.5 | 0.22174
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-8 | 50-FG-45020-03C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10580 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.275 | CML-8 | CML: type TBC | 3 | 2017-07-21 | 2017-07-11 | 2013-11-17 | 2.5 | 0.73432 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.2 | 5.2 | 5.4 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-5 | 50-WC-40081-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1221 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.4 | CML-5 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A3: Inside Quadrant |  | 2.54 |  |  | 6.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.6 | 6.4 | 6.2 | 6.4 | 0.1633
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-11 | 250-WC-40026-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1287 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 9.95 | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.8 | 6 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.1 | 9.9 | 9.8 | 10 | 0.1291
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-10 | 200-PL-20019-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21261 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 10.35 | CML-10 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.1 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.5 | 10.1 | 10.4 | 10.4 | 0.17321
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-4 | 50-WC-40081-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1220 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.525 | CML-4 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A4: Left Quadrant |  | 2.54 |  |  | 6.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.5 | 6.6 | 6.6 | 6.4 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-3 | 50-WC-40081-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1219 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.525 | CML-3 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A1: Outside Quadrant |  | 2.54 |  |  | 6.5 | 9 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.5 | 6.5 | 6.6 | 6.5 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-21 | 400-WC-40022-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 1115 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 10.35 | CML-21 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 10 | 12 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10 | 10.1 | 10.2 | 11.1 | 0.50662
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-9 | 250-WC-40017-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2072 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 10.35 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 6 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.3 | 10.2 | 9.9 | 11 | 0.46547
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40081-01C02 | CML-2 | 50-WC-40081-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1218 | Rope Access | 2014-03-22 14:30 | 2014-03-22 15:00 | [36 empty] | 6.425 | CML-2 | CML: type TBC | 3 |  |  | 2014-03-22 14:30 |  | 0 | A3: Inside Quadrant |  | 2.54 |  |  | 6.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40081-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.4 | 6.6 | 6.2 | 6.5 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-12 | 50-FH-43137-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22686 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.425 | CML-12 | CML: Reducing Tee | 3 | 2037-07-12 | 2040-02-12 | 2015-04-27 07:00 | 2.5 | 0.12599 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0 | 5.3 | 5.5 | 5.5 | 5.4 | 0.095743
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45040-03C02 | CML-2 | 25-FG-45040-03C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10560 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.725 | CML-2 | CML: type TBC | 3 | 2015-10-11 | 2015-07-08 | 2013-11-16 | 2.5 | 1.6295 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.925 | 5.6 | 3 O'Clock | 25 | 6.35 | 25-FG-45040-03C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 5.8 | 5.8 | 0.095743
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-8 | 50-FG-45302-01C02 CML-8 | Yes | FPSO 2014 | Pipe Wall Thickness | 5776 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 5.775 | CML-8 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 5.7 | 5.7 | 5.8 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-11 | 250-PW-44006-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1908 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 12.675 | CML-11 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-03-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.4 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 12.2 | 14 | 11.4 | 13.1 | 1.1236
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-12 | 25-FG-45455-01C02-E CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1246 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 6.075 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.1 | 6 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43106-01C02 | CML-6 | 100-FH-43106-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12775 |  | 2014-01-25 10:00 | 2014-01-25 11:00 | [36 empty] | 6.075 | CML-6 | CML: type TBC | 3 | 2128-04-20 | 2132-02-05 | 2014-01-25 10:00 | 2.5 | 0.03062 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 9 O'Clock | 100 | 6.02 | 100-FH-43106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.1 | 6 | 6 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40011-01C02 | CML-1 | 50-WC-40011-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1886 | Rope Access | 2014-03-25 13:00 | 2014-03-25 14:00 | [36 empty] | 10.2 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10 | 10.8 | 10.1 | 9.9 | 0.40825
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-7 | 200-FH-43114-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12815 |  | 2014-02-01 12:00 | 2014-02-01 14:00 | [36 empty] | 6.225 | CML-7 | CML: type TBC | 3 | 2023-10-07 | 2023-09-10 | 2014-02-01 12:00 | 2.5 | 0.37169 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.3 | 6.2 | 6.3 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43170-01C02 | CML-2 | 250-FL-43170-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23069 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.275 | CML-2 | CML: Fitting | 3 | 2062-12-23 | 2062-08-13 | 2015-05-07 07:00 | 2.5 | 0.07763 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | -0.096817 | 6.4 | 6.3 | 6.2 | 6.2 | 0.095743
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20016-01C02-P | CML-1 | 200-PL-20016-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21232 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 10.55 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.2 | 12 O'Clock | 300 | 6.35 | 200-PL-20016-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.2 | 10.4 | 11.3 | 10.3 | 0.50662
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-18 | 50-FG-45301-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 5804 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.275 | CML-18 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 6.4 | 6.2 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56064-01C02 | CML-2 | 50-DH-56064-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3272 | Rope Access | 2014-05-09 13:00 | 2014-05-09 14:00 | [36 empty] | 6.425 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-DH-56064-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.4 | 6.5 | 6.3 | 6.5 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-13 | 300-FL-43070-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12706 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.425 | CML-13 | CML: type TBC | 3 | 2065-02-21 | 2064-10-06 | 2014-02-01 09:00 | 2.5 | 0.07438 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 6 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 6.4 | 6.3 | 6.5 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-7 | 250-FH-43303-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12945 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.575 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 9 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.5 | 6.6 | 6.5 | 0.095743
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-2 | 300-PL-20011-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 23787 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 10.45 | CML-2 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.3 | 9 O'Clock | 350 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 10.8 | 10.4 | 10.3 | 0.23805
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-12 | 50-FG-45024-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1195 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.725 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 12 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.7 | 6.8 | 6.8 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-7 | 150-FL-43174-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12905 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.225 | CML-7 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 6 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.3 | 7.2 | 7.1 | 7.3 | 0.095743
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20331 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.275 | CML-2 | CML: Pipe Length | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.4 | 7.3 | 7.2 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40061-01C02 | CML-6 | 400-WC-40061-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1130 |  | 2014-03-21 08:30 | 2014-03-21 09:00 | [36 empty] | 10.4 | CML-6 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 08:30 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 10 | 3 O'Clock | 400 | 7.92 | 400-WC-40061-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.6 | 10 | 10.3 | 10.7 | 0.31623
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43085-01C02 | CML-6 | 350-FL-43085-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10016 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.725 | CML-6 | CML: type TBC | 3 | 2020-08-25 | 2019-09-11 | 2013-11-04 | 2.5 | 0.74872 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.6 | 3 O'Clock | 350 | 7.92 | 350-FL-43085-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.7 | 7.6 | 7.8 | 7.8 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43085-01C02 | CML-2 | 350-FL-43085-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10012 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.775 | CML-2 | CML: type TBC | 3 | 2023-12-09 | 2022-07-20 | 2013-11-04 | 2.5 | 0.51474 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.7 | 6 O'Clock | 350 | 7.92 | 350-FL-43085-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 7.7 | 7.9 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-44 | 400-FH-43508-01C02 CML-44 |  | FPSO 2015 | Pipe Wall Thickness | 23563 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.925 | CML-44 | CML: Pipe Length | 3 | 2112-05-20 | 2099-04-29 | 2015-08-10 07:30 | 2.5 | 0.05473 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 7.8 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8 | 7.9 | 8 | 7.8 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40049-01C02 | CML-5 | 50-WC-40049-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1234 |  | 2014-03-22 08:30 | 2014-03-22 09:00 | [36 empty] | 10.075 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.9 | 12 O'Clock | 50 | 5.54 | 50-WC-40049-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 10.1 | 10 | 10.3 | 0.17078
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-33 | 200-PL-20008-01C02-H CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 8830 | LAGGING REMOVAL REQUIRED, Reducer 200-400Ø | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 9.725 | CML-33 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-02-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 3 O'Clock | 300 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.5 | 9.5 | 10 | 9.9 | 0.263
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-11 | 50-FL-43454-01C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23510 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 7.275 | CML-11 | CML: Pipe Length | 3 | 2074-03-18 | 2063-04-04 | 2015-07-28 07:00 | 1.03 | 0 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.17 | 0.066123 | 7.3 | 7.2 | 7.4 | 7.2 | 0.095743
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-19 | 50-DH-56137-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 5687 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 0.454mm/ yr | [34 empty] | Low alarm breach | 17.075 | CML-19 | CML: Pipe Length | 3 | 2017-12-01 | 2016-01-09 | 2014-06-21 14:00 | 2.5 | 4.203 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 17 | 6 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.5 |  | 17 | 17.2 | 17 | 17.1 | 0.095743
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56141-01C02 | CML-14 | 50-DH-56141-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 5455 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 3.374mm/ yr | [34 empty] | Low alarm breach | 18.225 | CML-14 | CML: Straight | 3 | 2019-01-09 | 2016-08-30 | 2014-05-28 07:00 | 2.5 | 3.3743 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 18.1 | 6 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.6 |  | 18.3 | 18.3 | 18.1 | 18.2 | 0.095743
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45503-01C02 | CML-3 | 50-FG-45503-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 7738 | Line is FFS despite the High CR on CML-1 to 6. Current RBI frequency is 48m. Action: Inspect in 24m. RBI to be updated. | 2015-01-10 08:00 | 2015-01-10 10:00 |  |  | Administrator | 2015-09-21 14:29 | [32 empty] | 4.975 | CML-3 | CML: Pipe Length | 3 | 2021-01-24 | 2021-11-20 | 2015-01-10 08:00 | 2.5 | 0.39705 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-FG-45503-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 4.9 | 5.1 | 5 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56040-01C02 | CML-3 | 80-DH-56040-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20923 | Rope Access | 2014-05-21 07:00 | 2014-05-21 08:00 | [36 empty] | 5.025 | CML-3 | CML: Elbow | 3 | 2018-05-01 | 2018-11-26 | 2014-05-21 07:00 | 2.5 | 0.60783 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-DH-56040-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 5.1 | 5.1 | 0.095743
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45032-03C02 | CML-5 | 100-FG-45032-03C02 CML-5 | yes | FPSO 2013 | Pipe Wall Thickness | 10646 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.525 | CML-5 | CML: type TBC | 3 |  |  | 2013-11-18 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.4 | 6 O'Clock | 100 |  | 100-FG-45032-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.6 | 5.4 | 5.5 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-8 | 150-WC-40006-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1668 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 10.05 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 12 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 10.1 | 10.2 | 10 | 0.1291
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-16 | 400-WC-40022-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1110 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 10.775 | CML-16 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 10.1 | 6 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 11.2 | 11.2 | 10.1 | 10.6 | 0.53151
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44024-01X01-P | CML-1 | 80-PW-44024-01X01-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21899 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 11.675 | CML-1 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.5 | 12 O'Clock | 80 | 11.13 | 80-PW-44024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 11.5 | 11.8 | 11.7 | 11.7 | 0.12583
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5658 | Rope access | 2014-06-21 11:00 | 2014-06-21 12:00 | [36 empty] | 6.475 | CML-1 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2014-06-21 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-FH-43503-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.6 | 6.4 | 6.4 | 0.095743
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23017-03C03-A | CML-8 | 250-PG-23017-03C03-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10982 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 8.625 | CML-8 | CML: type TBC | 6 | 2014-08-13 | 2014-06-13 | 2014-01-09 | 4.4 | 6.9054 | A1: Outside Quadrant |  | 6.7 | 4.4 | 5.55 | 8.5 | 12 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 8.5 | 8.7 | 8.6 | 8.7 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43125-01C02 | CML-5 | 200-FH-43125-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2759 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 6.525 | CML-5 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-13 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.4 | 6 O'Clock | 200 | 6.35 | 200-FH-43125-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.06 |  | 6.6 | 6.6 | 6.4 | 6.5 | 0.095743
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40511-1CG | CML-4 | 300-WC-40511-1CG CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5657 | Material class 1CG | 2014-06-21 10:00 | 2014-06-21 11:00 | [36 empty] | 20.675 | CML-4 | CML: type TBC | 3 | 2163-03-18 | 2103-04-25 | 2014-06-21 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 14.48 | 2.5 | 8.49 | 20.3 | 3 O'Clock | 300 | 17.48 | 300-WC-40511-1CG-S1 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.8 |  | 21 | 20.3 | 20.4 | 21 | 0.37749
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-VA-23057-01C02 | CML-4 | 200-VA-23057-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3148 | Rope Access | 2014-05-02 14:00 | 2014-05-02 15:00 | [36 empty] | 8.075 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-05-02 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 9 O'Clock | 200 | 6.35 | 200-VA-23057-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.1 | 8 | 8 | 0.095743
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-22 | 50-PL-23020-01C03 CML-22 |  | FPSO 2013 | Pipe Wall Thickness | 10136 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.125 | CML-22 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 3 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.1 | 8 | 8.2 | 8.2 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40050-01C02 | CML-1 | 50-WC-40050-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1895 | Rope Access | 2014-03-25 14:00 | 2014-03-25 15:00 | [36 empty] | 10.35 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10 | 6 O'Clock | 50 | 5.54 | 50-WC-40050-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.8 | 10.2 | 10 | 10.4 | 0.34157
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23032-01C03 | CML-1 | 50-PL-23032-01C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20785 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 8.525 | CML-1 | CML: Pipe Length | 6 | 2038-05-09 | 2037-11-15 | 2014-10-10 07:00 | 2.5 | 0.25005 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 6 O'Clock | 50 | 8.74 | 50-PL-23032-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.6 | 8.5 | 8.4 | 8.6 | 0.095743
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-15 | 50-CG-24002-09C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2561 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 8.575 | CML-15 | CML: type TBC | 3 | 2035-03-28 | 2029-07-27 | 2014-04-03 13:00 | 2.5 | 0.28577 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 3 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.5 | 8.7 | 8.6 | 0.095743
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38483-01C02 | CML-6 | 25-CG-38483-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10395 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 8.575 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2013-11-12 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.5 | 6 O'Clock | 25 | 6.35 | 25-CG-38483-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 8.5 | 8.5 | 8.7 | 8.5 | 8.6 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43170-01C02 | CML-1 | 250-FL-43170-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23068 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 8.875 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.8 | 3 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 | 0 | 8.8 | 8.8 | 9 | 8.9 | 0.095743
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-21 | 50-PL-45016-03C03 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10461 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.125 | CML-21 | CML: type TBC | 6 | 2018-02-23 | 2017-08-11 | 2013-11-13 | 0.99 | 1.637 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 8 | 3 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.01 |  | 8.2 | 8 | 8.1 | 8.2 | 0.095743
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-8 | 50-PG-23024-03C03 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10040 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 8.125 | CML-8 | CML: Pipe Length | 6 | 2017-12-16 | 2017-06-10 | 2013-11-06 | 0.97 | 1.7095 | A1: Outside Quadrant |  | 2.74 | 0.97 | 1.855 | 8 | 12 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.03 |  | 8 | 8.1 | 8.2 | 8.2 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-13 | 50-WC-40028-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1693 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 10.35 | CML-13 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10 | 12 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 10.3 | 10.6 | 10.5 | 0.26458
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-13 | 300-PW-44003-01C03 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22878 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 13.45 | CML-13 | CML: Reducer | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 13.2 | 12 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 | -0.94072 | 13.2 | 13.9 | 13.3 | 13.4 | 0.31091
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20044-03C03-P | CML-2 | 80-PG-20044-03C03-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23334 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-19 07:00 | 2015-07-19 15:00 | [36 empty] | 11.025 | CML-2 | CML: Pipe Length | 6 | 2093-05-14 | 2081-03-09 | 2015-07-19 07:00 | 2.5 | 0.10786 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 12 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | -0.47415 | 10.9 | 11 | 11.1 | 11.1 | 0.095743
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-9 | 150-PG-20054-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21520 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 11.025 | CML-9 | CML: Reducer | 6 | 2142-10-18 | 2123-12-07 | 2014-06-26 13:00 | 2.5 | 0.06542 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.9 | 12 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 10.9 | 11.1 | 11 | 11.1 | 0.095743
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-9 | 300-PF-20500-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21629 | Protective mesh removed | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 13.875 | CML-9 | CML: Fitting | 6 | 2039-10-17 | 2035-01-19 | 2014-09-27 07:00 | 4.9 | 0.35496 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14 | 13.8 | 13.8 | 13.9 | 0.095743
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38486-09C02-P | CML-24 | 80-CG-38486-09C02-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 5692 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 1.59mm/ yr | [34 empty] | Low alarm breach | 15.875 | CML-24 | CML: Equal Tee | 3 | 2016-12-16 | 2015-06-20 | 2014-06-21 14:00 | 2.5 | 5.3389 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 15.8 | 6 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.3 |  | 16 | 15.8 | 15.8 | 15.9 | 0.095743
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-22 | 50-FG-45020-03C02 CML-22 |  | FPSO 2013 | Pipe Wall Thickness | 10594 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.025 | CML-22 | CML: type TBC | 3 | 2015-08-12 | 2015-08-07 | 2013-11-17 | 2.5 | 1.3822 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.1 | 5.1 | 4.9 | 0.095743
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1402 | Rope access | 2014-04-05 15:00 | 2014-04-05 16:00 | [36 empty] | 5.475 | CML-3 | CML: type TBC | 3 | 2031-10-06 | 2033-09-24 | 2014-04-05 15:00 | 2.5 | 0.16557 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 5.4 | 5.6 | 0.095743
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-20 | 50-PL-23020-01C03 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10134 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.125 | CML-20 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.2 | 8.1 | 8 | 0.095743
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-14 | 50-PL-23021-03C03 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10246 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.125 | CML-14 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.1 | 8.2 | 8.2 | 8 | 0.095743
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-1 | 50-PL-23021-03C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10233 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.125 | CML-1 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.2 | 8.1 | 8 | 0.095743
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-16 | 80-PW-44016-01C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21948 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 12.175 | CML-16 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.8 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.6 | 12.1 | 11.8 | 12.2 | 0.3304
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-11 | 50-CG-38452-09C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23751 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.575 | CML-11 | CML: Pipe Length | 3 | 2076-02-24 | 2059-11-11 | 2015-10-30 07:00 | 2.5 | 0.0994 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.5 | 8.6 | 8.7 | 0.095743
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20012-01C02-P | CML-1 | 200-PL-20012-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21203 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 10.925 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.4 | 3 O'Clock | 300 | 6.35 | 200-PL-20012-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.9 | 10.4 | 11.7 | 10.7 | 0.55603
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-1 | 50-PF-20300-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21567 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.075 | CML-1 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 6 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.1 | 9 | 9.2 | 0.095743
FG01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-FG-45024-01C02 | CML-13 | 50-FG-45024-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1107 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 9.375 | CML-13 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 9.3 | 3 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.3 | 9.3 | 9.4 | 9.5 | 0.095743
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-8 | 50-PL-23040-03C03 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10193 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.525 | CML-8 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 10.4 | 9 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.5 | 10.6 | 10.6 | 10.4 | 0.095743
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-33 | 50-CG-38001-09C02 CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 10948 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.625 | CML-33 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0.39638 | A4: Left Quadrant |  | 5.74 |  |  | 8.5 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.5 | 8.7 | 8.7 | 8.6 | 8.5 | 0.095743
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-14 | 250-PG-23015-06C03-A CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 13046 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 18 | CML-14 | CML: Pipe Length | 6 | 2029-12-30 | 2026-10-30 | 2014-01-11 13:00 | 8.55 | 0.58519 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.9 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.35 |  | 18 | 18 | 17.9 | 18.1 | 0.08165
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38486-09C02-P | CML-5 | 80-CG-38486-09C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20563 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [36 empty] | 21 | CML-5 | CML: Equal Tee | 3 | 2090-10-23 | 2076-08-20 | 2014-07-02 07:00 | 7.5 | 0 | A1: Outside Quadrant |  | 12.24 | 7.5 | 8.9175 | 20.9 | 12 O'Clock | 80 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.4 |  | 20.9 | 21 | 21.1 | 21 | 0.08165
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45044-03C02 | CML-10 | 50-FG-45044-03C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20849 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 28.275 | CML-10 | CML: Reducing Tee | 3 | 2072-12-31 | 2057-07-13 | 2014-10-02 07:00 | 2.5 | 0.10465 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 8.1824 | 8.7 | 8.7 | 8.8 | 8.6 | 0.08165
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-10 | 100-PG-23503-03C03-A CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2726 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.7 | CML-10 | CML: Pipe Length | 6 | 2021-06-24 | 2021-11-13 | 2014-03-13 09:00 | 5.66 | 0.67788 | A4: Left Quadrant |  | 5.13 | 5.66 | 5.395 | 10.6 | 9 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.94 |  | 10.7 | 10.8 | 10.7 | 10.6 | 0.08165
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-18 | 100-PG-23503-03C03-A CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2734 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.7 | CML-18 | CML: Pipe Length | 6 | 2021-06-24 | 2021-11-13 | 2014-03-13 09:00 | 5.66 | 0.67788 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.6 | 12 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.94 |  | 10.6 | 10.7 | 10.7 | 10.8 | 0.08165
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-2 | 150-FL-43514-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20495 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 8.3 | CML-2 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 8.2 | 12 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.4 | 8.3 | 8.3 | 0.08165
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-11 | 400-WC-40022-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1105 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 10.475 | CML-11 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 10.1 | 3 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.6 | 10.1 | 10.6 | 10.6 | 0.25
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45044-03C02 | CML-8 | 50-FG-45044-03C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20799 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 |  |  | Administrator | 2015-09-07 11:00 | [32 empty] | 8.7 | CML-8 | CML: Pipe Length | 3 | 2063-09-30 | 2050-09-06 | 2014-07-18 11:00 | 2.5 | 0.12389 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 15 | 8.74 | 50-CG-38002-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.7 | 8.8 | 8.6 | 0.08165
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-14 | 300-PL-20011-01C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 23799 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 11.425 | CML-14 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.9 | 9 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.7 | 11.5 | 11.6 | 10.9 | 0.3594
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-FH-43507-01C02 | CML-11 | 100-FH-43507-01C02 CML-11 | Yes | FPSO 2013 | Pipe Wall Thickness | 10737 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.7 | CML-11 | CML: type TBC | 3 | 2034-04-13 | 2028-11-12 | 2013-11-19 | 2.5 | 0.29883 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.7 | 8.8 | 8.6 | 0.08165
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40403-01C02 | CML-3 | 100-WC-40403-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20383 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 10.3 | CML-3 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 10 | 9 O'Clock | 100 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.5 | 10.4 | 10.3 | 10 | 0.21602
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-8 | 50-FL-43454-01C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22993 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.2 | CML-8 | CML: Pipe Length | 6 | 2090-02-04 | 2085-09-25 | 2015-05-05 07:00 | 2.5 | 0.08823 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.1 | 12 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | 0.37056 | 9.1 | 9.2 | 9.2 | 9.3 | 0.08165
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-3 | 50-FL-43454-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1859 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.2 | CML-3 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 12 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.3 | 9.2 | 9.2 | 0.08165
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-20 | 50-CG-38452-09C02-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23760 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.3 | CML-20 | CML: Fitting | 3 | 2075-10-24 | 2059-08-12 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.3 | 9.2 | 9.4 | 9.3 | 0.08165
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-15 | 250-PL-20006-01C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 13185 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 12.9667 | CML-15 | CML: Pipe Length | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A2: Right Quadrant |  | 3.35 | 3.61 | 3.0831 | 12.3 | 3 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.69 |  | 13 | 12.3 | 13.6 |  | 0.65064
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44024-01X01-P | CML-2 | 80-PW-44024-01X01-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22897 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 18.325 | CML-2 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2015-05-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 12.2 | 12 O'Clock | 80 | 11.13 | 80-PW-44024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 | 11.5125 | 12.2 | 20.4 | 20.4 | 20.3 | 4.0836
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45031-03C03 | CML-4 | 50-PL-45031-03C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10472 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 8.3 | CML-4 | CML: type TBC | 6 | 2019-12-09 | 2019-03-15 | 2013-11-14 | 0.99 | 1.1873 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 8.2 | 3 O'Clock | 50 | 8.74 | 50-PL-45031-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.21 |  | 8.4 | 8.2 | 8.3 | 8.3 | 0.08165
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-2 | 300-PG-20502-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 23889 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.2 | CML-2 | CML: Elbow | 6 | 2062-07-10 | 2056-10-31 | 2014-09-26 07:00 | 2.5 | 0.15893 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.1 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.1 | 10.2 | 10.2 | 10.3 | 0.08165
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-2 | 300-PG-20502-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20749 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.2 | CML-2 | CML: type TBC | 6 | 2062-07-10 | 2056-10-31 | 2014-09-26 07:00 | 2.5 | 0.15893 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.1 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.1 | 10.2 | 10.2 | 10.3 | 0.08165
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-12 | 50-PG-23024-03C03 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10044 | Rope Access | 2014-01-06 | 2014-01-06 | [36 empty] | 8.7 | CML-12 | CML: Pipe Length | 6 | 2046-09-10 | 2042-11-26 | 2014-01-06 | 0.97 | 0.23333 | A1: Outside Quadrant |  | 2.74 | 0.97 | 1.855 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.63 |  | 8.6 | 8.8 | 8.7 | 8.7 | 0.08165
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-16 | 50-PL-23042-09C03 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10081 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.7 | CML-16 | CML: type TBC | 6 | 2021-05-09 | 2020-02-29 | 2013-11-07 | 2.5 | 1.0789 | A3: Inside Quadrant |  | 5.07 | 2.5 | 3.785 | 10.6 | 6 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.7 | 10.8 | 10.6 | 10.7 | 0.08165
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-9 | 300-PG-20005-03C03-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23360 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 13.8 | CML-9 | CML: Pipe Length | 6 | 2048-06-27 | 2042-03-07 | 2015-07-20 07:00 | 4.9 | 0.26697 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | 1.7805 | 13.9 | 13.8 | 13.7 | 13.8 | 0.08165
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-19 | 80-DH-56004-01C02 CML-19 | yes | FPSO 2015 | Pipe Wall Thickness | 6652 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:24 | [32 empty] | 3.4 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 3 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 3.3 | 3.4 | 3.5 | 0.08165
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-4 | 150-FH-43141-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 5990 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.5 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.5 | 3.6 | 3.4 | 3.5 | 0.08165
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56117-01C02 | CML-5 | 50-DH-56117-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21018 | Rope Access | 2014-05-19 13:00 | 2014-05-19 14:00 | [36 empty] | 4.9 | CML-5 | CML: type TBC | 3 | 2017-05-19 | 2017-10-21 | 2014-05-19 13:00 | 2.5 | 0.76615 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 5 | 4.9 | 4.8 | 0.08165
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-17 | 250-PG-23003-06C02-PA CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 7696 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-13 13:51 | [32 empty] | 4.9 | CML-17 | CML: Elbow | 3 | 2020-01-05 | 2020-09-20 | 2015-01-08 13:00 | 2.5 | 0.4605 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.17483 | 4.8 | 4.9 | 4.9 | 5 | 0.08165
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-11 | 50-CG-38500-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 7883 |  | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:43 | [32 empty] | 5.2 | CML-11 | CML: Pipe Length | 3 | 2024-08-15 | 2025-10-28 | 2015-01-14 10:30 | 2.5 | 0.27108 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.2 | 5.2 | 5.1 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-14 | 80-FH-43158-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12895 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.3 | CML-14 | CML: type TBC | 3 | 2020-01-23 | 2020-11-01 | 2014-01-22 11:00 | 2.5 | 0.44955 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.3 | 5.3 | 0.08165
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-5 | 80-PW-44011-01X01-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22803 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 15.675 | CML-5 | CML: Equal Tee | 6 | 2099-09-17 | 2086-07-24 | 2015-04-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 14 | 9 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 | 4.7266 | 15.7 | 14.6 | 18.4 | 14 | 1.9483
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-1 | 80-PW-44011-01X01-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22799 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 18.025 | CML-1 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 15.2 | 12 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.7 | 2.7572 | 15.2 | 17.7 | 19.8 | 19.4 | 2.0918
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-9 | 80-PW-44011-01X01-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22807 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 16.6 | CML-9 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2015-04-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 15.6 | 9 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.1 | 7.0899 | 16.8 | 17.4 | 16.6 | 15.6 | 0.74833
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-1 | 80-PW-44011-01X01-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21872 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 18.475 | CML-1 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 17.3 | 12 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 |  | 17.3 | 17.6 | 18 | 21 | 1.7076
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-3 | 80-PW-44011-01X01-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22801 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 18.475 | CML-3 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2015-04-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 17.3 | 6 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 | 1.9694 | 20.5 | 17.6 | 17.3 | 18.5 | 1.4431
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-5 | 80-PW-44011-01X01-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21876 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 18.775 | CML-5 | CML: Equal Tee | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 17.6 | 12 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.1 |  | 17.6 | 21 | 18 | 18.5 | 1.5283
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-4 | 80-PW-44011-01X01-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22802 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 19 | CML-4 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 17.7 | 12 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.2 | 0.26259 | 17.7 | 18.1 | 20.5 | 19.7 | 1.3216
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43081-01C02 | CML-1 | 80-FH-43081-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12723 |  | 2014-01-27 08:00 | 2014-01-27 09:00 |  |  | Nestor | 2014-11-19 17:17 | [32 empty] | 5.4 | CML-1 | CML: Pipe Length | 3 | 2023-10-09 | 2024-12-22 | 2014-01-27 08:00 | 2.5 | 0.28856 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-FH-43081-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.5 | 5.3 | 5.4 | 0.08165
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-16 | 50-FG-45501-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6599 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.4 | CML-16 | CML: Pipe Length | 3 | 2036-07-22 | 2039-01-15 | 2015-03-30 07:00 | 2.5 | 0.13128 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.5 | 5.4 | 5.3 | 0.08165
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-7 | 50-FG-45501-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6590 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.4 | CML-7 | CML: Pipe Length | 3 | 2036-07-22 | 2039-01-15 | 2015-03-30 07:00 | 2.5 | 0.13128 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 5.4 | 5.5 | 0.08165
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38482-01C02 | CML-1 | 25-CG-38482-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10376 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.6 | CML-1 | CML: type TBC | 3 | 2015-06-13 | 2015-06-08 | 2013-11-12 | 2.5 | 1.8918 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 3 O'Clock | 25 | 6.35 | 25-CG-38482-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 5.5 | 5.7 | 5.5 | 5.6 | 5.6 | 0.08165
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38493-01C02 | CML-1 | 25-CG-38493-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10370 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.6 | CML-1 | CML: type TBC | 3 | 2015-06-13 | 2015-06-08 | 2013-11-12 | 2.5 | 1.8918 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 9 O'Clock | 25 | 6.35 | 25-CG-38493-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 5.5 | 5.6 | 5.7 | 5.6 | 5.5 | 0.08165
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-11 | 50-FL-43454-01C02-P CML-11 | Yes | FPSO 2014 | Pipe Wall Thickness | 20514 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.7 | CML-11 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.8 | 5.7 | 5.7 | 0.08165
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45034-03C02 | CML-2 | 25-FG-45034-03C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10482 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 5.8 | CML-2 | CML: type TBC | 3 | 2016-02-09 | 2015-10-23 | 2013-11-14 | 2.5 | 1.4292 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.925 | 5.7 | 12 O'Clock | 25 | 6.35 | 25-FG-45034-03C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 5.8 | 5.9 | 0.08165
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-23 | 250-WC-40026-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 1299 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 10.05 | CML-23 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10 | 6 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 10.1 | 10 | 10.1 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43106-01C02 | CML-3 | 100-FH-43106-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12772 |  | 2014-01-25 10:00 | 2014-01-25 11:00 | [36 empty] | 6.1 | CML-3 | CML: type TBC | 3 | 2128-04-20 | 2132-02-05 | 2014-01-25 10:00 | 2.5 | 0.03062 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-FH-43106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6.2 | 6.1 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43102-01C02 | CML-1 | 100-FH-43102-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12746 |  | 2014-01-24 08:00 | 2014-01-24 09:00 | [36 empty] | 6.1 | CML-1 | CML: type TBC | 3 | 2127-10-12 | 2131-07-23 | 2014-01-24 08:00 | 2.5 | 0.03076 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-FH-43102-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.1 | 6.1 | 0.08165
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-6 | 100-VA-80006-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2175 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 6.2 | CML-6 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-30 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 6 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.3 | 6.1 | 6.2 | 0.08165
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-14 | 400-WC-40022-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1108 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 10.525 | CML-14 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 10.2 | 9 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.3 | 10.7 | 10.9 | 10.2 | 0.3304
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-10 | 100-FH-43104-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12761 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 6.2 | CML-10 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 9 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.3 | 6.2 | 6.2 | 6.1 | 0.08165
PL01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-PL-24003-09C02 | CML-20 | 50-PL-24003-09C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 13159 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 12 | CML-20 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-01-18 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 11.3 | 12 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 11.3 | 12.3 | 12.2 | 12.2 | 0.46904
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-21 | 80-PW-44016-01C02-P CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 22923 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 12.2 | CML-21 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-05-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 11.9 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 12.4 | 12.4 | 11.9 | 12.1 | 0.24495
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-3 | 400-WC-40022-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1097 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 10.525 | CML-3 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 10.2 | 3 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.5 | 10.2 | 10.6 | 10.8 | 0.25
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-5 | 50-FG-45023-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1153 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.6 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | -8.9601 | 6.6 | 6.6 | 6.5 | 6.7 | 0.08165
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-8 | 200-PL-20008-01C02-H CML-8 | Yes | FPSO 2015 | Pipe Wall Thickness | 8805 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 8.25 | CML-8 | CML: Fitting | 3 | 2065-11-29 | 2058-08-19 | 2015-02-21 07:00 | 1.1 | 0 | A4: Left Quadrant |  | 3.35 | 1.1 | 1.8281 | 8.1 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 8.3 | 8.4 | 8.2 | 8.1 | 0.1291
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44032-01C02-P | CML-1 | 80-PW-44032-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21959 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 12.45 | CML-1 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 12 | 3 O'Clock | 80 | 5.49 | 80-PW-44032-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.6 | 12 | 12.8 | 12.4 | 0.34157
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-28 | 50-FG-45023-01C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 1176 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.7 | CML-28 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.6 | 6.7 | 6.7 | 0.08165
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-9 | 50-FG-45024-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1192 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.7 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.7 | 6.7 | 6.6 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43126-01C02 | CML-5 | 100-FH-43126-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2514 | Rope Access | 2014-03-24 14:30 | 2014-03-24 15:00 | [36 empty] | 6.7 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-24 14:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 9 O'Clock | 100 | 6.02 | 100-FH-43126-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.7 | 6.8 | 6.6 | 0.08165
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-7 | 80-PW-44011-01X01-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22805 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 19.325 | CML-7 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2015-04-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 17.8 | 9 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.3 | 2.8885 | 20.4 | 20.5 | 18.6 | 17.8 | 1.3401
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-15 | 300-PL-20011-01C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 23800 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 12.05 | CML-15 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.4 | 9 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 12.7 | 12.5 | 11.6 | 11.4 | 0.6455
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-10 | 150-FH-43027-01C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10572 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 6.8 | CML-10 | CML: type TBC | 3 | 2018-08-02 | 2018-03-08 | 2013-11-16 | 2.5 | 0.89077 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 12 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 6.8 | 6.8 | 6.9 | 0.08165
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2505 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.1 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7.1 | 7.2 | 7 | 0.08165
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-13 | 50-CG-38452-09C02-P CML-13 | Yes | FPSO 2015 | Pipe Wall Thickness | 23645 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 7.3 | CML-13 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 6 O'Clock | 100 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.3 | 7.3 | 7.2 | 7.4 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-6 | 80-FH-43009-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12584 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.4 | CML-6 | CML: Pipe Length | 3 | 2031-03-14 | 2028-12-05 | 2014-02-05 08:00 | 0.54 | 0.27814 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.4 | 5.5 | 5.4 | 5.3 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-17 | 80-FH-43158-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12898 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 7.6 | CML-17 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-22 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.5 | 9 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.7 | 7.6 | 7.6 | 7.5 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-9 | 200-FH-43037-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12678 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 7.6 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 6 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.6 | 7.7 | 7.5 | 7.6 | 0.08165
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-4 | 80-PW-44011-01X01-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21875 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 19.075 | CML-4 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 17.9 | 12 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 |  | 17.9 | 18.8 | 18.6 | 21 | 1.3401
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43029-01C02 | CML-8 | 400-FH-43029-01C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10024 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.8 | CML-8 | CML: Pipe Length | 3 | 2023-12-23 | 2022-07-27 | 2013-11-04 | 2.48 | 0.51474 | A2: Right Quadrant |  | 4.92 | 2.48 | 3.205 | 7.7 | 3 O'Clock | 400 | 7.92 | 400-FH-43029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 |  | 7.8 | 7.7 | 7.8 | 7.9 | 0.08165
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-28 | 200-PL-20008-01C02-H CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 8825 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 10.775 | CML-28 | CML: Elbow | 3 | 2065-11-29 | 2058-08-19 | 2015-02-21 07:00 | 1.1 | 0 | A4: Left Quadrant |  | 3.35 | 1.1 | 1.8281 | 9.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 12.2 | 10.8 | 10.3 | 9.8 | 1.034
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-12 | 150-FH-43026-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23511 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 7.2 | CML-12 | CML: Fitting | 3 | 520099 | 433841 | 2015-07-28 07:00 | 1.03 | 0.00464 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.1 | 12 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.07 | 0.13225 | 7.1 | 7.2 | 7.3 | 7.2 | 0.08165
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-30 | 150-FH-43141-01C02 CML-30 | yes | FPSO 2015 | Pipe Wall Thickness | 6908 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.5 | CML-30 | CML: type TBC | 0.5 | 2031-11-06 | 2027-03-29 | 2015-04-05 07:00 | 3.5 | 0.05421 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4.4 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 4.5 | 4.6 | 4.5 | 4.4 | 0.08165
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-29 | 150-FH-43141-01C02 CML-29 | yes | FPSO 2015 | Pipe Wall Thickness | 6907 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.5 | CML-29 | CML: type TBC | 0.5 | 2031-11-06 | 2027-03-29 | 2015-04-05 07:00 | 3.5 | 0.05421 | A3: Inside Quadrant |  | 4 | 3.5 | 3.75 | 4.4 | 6 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 4.5 | 4.6 | 4.4 | 4.5 | 0.08165
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-6 | 250-PL-20006-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13176 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 11.6667 | CML-6 | CML: Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-01-21 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.5 | 3 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 11.8 | 11.5 | 11.7 |  | 0.15275
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-5 | 50-WC-40048-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 882 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 10.9 | CML-5 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.2 | 12 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.2 | 11.3 |  | 11.2 | 0.60828
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-5 | 50-WC-40048-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1546 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 10.9 | CML-5 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.2 | 12 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.2 | 11.3 |  | 11.2 | 0.60828
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40061-01C02 | CML-4 | 400-WC-40061-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1128 |  | 2014-03-21 08:30 | 2014-03-21 09:00 | [36 empty] | 10.95 | CML-4 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 08:30 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 10.3 | 12 O'Clock | 400 | 7.92 | 400-WC-40061-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.3 | 11.1 | 11.5 | 10.9 | 0.5
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21117 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18.Update RBI study to include this line. | 2014-10-09 07:00 | 2014-10-09 15:00 |  |  | Nestor | 2014-11-21 14:25 | [32 empty] | 5.5 | CML-1 | CML: Pipe Length | 3 | 2042-11-10 | 2046-01-08 | 2014-10-09 07:00 | 2.5 | 0.10317 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56564-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.6 | 5.5 | 5.4 | 0.08165
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40055-01C02 | CML-1 | 50-WC-40055-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1707 | Rope Access | 2014-04-13 11:15 | 2014-04-13 12:15 | [36 empty] | 10.725 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 11:15 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40055-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.9 | 11.1 | 10.2 | 10.7 | 0.38622
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40401-01C02 | CML-2 | 200-WC-40401-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7918 |  | 2015-01-17 08:00 | 2015-01-17 09:00 |  |  | Administrator | 2015-09-08 11:21 | [32 empty] | 11.375 | CML-2 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-17 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.3 | 6 O'Clock | 200 | 6.35 | 200-WC-40401-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 11.2 | 11.7 | 10.3 | 12.3 | 0.84607
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-33 | 200-PL-20010-01C02-P CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 23833 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 14.275 | CML-33 | CML: Reducer | 3 | 2039-11-30 | 2045-08-19 | 2014-09-25 07:00 | 3.7 | 0 | A1: Outside Quadrant |  | 3.35 | 3.7 | 3.1281 | 13.7 | 12 O'Clock | 600 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 13.7 | 14.6 | 14 | 14.8 | 0.51235
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-9 | 50-CG-38452-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12972 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.5 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.5 | 6.6 | 6.5 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-4 | 100-FH-43507-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1774 | Rope access. Line is FFS. It has been re- check . The rechecked CR’s from data from Jan. 2015 are lower. | 2014-04-27 13:00 | 2014-04-27 14:00 |  |  | Administrator | 2015-09-07 17:01 | [32 empty] | 6.5 | CML-4 | CML: Elbow | 3 | 2019-04-17 | 2018-10-31 | 2014-04-27 13:00 | 2.5 | 0.78402 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 3 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.4 | 6.5 | 6.5 | 0.08165
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-9 | 50-PG-23063-09C02 CML-9 | Yes | FPSO 2013 | Pipe Wall Thickness | 10735 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.1 | CML-9 | CML: type TBC | 3 | 2017-05-12 | 2016-05-03 | 2013-11-19 | 2.5 | 1.5795 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8 | 3 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8 | 8.1 | 8.1 | 0.08165
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40051-01C02 | CML-1 | 50-WC-40051-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 900 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 10.85 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 | 0 | 11.4 | 11.3 | 10.3 | 10.4 | 0.58023
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38491-09C02 | CML-7 | 50-CG-38491-09C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2546 |  | 2014-04-03 10:00 | 2014-04-03 11:00 | [36 empty] | 8.5 | CML-7 | CML: type TBC | 3 | 2028-10-23 | 2024-10-24 | 2014-04-03 10:00 | 2.5 | 0.405 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 6 O'Clock | 50 | 8.74 | 50-CG-38491-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.6 | 8.5 | 8.4 | 8.5 | 0.08165
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38490-09C02 | CML-6 | 50-CG-38490-09C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2534 |  | 2014-04-03 07:00 | 2014-04-03 08:00 | [36 empty] | 8.5 | CML-6 | CML: type TBC | 3 | 2028-10-21 | 2024-10-22 | 2014-04-03 07:00 | 2.5 | 0.40517 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-CG-38490-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.5 | 8.6 | 8.5 | 8.4 | 0.08165
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23034-01C03 | CML-7 | 50-PL-23034-01C03 CML-7 | no | FPSO 2014 | Pipe Wall Thickness | 20575 | Reviewed on 26/11/14.FFS. Repeat Oct.19 | 2014-10-12 07:00 | 2014-10-12 12:00 |  |  | Nestor | 2014-11-26 16:19 | [32 empty] | 8.6 | CML-7 | CML: Fitting | 6 | 2048-11-19 | 2048-03-15 | 2014-10-12 07:00 | 2.5 | 0.1758 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-PL-23034-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.6 | 8.6 | 8.7 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-11 | 150-FH-43136-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2772 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.5 | CML-11 | CML: Pipe Length | 3 | 2074-03-18 | 2063-04-04 | 2014-03-13 09:00 | 1.03 | 0 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.37 |  | 7.5 | 7.6 | 7.4 | 7.5 | 0.08165
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-16 | 50-FL-43454-01C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12656 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.5 | CML-16 | CML: Elbow | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.4 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.37 |  | 7.6 | 7.4 | 7.5 | 7.5 | 0.08165
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40051-01C02 | CML-1 | 50-WC-40051-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1564 | Rope Access | 2014-04-09 11:00 | 2014-04-09 12:00 | [36 empty] | 10.85 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 11.4 | 11.3 | 10.3 | 10.4 | 0.58023
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-4 | 100-PG-23028-25C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 443 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 17.3 | CML-4 | CML: Pipe Length | 3 | 2090-08-11 | 2067-01-05 | 2014-03-12 09:00 | 9.4 | 0 | A1: Outside Quadrant |  | 14.12 | 9.4 | 11.76 | 17.2 | 12 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 17.2 | 17.3 | 17.3 | 17.4 | 0.08165
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23029-25C02-P | CML-7 | 80-PG-23029-25C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20565 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [36 empty] | 22.6 | CML-7 | CML: Reducer | 3 | 2024-10-24 | 2043-08-22 | 2014-07-02 07:00 | 14.1 | 0 | A2: Right Quadrant |  | 12.24 | 14.1 | 12.2175 | 22.5 | 3 O'Clock | 150 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 22.6 | 22.5 | 22.6 | 22.7 | 0.08165
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-38 | 250-PL-20006-01C02-P CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 13208 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-38 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23048-09C02 | CML-7 | 50-PG-23048-09C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20589 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 8.75 | CML-7 | CML: Fitting | 3 | 2189-07-31 | 2143-11-05 | 2014-07-18 11:00 | 2.5 | 0.0354 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 8.8 | 8.8 | 8.7 | 0.057735
FG01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-FG-45024-01C02 | CML-14 | 50-FG-45024-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1728 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 9.2333 | CML-14 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.2 | 9 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 |  | 9.3 | 9.2 | 0.057735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-6 | 80-PW-44011-01X01-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21877 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 20.175 | CML-6 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 18.7 | 9 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.2 |  | 21 | 21 | 20 | 18.7 | 1.0905
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-3 | 80-PW-44011-01X01-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21874 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 19.825 | CML-3 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 18.8 | 9 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.3 |  | 20 | 19.5 | 21 | 18.8 | 0.92511
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40028-01C02 | CML-6 | 50-WC-40028-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1686 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 10.6 | CML-6 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.7 | 10.4 | 11 | 10.3 | 0.31623
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23050-25C02-P | CML-6 | 80-PG-23050-25C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2741 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 14.25 | CML-6 | CML: Pipe Length | 3 | 2096-09-16 | 2070-01-23 | 2014-03-13 09:00 | 2.8 | 0 | A1: Outside Quadrant |  | 8.13 | 2.8 | 5.465 | 14.2 | 3 O'Clock | 80 | 11.13 | 80-PG-23050-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.4 |  | 14.2 | 14.2 | 14.3 | 14.3 | 0.057735
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38486-09C02-P | CML-2 | 80-CG-38486-09C02-P CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10067 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 15.7333 | CML-2 | CML: type TBC | 6 | 2099-02-10 | 2086-04-06 | 2013-11-07 | 2.5 | 0 | A1: Outside Quadrant |  | 5.07 | 2.5 | 3.785 | 15.7 | 3 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.2 |  | 15.7 | 15.7 | 15.8 |  | 0.057735
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-14 | 50-CG-38454-01C02-H CML-14 | yes | FPSO 2015 | Pipe Wall Thickness | 23678 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.15 | CML-14 | CML: Elbow | 3 | 2030-01-31 | 2031-11-16 | 2015-10-30 07:00 | 2.5 | 0.18223 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.1 | 5.2 | 5.2 | 0.057735
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3492 | Rope Access | 2014-05-14 14:00 | 2014-05-14 15:00 | [36 empty] | 5.15 | CML-2 | CML: type TBC | 3 | 2019-12-28 | 2020-09-11 | 2014-05-14 14:00 | 2.5 | 0.46205 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DN-56075-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.1 | 5.2 | 5.2 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43081-01C02 | CML-5 | 80-FH-43081-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12727 |  | 2014-01-27 08:00 | 2014-01-27 09:00 |  |  | Nestor | 2014-11-19 17:18 | [32 empty] | 5.35 | CML-5 | CML: type TBC | 3 | 2023-10-09 | 2024-12-22 | 2014-01-27 08:00 | 2.5 | 0.28856 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 80 | 5.49 | 80-FH-43081-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.4 | 5.4 | 0.057735
VA01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-VA-43519-01C02 | CML-7 | 50-VA-43519-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7760 |  | 2015-01-11 09:30 | 2015-01-11 10:30 | [36 empty] | 5.35 | CML-7 | CML: Elbow | 3 | 2033-11-08 | 2036-01-18 | 2015-01-11 09:30 | 2.5 | 0.14863 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-VA-43519-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.4 | 5.4 | 0.057735
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-6 | 50-FG-45301-01C02 CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 5792 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.35 | CML-6 | CML: Pipe Length | 3 | 2026-11-08 | 2028-04-18 | 2014-06-23 13:00 | 2.5 | 0.22604 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.4 | 5.3 | 5.3 | 0.057735
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38482-01C02 | CML-5 | 25-CG-38482-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10380 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.65 | CML-5 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 9 O'Clock | 25 | 6.35 | 25-CG-38482-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.7 | 5.7 | 5.6 | 5.6 | 0.057735
CG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2281 |  | 2014-03-16 14:30 | 2014-03-16 15:00 | [36 empty] | 7.15 | CML-2 | CML: type TBC | 3 | 2377-09-07 | 2349-03-10 | 2014-03-16 14:30 | 2.5 | 0.01265 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.1 | 9 O'Clock | 150 | 7.11 | 150-DC-57041-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.2 | 7.2 | 7.1 | 7.1 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43030-01C02 | CML-8 | 400-FH-43030-01C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10032 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.85 | CML-8 | CML: type TBC | 3 | 2032-09-15 | 2030-02-28 | 2013-11-04 | 2.5 | 0.28077 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.8 | 3 O'Clock | 400 | 7.92 | 400-FH-43030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.8 | 7.9 | 7.9 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43030-01C02 | CML-7 | 400-FH-43030-01C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10031 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.85 | CML-7 | CML: type TBC | 3 | 2032-09-15 | 2030-02-28 | 2013-11-04 | 2.5 | 0.28077 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.8 | 3 O'Clock | 400 | 7.92 | 400-FH-43030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.8 | 7.9 | 7.9 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-20 | 150-FH-43026-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 5529 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 7.15 | CML-20 | CML: Fitting | 3 | 263523 | 223501 | 2014-06-01 07:00 | 1.03 | 0.00999 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.1 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.07 |  | 7.2 | 7.2 | 7.1 | 7.1 | 0.057735
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-15 | 50-FG-45300-01C02 CML-15 | yes | FPSO 2015 | Pipe Wall Thickness | 7838 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:39 | [32 empty] | 4.85 | CML-15 | CML: Elbow | 3 | 2020-01-26 | 2020-10-12 | 2015-01-13 13:00 | 2.5 | 0.4566 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.9 | 4.9 | 4.8 | 0.057735
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44029-01C02 | CML-3 | 250-PW-44029-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21907 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 12.95 | CML-3 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 12.4 | 12 O'Clock | 250 | 6.35 | 250-PW-44029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 12.4 | 13.6 | 12.8 | 13 | 0.5
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-9 | 400-WC-40025-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1269 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 10.65 | CML-9 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 10.4 | 3 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.9 | 10.4 | 10.7 | 10.6 | 0.20817
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38483-01C02 | CML-3 | 25-CG-38483-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10392 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.65 | CML-3 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 9 O'Clock | 25 | 6.35 | 25-CG-38483-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.7 | 5.6 | 5.7 | 5.6 | 0.057735
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38486-09C02-P |  | 80-CG-38486-09C02-P |  | FPSO 2015 | Pipe Wall Thickness | 23652 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.65 | 80-CG-38486-01C02-H | Piping | 3 | 2043-04-25 |  | 2015-10-28 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.6 | 9 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 5.7 | 5.6 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43144-01C02 | CML-3 | 100-FH-43144-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10526 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.85 | CML-3 | CML: type TBC | 3 | 2020-09-24 | 2020-12-21 | 2013-11-15 | 2.5 | 0.48084 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 6 O'Clock | 100 | 6.02 | 100-FH-43144-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 5.8 | 5.9 | 0.057735
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-11 | 150-WC-40006-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1671 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 10.375 | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.3 | 9 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.5 | 10.4 | 10.3 | 10.3 | 0.095743
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-4 | 50-FG-45023-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1152 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.65 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 | -8.3628 | 6.7 | 6.6 | 6.7 | 6.6 | 0.057735
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40029-01C02 | CML-3 | 50-WC-40029-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1541 |  | 2014-04-06 16:30 | 2014-04-06 17:00 | [36 empty] | 10.35 | CML-3 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40029-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.4 | 10.3 | 10.3 | 10.4 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-5 | 200-FH-43037-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12674 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 6.65 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.6 | 6.7 | 6.6 | 0.057735
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-18 | 80-PW-44001-01C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 22009 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 12.9 | CML-18 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 12.6 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.1 |  | 13 | 12.7 | 12.6 | 13.3 | 0.31623
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-37 | 250-PL-20006-01C02-P CML-37 |  | FPSO 2014 | Pipe Wall Thickness | 13207 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-37 | CML: Pipe Length | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38002-09C02-P | CML-9 | 50-CG-38002-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20800 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 |  |  | Administrator | 2015-09-07 11:00 | [32 empty] | 7.35 | CML-9 | CML: Pipe Length | 3 | 2018-04-23 | 2017-01-14 | 2014-07-18 11:00 | 2.5 | 1.2743 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 7.3 | 6 O'Clock | 15 | 8.74 | 50-CG-38002-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.4 | 7.3 | 7.3 | 7.4 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43030-01C02 | CML-1 | 400-FH-43030-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10025 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.85 | CML-1 | CML: type TBC | 3 | 2032-09-15 | 2030-02-28 | 2013-11-04 | 2.5 | 0.28077 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.8 | 6 O'Clock | 400 | 7.92 | 400-FH-43030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.9 | 7.8 | 7.9 | 0.057735
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-46 | 350-FL-43512-01C02 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 23557 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.85 | CML-46 | CML: Elbow | 3 | 2112-05-20 | 2099-04-29 | 2015-08-10 07:30 | 2.5 | 0.05473 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.8 | 6 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.9 | 7.8 | 7.8 | 7.9 | 0.057735
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40029-01C02 | CML-3 | 50-WC-40029-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 877 |  | 2014-04-06 16:30 | 2014-04-06 17:00 | [36 empty] | 10.35 | CML-3 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40029-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.4 | 10.3 | 10.3 | 10.4 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43029-01C02 | CML-7 | 400-FH-43029-01C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10023 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.85 | CML-7 | CML: Pipe Length | 3 | 2032-10-11 | 2030-03-13 | 2013-11-04 | 2.48 | 0.28077 | A2: Right Quadrant |  | 4.92 | 2.48 | 3.205 | 7.8 | 9 O'Clock | 400 | 7.92 | 400-FH-43029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.32 |  | 7.9 | 7.8 | 7.9 | 7.8 | 0.057735
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-32 | 150-FH-43141-01C02 CML-32 | yes | FPSO 2015 | Pipe Wall Thickness | 6311 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.45 | CML-32 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.5 | 3.5 | 3.4 | 0.057735
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-3 | 150-FH-43141-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 5956 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.45 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.5 | 3.5 | 3.4 | 3.4 | 0.057735
FL01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-FL-43174-01C02 | CML-2 | 150-FL-43174-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 5011 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | [36 empty] | 3.45 | CML-2 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.4 | 6 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.5 | 3.4 | 3.5 | 0.057735
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-8 | 150-FL-43174-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6357 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.55 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.6 | 3.5 | 3.6 | 3.5 | 0.057735
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-17 | 150-FL-43174-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6296 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.55 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.5 | 3.6 | 3.5 | 3.6 | 0.057735
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-7 | 50-CG-38500-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7879 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:42 | [32 empty] | 3.65 | CML-7 | CML: Pipe Length | 3 | 2015-12-16 | 2016-03-24 | 2015-01-14 10:30 | 2.5 | 1.1952 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.6 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.7 | 3.7 | 3.6 | 0.057735
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-5 | 50-CG-38500-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7877 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:41 | [32 empty] | 3.65 | CML-5 | CML: Pipe Length | 3 | 2015-12-16 | 2016-03-24 | 2015-01-14 10:30 | 2.5 | 1.1952 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.6 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.6 | 3.7 | 3.6 | 0.057735
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23301-01C02 | CML-2 | 80-VA-23301-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22509 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 4.05 | CML-2 | CML: Elbow | 3 | 2017-03-13 | 2017-08-21 | 2015-04-20 07:00 | 2.5 | 0.79014 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4 | 3 O'Clock | 50 | 5.49 | 80-VA-23301-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4 | 4.1 | 4.1 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43156-01C02 | CML-5 | 80-FH-43156-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10723 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 4.95 | CML-5 | CML: type TBC | 3 | 2015-10-15 | 2016-01-24 | 2013-11-19 | 2.5 | 1.2594 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-FH-43156-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 4.9 | 5 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43156-01C02 | CML-2 | 80-FH-43156-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10720 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 4.95 | CML-2 | CML: type TBC | 3 | 2015-10-15 | 2016-01-24 | 2013-11-19 | 2.5 | 1.2594 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-FH-43156-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 4.9 | 5 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43155-01C02 | CML-4 | 80-FH-43155-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10717 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 4.95 | CML-4 | CML: type TBC | 3 | 2015-10-10 | 2016-01-18 | 2013-11-18 | 2.5 | 1.2668 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-FH-43155-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 4.9 | 5 | 0.057735
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56002-01C02 | CML-2 | 80-DH-56002-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3421 | Rope Access | 2014-05-11 14:00 | 2014-05-11 14:30 | [36 empty] | 4.95 | CML-2 | CML: type TBC | 3 | 2018-03-13 | 2018-10-02 | 2014-05-11 14:00 | 2.5 | 0.62496 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-DH-56002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 4.9 | 5 | 0.057735
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-9 | 250-PG-23003-06C02-PA CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 20028 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.95 | CML-9 | CML: type TBC | 3 | 2015-08-12 | 2015-11-06 | 2013-11-17 | 2.5 | 1.3822 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 | 5 | 4.9 | 0.057735
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-7 | 250-PG-23003-06C02-PA CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 20026 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.95 | CML-7 | CML: type TBC | 3 | 2015-08-12 | 2015-11-06 | 2013-11-17 | 2.5 | 1.3822 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 4.9 | 5 | 0.057735
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-12 | 150-WC-40006-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20634 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 11.175 | CML-12 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-07-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.4 | 9 O'Clock | 40 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 12.3 | 11 | 11 | 10.4 | 0.80156
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-3 | 50-FG-45018-03C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10502 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.25 | CML-3 | CML: type TBC | 3 | 2017-07-03 | 2017-06-23 | 2013-11-15 | 2.5 | 0.74311 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.3 | 5.3 | 0.057735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-6 | 80-PW-44011-01X01-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22804 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 64 | CML-6 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2015-04-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 19.1 | 6 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.6 | -0.52518 | 20.5 | 20.4 | 19.1 | 19.6 | 0.66833
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-7 | 80-PW-44011-01X01-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21878 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 20.825 | CML-7 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 20 | 3 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.5 |  | 21.1 | 20 | 21.1 | 21.1 | 0.55
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38301-01C02-P |  | 50-CG-38301-01C02-P | yes | FPSO 2014 | Pipe Wall Thickness | 22092 | Rope access | 2014-06-02 07:00 | 2014-06-02 08:00 | [36 empty] | 5.25 | 50-CG-38301-01C02-P | Piping | 3 | 2022-05-20 |  | 2014-06-02 07:00 |  | 0.3388 | A3: Inside Quadrant |  |  | 2.5 |  | 5.2 | 9 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 5.2 | 5.3 | 5.3 | 5.2 | 5.2 | 0.057735
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-12 | 50-FG-45023-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12998 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 5.25 | CML-12 | CML: type TBC | 3 | 2019-02-15 | 2019-09-27 | 2014-01-20 07:00 | 2.5 | 0.53195 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 5.2 | 5.3 | 0.057735
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-1 | 50-WC-40048-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 878 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 10.65 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.6 | 10.7 | 10.9 | 10.4 | 0.20817
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40048-01C02 | CML-1 | 50-WC-40048-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1542 | Rope Access | 2014-04-09 07:00 | 2014-04-09 08:00 | [36 empty] | 10.65 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40048-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.6 | 10.7 | 10.9 | 10.4 | 0.20817
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40014-01C02 | CML-1 | 50-WC-40014-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1548 | Rope Access | 2014-04-09 08:00 | 2014-04-09 09:00 | [36 empty] | 10.55 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.4 | 3 O'Clock | 50 | 5.54 | 50-WC-40014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 10.4 | 10.7 | 10.7 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40013-01C02 | CML-1 | 50-WC-40013-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1556 | Rope Access | 2014-04-09 10:00 | 2014-04-09 11:00 | [36 empty] | 10.975 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.5 | 9 O'Clock | 50 | 5.54 | 50-WC-40013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11.4 | 11.3 | 10.7 | 10.5 | 0.44253
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-14 | 250-WC-40026-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1290 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 10.9 | CML-14 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.5 | 9 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11 | 11.4 | 10.7 | 10.5 | 0.39158
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43138-01C02 | CML-1 | 50-FH-43138-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12865 |  | 2014-01-21 09:30 | 2014-01-21 10:00 | [36 empty] | 5.45 | CML-1 | CML: Pipe Length | 3 | 2027-05-08 | 2028-11-04 | 2014-01-21 09:30 | 2.5 | 0.21801 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-FH-43138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 5.4 | 5.5 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-6 | 50-FH-43137-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12858 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 5.55 | CML-6 | CML: Pipe Length | 3 | 2062-08-04 | 2067-11-13 | 2014-01-23 08:00 | 2.5 | 0.06178 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.5 | 5.5 | 5.6 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-13 | 50-FH-43016-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12612 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.55 | CML-13 | CML: Reducing Tee | 3 | 2062-08-20 | 2067-12-01 | 2014-01-23 13:00 | 2.5 | 0.06172 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.5 | 5.5 | 5.6 | 0.057735
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45033-03C02 | CML-1 | 25-FG-45033-03C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10479 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 5.75 | CML-1 | CML: type TBC | 3 | 2016-02-09 | 2015-10-23 | 2013-11-14 | 2.5 | 1.4292 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.925 | 5.7 | 9 O'Clock | 25 | 6.35 | 25-FG-45033-03C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.7 | 5.8 | 5.7 | 0.057735
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45034-03C02 | CML-1 | 25-FG-45034-03C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10481 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 5.75 | CML-1 | CML: type TBC | 3 | 2016-02-09 | 2015-10-23 | 2013-11-14 | 2.5 | 1.4292 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.925 | 5.7 | 9 O'Clock | 25 | 6.35 | 25-FG-45034-03C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.8 | 5.7 | 5.7 | 0.057735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44011-01X01-P | CML-9 | 80-PW-44011-01X01-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21880 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 21.5 | CML-9 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 21 | 9 O'Clock | 80 | 11.13 | 80-PW-44011-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 23 | 21 | 21 | 21 | 1
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44024-01X01-P | CML-2 | 80-PW-44024-01X01-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21900 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 21 | CML-2 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-07-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 21 | 9 O'Clock | 80 | 11.13 | 80-PW-44024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 21 | 0
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 828 |  | 2014-04-02 08:00 | 2014-04-02 09:00 | [36 empty] | 6.05 | CML-4 | CML: Pipe Length | 3 | 2160-07-18 | 2165-05-28 | 2014-04-02 08:00 | 2.5 | 0.02391 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 6 O'Clock | 100 | 6.02 | 100-WC-40062-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6 | 6.1 | 0.057735
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2413 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 6.05 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6 | 6.1 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-6 | 200-FH-43114-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12814 |  | 2014-02-01 12:00 | 2014-02-01 14:00 | [36 empty] | 6.25 | CML-6 | CML: type TBC | 3 | 2030-09-01 | 2030-07-17 | 2014-02-01 12:00 | 2.5 | 0.22301 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 6.2 | 6.3 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-12 | 100-FH-43104-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12763 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 6.25 | CML-12 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.2 | 6.3 | 6.2 | 0.057735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-16 | 250-PW-44006-01X01 CML-16 | Yes | FPSO 2015 | Pipe Wall Thickness | 23187 | No reading taken due to CML already having two clamps on it to stop leak. | 2015-05-11 07:00 | 2015-05-11 15:00 | [37 empty] | CML-16 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 200 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-7 | 150-FH-43157-01C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10663 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.45 | CML-7 | CML: type TBC | 3 | 2016-06-08 | 2016-03-14 | 2013-11-18 | 2.5 | 1.5244 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 9 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.5 | 6.4 | 6.4 | 0.057735
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12969 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.55 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.6 | 6.5 | 6.6 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43141-01C02 | CML-2 | 150-FH-43141-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10653 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.7333 | CML-2 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-18 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.7 | 9 O'Clock | 100 | 6.02 | 100-FH-43141-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.8 | 6.7 |  | 6.7 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-1 | 150-FH-43157-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10657 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.75 | CML-1 | CML: type TBC | 3 | 2018-08-25 | 2018-03-28 | 2013-11-18 | 2.5 | 0.88029 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 9 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.8 | 6.8 | 6.7 | 6.7 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43030-01C02 | CML-4 | 400-FH-43030-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10028 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.75 | CML-4 | CML: type TBC | 3 | 2023-12-09 | 2022-07-20 | 2013-11-04 | 2.5 | 0.51474 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.7 | 6 O'Clock | 400 | 7.92 | 400-FH-43030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.8 | 7.7 | 7.7 | 7.8 | 0.057735
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43085-01C02 | CML-5 | 350-FL-43085-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10015 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.75 | CML-5 | CML: type TBC | 3 | 2023-12-09 | 2022-07-20 | 2013-11-04 | 2.5 | 0.51474 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.7 | 6 O'Clock | 350 | 7.92 | 350-FL-43085-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.8 | 7.7 | 7.7 | 7.8 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-45 | 400-FH-43508-01C02 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 23564 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.95 | CML-45 | CML: Elbow | 3 | 258310 | 229699 | 2015-08-10 07:30 | 2.5 | 0.00912 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8 | 8 | 7.9 | 0.057735
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-2 | 50-PG-23063-09C02 CML-2 | Yes | FPSO 2013 | Pipe Wall Thickness | 10728 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.05 | CML-2 | CML: type TBC | 3 | 2017-05-12 | 2016-05-03 | 2013-11-19 | 2.5 | 1.5795 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8 | 9 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.1 | 8.1 | 8 | 0.057735
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23064-09C02 | CML-3 | 50-PG-23064-09C02 CML-3 | Yes | FPSO 2013 | Pipe Wall Thickness | 10726 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.15 | CML-3 | CML: type TBC | 3 | 2017-12-24 | 2016-10-17 | 2013-11-19 | 2.5 | 1.3661 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 9 O'Clock | 50 | 8.74 | 50-PG-23064-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.2 | 8.2 | 8.1 | 0.057735
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-24 | 50-PL-23020-01C03 CML-24 |  | FPSO 2013 | Pipe Wall Thickness | 10138 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-24 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.2 | 8.2 | 0.057735
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-14 | 50-PL-23020-01C03 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10128 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-14 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 9 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.2 | 8.2 | 8.1 | 8.1 | 0.057735
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-10 | 50-PL-23020-01C03 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10124 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-10 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.2 | 8.2 | 0.057735
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-17 | 50-PL-23021-03C03 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10249 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-17 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.2 | 8.2 | 0.057735
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-10 | 50-PL-23021-03C03 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10242 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-10 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.2 | 8.2 | 0.057735
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-7 | 50-PL-23021-03C03 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10239 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-7 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 6 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.2 | 8.1 | 8.1 | 8.2 | 0.057735
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-12 | 50-PL-23023-03C03 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10212 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.15 | CML-12 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 6 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.2 | 8.1 | 8.2 | 0.057735
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-8 | 150-WC-40006-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20686 | Rope Access | 2014-05-26 13:00 | 2014-05-26 14:00 | [36 empty] | 13.15 | CML-8 | CML: type TBC | 3 | 2077-02-10 | 2060-04-06 | 2014-05-26 13:00 | 4.7 | 0 | A3: Inside Quadrant |  | 8.07 | 4.7 | 6.385 | 12.7 | 6 O'Clock | 50 | 11.07 | 50-PG-23061-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 13.6 | 13 | 12.7 | 13.3 | 0.3873
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-5 | 50-PL-23023-03C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10205 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.35 | CML-5 | CML: type TBC | 6 | 2019-08-18 | 2019-07-05 | 2013-11-08 | 2.5 | 1.0037 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.4 | 8.4 | 8.3 | 0.057735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-13 | 250-PW-44006-01X01 CML-13 | Yes | FPSO 2015 | Pipe Wall Thickness | 23184 | CML Wrapped due to leak | 2015-05-11 07:00 | 2015-05-11 15:00 | [37 empty] | CML-13 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-13 | 150-FH-43136-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2774 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.05 | CML-13 | CML: Pipe Length | 3 | 2056-08-07 | 2048-10-26 | 2014-03-13 09:00 | 1.03 | 0.14069 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7 | 9 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.97 |  | 7.1 | 7 | 7.1 | 7 | 0.057735
PG01 | Montara_Topside | Yes | Process Gas (23) | Pipework | 50-PG-23044-03C03 | CML-1 | 50-PG-23044-03C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5483 | Rope Access | 2014-05-28 14:00 | 2014-05-28 15:00 | [36 empty] | 8.55 | CML-1 | CML: Fitting | 6 | 2039-02-26 | 2038-08-29 | 2014-05-28 14:00 | 2.5 | 0.24227 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 6 O'Clock | 50 | 8.74 | 50-PG-23044-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.6 | 8.5 | 8.6 | 0.057735
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-13 | 400-WC-40025-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1273 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 11 | CML-13 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 10.6 | 9 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.9 | 11 | 11.5 | 10.6 | 0.37417
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45044-03C02 | CML-3 | 50-FG-45044-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20787 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 8.65 | CML-3 | CML: Elbow | 6 | 2073-12-23 | 2072-10-24 | 2014-10-10 07:00 | 2.5 | 0.10296 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PL-23032-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.7 | 8.6 | 8.6 | 0.057735
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38491-09C02 | CML-3 | 50-CG-38491-09C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2542 |  | 2014-04-03 10:00 | 2014-04-03 11:00 | [36 empty] | 8.65 | CML-3 | CML: type TBC | 3 | 2050-10-22 | 2041-02-05 | 2014-04-03 10:00 | 2.5 | 0.16677 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-CG-38491-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.7 | 8.6 | 8.6 | 0.057735
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-36 | 250-PL-20006-01C02-P CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 13206 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-36 | CML: Pipe Length | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-35 | 250-PL-20006-01C02-P CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 13205 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-35 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-34 | 250-PL-20006-01C02-P CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 13204 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-34 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-33 | 250-PL-20006-01C02-P CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 13203 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-33 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40047-01C02 | CML-1 | 50-WC-40047-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1701 | Rope Access | 2014-04-13 10:15 | 2014-04-13 11:15 | [36 empty] | 10.825 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 10:15 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.5 | 12 O'Clock | 50 | 5.54 | 50-WC-40047-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.5 | 10.6 | 11.1 | 11.1 | 0.32016
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-26 | 400-FH-43508-01C02 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6575 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.15 | CML-26 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 9.1 | 6 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.2 | 9.1 | 9.1 | 9.2 | 0.057735
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-9 | 50-FL-43454-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1881 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.15 | CML-9 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 9 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.2 | 9.2 | 9.1 | 9.1 | 0.057735
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-3 | 50-FL-43454-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1875 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.15 | CML-3 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 9 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.2 | 9.2 | 9.1 | 0.057735
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-1 | 50-FL-43454-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1873 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.15 | CML-1 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9.1 | 6 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.2 | 9.1 | 9.1 | 9.2 | 0.057735
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-3 | 25-PW-44028-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10309 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 9.4333 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2013-11-10 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.4 | 9 O'Clock | 25 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  |  | 9.4 | 9.5 | 9.4 | 0.057735
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-2 | 25-PW-44028-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22951 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 9.55 | CML-2 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.5 | 3 O'Clock | 20 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | -0.46497 | 9.5 | 9.5 | 9.6 | 9.6 | 0.057735
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-3 | 100-PG-23406-03C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20729 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 18.35 | CML-3 | CML: Reducing Tee | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 18 | 3 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.5 |  | 18.6 | 18 | 18.5 | 18.3 | 0.26458
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-13 | 100-PG-23406-03C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20739 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 18.65 | CML-13 | CML: Reducing Tee | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 18 | 12 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.5 |  | 18 | 19.1 | 19 | 18.5 | 0.50662
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-2 | 50-PG-23024-03C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10034 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 8.15 | CML-2 | CML: Pipe Length | 6 | 2018-09-01 | 2018-01-25 | 2013-11-06 | 0.97 | 1.4785 | A1: Outside Quadrant |  | 2.74 | 0.97 | 1.855 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.13 |  | 8.1 | 8.1 | 8.2 | 8.2 | 0.057735
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-23 | 250-PW-20040-03C03-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21407 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 15.45 | CML-23 | CML: Reducer | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 15.3 | 6 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.2 |  | 15.8 | 15.3 | 15.3 | 15.4 | 0.23805
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45030-03C03 | CML-2 | 50-PL-45030-03C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10465 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.35 | CML-2 | CML: type TBC | 6 | 2021-05-16 | 2020-06-22 | 2013-11-13 | 0.99 | 0.97333 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 8.3 | 3 O'Clock | 50 | 8.74 | 50-PL-45030-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.31 |  | 8.3 | 8.3 | 8.4 | 8.4 | 0.057735
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-6 | 50-PL-23300-09C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13122 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.35 | CML-6 | CML: type TBC | 6 | 2020-09-15 | 2019-09-17 | 2014-02-04 07:00 | 2.81 | 1.1319 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.3 | 9 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.49 |  | 10.4 | 10.4 | 10.3 | 10.3 | 0.057735
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-12 | 150-PG-20507-01C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2856 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.05 | CML-12 | CML: type TBC | 6 | 2020-04-22 | 2019-04-21 | 2014-03-16 07:00 | 2.5 | 1.2281 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10 | 3 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 10 | 10.1 | 10.1 | 0.057735
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-13 | 150-WC-40006-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1673 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 10.75 | CML-13 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.5 | 6 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.9 | 10.7 | 10.5 | 10.9 | 0.19149
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-8 | 50-PL-23300-09C03 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13124 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.45 | CML-8 | CML: type TBC | 6 | 2021-10-18 | 2020-08-25 | 2014-02-04 07:00 | 2.81 | 0.98493 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.4 | 9 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.59 |  | 10.5 | 10.5 | 10.4 | 10.4 | 0.057735
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-14 | 300-PW-44003-01C03 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 22879 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 14.85 | CML-14 | CML: Reducing Tee | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 14 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 | 0.56443 | 16.1 | 14.8 | 14 | 14.5 | 0.89629
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-6 | 400-WC-40025-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1266 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 10.8 | CML-6 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 10.6 | 6 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.8 | 10.8 | 10.6 | 11 | 0.1633
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40018-01C02 | CML-1 | 50-WC-40018-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1695 | Rope Access | 2014-04-13 09:15 | 2014-04-13 10:15 | [36 empty] | 10.875 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 09:15 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.7 | 9 O'Clock | 50 | 5.54 | 50-WC-40018-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.8 | 10.8 | 11.2 | 10.7 | 0.22174
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-13 | 300-FL-43080-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2392 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 10.45 | CML-13 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.4 | 6 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.5 | 10.4 | 10.4 | 10.5 | 0.057735
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-6 | 100-PG-23071-01C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2404 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 10.55 | CML-6 | CML: type TBC | 6 | 2027-10-19 | 2025-09-13 | 2014-03-19 13:00 | 2.5 | 0.58842 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.5 | 9 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.5 | 10.6 | 10.6 | 10.5 | 0.057735
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-11 | 100-DH-56088-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5204 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 10.65 | CML-11 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 10.6 | 9 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.7 | 10.6 | 10.7 | 10.6 | 0.057735
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23017-03C03-A | CML-3 | 250-PG-23017-03C03-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10977 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 12.65 | CML-3 | CML: Elbow | 6 | 2063-11-12 | 2056-11-15 | 2014-01-09 | 4.4 | 0.16441 | A1: Outside Quadrant |  | 6.7 | 4.4 | 5.55 | 12.6 | 3 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 12.6 | 12.6 | 12.7 | 12.7 | 0.057735
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-8 | 80-PG-23025-06C03 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13079 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 11.05 | CML-8 | CML: Pipe Length | 6 | 2057-07-12 | 2051-05-12 | 2014-02-07 11:00 | 2.8 | 0.1887 | A2: Right Quadrant |  | 5.13 | 2.8 | 3.965 | 11 | 6 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11.1 | 11 | 11 | 11.1 | 0.057735
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-6 | 50-PG-44022-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5849 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 12.1333 | CML-6 | CML: Reducing Tee | 6 | 2075-10-24 | 2074-08-12 | 2014-06-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 12.1 | 3 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 12.1 | 12.1 |  | 12.2 | 0.057735
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 80-FG-45453-01C02-P | CML-1 | 80-FG-45453-01C02-P CML-1 | yes | FPSO 2016 | Pipe Wall Thickness | 24311 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.925 | CML-1 | CML: Elbow | 3 | 2022-06-09 | 2023-06-28 | 2016-05-27 07:00 | 2.5 | 0.33112 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 3 O'Clock | 80 | 5.49 | 80-FG-45453-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.8 | 4.5 | 5.3 | 5.1 | 0.35
FG06 | Montara_Topside | No | Separation (20) | Pipework | 80-FG-45453-01C02-P | CML-6 | 80-FG-45453-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21809 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 19.75 | CML-6 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-10-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 18.3 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.8 |  | 20.8 | 20.9 | 19 | 18.3 | 1.3026
FG06 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-FG-45453-01C02-P | CML-3 | 80-FG-45453-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20580 | Rope Access | 2014-05-27 07:00 | 2014-05-27 08:00 | [36 empty] | 18.85 | CML-3 | CML: Fitting | 6 | 2096-09-16 | 2085-01-22 | 2014-05-27 07:00 | 2.8 | 0 | A3: Inside Quadrant |  | 5.13 | 2.8 | 3.965 | 18.6 | 6 O'Clock | 80 | 11.13 | 80-PG-23046-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.8 |  | 18.9 | 18.7 | 18.6 | 19.2 | 0.26458
FG06 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-FG-45453-01C02-P | CML-12 | 80-FG-45453-01C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23440 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 19.175 | CML-12 | CML: Reducing Tee | 3 | 2026-10-04 | 2021-02-21 | 2015-07-23 07:00 | 2.5 | 1.4184 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 18.4 | 6 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.9 | 0.092007 | 20.2 | 18.6 | 18.4 | 19.5 | 0.83417
FG06 | Montara_Topside | No | Separation (20) | Pipework | 80-FG-45453-01C02-P | CML-13 | 80-FG-45453-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21751 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 20.875 | CML-13 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 20.8 | 12 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.9 |  | 20.8 | 20.9 | 20.9 | 20.9 | 0.05
FG06 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 80-FG-45453-01C02-P | CML-5 | 80-FG-45453-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20796 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 |  |  | Administrator | 2015-09-07 10:59 | [32 empty] | 20.8 | CML-5 | CML: Reducer | 3 | 2054-10-24 | 2049-02-10 | 2014-07-18 11:00 | 4.6 | 0 | A3: Inside Quadrant |  | 5.74 | 4.6 | 5.17 | 20.5 | 9 O'Clock | 100 | 8.74 | 50-CG-38002-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.9 |  | 21.1 | 21.1 | 20.5 | 20.5 | 0.34641
FG06 | Montara_Topside | No | Separation (20) | Pipework | 80-FG-45453-01C02-P | CML-15 | 80-FG-45453-01C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 6138 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 20.85 | CML-15 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 20.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.9 |  | 20.9 | 20.8 | 20.9 | 20.8 | 0.057735
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 80-FG-45453-01C02-P | CML-2 | 80-FG-45453-01C02-P CML-2 | yes | FPSO 2016 | Pipe Wall Thickness | 24312 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.675 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2016-05-27 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 9 O'Clock | 80 | 5.49 | 80-FG-45453-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 5.5 | 5.8 | 5.5 | 0.20616
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23406-03C03 | CML-10 | 100-PG-23406-03C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20736 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 20.25 | CML-10 | CML: Reducing Tee | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 18.5 | 3 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16 |  | 21 | 18.5 | 21 | 20.5 | 1.1902
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-4 | 300-PG-20005-03C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22766 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.65 | CML-4 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.6 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 | 0 | 14.7 | 14.6 | 14.7 | 14.6 | 0.057735
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-1 | 25-VA-23054-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2044 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 13.05 | CML-1 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 13 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.5 |  | 13.1 | 13.1 | 13 | 13 | 0.057735
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-11 | 50-CG-38001-09C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10924 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.05 | CML-11 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.2222 | A1: Outside Quadrant |  | 5.74 |  |  | 8 | 6 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8 | 8 | 8.1 | 8 | 8.1 | 0.057735
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-5 | 50-CG-38001-09C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10918 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.05 | CML-5 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.2222 | A3: Inside Quadrant |  | 5.74 |  |  | 8 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8 | 8.1 | 8.1 | 8 | 8 | 0.057735
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-3 | 50-CG-38001-09C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10916 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.05 | CML-3 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.2222 | A2: Right Quadrant |  | 5.74 |  |  | 8 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8 | 8.1 | 8 | 8.1 | 8 | 0.057735
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-6 | 200-PG-23008-15S01-A CML-6 | Yes | FPSO 2013 | Pipe Wall Thickness | 10092 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 20.35 | CML-6 | CML: Elbow | 1 | 2014-11-08 | 2014-03-19 | 2013-11-07 | 14.06 | 6.2211 | A3: Inside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.3 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.24 |  | 20.4 | 20.4 | 20.3 | 20.3 | 0.057735
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-19 | 200-PG-23006-09C02-PA CML-19 | Yes | FPSO 2014 | Pipe Wall Thickness | 23852 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 20.85 | CML-19 | CML: Elbow | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 20.8 | 3 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 20.8 | 20.8 | 20.9 | 20.9 | 0.057735
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-11 | 50-OL-69005-01S01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8188 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Medium alarm breach | 3.95 | CML-11 | CML: type TBC | 1 | 2015-08-17 | 2014-12-10 | 2015-01-24 07:30 | 2.5 | 2.3149 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 3.8 | 12 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4 | 4.1 | 3.9 | 0.1291
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-10 | 50-OL-69005-01S01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8187 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Medium alarm breach | 4.175 | CML-10 | CML: type TBC | 1 | 2015-08-17 | 2014-12-10 | 2015-01-24 07:30 | 2.5 | 2.3149 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 3.8 | 12 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4.1 | 4.4 | 4.4 | 0.28723
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-3 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 21141 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 21.2 | CML-3 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 21.1 | 6 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.2 |  | 21.2 | 21.3 | 21.1 | 21.2 | 0.08165
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-1 | 50-OL-69005-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8178 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Medium alarm breach | 4.325 | CML-1 | CML: type TBC | 1 | 2015-08-17 | 2014-12-10 | 2015-01-24 07:30 | 2.5 | 2.3149 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 3.8 | 12 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4.5 | 5 | 4 | 0.53774
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-12 | 50-OL-69005-01S01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8189 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Medium alarm breach | 3.975 | CML-12 | CML: type TBC | 1 | 2015-09-07 | 2014-12-25 | 2015-01-24 07:30 | 2.5 | 2.2543 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 3.9 | 9 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.1 | 4 | 3.9 | 0.095743
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-15 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 5456 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 2.667mm/ yr | [35 empty] | 19.225 | CML-15 | CML: Reducing Tee | 3 | 2020-07-05 | 2017-07-11 | 2014-05-28 07:00 | 2.5 | 2.6671 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 18.8 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.3 |  | 19.1 | 19 | 20 | 18.8 | 0.53151
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-2 | 50-OL-69005-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8179 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Medium alarm breach | 4.15 | CML-2 | CML: type TBC | 1 | 2015-09-07 | 2014-12-25 | 2015-01-24 07:30 | 2.5 | 2.2543 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 3.9 | 12 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4 | 4.4 | 4.3 | 0.23805
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-10 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 5875 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | [36 empty] | 20.4 | CML-10 | CML: Reducer | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 09:30 | 3.3 | 0 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 19.7 | 12 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.4 |  | 19.7 | 20.1 | 20.9 | 20.9 | 0.6
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-1 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23462 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 20.15 | CML-1 | CML: Reducer | 3 | 2059-02-11 | 2051-04-06 | 2015-07-24 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 20.1 | 3 O'Clock | 300 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.49 | -9.8081 | 20.1 | 20.1 | 20.2 | 20.2 | 0.057735
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-6 | 50-OL-69005-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8183 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 5.3 | CML-6 | CML: type TBC | 1 | 2016-03-18 | 2015-05-07 | 2015-01-24 07:30 | 2.5 | 1.8301 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 4.6 | 12 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.5 | 5.6 | 5.5 | 0.46904
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-2 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 21530 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 19.9 | CML-2 | CML: Reducer | 6 | 2098-02-09 | 2085-10-05 | 2014-07-13 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 19 | 9 O'Clock | 80 | 10.97 | 150-PG-20055-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.5 |  | 19.4 | 21 | 20.2 | 19 | 0.88694
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-9 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23053 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 19.925 | CML-9 | CML: Reducing Tee | 6 | 2099-09-17 | 2086-07-24 | 2015-05-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 19.1 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.6 |  | 19.8 | 20.4 | 20.4 | 19.1 | 0.61847
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-7 | 50-OL-69005-01S01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8184 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 5.875 | CML-7 | CML: type TBC | 1 | 2017-03-21 | 2016-01-16 | 2015-01-24 07:30 | 2.5 | 1.3453 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 5.4 | 12 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.9 | 6.5 | 5.7 | 0.46458
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-9 | 50-OL-69005-01S01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8186 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 6.55 | CML-9 | CML: type TBC | 1 | 2017-10-24 | 2016-06-14 | 2015-01-24 07:30 | 2.5 | 1.1635 | A4: Left Quadrant |  | 6.62 | 2.5 | 4.0838 | 5.7 | 9 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.4 | 7.5 | 6.6 | 5.7 | 0.74162
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-4 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 5879 |  | 2014-06-25 13:00 | 2014-06-25 14:00 | [36 empty] | 20.5 | CML-4 | CML: Reducer | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 13:00 | 3.3 | 0 | A2: Right Quadrant |  | 6.7 | 3.3 | 5 | 20.1 | 9 O'Clock | 200 | 12.7 | 200-PG-20303-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.8 |  | 20.9 | 20.1 | 20.9 | 20.1 | 0.46188
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-6 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 22824 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 20.175 | CML-6 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 19.4 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.9 | -1.9975 | 19.4 | 20.3 | 20.5 | 20.5 | 0.5252
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-5 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 5884 |  | 2014-06-25 14:00 | 2014-06-25 15:00 | [36 empty] | 21.15 | CML-5 | CML: Reducer | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 14:00 | 3.3 | 0 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 20.2 | 9 O'Clock | 200 | 12.7 | 200-PG-20301-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.9 |  | 21 | 20.9 | 22.5 | 20.2 | 0.96782
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-5 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 21664 |  | 2014-06-25 14:00 | 2014-06-25 15:00 | [36 empty] | 21.15 | CML-5 | CML: Reducer | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 14:00 | 3.3 | 0 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 20.2 | 9 O'Clock | 200 | 12.7 | 200-PG-20301-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.9 |  | 21 | 20.9 | 22.5 | 20.2 | 0.96782
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-3 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 5671 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 1.931mm/ yr | [35 empty] | 20.6 | CML-3 | CML: Elbow | 3 | 2023-03-20 | 2019-02-03 | 2014-06-21 14:00 | 2.5 | 1.9311 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 19.4 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.9 |  | 21 | 21 | 21 | 19.4 | 0.8
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-8 | 50-OL-69005-01S01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8185 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 6.3 | CML-8 | CML: type TBC | 1 | 2018-04-28 | 2016-10-21 | 2015-01-24 07:30 | 2.5 | 1.0423 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 5.9 | 12 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.2 | 6.7 | 6.4 | 0.33665
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-9 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23437 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 20.05 | CML-9 | CML: Reducing Tee | 3 | 2035-06-18 | 2026-03-08 | 2015-07-23 07:00 | 2.5 | 0.8585 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 19.6 | 12 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.1 | 1.2881 | 19.6 | 20.2 | 20.2 | 20.2 | 0.3
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-8 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23436 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | Check Corrosion Rate of 0.859mm/ yr |  | John Wilson | 2017-03-23 11:02 | Anomily raised CML still on 12 monthly frequancy | [31 empty] | 19.9 | CML-8 | CML: Pipe Length | 3 | 2035-06-18 | 2026-03-08 | 2015-07-23 07:00 | 2.5 | 0.8585 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 19.6 | 3 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.1 | 1.2881 | 19.6 | 19.6 | 20.2 | 20.2 | 0.34641
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-4 | 50-OL-69005-01S01 |  | FPSO 2016 | Pipe Wall Thickness | 24424 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.563mm/ yr |  | John Wilson | 2017-03-23 11:12 | Anomily raised CML on 12 Monthly schedule | [31 empty] | 20.325 | CML-4 | CML: Fitting | 3 | 2047-01-04 | 2032-11-15 | 2016-07-02 07:00 | 2.5 | 0.56339 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 19.7 | 6 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.2 | 0.42319 | 20 | 20.9 | 19.7 | 20.7 | 0.56789
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-10 | 50-OL-69005-01S01 |  | FPSO 2016 | Pipe Wall Thickness | 24428 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.531mm/ yr | [35 empty] | 20.45 | CML-10 | CML: Reducer | 3 | 2049-01-21 | 2034-01-22 | 2016-07-02 07:00 | 2.5 | 0.53101 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 19.8 | 12 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.3 | 0.42319 | 19.8 | 20.4 | 20.9 | 20.7 | 0.47958
OL01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-OL-69005-01S01 | CML-19 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 22884 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 20.25 | CML-19 | CML: Equal Tee | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 19.8 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.3 | 0.18814 | 20.4 | 20.4 | 20.4 | 19.8 | 0.3
OL01 | Montara_Topside | No | Separation (20) | Pipework | 50-OL-69005-01S01 | CML-6 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 21454 | Protective mesh removed | 2014-06-29 09:30 | 2014-06-29 11:00 | [36 empty] | 20.475 | CML-6 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-06-29 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 19.8 | 12 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.3 |  | 19.8 | 20.9 | 20.9 | 20.3 | 0.53151
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-24 | 50-OL-69005-01S01 |  | FPSO 2016 | Pipe Wall Thickness | 24430 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | [36 empty] | 20.45 | CML-24 | CML: Equal Tee | 3 | 2051-05-17 | 2035-05-27 | 2016-07-02 07:00 | 2.5 | 0.49863 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 19.9 | 12 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.4 | 0.31739 | 19.9 | 20.7 | 20.2 | 21 | 0.49329
OL01 | Montara_Topside | No | Produced Water (44) | Pipework | 50-OL-69005-01S01 | CML-19 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 21861 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 16:27 | [32 empty] | 21.4 | CML-19 | CML: Equal Tee | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 19.9 | 12 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.4 |  | 19.9 | 22.4 | 21.4 | 21.9 | 1.0801
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-4 | 50-OL-69005-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8181 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 6.175 | CML-4 | CML: type TBC | 1 | 2018-08-17 | 2017-01-05 | 2015-01-24 07:30 | 2.5 | 0.98172 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 6 | 12 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.3 | 6.3 | 0.15
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-5 | 50-OL-69005-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8182 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 7.2 | CML-5 | CML: type TBC | 1 | 2019-10-24 | 2017-10-31 | 2015-01-24 07:30 | 2.5 | 0.79992 | A1: Outside Quadrant |  | 6.62 | 2.5 | 4.0838 | 6.3 | 12 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7.1 | 8.3 | 7.1 | 0.82462
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-1 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 5442 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 1.455mm/ yr | [35 empty] | 20.25 | CML-1 | CML: Elbow | 3 | 2026-06-04 | 2020-12-13 | 2014-05-28 07:00 | 2.5 | 1.4548 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20 | 12 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.5 |  | 20 | 20.2 | 20.4 | 20.4 | 0.19149
OL01 | Montara_Topside | No | Flare (43) | Pipework | 50-OL-69005-01S01 | CML-8 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 12735 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 5.625 | CML-8 | CML: Pipe Length | 3 | 2015-11-26 | 2015-12-26 | 2014-01-24 09:00 | 2.5 | 1.4146 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 9 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.8 | 6.1 | 5.5 | 5.1 | 0.4272
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-3 | 50-OL-69005-01S01 |  | FPSO 2016 | Pipe Wall Thickness | 24423 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.434mm/ yr | [35 empty] | 20.375 | CML-3 | CML: Elbow | 3 | 2057-01-14 | 2038-09-06 | 2016-07-02 07:00 | 2.5 | 0.43387 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 20.1 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.6 | 0.1058 | 20.9 | 20.1 | 20.4 | 20.1 | 0.37749
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-4 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23432 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 20.175 | CML-4 | CML: Fitting | 3 | 2043-09-09 | 2030-12-13 | 2015-07-23 07:00 | 2.5 | 0.62521 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.1 | 12 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.6 | 0.27602 | 20.1 | 20.2 | 20.2 | 20.2 | 0.05
OL01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-OL-69005-01S01 | CML-2 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 20772 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 20.7 | CML-2 | CML: Equal Tee | 6 | 2074-02-03 | 2073-10-17 | 2014-10-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 20.1 | 12 O'Clock | 100 | 8.56 | 100-PG-23410-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.6 |  | 20.1 | 20.9 | 20.9 | 20.9 | 0.4
OL01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-OL-69005-01S01 | CML-18 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 20315 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 20.475 | CML-18 | CML: type TBC | 6 | 2098-02-09 | 2085-10-05 | 2014-10-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 20.1 | 6 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.6 |  | 20.8 | 20.8 | 20.1 | 20.2 | 0.37749
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-23 | 50-OL-69005-01S01 |  | FPSO 2014 | Pipe Wall Thickness | 5464 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 1.354mm/ yr | [35 empty] | 20.375 | CML-23 | CML: Elbow | 3 | 2027-05-25 | 2021-07-06 | 2014-05-28 07:00 | 2.5 | 1.3538 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.1 | 12 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.6 |  | 20.1 | 20.3 | 20.9 | 20.2 | 0.3594
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-24 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23452 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 20.2 | CML-24 | CML: Equal Tee | 3 | 2046-02-16 | 2032-05-12 | 2015-07-23 07:00 | 2.5 | 0.57856 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.2 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 | -4.0483 | 20.2 | 20.2 | 20.2 | 20.2 | 0
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-10 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23438 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 20.2 | CML-10 | CML: Reducer | 3 | 2046-02-16 | 2032-05-12 | 2015-07-23 07:00 | 2.5 | 0.57856 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.2 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 | -2.9442 | 20.2 | 20.2 | 20.2 | 20.2 | 0
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-7 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23435 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 20.2 | CML-7 | CML: Pipe Length | 3 | 2046-02-16 | 2032-05-12 | 2015-07-23 07:00 | 2.5 | 0.57856 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.2 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 | 0.73606 | 20.2 | 20.2 | 20.2 | 20.2 | 0
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-5 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23433 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 20.2 | CML-5 | CML: Reducing Tee | 3 | 2046-02-16 | 2032-05-12 | 2015-07-23 07:00 | 2.5 | 0.57856 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.2 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 | 0.18401 | 20.2 | 20.2 | 20.2 | 20.2 | 0
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-3 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23431 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 20.2 | CML-3 | CML: Elbow | 3 | 2046-02-16 | 2032-05-12 | 2015-07-23 07:00 | 2.5 | 0.57856 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.2 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 | -0.73606 | 20.2 | 20.2 | 20.2 | 20.2 | 0
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-2 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23430 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 20.2 | CML-2 | CML: Elbow | 3 | 2046-02-16 | 2032-05-12 | 2015-07-23 07:00 | 2.5 | 0.57856 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.2 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 | 0.73606 | 20.2 | 20.2 | 20.2 | 20.2 | 0
OL01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-OL-69005-01S01 | CML-1 | 50-OL-69005-01S01 |  | FPSO 2015 | Pipe Wall Thickness | 23429 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 20.2 | CML-1 | CML: Pipe Length | 3 | 2046-02-16 | 2032-05-12 | 2015-07-23 07:00 | 2.5 | 0.57856 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.2 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 | 0.73606 | 20.2 | 20.2 | 20.2 | 20.2 | 0
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69005-01S01 | CML-3 | 50-OL-69005-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8180 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 6.85 | CML-3 | CML: type TBC | 1 | 2021-09-10 | 2019-02-18 | 2015-01-24 07:30 | 2.5 | 0.61812 | A3: Inside Quadrant |  | 6.62 | 2.5 | 4.0838 | 6.6 | 6 O'Clock | 80 | 7.62 | 80-OL-69005-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.3 | 6.8 | 6.6 | 6.7 | 0.31091
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-1 | 200-PG-23051-09C02-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13106 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.5 | CML-1 | CML: type TBC | 3 | 2103-01-05 | 2073-03-18 | 2014-02-07 11:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 19 | 12 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 19 | 19.1 | 20 | 19.9 | 0.52281
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-35 | 150-PG-23506-25C02 CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 20662 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | [36 empty] | 21.025 | CML-35 | CML: Pipe Length | 3 | 2019-09-26 | 2018-02-19 | 2014-05-28 07:00 | 15.88 | 0.95975 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 21 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.12 | -0.4938 | 21.1 | 21 | 21 | 21 | 0.05
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56141-01C02 | CML-14 | 50-DH-56141-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 22776 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 20.525 | CML-14 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 20.5 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.6 | -0.25002 | 20.5 | 20.6 | 20.5 | 20.5 | 0.05
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-15 | 100-FG-45001-09C02 CML-15 | Yes | FPSO 2015 | Pipe Wall Thickness | 23320 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.225 | CML-15 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 11.2 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | -0.72362 | 11.2 | 11.2 | 11.2 | 11.3 | 0.05
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-32 | 250-PL-20006-01C02-P CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 13202 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-32 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44017-01X01 | CML-3 | 80-PL-44017-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21883 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.975 | CML-3 | CML: Elbow | 3 | 2058-07-22 | 2063-10-24 | 2014-10-10 07:00 | 2.5 | 0.06619 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 12 O'Clock | 80 | 5.49 | 80-PL-44017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.3 | 5.9 | 6.3 | 0.4272
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-30 | 80-PL-44017-01X01 CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 5471 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 1.152mm/ yr | [35 empty] | 20.825 | CML-30 | CML: Straight | 3 | 2029-11-06 | 2022-12-07 | 2014-05-28 07:00 | 2.5 | 1.1517 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 20.3 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.8 |  | 21 | 21 | 21 | 20.3 | 0.35
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-22 | 80-PL-44017-01X01 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 5463 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 1.152mm/ yr | [35 empty] | 20.375 | CML-22 | CML: Reducing Tee | 3 | 2029-11-06 | 2022-12-07 | 2014-05-28 07:00 | 2.5 | 1.1517 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.3 | 12 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.8 |  | 20.3 | 20.4 | 20.4 | 20.4 | 0.05
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 13063 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 30.175 | CML-2 | CML: type TBC | 6 | 2117-11-29 | 2095-08-30 | 2014-01-10 07:00 | 10.17 | 0 | A1: Outside Quadrant |  | 14.62 | 10.17 | 12.395 | 28 | 12 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.83 |  | 28 | 31 | 28.7 | 33 | 2.278
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-7 | 80-PL-44017-01X01 CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24426 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 |  |  | John Wilson | 2017-03-23 11:33 | Loss within CA include this CML in the next inspection. | [31 empty] | 20.75 | CML-7 | CML: Pipe Length | 3 | 2069-08-15 | 2045-12-20 | 2016-07-02 07:00 | 2.5 | 0.33674 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.4 | 12 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.9 | -0.21159 | 20.4 | 20.9 | 20.9 | 20.8 | 0.23805
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-5 | 80-PL-44017-01X01 CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24425 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.337mm/ yr |  | John Wilson | 2017-03-23 11:32 | Loss within CA include this CML in the next inspection | [31 empty] | 20.775 | CML-5 | CML: Reducing Tee | 3 | 2069-08-15 | 2045-12-20 | 2016-07-02 07:00 | 2.5 | 0.33674 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.4 | 6 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.9 | -0.21159 | 20.9 | 20.9 | 20.4 | 20.9 | 0.25
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-5 | 80-PL-44017-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5673 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 0.984mm/ yr | [35 empty] | 20.85 | CML-5 | CML: Reducing Tee | 3 | 2032-08-22 | 2024-07-20 | 2014-06-21 14:00 | 2.5 | 0.98448 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 20.4 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.9 |  | 21 | 21 | 21 | 20.4 | 0.3
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-4 | 80-PL-44017-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5672 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 0.984mm/ yr | [35 empty] | 21.6 | CML-4 | CML: Fitting | 3 | 2032-08-22 | 2024-07-20 | 2014-06-21 14:00 | 2.5 | 0.98448 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.4 | 6 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.9 |  | 21 | 22.5 | 20.4 | 22.5 | 1.0677
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-20 | 80-PL-44017-01X01 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 5461 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 1.051mm/ yr | [35 empty] | 20.825 | CML-20 | CML: Straight | 3 | 2031-06-06 | 2023-11-06 | 2014-05-28 07:00 | 2.5 | 1.0507 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.4 | 6 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.9 |  | 21 | 21 | 20.4 | 20.9 | 0.28723
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-12 | 80-PL-44017-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20738 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 20.875 | CML-12 | CML: Reducing Tee | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 20.5 | 9 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18 |  | 21 | 21 | 21 | 20.5 | 0.25
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-11 | 80-PL-44017-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20737 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 20.9 | CML-11 | CML: Reducing Tee | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 20.5 | 3 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18 |  | 21 | 20.5 | 21 | 21.1 | 0.2708
PL04 | Montara_Topside | No | Fuel Gas (45) | Pipework | 80-PL-44017-01X01 | CML-7 | 80-PL-44017-01X01 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10410 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 20.5 | CML-7 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 20.5 | 9 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18 |  | 20.5 |  | 20.5 | 20.5 | 0
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24421 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | [36 empty] | 20.825 | CML-1 | CML: Pipe Length | 3 | 2083-01-02 | 2053-09-20 | 2016-07-02 07:00 | 2.5 | 0.27198 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 20.6 | 12 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.1 | -0.42319 | 20.6 | 20.9 | 20.9 | 20.9 | 0.15
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-23 | 80-PL-44017-01X01 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 13139 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 21.05 | CML-23 | CML: type TBC | 6 | 2096-01-05 | 2084-09-16 | 2014-02-04 07:00 | 2.81 | 0 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 21 | 9 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.19 |  | 21 | 21.1 | 21.1 | 21 | 0.057735
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-9 | 80-PL-44017-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2744 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 21.3667 | CML-9 | CML: Pipe Length | 3 | 2096-09-16 | 2070-01-23 | 2014-03-13 09:00 | 2.8 | 0 | A1: Outside Quadrant |  | 8.13 | 2.8 | 5.465 | 21 | 12 O'Clock | 150 | 11.13 | 80-PG-23050-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.2 |  | 21 | 22 |  | 21.1 | 0.55076
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-8 | 80-PL-44017-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2743 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 21.45 | CML-8 | CML: Reducer | 3 | 2096-09-16 | 2070-01-23 | 2014-03-13 09:00 | 2.8 | 0 | A1: Outside Quadrant |  | 8.13 | 2.8 | 5.465 | 21 | 12 O'Clock | 150 | 11.13 | 80-PG-23050-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.2 |  | 21 | 22.6 | 21.1 | 21.1 | 0.76811
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20317 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 21.125 | CML-1 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 20.8 | 6 O'Clock | 80 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.3 |  | 21.6 | 20.8 | 20.8 | 21.3 | 0.39476
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21882 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 6 | CML-2 | CML: Pipe Length | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-PL-44017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.3 | 6.4 | 5.6 | 5.7 | 0.40825
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21881 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.775 | CML-1 | CML: Pipe Length | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-PL-44017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 5.7 | 5.6 | 5.9 | 0.15
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-9 | 80-PL-44017-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5677 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 0.417mm/ yr | [35 empty] | 21.1 | CML-9 | CML: Reducing Tee | 3 | 2058-11-09 | 2039-09-26 | 2014-06-21 14:00 | 2.5 | 0.41651 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21.4 | 21 | 0.2
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-8 | 80-PL-44017-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5676 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 0.417mm/ yr | [35 empty] | 21 | CML-8 | CML: Pipe Length | 3 | 2058-11-09 | 2039-09-26 | 2014-06-21 14:00 | 2.5 | 0.41651 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 21 | 0
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-7 | 80-PL-44017-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5675 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 0.417mm/ yr | [35 empty] | 21 | CML-7 | CML: Pipe Length | 3 | 2058-11-09 | 2039-09-26 | 2014-06-21 14:00 | 2.5 | 0.41651 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 21 | 0
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5674 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [36 empty] | 21.025 | CML-6 | CML: Elbow | 3 | 2058-11-09 | 2039-09-26 | 2014-06-21 14:00 | 2.5 | 0.41651 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 200 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21.1 | 21 | 0.05
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5670 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 0.417mm/ yr | [35 empty] | 21.2 | CML-2 | CML: Elbow | 3 | 2058-11-09 | 2039-09-26 | 2014-06-21 14:00 | 2.5 | 0.41651 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21.8 | 21 | 0.4
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5669 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 0.417mm/ yr | [35 empty] | 21 | CML-1 | CML: Pipe Length | 3 | 2058-11-09 | 2039-09-26 | 2014-06-21 14:00 | 2.5 | 0.41651 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 21 | 0
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-29 | 80-PL-44017-01X01 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 5470 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 0.445mm/ yr | [35 empty] | 21.2 | CML-29 | CML: Reducing Tee | 3 | 2055-12-29 | 2038-01-28 | 2014-05-28 07:00 | 2.5 | 0.44452 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21.8 | 21 | 0.4
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-28 | 80-PL-44017-01X01 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 5469 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 0.445mm/ yr | [35 empty] | 21.2 | CML-28 | CML: Elbow | 3 | 2055-12-29 | 2038-01-28 | 2014-05-28 07:00 | 2.5 | 0.44452 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 6 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 21.8 | 0.4
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-26 | 80-PL-44017-01X01 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 5467 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 0.445mm/ yr | [35 empty] | 21 | CML-26 | CML: Straight | 3 | 2055-12-29 | 2038-01-28 | 2014-05-28 07:00 | 2.5 | 0.44452 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 21 | 0
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-25 | 80-PL-44017-01X01 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 5466 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 0.445mm/ yr | [35 empty] | 21 | CML-25 | CML: Reducing Tee | 3 | 2055-12-29 | 2038-01-28 | 2014-05-28 07:00 | 2.5 | 0.44452 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 21 | 0
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-24 | 80-PL-44017-01X01 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 5465 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 0.445mm/ yr | [35 empty] | 21.025 | CML-24 | CML: Straight | 3 | 2055-12-29 | 2038-01-28 | 2014-05-28 07:00 | 2.5 | 0.44452 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21.1 | 21 | 21 | 21 | 0.05
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-21 | 80-PL-44017-01X01 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 5462 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 0.445mm/ yr | [35 empty] | 21.125 | CML-21 | CML: Straight | 3 | 2055-12-29 | 2038-01-28 | 2014-05-28 07:00 | 2.5 | 0.44452 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21.4 | 21 | 21.1 | 21 | 0.1893
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-27 | 80-PL-44017-01X01 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 5468 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 0.445mm/ yr | [35 empty] | 21.25 | CML-27 | CML: Elbow | 3 | 2055-12-29 | 2038-01-28 | 2014-05-28 07:00 | 2.5 | 0.44452 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 6 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 22 | 0.5
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-19 | 80-PL-44017-01X01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 5460 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 0.445mm/ yr | [35 empty] | 21 | CML-19 | CML: Reducing Tee | 3 | 2055-12-29 | 2038-01-28 | 2014-05-28 07:00 | 2.5 | 0.44452 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 21 | 0
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-17 | 80-PL-44017-01X01 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 5458 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 0.445mm/ yr | [35 empty] | 21 | CML-17 | CML: Reducer | 3 | 2055-12-29 | 2038-01-28 | 2014-05-28 07:00 | 2.5 | 0.44452 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.5 |  | 21 | 21 | 21 | 21 | 0
PL04 | Montara_Topside | No | Cooling Medium (40) | Pipework | 80-PL-44017-01X01 | CML-21 | 80-PL-44017-01X01 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 5689 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [36 empty] | 21.925 | CML-21 | CML: Pipe Length | 3 | 223999 | 2302-12-10 | 2014-06-21 14:00 | 2.5 | 0.03786 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 21.4 | 12 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 18.9 |  | 21.4 | 22 | 22.3 | 22 | 0.37749
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23537 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 | [36 empty] | 28.825 | CML-1 | CML: Reducer | 6 | 2110-07-06 | 2091-12-17 | 2015-08-03 09:30 | 8.55 | 0 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 27.8 | 3 O'Clock | 250 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 19.25 |  | 29 | 27.8 | 28.9 | 29.6 | 0.75
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44017-01X01 | CML-4 | 80-PL-44017-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21884 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 6.3 | CML-4 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-PL-44017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 6.6 | 6.6 | 0.42426
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21886 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 6.125 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-PL-44017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 6 | 6.5 | 0.35
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44017-01X01 | CML-5 | 80-PL-44017-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21885 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 6.35 | CML-5 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 12 O'Clock | 80 | 5.49 | 80-PL-44017-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.3 | 6.9 | 6.3 | 0.41231
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-7 | 80-PW-20024-01C03-P CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 23051 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 5.675 | CML-7 | CML: Reducing Tee | 6 | 2016-04-08 | 2015-11-01 | 2015-05-06 07:00 | 2.5 | 3.0214 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 5.3 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.8 | 5.3 | 5.8 | 0.25
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-19 | 50-PL-23300-09C03 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 13135 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.775 | CML-19 | CML: type TBC | 6 | 2028-08-03 | 2026-07-07 | 2014-02-04 07:00 | 2.81 | 0.54392 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.7 | 6 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.89 |  | 10.8 | 10.8 | 10.7 | 10.8 | 0.05
PG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45303-03C03-P | CML-1 | 80-FG-45303-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22055 | Protective mesh removed. | 2014-06-30 07:00 | 2014-06-30 08:00 | [36 empty] | 10.775 | CML-1 | CML: Fitting | 6 | 2035-01-30 | 2031-10-12 | 2014-06-30 07:00 | 2.5 | 0.39806 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 10.7 | 3 O'Clock | 80 | 11.13 | 80-FG-45303-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.8 | 10.7 | 10.8 | 10.8 | 0.05
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-31 | 250-PL-20006-01C02-P CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 13201 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-31 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-17 | 50-FG-45300-01C02 CML-17 | yes | FPSO 2015 | Pipe Wall Thickness | 7840 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:40 | [32 empty] | 5.175 | CML-17 | CML: Pipe Length | 3 | 2024-08-09 | 2025-10-21 | 2015-01-13 13:00 | 2.5 | 0.27149 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.1 | 5.2 | 5.2 | 0.05
PG06 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 200-PG-23008-15S01-A |  | 200-PG-23008-15S01-A | yes | FPSO 2014 | Pipe Wall Thickness | 22105 | Rope access | 2014-06-02 09:30 | 2014-06-02 11:00 | [36 empty] | 5.125 | 50-CG-38302-01C02-P | Piping | 3 | 2020-05-06 |  | 2014-06-02 09:30 |  | 0.43832 | A2: Right Quadrant |  |  | 2.5 |  | 5.1 | 9 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 5.1 | 5.2 | 5.1 | 5.1 | 5.1 | 0.05
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-5 | 50-FG-45301-01C02 CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 5791 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.325 | CML-5 | CML: Fitting | 3 | 2026-11-08 | 2028-04-18 | 2014-06-23 13:00 | 2.5 | 0.22604 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 5.3 | 5.3 | 0.05
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-4 | 80-PL-44031-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22696 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 4.225 | CML-4 | CML: Elbow | 3 | 2015-10-18 | 2016-01-28 | 2015-04-27 07:00 | 2.5 | 1.2547 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.1 | 9 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 | 1.1814 | 4.7 | 4.8 | 4.3 | 3.1 | 0.78049
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-4 | 80-PL-44031-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5701 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 4.55 | CML-4 | CML: Elbow | 3 | 2015-09-10 | 2015-12-15 | 2014-06-22 08:00 | 2.5 | 1.3132 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.1 | 9 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 5 | 4.7 | 4.4 | 4.1 | 0.3873
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-10 | 80-PL-44031-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22702 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.275 | CML-10 | CML: Reducing Tee | 3 | 2025-01-11 | 2026-05-20 | 2015-04-27 07:00 | 2.5 | 0.25723 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 6 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.23628 | 5.4 | 5.4 | 5 | 5.3 | 0.1893
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-9 | 80-PL-44031-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22701 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.25 | CML-9 | CML: Reducing Tee | 3 | 2025-01-11 | 2026-05-20 | 2015-04-27 07:00 | 2.5 | 0.25723 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 6 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.11814 | 5.5 | 5.1 | 5 | 5.4 | 0.23805
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-3 | 80-PL-44031-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22695 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 6.025 | CML-3 | CML: Elbow | 3 | 2028-01-04 | 2029-09-16 | 2015-04-27 07:00 | 2.5 | 0.20473 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 12 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.11814 | 5.1 | 5.9 | 6.9 | 6.2 | 0.74554
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-1 | 80-PL-44031-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22693 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 6.55 | CML-1 | CML: Equal Tee | 3 | 2028-01-04 | 2029-09-16 | 2015-04-27 07:00 | 2.5 | 0.20473 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 9 O'Clock | 50 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.11814 | 5.8 | 7.7 | 7.6 | 5.1 | 1.3026
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-9 | 80-PL-44031-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5706 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 5.35 | CML-9 | CML: Reducing Tee | 3 | 2021-07-10 | 2022-06-20 | 2014-06-22 08:00 | 2.5 | 0.36846 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.6 | 5.1 | 5.5 | 0.23805
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-10 | 80-PL-44031-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5707 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 5.375 | CML-10 | CML: Reducing Tee | 3 | 2024-04-27 | 2025-08-03 | 2014-06-22 08:00 | 2.5 | 0.27399 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 9 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.7 | 5.2 | 5.2 | 0.23629
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-3 | 80-PL-44031-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5700 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 6.075 | CML-3 | CML: Elbow | 3 | 2024-04-27 | 2025-08-03 | 2014-06-22 08:00 | 2.5 | 0.27399 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6.2 | 6.5 | 6.4 | 0.59652
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-1 | 80-PL-44031-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5698 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 5.7 | CML-1 | CML: Equal Tee | 3 | 2024-04-27 | 2025-08-03 | 2014-06-22 08:00 | 2.5 | 0.27399 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 9 O'Clock | 50 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 7 | 5.2 | 0.87178
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-7 | 80-PL-44031-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22699 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 6.2 | CML-7 | CML: Elbow | 3 | 2043-05-16 | 2046-11-10 | 2015-04-27 07:00 | 2.5 | 0.09974 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0 | 6.4 | 6.8 | 5.3 | 6.3 | 0.6377
PL04 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 80-PL-44031-01X01 | CML-13 | 80-PL-44031-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23677 | LAGGED UP AGAINST GRID MESH, PTTEP WILL HAVE TO REMOVE | 2015-10-30 07:00 | 2015-10-30 15:00 | [37 empty] | CML-13 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 80 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 80-PL-44031-01X01 | CML-12 | 80-PL-44031-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23676 | LAGGED UP AGAINST GRID MESH, PTTEP WILL HAVE TO REMOVE | 2015-10-30 07:00 | 2015-10-30 15:00 | [37 empty] | CML-12 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 80 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-7 | 80-PL-44031-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5704 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 5.85 | CML-7 | CML: Elbow | 3 | 2030-01-22 | 2031-12-31 | 2014-06-22 08:00 | 2.5 | 0.17951 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 12 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.4 | 5.5 | 6.2 | 0.53229
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-5 | 80-PL-44031-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5702 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 5.9 | CML-5 | CML: Elbow | 3 | 2030-01-22 | 2031-12-31 | 2014-06-22 08:00 | 2.5 | 0.17951 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.4 | 6 | 5.3 | 5.9 | 0.45461
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-8 | 80-PL-44031-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5705 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 6.275 | CML-8 | CML: Elbow | 3 | 2048-07-21 | 2052-08-24 | 2014-06-22 08:00 | 2.5 | 0.08503 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 12 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.4 | 6.8 | 6.5 | 0.60759
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-13 | 80-PL-44031-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22705 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 6.35 | CML-13 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-04-27 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 0.35442 | 5.5 | 6.5 | 6.9 | 6.5 | 0.59722
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-5 | 80-PL-44031-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22697 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.85 | CML-5 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-04-27 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -0.23628 | 5.5 | 5.9 | 5.5 | 6.5 | 0.47258
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-6 | 80-PL-44031-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22698 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.925 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-04-27 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.23628 | 5.6 | 5.8 | 6.1 | 6.2 | 0.27538
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-8 | 80-PL-44031-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22700 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 6.325 | CML-8 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-04-27 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | -0.35442 | 5.7 | 6.3 | 6.5 | 6.8 | 0.46458
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-13 | 80-PL-44031-01X01 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5710 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 6.575 | CML-13 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 9 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.7 | 7.4 | 5.8 | 0.66521
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-6 | 80-PL-44031-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5703 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 6.2 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 3 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6.8 | 6.4 | 0.4899
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-12 | 80-PL-44031-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5709 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 6.675 | CML-12 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 6 O'Clock | 40 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 6.9 | 6 | 6.9 | 0.45
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-11 | 80-PL-44031-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22703 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 6.9 | CML-11 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-04-27 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.2 | 3 O'Clock | 40 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | 0.23628 | 7.8 | 6.2 | 6.8 | 6.8 | 0.66332
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-12 | 80-PL-44031-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22704 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 6.775 | CML-12 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-04-27 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.4 | 3 O'Clock | 40 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 | -0.47256 | 7.1 | 6.4 | 6.6 | 7 | 0.3304
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-11 | 80-PL-44031-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5708 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 7.15 | CML-11 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.4 | 12 O'Clock | 40 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.4 | 7.8 | 7 | 0.59722
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-2 | 80-PL-44031-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22694 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 7.15 | CML-2 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-04-27 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.8 | 9 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 | 0.11814 | 7.8 | 7.2 | 6.8 | 6.8 | 0.47258
PL04 | Montara_Topside | No | Produced Water (44) | Pipework | 80-PL-44031-01X01 | CML-2 | 80-PL-44031-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5699 | Rope access | 2014-06-22 08:00 | 2014-06-22 10:00 | [36 empty] | 7.4 | CML-2 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.9 | 3 O'Clock | 80 | 5.49 | 80-PL-44031-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.1 | 6.9 | 7.7 | 7.9 | 0.4761
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-5 | 80-PL-44017-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21964 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 8.375 | CML-5 | CML: type TBC | 6 | 2016-12-18 | 2016-06-03 | 2014-10-14 07:00 | 2.5 | 2.4295 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 7.8 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.3 | 8.9 | 8.5 | 0.45735
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-8 | 80-PL-44017-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21967 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 11.85 | CML-8 | CML: type TBC | 6 | 2064-10-22 | 2056-12-23 | 2014-10-14 07:00 | 2.5 | 0.1678 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 10.9 | 12 | 12.8 | 11.7 | 0.78528
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-3 | 80-PL-44017-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12730 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 5.95 | CML-3 | CML: Elbow | 3 | 2017-02-07 | 2017-03-24 | 2014-01-24 09:00 | 2.5 | 0.95334 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 12 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.2 | 6.5 | 5.7 | 0.49329
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-11 | 80-PL-44017-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12738 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 5.975 | CML-11 | CML: Elbow | 3 | 2017-02-07 | 2017-03-24 | 2014-01-24 09:00 | 2.5 | 0.95334 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 12 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.4 | 6.5 | 5.6 | 0.55603
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-12 | 80-PL-44017-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12739 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 5.975 | CML-12 | CML: Pipe Length | 3 | 2020-07-25 | 2020-10-19 | 2014-01-24 09:00 | 2.5 | 0.49205 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 3 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.2 | 5.7 | 6 | 6 | 0.20616
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12733 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 6.175 | CML-6 | CML: Pipe Length | 3 | 2127-10-20 | 2131-07-30 | 2014-01-24 09:00 | 2.5 | 0.03075 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 6 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6.1 | 6 | 6.3 | 0.15
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12729 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 6.125 | CML-2 | CML: Pipe Length | 3 | 2127-10-20 | 2131-07-30 | 2014-01-24 09:00 | 2.5 | 0.03075 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 6 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6 | 6.3 | 0.15
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-10 | 80-PL-44017-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12737 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 6.375 | CML-10 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2014-01-24 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 6 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.6 | 6.2 | 6.5 | 0.20616
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-5 | 80-PL-44017-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12732 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 8.1 | CML-5 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-01-24 09:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 3 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8.6 | 7.1 | 8.6 |  | 0.86603
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-7 | 80-PL-44017-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12734 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 7.8 | CML-7 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-01-24 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.3 | 12 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 8.1 | 8 |  | 0.43589
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-5 | 80-PL-44017-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3164 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 5.125 | CML-5 | CML: type TBC | 3 | 2016-08-01 | 2016-09-08 | 2014-05-02 07:00 | 2.5 | 1.1104 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 9 O'Clock | 100 | 6.02 | 100-FH-43075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 5.2 | 5 | 0.15
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3165 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 5.3 | CML-6 | CML: type TBC | 3 | 2016-08-01 | 2016-09-08 | 2014-05-02 07:00 | 2.5 | 1.1104 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-FH-43075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.3 | 5.4 | 5.5 | 0.21602
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-3 | 80-PL-44017-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3162 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 5.25 | CML-3 | CML: type TBC | 3 | 2016-08-01 | 2016-09-08 | 2014-05-02 07:00 | 2.5 | 1.1104 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-FH-43075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.3 | 5.3 | 5.4 | 0.17321
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3160 | Rope Access | 2014-05-02 08:00 | 2014-05-02 09:00 | [36 empty] | 6.025 | CML-1 | CML: type TBC | 3 | 2028-02-08 | 2028-08-03 | 2014-05-02 08:00 | 2.5 | 0.23946 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-FH-43075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 6 | 6.2 | 5.8 | 0.17078
PL04 | Montara_Topside | No | Flare (43) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3161 | Rope Access | 2014-05-02 07:00 | 2014-05-02 08:00 | [36 empty] | 6.175 | CML-2 | CML: type TBC | 3 | 2174-12-25 | 2180-04-26 | 2014-05-02 07:00 | 2.5 | 0.02177 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 12 O'Clock | 100 | 6.02 | 100-FH-43075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.3 | 6.3 | 0.15
PL04 | Montara_Topside | No | Fuel Gas (45) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22652 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-6 | CML: Pipe Length | 3 | 2054-10-24 | 2049-02-10 | 2015-04-27 07:00 | 1.88 | 0 |  |  | 3.02 | 1.88 | 2.45 |  | 9 O'Clock | 100 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-13 | 80-PL-44017-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22545 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.975 | CML-13 | CML: Reducing Tee | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A2: Right Quadrant |  |  |  |  | 2.8 | 3 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 3 | 2.8 | 3 | 3.1 | 0.12583
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-12 | 80-PL-44017-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22544 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.4 | CML-12 | CML: Elbow | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A3: Inside Quadrant |  |  |  |  | 2.2 | 6 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 2.6 | 2.4 | 2.2 | 2.4 | 0.1633
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-11 | 80-PL-44017-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22543 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.4 | CML-11 | CML: Elbow | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A2: Right Quadrant |  |  |  |  | 2.2 | 3 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 2.5 | 2.2 | 2.5 | 2.4 | 0.14142
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-10 | 80-PL-44017-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22542 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.525 | CML-10 | CML: Elbow | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A4: Left Quadrant |  |  |  |  | 2.3 | 9 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 2.5 | 2.8 | 2.5 | 2.3 | 0.20616
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-9 | 80-PL-44017-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22541 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.675 | CML-9 | CML: Elbow | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A2: Right Quadrant |  |  |  |  | 2.3 | 3 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 2.9 | 2.3 | 2.7 | 2.8 | 0.263
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-8 | 80-PL-44017-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22540 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 3.025 | CML-8 | CML: Elbow | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A1: Outside Quadrant |  |  |  |  | 2.2 | 12 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 2.2 | 3.3 | 3.4 | 3.2 | 0.55603
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-7 | 80-PL-44017-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22539 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.8 | CML-7 | CML: Reducing Tee | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A4: Left Quadrant |  |  |  |  | 2.4 | 9 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 2.9 | 3 | 2.9 | 2.4 | 0.2708
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22538 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 3.65 | CML-6 | CML: Equal Tee | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A1: Outside Quadrant |  |  |  |  | 3.3 | 12 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 3.3 | 3.8 | 4.1 | 3.4 | 0.36968
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-5 | 80-PL-44017-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22537 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.925 | CML-5 | CML: Reducing Tee | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A4: Left Quadrant |  |  |  |  | 2.8 | 9 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 3.1 | 2.9 | 2.9 | 2.8 | 0.12583
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-4 | 80-PL-44017-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22536 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.275 | CML-4 | CML: Reducing Tee | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A1: Outside Quadrant |  |  |  |  | 2 | 12 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 2 | 2.8 | 2.2 | 2.1 | 0.3594
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-3 | 80-PL-44017-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22535 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.3 | CML-3 | CML: Elbow | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A1: Outside Quadrant |  |  |  |  | 2.1 | 3 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 2.1 | 2.1 | 2.5 | 2.5 | 0.23094
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22534 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 2.7 | CML-2 | CML: Elbow | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A4: Left Quadrant |  |  |  |  | 2.5 | 9 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 2.8 | 2.6 | 2.9 | 2.5 | 0.18257
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22533 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 3.025 | CML-1 | CML: Reducer | 0.5 |  |  | 2015-04-23 07:00 |  | 0 | A2: Right Quadrant |  |  |  |  | 2.8 | 6 O'Clock | 25 |  | 0100-WF-71L9005-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 3.4 | 2.8 | 2.8 | 3.1 | 0.28723
PL04 | Montara_Topside | No | Nitrogen (67) | Pipework | 80-PL-44017-01X01 | CML-8 | 80-PL-44017-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22492 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [37 empty] | CML-8 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-04-20 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML17 | 80-PL-44017-01X01 CML17 |  | FPSO 2015 | Pipe Wall Thickness | 7612 | Does not exist on line. | 2015-04-15 07:00 | 2015-04-15 15:00 | [37 empty] | CML17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-15 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML16 | 80-PL-44017-01X01 CML16 |  | FPSO 2015 | Pipe Wall Thickness | 7611 | Does not exist on line. | 2015-04-15 07:00 | 2015-04-15 15:00 | [37 empty] | CML16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-15 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML15 | 80-PL-44017-01X01 CML15 |  | FPSO 2015 | Pipe Wall Thickness | 7610 | Does not exist on line. | 2015-04-15 07:00 | 2015-04-15 15:00 | [37 empty] | CML15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-15 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML5 | 80-PL-44017-01X01 CML5 |  | FPSO 2015 | Pipe Wall Thickness | 7600 | Does not exist on line. | 2015-04-15 07:00 | 2015-04-15 15:00 | [37 empty] | CML5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-15 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML4 | 80-PL-44017-01X01 CML4 |  | FPSO 2015 | Pipe Wall Thickness | 7599 | Does not exist on line. | 2015-04-15 07:00 | 2015-04-15 15:00 | [37 empty] | CML4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-15 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML37 | 80-PL-44017-01X01 CML37 |  | FPSO 2015 | Pipe Wall Thickness | 7083 | Does not exist on site | 2015-04-07 07:00 | 2015-04-07 15:00 | [37 empty] | CML37 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML36 | 80-PL-44017-01X01 CML36 |  | FPSO 2015 | Pipe Wall Thickness | 7082 | Does not exist on site | 2015-04-07 07:00 | 2015-04-07 15:00 | [37 empty] | CML36 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-148 | 80-PL-44017-01X01 CML-148 |  | FPSO 2015 | Pipe Wall Thickness | 6822 | Does not exist on site | 2015-04-04 07:00 | 2015-04-04 15:00 | [37 empty] | CML-148 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 |  |  | 2.5 | 2.5 | 2.5 |  | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-147 | 80-PL-44017-01X01 CML-147 |  | FPSO 2015 | Pipe Wall Thickness | 6821 | Does not exist on site | 2015-04-04 07:00 | 2015-04-04 15:00 | [37 empty] | CML-147 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 |  |  | 2.5 | 2.5 | 2.5 |  | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-146 | 80-PL-44017-01X01 CML-146 |  | FPSO 2015 | Pipe Wall Thickness | 6820 | Does not exist on site | 2015-04-04 07:00 | 2015-04-04 15:00 | [37 empty] | CML-146 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 |  |  | 2.5 | 2.5 | 2.5 |  | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-15 | 80-PL-44017-01X01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6058 | No Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [37 empty] | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-31 | 80-PL-44017-01X01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6074 | CAST Fitting. Readings taken on piping adjacent to fitting. No Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [37 empty] | CML-31 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-13 | 80-PL-44017-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5433 | Pipe Schedule Estimated. All fittings CAST. Readings could not be taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [37 empty] | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-10 | 80-PL-44017-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5430 | Pipe Schedule Estimated. All fittings CAST. Readings could not be taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [37 empty] | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-7 | 80-PL-44017-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5427 | Pipe Schedule Estimated. All fittings CAST. Readings could not be taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [37 empty] | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-19 | 80-PL-44017-01X01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 5439 | Pipe Schedule Estimated. All fittings CAST. Readings could not be taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [37 empty] | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-16 | 80-PL-44017-01X01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 5436 | Pipe Schedule Estimated. All fittings CAST. Readings could not be taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [37 empty] | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-22 | 80-PL-44017-01X01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 5267 | Pipe Schedule Estimated. Rope Access. Fitting elbow reading could not be taken | 2015-03-12 07:00 | 2015-03-12 15:00 | [37 empty] | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-56 | 80-PL-44017-01X01 CML-56 |  | FPSO 2015 | Pipe Wall Thickness | 5301 | Pipe Schedule Estimated. Rope Access. Fitting elbow reading could not be taken | 2015-03-12 07:00 | 2015-03-12 15:00 | [37 empty] | CML-56 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Fire Water (71) | Pipework | 80-PL-44017-01X01 | CML-54 | 80-PL-44017-01X01 CML-54 |  | FPSO 2015 | Pipe Wall Thickness | 5299 | Pipe Schedule Estimated. Rope Access. Fitting elbow reading could not be taken | 2015-03-12 07:00 | 2015-03-12 15:00 | [37 empty] | CML-54 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 |  |  | 2 | 2.5 | 2.25 |  | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5083 | Insulated could not test | 2015-03-06 07:00 | 2015-03-06 15:00 | [37 empty] | CML-6 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 |  |  | 3.38 | 2.5 | 2.7287 |  | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-5 | 80-PL-44017-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5082 | Insulated could not test | 2015-03-06 07:00 | 2015-03-06 15:00 | [37 empty] | CML-5 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 |  |  | 3.38 | 2.5 | 2.7287 |  | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-4 | 80-PL-44017-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5081 | Insulated could not test | 2015-03-06 07:00 | 2015-03-06 15:00 | [37 empty] | CML-4 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 |  |  | 3.38 | 2.5 | 2.7287 |  | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-3 | 80-PL-44017-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5080 | Insulated could not test | 2015-03-06 07:00 | 2015-03-06 15:00 | [37 empty] | CML-3 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 |  |  | 3.38 | 2.5 | 2.7287 |  | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5079 | Insulated could not test | 2015-03-06 07:00 | 2015-03-06 15:00 | [37 empty] | CML-2 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 |  |  | 3.38 | 2.5 | 2.7287 |  | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5078 | Insulated could not test | 2015-03-06 07:00 | 2015-03-06 15:00 | [37 empty] | CML-1 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 |  |  | 3.38 | 2.5 | 2.7287 |  | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-13 | 80-PL-44017-01X01 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21972 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 11.5 | CML-13 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 11.2 | 3 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.9 | 11.2 | 11.6 | 11.3 | 0.31623
PL04 | Montara_Topside | No | Steam (55) | Pipework | 80-PL-44017-01X01 | CML-21 | 80-PL-44017-01X01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 8851 | LAGGED | 2015-02-24 07:00 | 2015-02-24 11:00 | [37 empty] | CML-21 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.1519 |  | 9 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Steam (55) | Pipework | 80-PL-44017-01X01 | CML-20 | 80-PL-44017-01X01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 8850 | LAGGED | 2015-02-24 07:00 | 2015-02-24 11:00 | [37 empty] | CML-20 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.1519 |  | 9 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Steam (55) | Pipework | 80-PL-44017-01X01 | CML-19 | 80-PL-44017-01X01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8849 | LAGGED | 2015-02-24 07:00 | 2015-02-24 11:00 | [37 empty] | CML-19 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.1519 |  | 9 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Nitrogen (67) | Pipework | 80-PL-44017-01X01 | CML-11 | 80-PL-44017-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8789 | Cast fitting | 2015-02-15 07:00 | 2015-02-15 09:00 | [37 empty] | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Nitrogen (67) | Pipework | 80-PL-44017-01X01 | CML-8 | 80-PL-44017-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8786 | Cast fitting | 2015-02-15 07:00 | 2015-02-15 09:00 | [37 empty] | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Nitrogen (67) | Pipework | 80-PL-44017-01X01 | CML-7 | 80-PL-44017-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8785 | Cast fitting | 2015-02-15 07:00 | 2015-02-15 09:00 | [37 empty] | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Nitrogen (67) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8784 | Cast fitting | 2015-02-15 07:00 | 2015-02-15 09:00 | [37 empty] | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Nitrogen (67) | Pipework | 80-PL-44017-01X01 | CML-11 | 80-PL-44017-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8714 | Cast fitting | 2015-02-14 07:00 | 2015-02-14 09:00 | [37 empty] | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-14 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Nitrogen (67) | Pipework | 80-PL-44017-01X01 | CML-8 | 80-PL-44017-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8711 | Cast fitting | 2015-02-14 07:00 | 2015-02-14 09:00 | [37 empty] | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-14 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Nitrogen (67) | Pipework | 80-PL-44017-01X01 | CML-7 | 80-PL-44017-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8710 | Cast fitting | 2015-02-14 07:00 | 2015-02-14 09:00 | [37 empty] | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-14 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Nitrogen (67) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8709 | Cast fitting | 2015-02-14 07:00 | 2015-02-14 09:00 | [37 empty] | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-14 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21965 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 11.5 | CML-6 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.2 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 12 | 11.5 | 11.2 | 11.3 | 0.3559
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-16 | 80-PL-44017-01X01 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21975 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 11.675 | CML-16 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 11.3 | 3 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 12 | 11.3 | 11.9 | 11.5 | 0.3304
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-4 | 80-PL-44017-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8378 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.4 | CML-4 | CML: type TBC | 6 |  |  | 2015-01-29 07:30 |  | 0.38465 | A1: Outside Quadrant |  | 2.74 |  |  | 8.1 | 12 O'Clock | 50 | 8.74 | 50-PG-23407-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 8.1 | 9.4 | 10.2 | 9.9 | 0.92736
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-3 | 80-PL-44017-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8377 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 8.975 | CML-3 | CML: type TBC | 6 |  |  | 2015-01-29 07:30 |  | 0.38465 | A1: Outside Quadrant |  | 2.74 |  |  | 8.1 | 12 O'Clock | 50 | 8.74 | 50-PG-23407-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 8.1 | 9 | 9.1 | 9.7 | 0.66018
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8376 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.825 | CML-2 | CML: type TBC | 6 |  |  | 2015-01-29 07:30 |  | 0 | A1: Outside Quadrant |  | 2.74 |  |  | 8.8 | 12 O'Clock | 50 | 8.74 | 50-PG-23407-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 8.8 | 10.1 | 10.8 | 9.6 | 0.84212
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8375 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 9.5 | CML-1 | CML: type TBC | 6 |  |  | 2015-01-29 07:30 |  | 0 | A1: Outside Quadrant |  | 2.74 |  |  | 8.8 | 12 O'Clock | 50 | 8.74 | 50-PG-23407-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 8.8 | 9.5 | 10.3 | 9.4 | 0.61644
PL04 | Montara_Topside | No | Potable Water (53) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8227 | Reducing Hose Coupling | 2015-01-25 07:30 | 2015-01-25 15:00 | [37 empty] | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-PL-44017-01X01 | CML-9 | 80-PL-44017-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8198 | Pipe not in line | 2015-01-24 07:30 | 2015-01-24 15:00 | [37 empty] | CML-9 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-01-24 07:30 | 2.5 | 0 |  |  | 4.54 | 2.5 | 3.1738 |  | 9 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-PL-44017-01X01 | CML-8 | 80-PL-44017-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8197 | Pipe not in line | 2015-01-24 07:30 | 2015-01-24 15:00 | [37 empty] | CML-8 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-01-24 07:30 | 2.5 | 0 |  |  | 4.54 | 2.5 | 3.1738 |  | 9 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Potable Water (53) | Pipework | 80-PL-44017-01X01 | CML-24 | 80-PL-44017-01X01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 8163 | Reducing Hose Coupling NOT ON LINE | 2015-01-24 07:30 | 2015-01-24 15:00 | [37 empty] | CML-24 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-7 | 80-PL-44017-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21966 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 12 | CML-7 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.4 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.4 | 11.5 | 12.4 | 12.7 | 0.64807
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-22 | 80-PL-44017-01X01 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21981 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 11.85 | CML-22 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.5 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 11.5 | 11.8 | 12.4 | 11.7 | 0.3873
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-10 | 80-PL-44017-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21969 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 12.1 | CML-10 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.7 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 11.7 | 11.8 | 11.7 | 13.2 | 0.73485
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-19 | 80-PL-44017-01X01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21978 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 12.225 | CML-19 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.8 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.4 | 12.3 | 11.8 | 12.4 | 0.28723
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21960 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 12.375 | CML-1 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 12.2 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 12.2 | 12.3 | 12.8 | 12.2 | 0.28723
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-17 | 80-PL-44017-01X01 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21976 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 15.925 | CML-17 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 15.4 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.9 |  | 15.4 | 15.9 | 15.4 | 17 | 0.75443
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-15 | 80-PL-44017-01X01 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21974 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 16.25 | CML-15 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 15.5 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13 |  | 15.5 | 17.5 | 15.9 | 16.1 | 0.86987
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-14 | 80-PL-44017-01X01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21973 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 16.975 | CML-14 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 15.8 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.3 |  | 17.8 | 16.9 | 17.4 | 15.8 | 0.86554
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-11 | 80-PL-44017-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21970 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 17.8 | CML-11 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 16.9 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.4 |  | 17.7 | 17.8 | 16.9 | 18.8 | 0.77889
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-18 | 80-PL-44017-01X01 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21977 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 19.575 | CML-18 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 18.1 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.6 |  | 18.2 | 20.9 | 18.1 | 21.1 | 1.648
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7925 |  | 2015-01-17 09:30 | 2015-01-17 10:30 | [36 empty] | 9.025 | CML-2 | CML: type TBC | 6 |  |  | 2015-01-17 09:30 |  | 0 | A1: Outside Quadrant |  |  |  |  | 8.8 | 12 O'Clock | 25 |  | 25-DC-57305-09C03 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 8.8 | 8.9 | 8.9 | 9.5 | 0.32016
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7924 |  | 2015-01-17 09:30 | 2015-01-17 10:30 | [36 empty] | 8.05 | CML-1 | CML: type TBC | 6 |  |  | 2015-01-17 09:30 |  | 0 | A4: Left Quadrant |  |  |  |  | 7.6 | 9 O'Clock | 25 |  | 25-DC-57305-09C03 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 7.7 | 7.9 | 9 | 7.6 | 0.6455
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-6 | 80-PL-44017-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7916 |  | 2015-01-17 07:00 | 2015-01-17 08:00 | [36 empty] | 10.05 | CML-6 | CML: type TBC | 6 |  |  | 2015-01-17 07:00 |  | 0 | A4: Left Quadrant |  | -0.44 |  |  | 8.3 | 9 O'Clock | 20 | 5.56 | 20-DC-57304-06C03 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.2 | 10.2 | 10.5 | 8.3 | 1.2396
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-5 | 80-PL-44017-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7915 |  | 2015-01-17 07:00 | 2015-01-17 08:00 | [36 empty] | 11.425 | CML-5 | CML: type TBC | 6 |  |  | 2015-01-17 07:00 |  | 0 | A4: Left Quadrant |  | -0.44 |  |  | 11 | 9 O'Clock | 20 | 5.56 | 20-DC-57304-06C03 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.1 | 11.6 | 12 | 11 | 0.46458
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-4 | 80-PL-44017-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7914 |  | 2015-01-17 07:00 | 2015-01-17 08:00 | [36 empty] | 15.875 | CML-4 | CML: type TBC | 6 |  |  | 2015-01-17 07:00 |  | 0 | A1: Outside Quadrant |  | -0.44 |  |  | 15 | 12 O'Clock | 20 | 5.56 | 20-DC-57304-06C03 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 15 | 15.8 | 15.7 | 17 | 0.83016
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-3 | 80-PL-44017-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7913 |  | 2015-01-17 07:00 | 2015-01-17 08:00 | [36 empty] | 12.275 | CML-3 | CML: type TBC | 6 |  |  | 2015-01-17 07:00 |  | 0 | A4: Left Quadrant |  | -0.44 |  |  | 11.2 | 9 O'Clock | 20 | 5.56 | 20-DC-57304-06C03 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 12.7 | 12.8 | 12.4 | 11.2 | 0.73655
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7912 |  | 2015-01-17 07:00 | 2015-01-17 08:00 | [36 empty] | 6.55 | CML-2 | CML: type TBC | 6 |  |  | 2015-01-17 07:00 |  | 0 | A4: Left Quadrant |  | -0.44 |  |  | 6 | 9 O'Clock | 20 | 5.56 | 20-DC-57304-06C03 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.7 | 6.7 | 6.8 | 6 | 0.36968
PL04 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-PL-44017-01X01 | CML-1 | 80-PL-44017-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7911 |  | 2015-01-17 07:00 | 2015-01-17 08:00 | [36 empty] | 6.875 | CML-1 | CML: type TBC | 6 |  |  | 2015-01-17 07:00 |  | 0 | A4: Left Quadrant |  | -0.44 |  |  | 6.7 | 9 O'Clock | 20 | 5.56 | 20-DC-57304-06C03 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.9 | 7.1 | 6.8 | 6.7 | 0.17078
PL04 | Montara_Topside | No | Gas Compression (23) | Pipework | 80-PL-44017-01X01 | CML-9 | 80-PL-44017-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7797 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:04 | [33 empty] | CML-9 | CML: Fitting | 6 | 2075-10-24 | 2074-08-12 | 2015-01-13 07:00 | 2.5 | 0 |  |  | 2.74 | 2.5 | 2.62 |  | 9 O'Clock | 25 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-12 | 80-PL-44017-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21971 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 19.8 | CML-12 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 18.1 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.6 |  | 19.7 | 22.5 | 18.9 | 18.1 | 1.9149
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-9 | 80-PL-44017-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21968 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 19.375 | CML-9 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 18.1 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.6 |  | 19.4 | 19.7 | 20.3 | 18.1 | 0.92871
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-23 | 80-PL-44017-01X01 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21982 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 19.275 | CML-23 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 18.2 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.7 |  | 19.3 | 20 | 18.2 | 19.6 | 0.7719
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-4 | 80-PL-44017-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21963 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 19.5 | CML-4 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 18.2 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.7 |  | 20.4 | 20 | 19.4 | 18.2 | 0.95917
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-20 | 80-PL-44017-01X01 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21979 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 19.025 | CML-20 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 18.5 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16 |  | 20.1 | 18.5 | 18.5 | 19 | 0.75443
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-3 | 80-PL-44017-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21962 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 20.6 | CML-3 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 18.7 | 3 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.2 |  | 20.4 | 18.7 | 21.3 | 22 | 1.4259
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-21 | 80-PL-44017-01X01 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21980 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 20.15 | CML-21 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 19 | 3 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.5 |  | 19.8 | 19 | 19.7 | 22.1 | 1.3478
PL04 | Montara_Topside | No | Separation (20) | Pipework | 80-PL-44017-01X01 | CML-2 | 80-PL-44017-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21961 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 20.875 | CML-2 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 19.1 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.6 |  | 20 | 22.9 | 19.1 | 21.5 | 1.6741
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-12 | 250-PW-44006-01X01 CML-12 | Yes | FPSO 2015 | Pipe Wall Thickness | 23183 | CML Wrapped due to leak | 2015-05-11 07:00 | 2015-05-11 15:00 | [37 empty] | CML-12 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-11 | 250-PW-44006-01X01 CML-11 | Yes | FPSO 2015 | Pipe Wall Thickness | 23182 | CML Wrapped due to leak | 2015-05-11 07:00 | 2015-05-11 15:00 | [37 empty] | CML-11 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-16 | 100-DH-56082-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 3384 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 5.625 | CML-16 | CML: type TBC | 3 | 2021-04-17 | 2021-07-22 | 2014-05-10 09:30 | 2.5 | 0.44642 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 5.7 | 5.6 | 0.05
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38483-01C02 | CML-5 | 25-CG-38483-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10394 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.675 | CML-5 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 25 | 6.35 | 25-CG-38483-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.7 | 5.7 | 5.6 | 5.7 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40053-01C02 | CML-3 | 50-WC-40053-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 874 |  | 2014-04-06 16:00 | 2014-04-06 16:30 | [36 empty] | 10.975 | CML-3 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40053-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 10.9 | 11.1 | 11.1 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43144-01C02 | CML-5 | 100-FH-43144-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10528 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.675 | CML-5 | CML: type TBC | 3 | 2017-03-31 | 2017-05-16 | 2013-11-15 | 2.5 | 0.91796 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 6 O'Clock | 100 | 6.02 | 100-FH-43144-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.7 | 5.6 | 5.7 | 0.05
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-10 | 250-PW-44006-01X01 CML-10 | Yes | FPSO 2015 | Pipe Wall Thickness | 23181 | CML Wrapped due to leak | 2015-05-11 07:00 | 2015-05-11 15:00 | [37 empty] | CML-10 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56083-01C02 | CML-2 | 100-DH-56083-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22527 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.825 | CML-2 | CML: Pipe Length | 3 | 2043-07-26 | 2044-07-24 | 2015-04-20 07:00 | 2.5 | 0.11667 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-DH-56083-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 5.9 | 5.8 | 0.05
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56083-01C02 | CML-1 | 100-DH-56083-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22526 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.875 | CML-1 | CML: Elbow | 3 | 2043-07-26 | 2044-07-24 | 2015-04-20 07:00 | 2.5 | 0.11667 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 3 O'Clock | 100 | 6.02 | 100-DH-56083-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 5.8 | 5.9 | 5.9 | 0.05
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-30 | 250-PL-20006-01C02-P CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 13200 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-30 | CML: Pipe Length | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43170-01C02 | CML-2 | 250-FL-43170-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2887 | Rope Access | 2014-04-25 07:00 | 2014-04-25 08:00 | [36 empty] | 6.175 | CML-2 | CML: Fitting | 3 | 2027-04-04 | 2027-02-26 | 2014-04-25 07:00 | 2.5 | 0.27795 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.1 | 6.2 | 6.2 | 0.05
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-6 | 25-PW-44026-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22738 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 6.175 | CML-6 | CML: Pipe Length | 3 | 2042-10-09 | 2042-07-23 | 2015-04-28 07:00 | 2.5 | 0.13105 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 9 O'Clock | 25 | 6.35 | 25-PW-44026-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.2 | 6.2 | 6.1 | 0.05
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-1 | 25-PW-44026-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22733 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 6.175 | CML-1 | CML: Pipe Length | 3 | 2042-10-09 | 2042-07-23 | 2015-04-28 07:00 | 2.5 | 0.13105 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 25 | 6.35 | 25-PW-44026-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 6.2 | 6.2 | 0.05
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-8 | 50-PW-44012-01X01 CML-8 | Yes | FPSO 2015 | Pipe Wall Thickness | 23167 | CML Wrapped due to leak | 2015-05-11 07:00 | 2015-05-11 15:00 | [37 empty] | CML-8 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-11 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1284 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.175 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 6 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.2 | 7.2 | 7.1 | 7.2 | 0.05
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-16 | 50-CG-38452-09C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2260 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 7.125 | CML-16 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.1 | 9 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.1 | 7.2 | 7.1 | 0.05
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2503 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.125 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 9 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.2 | 7.1 | 7.1 | 0.05
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2502 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.125 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 6 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.1 | 7.1 | 7.2 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40053-01C02 | CML-3 | 50-WC-40053-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1538 |  | 2014-04-06 16:00 | 2014-04-06 16:30 | [36 empty] | 10.975 | CML-3 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40053-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 10.9 | 11.1 | 11.1 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40023-01C02 | CML-1 | 50-WC-40023-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1249 |  | 2014-03-23 08:30 | 2014-03-23 09:00 | [36 empty] | 10.9 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 08:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.8 | 9 O'Clock | 50 | 5.54 | 50-WC-40023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.1 | 10.9 | 10.8 | 10.8 | 0.14142
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-3 | 150-FL-43174-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12901 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.675 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.6 | 3 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.7 | 7.6 | 7.7 | 7.7 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-48 | 400-FH-43508-01C02 CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 23567 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 7.825 | CML-48 | CML: Pipe Length | 3 | 2112-05-20 | 2099-04-29 | 2015-08-10 07:30 | 2.5 | 0.05473 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.8 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.8 | 7.9 | 7.8 | 0.05
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-VA-23058-01C02 | CML-1 | 200-VA-23058-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3141 | Rope Access | 2014-05-02 13:00 | 2014-05-02 14:00 | [36 empty] | 7.825 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-05-02 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 6 O'Clock | 200 | 6.35 | 200-VA-23058-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.8 | 7.8 | 7.9 | 0.05
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-43 | 250-PL-20006-01C02-P CML-43 |  | FPSO 2014 | Pipe Wall Thickness | 13213 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-43 | CML: Pipe Length | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-11 | 50-FL-43454-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12651 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.325 | CML-11 | CML: Pipe Length | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.3 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.27 |  | 7.3 | 7.4 | 7.3 | 7.3 | 0.05
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-17 | 150-FH-43141-01C02 CML-17 | yes | FPSO 2015 | Pipe Wall Thickness | 6366 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.425 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.5 | 3.4 | 3.4 | 0.05
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-12 | 150-FH-43141-01C02 CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 6361 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.425 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.5 | 3.4 | 3.4 | 3.4 | 0.05
FL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-FL-43174-01C02 | CML-8 | 150-FL-43174-01C02 CML-8 | yes | FPSO 2014 | Pipe Wall Thickness | 1983 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 3.475 | CML-8 | CML: Pipe Length | 3 | 2014-07-31 | 2014-09-14 | 2014-03-27 07:00 | 2.5 | 2.6098 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.5 | 3.5 | 3.4 | 3.5 | 0.05
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-3 | 50-FG-45019-03C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10485 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.225 | CML-3 | CML: type TBC | 3 | 2017-07-03 | 2017-06-23 | 2013-11-15 | 2.5 | 0.74311 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.2 | 5.2 | 5.2 | 0.05
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56083-01C02 | CML-6 | 100-DH-56083-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22531 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.775 | CML-6 | CML: Pipe Length | 3 | 2034-02-22 | 2034-10-30 | 2015-04-20 07:00 | 2.5 | 0.1697 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-DH-56083-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 5.8 | 5.8 | 0.05
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23413-01C03-A | CML-6 | 100-PG-23413-01C03-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20780 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.175 | CML-6 | CML: type TBC | 6 |  |  | 2014-10-02 07:00 |  | 1.6968 | A2: Right Quadrant |  | 4.97 |  |  | 8.7 | 3 O'Clock | 150 | 10.97 | 150-PG-23413-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 9.9 | 8.7 | 9.2 | 8.9 | 0.5252
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23413-01C03-A | CML-5 | 100-PG-23413-01C03-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20779 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.35 | CML-5 | CML: type TBC | 6 |  |  | 2014-10-02 07:00 |  | 2.4443 | A3: Inside Quadrant |  | 4.97 |  |  | 7.7 | 6 O'Clock | 150 | 10.97 | 150-PG-23413-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 8.4 | 9 | 7.7 | 8.3 | 0.53229
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23413-01C03-A | CML-4 | 100-PG-23413-01C03-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20778 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 17.775 | CML-4 | CML: type TBC | 6 |  |  | 2014-10-02 07:00 |  | 0 | A2: Right Quadrant |  | 4.97 |  |  | 15.7 | 3 O'Clock | 150 | 10.97 | 150-PG-23413-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 15.8 | 15.7 | 20 | 19.6 | 2.3443
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23413-01C03-A | CML-3 | 100-PG-23413-01C03-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20777 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.475 | CML-3 | CML: type TBC | 6 |  |  | 2014-10-02 07:00 |  | 1.9211 | A3: Inside Quadrant |  | 4.97 |  |  | 8.4 | 9 O'Clock | 150 | 10.97 | 150-PG-23413-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 8.5 | 8.6 | 8.4 | 8.4 | 0.095743
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23413-01C03-A | CML-2 | 100-PG-23413-01C03-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20776 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9 | CML-2 | CML: type TBC | 6 |  |  | 2014-10-02 07:00 |  | 1.7716 | A3: Inside Quadrant |  | 4.97 |  |  | 8.6 | 6 O'Clock | 150 | 10.97 | 150-PG-23413-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 9.4 | 9.3 | 8.6 | 8.7 | 0.40825
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23413-01C03-A | CML-1 | 100-PG-23413-01C03-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20775 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.7 | CML-1 | CML: type TBC | 6 |  |  | 2014-10-02 07:00 |  | 2.0706 | A1: Outside Quadrant |  | 4.97 |  |  | 8.2 | 12 O'Clock | 150 | 10.97 | 150-PG-23413-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 8.2 | 9.5 | 8.4 | 8.7 | 0.57155
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-1 | 50-WC-40032-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1235 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 11.7 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.9 | 12 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 10.9 | 11.5 | 11.9 | 12.5 | 0.6733
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-3 | 200-FH-43114-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12811 |  | 2014-02-01 12:00 | 2014-02-01 14:00 | [36 empty] | 6.275 | CML-3 | CML: type TBC | 3 | 2030-09-01 | 2030-07-17 | 2014-02-01 12:00 | 2.5 | 0.22301 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 6.3 | 6.3 | 0.05
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40500-1CG | CML-2 | 400-WC-40500-1CG CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24422 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.369mm/ yr |  | John Wilson | 2017-03-23 11:29 | Loss within CA include this CML at the next inspection | [31 empty] | 20.6 | CML-2 | CML: Elbow | 3 | 2064-09-09 | 2043-02-11 | 2016-07-02 07:00 | 2.5 | 0.36911 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 20.3 | 3 O'Clock | 400 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.8 | -0.1058 | 20.4 | 20.3 | 20.9 | 20.8 | 0.29439
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-29 | 50-PF-20300-03C03-P CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 21595 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 8.675 | CML-29 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.7 | 8.6 | 8.7 | 0.05
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-5 | 50-PG-23024-03C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10037 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 8.075 | CML-5 | CML: Pipe Length | 6 | 2017-12-16 | 2017-06-10 | 2013-11-06 | 0.97 | 1.7095 | A2: Right Quadrant |  | 2.74 | 0.97 | 1.855 | 8 | 3 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.03 |  | 8.1 | 8 | 8.1 | 8.1 | 0.05
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-8 | 50-PL-45016-03C03 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10448 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.175 | CML-8 | CML: type TBC | 6 | 2018-11-20 | 2018-04-08 | 2013-11-13 | 0.99 | 1.4158 | A3: Inside Quadrant |  | 2.74 | 0.99 | 1.865 | 8.1 | 6 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.11 |  | 8.2 | 8.2 | 8.1 | 8.2 | 0.05
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-12 | 50-PL-23300-09C03 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 13128 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.425 | CML-12 | CML: type TBC | 6 | 2021-10-18 | 2020-08-25 | 2014-02-04 07:00 | 2.81 | 0.98493 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.4 | 9 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.59 |  | 10.4 | 10.5 | 10.4 | 10.4 | 0.05
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-15 | 80-PG-23025-06C03 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 13086 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 11.175 | CML-15 | CML: Elbow | 6 | 2204-07-31 | 2177-11-04 | 2014-02-07 11:00 | 2.8 | 0.04355 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 11.1 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.1 | 11.2 | 11.2 | 11.2 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43155-01C02 | CML-5 | 80-FH-43155-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10718 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 4.975 | CML-5 | CML: type TBC | 3 | 2015-10-10 | 2016-01-18 | 2013-11-18 | 2.5 | 1.2668 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-FH-43155-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 | 5 | 5 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43146-01C02 | CML-5 | 80-FH-43146-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10558 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 4.975 | CML-5 | CML: type TBC | 3 | 2015-09-30 | 2016-01-07 | 2013-11-16 | 2.5 | 1.2818 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-FH-43146-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 5 | 5 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-14 | 250-WC-40017-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2077 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 11.125 | CML-14 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.9 | 12 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 10.9 | 11.4 | 11 | 11.2 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40061-01C02 | CML-1 | 400-WC-40061-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1125 |  | 2014-03-21 08:30 | 2014-03-21 09:00 | [36 empty] | 11.4 | CML-1 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 08:30 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 11.1 | 9 O'Clock | 400 | 7.92 | 400-WC-40061-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11.5 | 11.5 | 11.5 | 11.1 | 0.2
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-7 | 50-PW-44012-01X01 CML-7 | Yes | FPSO 2015 | Pipe Wall Thickness | 23166 | CML Wrapped due to leak | 2015-05-11 07:00 | 2015-05-11 15:00 | [37 empty] | CML-7 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-11 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-8 | 50-PW-44014-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23153 | CML Wrapped due to leak | 2015-05-10 07:00 | 2015-05-10 15:00 | [37 empty] | CML-8 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-10 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-1 | 400-WC-40024-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1070 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 11.65 | CML-1 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 11.2 | 9 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.5 | 12.5 | 11.4 | 11.2 | 0.58023
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-7 | 250-WC-40017-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2070 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | [36 empty] | 12.3 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-28 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.3 | 3 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 12 | 11.3 | 13.6 | 12.3 | 0.96264
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1665 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 12.0667 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.7 | 12 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 11.7 | 12.7 | 11.8 |  | 0.55076
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-16 | 400-WC-40025-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1276 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 12.65 | CML-16 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 12 | 3 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 12.6 | 12 | 12.6 | 13.4 | 0.57446
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 250-PG-23401-01D03-PA | CML-2 | 250-PG-23401-01D03-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20726 |  | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 4.225 | CML-2 | CML: Pipe Length |  |  |  | 2014-07-25 07:30 |  | 0 | A1: Outside Quadrant |  |  |  |  | 4.2 | 9 O'Clock | 250 | 4.19 | 250-PG-23401-01D03 | 10S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 4.2 | 4.3 | 4.2 | 4.2 | 0.05
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 250-PG-23401-01D03-PA | CML-1 | 250-PG-23401-01D03-PA CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20725 |  | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 4.275 | CML-1 | CML: Fitting |  |  |  | 2014-07-25 07:30 |  | 0 | A1: Outside Quadrant |  |  |  |  | 4.2 | 12 O'Clock | 250 | 4.19 | 250-PG-23401-01D03 | 10S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 4.2 | 4.3 | 4.3 | 4.3 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-24 | 400-WC-40024-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 1093 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 12.75 | CML-24 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 12 | 9 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 13 | 12.7 | 13.3 | 12 | 0.55678
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-13 | 50-FH-43016-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22674 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.425 | CML-13 | CML: Reducing Tee | 3 | 2054-10-01 | 2059-03-10 | 2015-04-27 07:00 | 2.5 | 0.07349 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.079564 | 5.5 | 5.4 | 5.4 | 5.4 | 0.05
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56106-01C02 | CML-7 | 80-DH-56106-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2033 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 5.575 | CML-7 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-27 14:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 5.6 | 5.6 | 0.05
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-1 | 25-PW-44028-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10307 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.775 | CML-1 | CML: Elbow | 3 | 2016-01-16 | 2016-01-09 | 2013-11-10 | 2.5 | 1.4645 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 6 O'Clock | 25 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.8 | 5.7 | 5.8 | 0.05
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-7 | 100-FL-43455-01C02-P CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 20490 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 5.925 | CML-7 | CML: Fitting | 3 | 2052-09-16 | 2054-01-03 | 2014-10-03 07:00 | 2.5 | 0.08952 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 5.9 | 5.9 | 0.05
FG02 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 25-FG-45455-01C02-E | CML-1 | 25-FG-45455-01C02-E CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8395 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.025 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-AI-63031-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.1 | 6 | 0.05
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-24 | 25-FG-45455-01C02-E CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21827 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6.025 | CML-24 | CML: Reducing Tee | 3 | 2253-01-17 | 2260-12-16 | 2014-10-11 07:00 | 2.5 | 0.01468 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6 | 6 | 0.05
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-7 | 80-WF-71370-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6322 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.775 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 3 | 2.6 | 2.9 | 0.20616
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-32 | 80-WF-71370-01K01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6347 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.925 | CML-32 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 3 | 3 | 3.1 | 0.22174
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-24 | 80-WF-71370-01K01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6339 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.05 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 3 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 2.8 | 3.2 | 3.1 | 0.17321
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-22 | 80-WF-71370-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6337 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.025 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 3 | 3.4 | 2.8 | 0.263
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-12 | 80-WF-71370-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6327 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3 | 3.2 | 3 | 0.1633
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-3 | 80-WF-71370-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6318 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.025 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3 | 3.2 | 3.1 | 0.17078
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-33 | 80-WF-71370-01K01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 6348 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-33 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3.1 | 3.3 | 3.1 | 0.20616
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-26 | 80-WF-71370-01K01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6341 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.05 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3.1 | 3.2 | 3.1 | 0.17321
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-21 | 80-WF-71370-01K01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6336 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.25 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.5 | 3.4 | 3.2 | 2.9 | 0.26458
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-19 | 80-WF-71370-01K01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6334 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.3 | 3.1 | 0.17078
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-14 | 80-WF-71370-01K01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6329 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.05 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.2 | 3 | 0.1291
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-10 | 80-WF-71370-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6325 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.125 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.2 | 3.3 | 3.1 | 0.17078
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-8 | 80-WF-71370-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6323 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.1 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 2.9 | 3.1 | 3.3 | 0.1633
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-34 | 80-WF-71370-01K01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 6349 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.125 | CML-34 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.3 | 3.1 | 2.9 | 3.2 | 0.17078
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-25 | 80-WF-71370-01K01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6340 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.1 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.3 | 3.1 | 0.1633
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-20 | 80-WF-71370-01K01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6335 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.225 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.5 | 3.3 | 0.22174
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-18 | 80-WF-71370-01K01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6333 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.05 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3.1 | 0.057735
PF04 | Montara_Topside | No | Separation (20) | Pipework | 1000-PL-13L9006-BD20X-P-50 | CML-5 | 1000-PL-13L9006-BD20X-P-50 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6467 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.525 | CML-5 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A3: Inside Quadrant |  | 9.27 |  |  | 11.4 | 6 O'Clock | 250 | 9.27 | 1000-PL-13L9006-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.5 | 11.6 | 11.4 | 11.6 | 0.095743
PF04 | Montara_Topside | No | Separation (20) | Pipework | 1000-PL-13L9006-BD20X-P-50 | CML-4 | 1000-PL-13L9006-BD20X-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6466 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.45 | CML-4 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A4: Left Quadrant |  | 9.27 |  |  | 10.9 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9006-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.1 | 11.8 | 12 | 10.9 | 0.53229
PF04 | Montara_Topside | No | Separation (20) | Pipework | 1000-PL-13L9006-BD20X-P-50 | CML-3 | 1000-PL-13L9006-BD20X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6465 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.45 | CML-3 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A4: Left Quadrant |  | 9.27 |  |  | 11 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9006-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.4 | 11.8 | 11.6 | 11 | 0.34157
PF04 | Montara_Topside | No | Separation (20) | Pipework | 1000-PL-13L9006-BD20X-P-50 | CML-2 | 1000-PL-13L9006-BD20X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6464 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.775 | CML-2 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A2: Right Quadrant |  | 9.27 |  |  | 11.3 | 3 O'Clock | 250 | 9.27 | 1000-PL-13L9006-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.9 | 11.3 | 12 | 11.9 | 0.32016
PF04 | Montara_Topside | No | Separation (20) | Pipework | 1000-PL-13L9006-BD20X-P-50 | CML-1 | 1000-PL-13L9006-BD20X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6463 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.325 | CML-1 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A2: Right Quadrant |  | 9.27 |  |  | 11 | 3 O'Clock | 250 | 9.27 | 1000-PL-13L9006-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.2 | 11 | 11.5 | 11.6 | 0.27538
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-17 | 80-WF-71370-01K01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6332 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.2 | 3 | 0.095743
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-16 | 80-WF-71370-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6331 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.1 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.2 | 3.1 | 3 | 0.08165
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-15 | 80-WF-71370-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6330 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3.2 | 0.095743
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-11 | 80-WF-71370-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6326 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.2 | 3 | 0.095743
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-9 | 80-WF-71370-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6324 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3.1 | 0.05
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-31 | 80-WF-71370-01K01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6346 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.125 | CML-31 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.2 | 3.2 | 3.1 | 0.095743
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-30 | 80-WF-71370-01K01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6345 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3.1 | 0.05
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-29 | 80-WF-71370-01K01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6344 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3.1 | 3 | 0.05
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-28 | 80-WF-71370-01K01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6343 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.2 | 3.1 | 0.095743
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-27 | 80-WF-71370-01K01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6342 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.05 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3.1 | 0.057735
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-1 | 80-WF-71370-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6316 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.475 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.6 | 3.6 | 3.7 | 3 | 0.32016
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-23 | 80-WF-71370-01K01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6338 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.25 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 3 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.2 | 3.5 | 0.17321
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-45 | 300-PF-20003-03C03-P CML-45 | yes | FPSO 2014 | Pipe Wall Thickness | 21783 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [35 empty] | Low alarm breach | 6.475 | CML-45 | CML: Reducer | 6 | 2015-05-30 | 2014-12-03 | 2014-10-01 07:00 | 2.5 | 5.8949 | A1: Outside Quadrant |  | 8.27 | 2.5 | 5.385 | 6.4 | 12 O'Clock | 40 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.5 | 6.5 | 6.5 | 0.05
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-14 | 50-FG-45024-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1197 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 6.425 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 | -1.7951 | 6.4 | 6.5 | 6.4 | 6.4 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-14 | 150-WC-40006-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1674 |  | 2014-04-12 09:30 | 2014-04-12 11:00 | [36 empty] | 12.2667 | CML-14 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-04-12 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.9 | 12 O'Clock | 200 | 6.35 | 200-WC-40006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 11.9 |  | 12.6 | 12.3 | 0.35119
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-13 | 80-WF-71370-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6328 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.175 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.2 | 3.3 | 3.1 | 0.095743
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-6 | 80-WF-71370-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6321 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.6 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.5 | 4.1 | 3.5 | 0.34641
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-5 | 80-WF-71370-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6320 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 4.65 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 4.1 | 3 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.7 | 4.1 | 5 | 4.8 | 0.3873
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-2 | 80-WF-71370-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6317 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 5.325 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.8 | 5.1 | 5.5 | 4.9 | 0.40311
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71370-01K01 | CML-4 | 80-WF-71370-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6319 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 5.85 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 5.6 | 12 O'Clock | 80 | 2.5 | 80-WF-71370-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.9 | 5.8 | 6.1 | 0.20817
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50810-1LC | CML-1 | 80-WS-50810-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10830 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.675 | CML-1 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A2: Right Quadrant |  | 4.62 | 2.5 | 3.56 | 8 | 3 O'Clock | 80 | 7.62 | 80-WS-50810-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 9.1 | 8 | 8.3 | 9.3 | 0.62383
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50810-1LC | CML-3 | 80-WS-50810-1LC CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10832 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.05 | CML-3 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A2: Right Quadrant |  | 4.62 | 2.5 | 3.56 | 8.1 | 3 O'Clock | 80 | 7.62 | 80-WS-50810-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 9.2 | 8.1 | 8.9 | 10 | 0.78528
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50810-1LC | CML-4 | 80-WS-50810-1LC CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10833 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.4 | CML-4 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A1: Outside Quadrant |  | 4.62 | 2.5 | 3.56 | 8.3 | 12 O'Clock | 80 | 7.62 | 80-WS-50810-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.5 | 8.4 |  | 0.1
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50810-1LC | CML-2 | 80-WS-50810-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10831 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.375 | CML-2 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A1: Outside Quadrant |  | 4.62 | 2.5 | 3.56 | 8.3 | 6 O'Clock | 80 | 7.62 | 80-WS-50810-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.3 | 8.3 | 8.6 | 0.15
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-4 | 80-WS-50811-1LC CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10837 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.05 | CML-4 | CML: type TBC | 3 | 2018-04-28 | 2017-04-22 | 2014-01-04 | 2.5 | 1.0429 | A1: Outside Quadrant |  | 4.62 | 2.5 | 3.56 | 7 | 12 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 8.5 | 7.5 | 9.2 | 0.98826
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-6 | 80-WS-50811-1LC CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10839 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.35 | CML-6 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A4: Left Quadrant |  | 4.62 | 2.5 | 3.56 | 8.1 | 9 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.3 | 8.7 | 8.3 | 8.1 | 0.25166
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-8 | 80-WS-50811-1LC CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10841 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.675 | CML-8 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A3: Inside Quadrant |  | 4.62 | 2.5 | 3.56 | 8.2 | 6 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.8 | 8.4 | 8.2 | 9.3 | 0.48563
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-12 | 80-WS-50811-1LC CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10845 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.125 | CML-12 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A4: Left Quadrant |  | 4.62 | 2.5 | 3.56 | 8.3 | 9 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.4 | 9.5 | 9.3 | 8.3 | 0.55603
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-1 | 50-DC-57056-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1133 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [37 empty] | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.52 |  | 9 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-8 | 50-FG-45023-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1156 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.575 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.5 | 6.6 | 6.6 | 0.05
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-17 | 80-WS-50811-1LC CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 10850 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.85 | CML-17 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A2: Right Quadrant |  | 4.62 | 2.5 | 3.56 | 8.4 | 3 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.2 | 8.4 | 8.7 | 9.1 | 0.36968
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-14 | 80-WS-50811-1LC CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 10847 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.95 | CML-14 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A4: Left Quadrant |  | 4.62 | 2.5 | 3.56 | 8.4 | 9 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.3 | 9.1 | 9 | 8.4 | 0.3873
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-3 | 80-WS-50811-1LC CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10836 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 8.8 | CML-3 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A4: Left Quadrant |  | 4.62 | 2.5 | 3.56 | 8.4 | 9 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.8 | 9.5 | 8.5 | 8.4 | 0.49666
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-1 | 80-WS-50811-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10834 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9 | CML-1 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A3: Inside Quadrant |  | 4.62 | 2.5 | 3.56 | 8.5 | 6 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.3 | 9.2 | 8.5 | 9 | 0.3559
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23029-25C02-P | CML-10 | 80-PG-23029-25C02-P CML-10 | Yes | FPSO 2014 | Pipe Wall Thickness | 20568 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [35 empty] | Low alarm breach | 7.525 | CML-10 | CML: Pipe Length | 3 | 2015-03-15 | 2014-08-26 | 2014-07-02 07:00 | 2.5 | 7.1288 | A1: Outside Quadrant |  | 12.24 | 2.5 | 6.4175 | 7.5 | 9 O'Clock | 20 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.6 | 7.5 | 7.5 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-8 | 400-WC-40022-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1102 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | [36 empty] | 12.7 | CML-8 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 09:30 | 2.6 | 0 | A2: Right Quadrant |  | 4.92 | 2.6 | 3.265 | 12.1 | 3 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 13.3 | 12.1 | 13.2 | 12.2 | 0.6377
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45009-01C02-E | CML-4 | 150-FG-45009-01C02-E CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24298 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.725 | CML-4 | CML: Fitting | 3 | 2057-09-21 | 2049-09-26 | 2016-05-27 07:00 | 1.03 | 0.13713 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.7 | 9 O'Clock | 150 | 7.11 | 150-FG-45009-01C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.67 |  | 6.7 | 6.7 | 6.8 | 6.7 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-25 | 400-WC-40024-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 1094 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 12.4 | CML-25 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 12.2 | 12 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 12.2 | 12.3 | 12.6 | 12.5 | 0.18257
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23032-01C03 | CML-5 | 50-PL-23032-01C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20789 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 8.525 | CML-5 | CML: Elbow | 6 | 2048-09-28 | 2048-01-24 | 2014-10-10 07:00 | 2.5 | 0.17651 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-PL-23032-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.6 | 8.5 | 8.5 | 0.05
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45044-03C02 | CML-3 | 50-FG-45044-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21671 | Protective mesh removed | 2014-06-26 09:30 | 2014-06-26 11:00 | [36 empty] | 8.625 | CML-3 | CML: type TBC | 6 | 2017-01-22 | 2016-07-03 | 2014-06-26 09:30 | 2.5 | 2.3654 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 8.6 | 9 O'Clock | 80 | 11.13 | 80-PG-20030-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 8.7 | 8.6 | 8.6 | 0.05
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38490-09C02 | CML-5 | 50-CG-38490-09C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2533 |  | 2014-04-03 07:00 | 2014-04-03 08:00 | [36 empty] | 8.625 | CML-5 | CML: type TBC | 3 | 2050-10-16 | 2041-02-01 | 2014-04-03 07:00 | 2.5 | 0.16683 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-CG-38490-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.6 | 8.6 | 8.6 | 0.05
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-44 | 250-PL-20006-01C02-P CML-44 |  | FPSO 2014 | Pipe Wall Thickness | 13214 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-44 | CML: Pipe Length | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44023-01C03-P | CML-1 | 250-PW-44023-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21916 | Protective mesh removed | 2014-06-24 08:00 | 2014-06-24 09:00 | [36 empty] | 9.025 | CML-1 | CML: Fitting | 6 | 2040-01-28 | 2038-07-23 | 2014-06-24 08:00 | 2.5 | 0.25378 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9 | 9 O'Clock | 250 | 9.27 | 250-PW-44023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.1 | 9 | 9 | 9 | 0.05
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44023-01C03-P | CML-1 | 250-PW-44023-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5818 | Protective mesh removed | 2014-06-24 08:00 | 2014-06-24 09:00 | [36 empty] | 9.025 | CML-1 | CML: Fitting | 6 | 2040-01-28 | 2038-07-23 | 2014-06-24 08:00 | 2.5 | 0.25378 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9 | 9 O'Clock | 250 | 9.27 | 250-PW-44023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.1 | 9 | 9 | 9 | 0.05
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-6 | 50-PL-23022-03C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1862 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.025 | CML-6 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 9 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.1 | 9 | 9 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-15 | 400-WC-40025-01C02 CML-15 | yes | FPSO 2014 | Pipe Wall Thickness | 1275 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 13.5 | CML-15 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 12.7 | 6 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.1 |  | 15.6 | 12.8 | 12.7 | 12.9 | 1.4024
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40024-01C02 | CML-13 | 400-WC-40024-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1082 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | [36 empty] | 13 | CML-13 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-21 13:00 | 2.6 | 0 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 12.7 | 6 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.1 |  | 13.5 | 12.9 | 12.7 | 12.9 | 0.34641
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-7 | 50-PL-45016-03C03 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10447 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.375 | CML-7 | CML: type TBC | 6 | 2021-05-16 | 2020-06-22 | 2013-11-13 | 0.99 | 0.97333 | A3: Inside Quadrant |  | 2.74 | 0.99 | 1.865 | 8.3 | 6 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.31 |  | 8.4 | 8.4 | 8.3 | 8.4 | 0.05
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-4 | 50-CG-38488-09C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23593 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 10.175 | CML-4 | CML: Reducer | 3 | 2075-10-24 | 2059-08-12 | 2015-09-15 15:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.1 | 12 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 | 0.34419 | 10.1 | 10.2 | 10.2 | 10.2 | 0.05
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-3 | 50-PL-23042-09C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10068 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.325 | CML-3 | CML: type TBC | 6 | 2018-04-05 | 2017-07-14 | 2013-11-07 | 2.5 | 1.7676 | A2: Right Quadrant |  | 5.07 | 2.5 | 3.785 | 10.3 | 9 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.4 | 10.3 | 10.3 | 10.3 | 0.05
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-13 | 50-FG-45300-01C02 CML-13 | yes | FPSO 2015 | Pipe Wall Thickness | 7836 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:39 | [32 empty] | 5.025 | CML-13 | CML: Pipe Length | 3 | 2022-07-14 | 2023-07-06 | 2015-01-13 13:00 | 2.5 | 0.3332 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5 | 5.1 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-4 | 80-FH-43158-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12885 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.425 | CML-4 | CML: type TBC | 3 | 2034-10-31 | 2037-04-29 | 2014-01-22 11:00 | 2.5 | 0.13952 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.5 | 0.05
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 842 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.475 | CML-2 | CML: Pipe Length | 3 | 2031-08-01 | 2033-07-13 | 2014-04-02 14:00 | 2.5 | 0.16722 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.5 | 5.5 | 5.4 | 0.05
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45039-03C02 | CML-1 | 25-FG-45039-03C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10561 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.775 | CML-1 | CML: type TBC | 3 | 2016-02-21 | 2015-11-03 | 2013-11-16 | 2.5 | 1.4122 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.925 | 5.7 | 9 O'Clock | 25 | 6.35 | 25-FG-45039-03C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.8 | 5.8 | 5.7 | 0.05
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-42 | 250-PL-20006-01C02-P CML-42 |  | FPSO 2014 | Pipe Wall Thickness | 13212 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-42 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-7 | 50-PG-23063-09C02 CML-7 | Yes | FPSO 2013 | Pipe Wall Thickness | 10733 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.125 | CML-7 | CML: type TBC | 3 | 2017-12-24 | 2016-10-17 | 2013-11-19 | 2.5 | 1.3661 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 6 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.1 | 8.2 | 0.05
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23064-09C02 | CML-2 | 50-PG-23064-09C02 CML-2 | Yes | FPSO 2013 | Pipe Wall Thickness | 10725 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.125 | CML-2 | CML: type TBC | 3 | 2017-12-24 | 2016-10-17 | 2013-11-19 | 2.5 | 1.3661 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 6 O'Clock | 50 | 8.74 | 50-PG-23064-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.1 | 8.2 | 0.05
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-26 | 50-PL-23020-01C03 CML-26 |  | FPSO 2013 | Pipe Wall Thickness | 10140 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.125 | CML-26 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 6 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.1 | 8.2 | 0.05
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45044-03C02 | CML-4 | 50-FG-45044-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20774 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.675 | CML-4 | CML: Pipe Length | 6 | 2074-02-03 | 2073-10-17 | 2014-10-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 8.6 | 9 O'Clock | 100 | 8.56 | 100-PG-23410-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.7 | 8.7 | 8.6 | 0.05
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38491-09C02 | CML-6 | 50-CG-38491-09C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2545 |  | 2014-04-03 10:00 | 2014-04-03 11:00 | [36 empty] | 8.675 | CML-6 | CML: type TBC | 3 | 2050-10-22 | 2041-02-05 | 2014-04-03 10:00 | 2.5 | 0.16677 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-CG-38491-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.7 | 8.7 | 8.7 | 8.6 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40025-01C02 | CML-3 | 400-WC-40025-01C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 1263 | Rope Access | 2014-03-23 07:00 | 2014-03-23 08:30 | [36 empty] | 14.125 | CML-3 | CML: type TBC | 3 | 2066-08-12 | 2059-12-18 | 2014-03-23 07:00 | 2.6 | 0 | A4: Left Quadrant |  | 4.92 | 2.6 | 3.265 | 13.3 | 9 O'Clock | 400 | 7.92 | 400-WC-40025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 13.4 | 13.5 | 16.3 | 13.3 | 1.4523
FL02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-FL-43454-01C02-P | CML-5 | 50-FL-43454-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2313 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | [36 empty] | 9.125 | CML-5 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 9.1 | 6 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.1 | 9.1 | 9.2 | 0.05
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-13 | 50-CG-38452-09C02-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23753 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.325 | CML-13 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.3 | 6 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.3 | 9.3 | 9.3 | 9.4 | 0.05
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23044-03C03 | CML-3 | 50-PG-23044-03C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13105 |  | 2014-02-07 07:00 | 2014-02-07 08:00 | [36 empty] | 8.625 | CML-3 | CML: type TBC | 6 | 2051-08-07 | 2047-04-02 | 2014-02-07 07:00 | 0.97 | 0.20335 | A1: Outside Quadrant |  | 2.74 | 0.97 | 1.855 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PG-23044-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.63 |  | 8.6 | 8.6 | 8.6 | 8.7 | 0.05
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-4 | 100-PG-23071-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2402 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 10.475 | CML-4 | CML: type TBC | 6 | 2025-04-11 | 2023-07-19 | 2014-03-19 13:00 | 2.5 | 0.71362 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 10.4 | 9 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.5 | 10.5 | 10.5 | 10.4 | 0.05
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38493-01C02 | CML-6 | 25-CG-38493-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10375 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 10.675 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2013-11-12 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.6 | 9 O'Clock | 25 | 6.35 | 25-CG-38493-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | 10.6 | 10.7 | 10.7 | 10.7 | 10.6 | 0.05
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-28 | 50-CG-38001-09C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 10943 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.075 | CML-28 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.2222 | A4: Left Quadrant |  | 5.74 |  |  | 8 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8 | 8.1 | 8.1 | 8.1 | 8 | 0.05
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-9 | 50-CG-38001-09C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10922 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.075 | CML-9 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.2222 | A4: Left Quadrant |  | 5.74 |  |  | 8 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8 | 8.1 | 8.1 | 8.1 | 8 | 0.05
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-1 | 50-CG-38001-09C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10914 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.175 | CML-1 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.057 | A4: Left Quadrant |  | 5.74 |  |  | 8.1 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.1 | 8.2 | 8.2 | 8.2 | 8.1 | 0.05
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-10 | 200-PG-23008-15S01-A CML-10 | Yes | FPSO 2013 | Pipe Wall Thickness | 10096 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 20.375 | CML-10 | CML: Elbow | 1 | 2014-11-08 | 2014-03-19 | 2013-11-07 | 14.06 | 6.2211 | A4: Left Quadrant |  | 22.01 | 14.06 | 18.035 | 20.3 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.24 |  | 20.4 | 20.4 | 20.4 | 20.3 | 0.05
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-29 | 200-PG-23007-09C03-PA CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 23407 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 19.625 | CML-29 | CML: Fitting | 6 | 2035-03-24 | 2030-08-11 | 2015-07-22 07:00 | 10.22 | 0.47652 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 19.6 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.38 | 0.18875 | 19.6 | 19.7 | 19.6 | 19.6 | 0.05
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-2 | 200-PG-24001-09C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10258 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 20.325 | CML-2 | CML: Pipe Length | 3 | 2104-01-05 | 2073-09-17 | 2013-11-09 | 9.2 | 0 | A2: Right Quadrant |  | 15.26 | 9.2 | 12.23 | 20.3 | 9 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 20.4 | 20.3 | 20.3 | 20.3 | 0.05
FH02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23062-25S01 | CML-5 | 50-PG-23062-25S01 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 20597 | Rope Access | 2014-05-26 14:00 | 2014-05-26 15:00 | [35 empty] | High alarm breach | 5.7 | CML-5 | CML: type TBC | 1 | 2014-01-03 | 2013-11-15 | 2014-05-26 14:00 | 6.91 | 3.0858 | A1: Outside Quadrant |  | 7.74 | 6.91 | 7.325 | 5.7 | 9 O'Clock | 50 | 8.74 | 50-PG-23062-25S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -1.21 |  | 5.7 | 5.7 | 5.7 | 5.7 | 0
DH01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 80-DH-56004-01C02 | CML-3 | 80-DH-56004-01C02 CML-3 | yes | FPSO 2013 | Pipe Wall Thickness | 10009 | Deck Level | 2013-11-04 | 2013-11-04 | Check Corrosion Rate of 5.475mm/ yr | [35 empty] | 3.2 | CML-3 | CML: Elbow | 3 | 2013-12-20 | 2014-01-11 | 2013-11-04 | 2.5 | 5.475 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.2 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.2 | 3.2 | 3.2 | 0
FL01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-FL-43174-01C02 | CML-4 | 150-FL-43174-01C02 CML-4 | yes | FPSO 2013 | Pipe Wall Thickness | 10010 | Deck Level | 2013-11-04 | 2013-11-04 | Check Corrosion Rate of 5.007mm/ yr | [35 empty] | 3.4 | CML-4 | CML: Elbow | 3 | 2014-01-08 | 2014-02-01 | 2013-11-04 | 2.5 | 5.007 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.4 | 3.4 | 3.4 | 0
FL01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-FL-43174-01C02 | CML-2 | 150-FL-43174-01C02 CML-2 | yes | FPSO 2013 | Pipe Wall Thickness | 10008 | Deck Level | 2013-11-04 | 2013-11-04 | Check Corrosion Rate of 5.007mm/ yr | [35 empty] | 3.4 | CML-2 | CML: Elbow | 3 | 2014-01-08 | 2014-02-01 | 2013-11-04 | 2.5 | 5.007 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.4 | 3.4 | 3.4 | 0
FL01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-FL-43174-01C02 | CML-1 | 150-FL-43174-01C02 CML-1 | yes | FPSO 2013 | Pipe Wall Thickness | 10007 | Deck Level | 2013-11-04 | 2013-11-04 | Check Corrosion Rate of 5.007mm/ yr | [35 empty] | 3.4 | CML-1 | CML: Elbow | 3 | 2014-01-08 | 2014-02-01 | 2013-11-04 | 2.5 | 5.007 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.4 | 3.4 | 3.4 | 0
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-36 | 150-FL-43174-01C02 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 6914 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.5 | CML-36 | CML: type TBC | 0.5 | 2023-06-01 | 2020-11-30 | 2015-04-05 07:00 | 3.5 | 0 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4.5 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4.5 | 4.5 | 4.5 | 4.5 | 0
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-14 | 150-FL-43174-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6241 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.5 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 9 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.5 | 3.5 | 3.5 | 3.5 | 0
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-41 | 250-PL-20006-01C02-P CML-41 |  | FPSO 2014 | Pipe Wall Thickness | 13211 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-41 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-40 | 250-PL-20006-01C02-P CML-40 |  | FPSO 2014 | Pipe Wall Thickness | 13210 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-40 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43146-01C02 | CML-3 | 80-FH-43146-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10556 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5 | CML-3 | CML: type TBC | 3 | 2016-03-22 | 2016-07-19 | 2013-11-16 | 2.5 | 1.0646 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-FH-43146-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5 | 5 | 0
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40026-01C02 | CML-4 | 250-WC-40026-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1280 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 13.75 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 13.2 | 12 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 13.2 | 13.3 | 13.4 | 15.1 | 0.9037
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-19 | 50-FG-45300-01C02 CML-19 | yes | FPSO 2015 | Pipe Wall Thickness | 7842 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:40 | [32 empty] | 5 | CML-19 | CML: Pipe Length | 3 | 2022-07-14 | 2023-07-06 | 2015-01-13 13:00 | 2.5 | 0.3332 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5 | 5 | 0
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-2 | 50-FG-45020-03C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10574 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5 | CML-2 | CML: type TBC | 3 | 2016-01-08 | 2016-01-02 | 2013-11-17 | 2.5 | 1.1663 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5 | 5 | 0
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10530 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5 | CML-2 | CML: type TBC | 3 | 2016-01-02 | 2015-12-27 | 2013-11-16 | 2.5 | 1.1732 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5 | 5 | 0
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-22 | 50-FG-45021-03C02 CML-22 |  | FPSO 2013 | Pipe Wall Thickness | 10550 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5 | CML-22 | CML: type TBC | 3 | 2016-01-02 | 2015-12-27 | 2013-11-16 | 2.5 | 1.1732 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5 | 5 | 0
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-3 | 50-FG-45021-03C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10531 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5 | CML-3 | CML: type TBC | 3 | 2016-01-02 | 2015-12-27 | 2013-11-16 | 2.5 | 1.1732 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5 | 5 | 0
PG06 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 200-PG-23008-15S01-A |  | 200-PG-23008-15S01-A | yes | FPSO 2014 | Pipe Wall Thickness | 22097 | Rope access | 2014-06-02 08:00 | 2014-06-02 09:00 |  |  | Administrator | 2015-09-07 10:56 | [32 empty] | 5.1 | 50-CG-38300-01C02-P | Piping | 3 | 2020-05-06 |  | 2014-06-02 08:00 |  | 0.4384 | A1: Outside Quadrant |  |  | 2.5 |  | 5.1 | 9 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 0
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-2 | 50-FG-45019-03C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10484 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 5.2 | CML-2 | CML: type TBC | 3 | 2017-07-03 | 2017-06-23 | 2013-11-15 | 2.5 | 0.74311 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.2 | 5.2 | 0
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-14 | 150-WC-40006-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20636 | Casting - No UT | 2014-07-26 07:00 | 2014-07-26 15:00 | [37 empty] | CML-14 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-07-26 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 15 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
VA01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-VA-43519-01C02 | CML-6 | 50-VA-43519-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7759 |  | 2015-01-11 09:30 | 2015-01-11 10:30 | [36 empty] | 5.4 | CML-6 | CML: Elbow | 3 | 2048-06-15 | 2052-03-19 | 2015-01-11 09:30 | 2.5 | 0.0867 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-VA-43519-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-7 | 250-PG-23003-06C02-PA CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10006 | Deck Level | 2013-11-01 | 2013-11-01 | [36 empty] | 5.4 | CML-7 | CML: type TBC | 3 | 2027-05-02 | 2028-12-13 | 2013-11-01 | 2.5 | 0.21471 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10005 | Deck Level | 2013-11-01 | 2013-11-01 | [36 empty] | 5.4 | CML-6 | CML: type TBC | 3 | 2027-05-02 | 2028-12-13 | 2013-11-01 | 2.5 | 0.21471 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-5 | 250-PG-23003-06C02-PA CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10004 | Deck Level | 2013-11-01 | 2013-11-01 | [36 empty] | 5.4 | CML-5 | CML: type TBC | 3 | 2027-05-02 | 2028-12-13 | 2013-11-01 | 2.5 | 0.21471 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10002 | Deck Level | 2013-11-01 | 2013-11-01 | [36 empty] | 5.4 | CML-3 | CML: type TBC | 3 | 2027-05-02 | 2028-12-13 | 2013-11-01 | 2.5 | 0.21471 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10001 | Deck Level | 2013-11-01 | 2013-11-01 | [36 empty] | 5.4 | CML-2 | CML: type TBC | 3 | 2027-05-02 | 2028-12-13 | 2013-11-01 | 2.5 | 0.21471 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10000 | Deck Level | 2013-11-01 | 2013-11-01 | [36 empty] | 5.4 | CML-1 | CML: type TBC | 3 | 2027-05-02 | 2028-12-13 | 2013-11-01 | 2.5 | 0.21471 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38495-01C02 | CML-1 | 25-CG-38495-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10397 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 5.7 | CML-1 | CML: type TBC | 3 | 2016-01-28 | 2016-01-21 | 2013-11-12 | 2.5 | 1.4466 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 9 O'Clock | 25 | 6.35 | 25-CG-38495-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 0
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45033-03C02 | CML-2 | 25-FG-45033-03C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10480 | Deck Level | 2013-11-14 | 2013-11-14 | [36 empty] | 5.8 | CML-2 | CML: type TBC | 3 | 2016-08-06 | 2016-03-30 | 2013-11-14 | 2.5 | 1.2093 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.925 | 5.8 | 9 O'Clock | 25 | 6.35 | 25-FG-45033-03C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 5.8 | 5.8 | 0
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-30 | 50-FG-45023-01C02 CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 1178 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.4 | CML-30 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 6.4 | 6.4 | 0
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-17 | 300-PG-23002-03C03-A CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10113 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 9.5 | CML-17 | CML: Elbow | 6 | 2014-03-29 | 2014-02-06 | 2013-11-07 | 5.22 | 10.95 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 9.5 | 9 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.28 |  | 9.5 | 9.5 | 9.5 | 9.5 | 0
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43116-01C02 | CML-6 | 150-FH-43116-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7870 | Line is FFS. It has been check twice. The higher values reported here are from the data collected in Apr. 2014. The rechecked CR’s from data from Jan. 2015 are lower. Current RBI frequency is 48m. Action: to recheck line in a 24m (Jan. 2017) to confirm CR. | 2015-01-14 09:30 | 2015-01-14 10:30 |  |  | Administrator | 2015-09-07 17:06 | [32 empty] | 7.2 | CML-6 | CML: Pipe Length | 3 | 2059-07-07 | 2055-11-27 | 2015-01-14 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 | -0.97573 | 7.2 | 7.2 | 7.2 | 7.2 | 0
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-14 | 80-PW-44001-01C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 22005 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 13.725 | CML-14 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 13.2 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 13.8 | 14 | 13.9 | 13.2 | 0.3594
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-38 | 150-PG-23506-25C02 CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 20664 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | [36 empty] | 21 | CML-38 | CML: Pipe Length | 3 | 2019-09-26 | 2018-02-19 | 2014-05-28 07:00 | 15.88 | 0.95975 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.12 | -0.4938 | 21 | 21 | 21 | 21 | 0
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-36 | 150-PG-23506-25C02 CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 20663 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | [36 empty] | 21 | CML-36 | CML: Elbow | 3 | 2019-09-26 | 2018-02-19 | 2014-05-28 07:00 | 15.88 | 0.95975 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.12 | -4.938 | 21 | 21 | 21 | 21 | 0
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-18 | 300-PG-23002-03C03-A CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10114 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.4 | CML-18 | CML: Elbow | 6 | 2014-06-07 | 2014-04-06 | 2013-11-07 | 5.22 | 8.884 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 10.4 | 9 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.18 |  | 10.4 | 10.4 | 10.4 | 10.4 | 0
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-28 | 50-PF-20301-03C03-P CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 3026 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.8 | CML-28 | CML: Fitting | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.8 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.19 | 0 | 8.8 | 8.8 | 8.8 | 8.8 | 0
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-28 | 50-PF-20301-03C03-P CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 22305 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.8 | CML-28 | CML: Fitting | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.8 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.19 |  | 8.8 | 8.8 | 8.8 | 8.8 | 0
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-6 | 200-PG-23051-09C02-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13111 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.425 | CML-6 | CML: type TBC | 3 | 2103-01-05 | 2073-03-18 | 2014-02-07 11:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 19.1 | 12 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 19.1 | 19.3 | 19.7 | 19.6 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43030-01C02 | CML-5 | 400-FH-43030-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10029 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.8 | CML-5 | CML: type TBC | 3 | 2032-09-15 | 2030-02-28 | 2013-11-04 | 2.5 | 0.28077 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.8 | 9 O'Clock | 400 | 7.92 | 400-FH-43030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.8 | 7.8 | 7.8 | 0
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43085-01C02 | CML-3 | 350-FL-43085-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10013 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.8 | CML-3 | CML: type TBC | 3 | 2032-09-15 | 2030-02-28 | 2013-11-04 | 2.5 | 0.28077 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.8 | 9 O'Clock | 350 | 7.92 | 350-FL-43085-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 7.8 | 7.8 | 7.8 | 0
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23070-01C03-P | CML-7 | 300-PG-23070-01C03-P CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 20604 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 7.9 | CML-7 | CML: Pipe Length | 6 | 2017-02-18 | 2016-09-14 | 2014-07-25 07:30 | 2.5 | 2.0978 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 7.9 | 9 O'Clock | 20 | 10.31 | 300-PG-23070-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 7.9 | 7.9 | 7.9 | 0
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43085-01C02 | CML-1 | 350-FL-43085-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10011 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.9 | CML-1 | CML: type TBC | 3 | 2129-03-01 | 2113-11-23 | 2013-11-04 | 2.5 | 0.04679 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 9 O'Clock | 350 | 7.92 | 350-FL-43085-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 7.9 | 7.9 | 7.9 | 0
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-5 | 150-FH-43136-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5518 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 6.5 | CML-5 | CML: Elbow | 3 | 2023-05-20 | 2021-08-02 | 2014-06-01 07:00 | 1.03 | 0.60951 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.5 | 9 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.47 | -0.91345 | 6.5 | 6.5 | 6.5 | 6.5 | 0
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-13 | 150-WC-40006-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20635 | Casting - No UT | 2014-07-26 07:00 | 2014-07-26 15:00 | [37 empty] | CML-13 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-07-26 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 40 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-5 | 50-PG-23063-09C02 CML-5 | Yes | FPSO 2013 | Pipe Wall Thickness | 10731 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.1 | CML-5 | CML: type TBC | 3 | 2017-12-24 | 2016-10-17 | 2013-11-19 | 2.5 | 1.3661 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 9 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.1 | 8.1 | 0
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-13 | 80-WS-50811-1LC CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10846 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.875 | CML-13 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A2: Right Quadrant |  | 4.62 | 2.5 | 3.56 | 8.6 | 3 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 10 | 8.6 | 10.8 | 10.1 | 0.9215
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-11 | 80-WS-50811-1LC CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10844 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.225 | CML-11 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A2: Right Quadrant |  | 4.62 | 2.5 | 3.56 | 8.6 | 3 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.2 | 8.6 | 10 | 9.1 | 0.57951
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-2 | 80-WS-50811-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10835 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.025 | CML-2 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A1: Outside Quadrant |  | 4.62 | 2.5 | 3.56 | 8.9 | 6 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9.2 | 8.9 | 9.1 | 0.15
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-18 | 80-WS-50811-1LC CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 10851 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.55 | CML-18 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A3: Inside Quadrant |  | 4.62 | 2.5 | 3.56 | 9 | 9 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.2 | 11 | 9 | 9 | 0.97125
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-16 | 80-WS-50811-1LC CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 10849 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.2 | CML-16 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A3: Inside Quadrant |  | 4.62 | 2.5 | 3.56 | 9 | 6 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.3 | 9.2 | 9 | 9.3 | 0.14142
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-7 | 80-WS-50811-1LC CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10840 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.175 | CML-7 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A1: Outside Quadrant |  | 4.62 | 2.5 | 3.56 | 9.1 | 9 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.3 | 9.2 | 9.1 | 0.095743
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-15 | 80-WS-50811-1LC CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 10848 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.875 | CML-15 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A4: Left Quadrant |  | 4.62 | 2.5 | 3.56 | 9.2 | 9 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.8 | 10.5 | 10 | 9.2 | 0.53774
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-10 | 80-WS-50811-1LC CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10843 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 9.5 | CML-10 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A4: Left Quadrant |  | 4.62 | 2.5 | 3.56 | 9.2 | 9 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.6 | 9.4 | 9.8 | 9.2 | 0.2582
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-9 | 80-WS-50811-1LC CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10842 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 10.025 | CML-9 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A2: Right Quadrant |  | 4.62 | 2.5 | 3.56 | 9.5 | 3 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.2 | 9.5 | 9.7 | 10.7 | 0.53774
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 80-WS-50811-1LC | CML-5 | 80-WS-50811-1LC CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10838 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 12.5333 | CML-5 | CML: type TBC | 3 | 2064-08-11 | 2054-01-05 | 2014-01-04 | 2.5 | 0 | A4: Left Quadrant |  | 4.62 | 2.5 | 3.56 | 12.1 | 9 O'Clock | 80 | 7.62 | 80-WS-50811-1LC | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 12.3 |  | 13.2 | 12.1 | 0.58595
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-3 | 50-PG-23063-09C02 CML-3 | Yes | FPSO 2013 | Pipe Wall Thickness | 10729 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.1 | CML-3 | CML: type TBC | 3 | 2017-12-24 | 2016-10-17 | 2013-11-19 | 2.5 | 1.3661 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 9 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.1 | 8.1 | 8.1 | 0
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-7 | 50-PL-23023-03C03 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10207 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.2 | CML-7 | CML: type TBC | 6 | 2018-06-23 | 2018-05-19 | 2013-11-08 | 2.5 | 1.2319 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 9 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.2 | 8.2 | 8.2 | 0
FH01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 100-FH-43507-01C02 | CML-8 | 100-FH-43507-01C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10383 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 8.6 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2013-11-12 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.6 | 9 O'Clock | 25 | 6.35 | 25-CG-38482-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 8.6 |  | 8.6 | 8.6 | 8.6 | 0
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-39 | 250-PL-20006-01C02-P CML-39 |  | FPSO 2014 | Pipe Wall Thickness | 13209 | Piping being covered no insp. | 2014-01-21 13:00 | 2014-01-21 18:00 | [37 empty] | CML-39 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 |  |  | 3.35 | 3.61 | 3.0831 |  | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-9 | 200-PG-23008-15S01-A CML-9 | Yes | FPSO 2013 | Pipe Wall Thickness | 10095 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 20.4 | CML-9 | CML: Elbow | 1 | 2014-11-28 | 2014-03-31 | 2013-11-07 | 14.06 | 5.9915 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 20.4 | 20.4 | 0
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-4 | 200-PG-23008-15S01-A CML-4 | Yes | FPSO 2013 | Pipe Wall Thickness | 10090 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 20.4 | CML-4 | CML: Elbow | 1 | 2014-11-28 | 2014-03-31 | 2013-11-07 | 14.06 | 5.9915 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 20.4 | 20.4 | 0
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 | Yes | FPSO 2013 | Pipe Wall Thickness | 10088 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 20.4 | CML-2 | CML: Elbow | 1 | 2014-11-28 | 2014-03-31 | 2013-11-07 | 14.06 | 5.9915 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 20.4 | 20.4 | 0
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45024-01C02 | CML-7 | 50-FG-45024-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1863 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.2 | CML-7 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.2 | 9 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.2 | 9.2 | 9.2 | 0
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-57066-01C03 | CML-8 | 50-PL-57066-01C03 CML-8 | Yes | FPSO 2013 | Pipe Wall Thickness | 10734 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 9.2 | CML-8 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2013-11-19 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 9 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.2 | 9.2 | 9.2 | 0
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-3 | 50-PG-23024-03C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10035 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 8.1 | CML-3 | CML: Pipe Length | 6 | 2018-09-01 | 2018-01-25 | 2013-11-06 | 0.97 | 1.4785 | A1: Outside Quadrant |  | 2.74 | 0.97 | 1.855 | 8.1 | 9 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.13 |  | 8.1 | 8.1 | 8.1 | 8.1 | 0
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-1 | 300-FH-43001-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12513 |  | 2014-01-24 13:00 | 2014-01-24 15:00 | [36 empty] | 9.9 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-24 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 9 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 9.9 | 9.9 | 9.9 | 0
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-8 | 80-PW-20024-01C03-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23052 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 10.625 | CML-8 | CML: Reducing Tee | 6 | 2029-07-28 | 2027-02-09 | 2015-05-06 07:00 | 2.5 | 0.5338 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.1 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.8 | 10.6 | 10.1 | 11 | 0.38622
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-5 | 80-CG-38459-09C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23373 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 20.2 | CML-5 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2015-07-21 07:00 | 8.55 | 0 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 20.2 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.65 |  | 20.2 | 20.2 | 20.2 | 20.2 | 0
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-11 | 80-CG-38459-09C02-P CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10057 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 20.4 | CML-11 | CML: Elbow | 6 | 2110-01-05 | 2091-09-17 | 2013-11-06 | 8.6 | 0 | A1: Outside Quadrant |  | 12.26 | 8.6 | 10.43 | 20.4 | 9 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.8 |  | 20.4 | 20.4 | 20.4 | 20.4 | 0
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-6 | 300-PG-20005-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 6162 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 20.9 | CML-6 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 20.9 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16 |  | 20.9 | 20.9 | 20.9 | 20.9 | 0
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-7 | 50-PW-44014-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23152 | CML Wrapped due to leak | 2015-05-10 07:00 | 2015-05-10 15:00 | [37 empty] | CML-7 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-10 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-26 | 50-CG-38001-09C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 10941 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.1 | CML-26 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.057 | A1: Outside Quadrant |  | 5.74 |  |  | 8.1 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 0
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-25 | 50-CG-38001-09C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 10940 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.1 | CML-25 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.057 | A1: Outside Quadrant |  | 5.74 |  |  | 8.1 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.1 | 8.1 | 8.1 |  | 8.1 | 0
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-20 | 50-CG-38001-09C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 10934 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.1 | CML-20 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.057 | A1: Outside Quadrant |  | 5.74 |  |  | 8.1 | 9 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 0
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-1 | 100-FG-45003-03C02 CML-1 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.2
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-2 | 100-FG-45003-03C02 CML-2 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.5
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-3 | 100-FG-45003-03C02 CML-3 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.4
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-4 | 100-FG-45003-03C02 CML-4 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.5
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-5 | 100-FG-45003-03C02 CML-5 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-6 | 100-FG-45003-03C02 CML-6 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.4
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-7 | 100-FG-45003-03C02 CML-7 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.7
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-8 | 100-FG-45003-03C02 CML-8 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.5
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-9 | 100-FG-45003-03C02 CML-9 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-10 | 100-FG-45003-03C02 CML-10 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-11 | 100-FG-45003-03C02 CML-11 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.2
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-12 | 100-FG-45003-03C02 CML-12 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.5
FG04 | Montara_Topside | Yes | Fuel Gas (45) |  | 100-FG-45003-03C02 | CML-13 | 100-FG-45003-03C02 CML-13 | yes |  |  |  |  | 2008-12-11 | [63 empty] | 7.2
Note on J2: Alphanumeric - Required
Note on K2: Alphanumeric - Required
Note on L2: Whole Number
Note on M2: Large Text
Note on N2: Date and Time
Note on O2: Date and Time
Note on P2: Large Text
Note on Q2: Whole Number
Note on R2: Alphanumeric
Note on S2: Date and Time
Note on T2: Alphanumeric
Note on U2: Date and Time
Note on V2: Yes / No
Note on W2: Alphanumeric
Note on X2: Alphanumeric
Note on Y2: Alphanumeric
Note on Z2: Alphanumeric
Note on AA2: Alphanumeric
Note on AB2: Alphanumeric
Note on AC2: Alphanumeric
Note on AD2: Alphanumeric
Note on AE2: Yes / No
Note on AF2: Whole Number
Note on AG2: Alphanumeric
Note on AH2: Alphanumeric
Note on AI2: Alphanumeric
Note on AJ2: Alphanumeric
Note on AK2: Alphanumeric
Note on AL2: Alphanumeric
Note on AM2: Alphanumeric
Note on AN2: Alphanumeric
Note on AO2: Alphanumeric
Note on AP2: Alphanumeric
Note on AQ2: Alphanumeric
Note on AR2: Alphanumeric
Note on AS2: Alphanumeric
Note on AT2: Alphanumeric
Note on AU2: Alphanumeric
Note on AV2: Alphanumeric
Note on AW2: Alphanumeric
Note on AX2: Alphanumeric
Note on AY2: Alphanumeric
Note on AZ2: Numeric
Note on BA2: Alphanumeric
Note on BB2: Alphanumeric
Note on BC2: Whole Number
Note on BD2: Date
Note on BE2: Date
Note on BF2: Date and Time
Note on BG2: Numeric
Note on BH2: Numeric
Note on BI2: Alphanumeric
Note on BJ2: Alphanumeric
Note on BK2: Numeric
Note on BL2: Numeric (mm)
Note on BM2: Numeric
Note on BN2: Numeric
Note on BO2: Alphanumeric
Note on BP2: Numeric (mm)
Note on BQ2: Numeric (mm)
Note on BR2: Alphanumeric
Note on BS2: Alphanumeric
Note on BT2: Alphanumeric
Note on BU2: Alphanumeric
Note on BV2: Alphanumeric
Note on BW2: Alphanumeric
Note on BX2: Numeric
Note on BY2: Numeric
Note on BZ2: Numeric (mm)
Note on CA2: Numeric (mm)
Note on CB2: Numeric (mm)
Note on CC2: Numeric (mm)
Note on CD2: Alphanumeric
Note on CE2: Numeric
Note on CF2: Numeric

## Sheet3
Line vs loop |  | loop in scope 2020?
50-PG-23073-01C03-P | RP01 | AD01 | No
50-PG-23075-03C02-P | RP01 | AD02 | No
50-AI-63001-01E01 | AD01 | CG01 | Yes
50-AI-63002-01E01 | AD01 | CG02 | Yes
50-AI-63004-01E01 | AD01 | CG03 | Yes
50-AI-63005-01E01 | AD01 | CG04 | Yes
25-AI-63006-01E01 | AD01 | CG05 | Yes
50-AI-63007-01E01 | AD01 | CI01 | No
50-AI-63009-01E01 | AD01 | DC01 | No
50-AI-63010-01E01 | AD01 | DC02 | No
50-AI-63011-01E01 | AD01 | DC03 | No
50-AI-63012-01E01 | AD01 | DH01 | Yes
50-AI-63013-01E01 | AD01 | DH02 | No
50-AI-63014-01E01 | AD01 | DN01 | No
50-AU-63015-01E01 | AD01 | DO01 | No
50-AU-63016-01E01 | AD01 | DO02 | No
50-AU-63017-01E01 | AD01 | FG01 | Yes
50-AU-63018-01E01 | AD01 | FG02 | Yes
50-AU-63019-01E01 | AD01 | FG03 | No
50-AU-63020-01E01 | AD01 | FG04 | Yes
50-AU-63021-01E01 | AD01 | FG05 | No
50-AU-63022-01E01 | AD01 | FG06 | No
50-AU-63023-01E01 | AD01 | FG07 | No
50-AI-63030-01E01 | AD01 | FH01 | Yes
50-AI-63031-01E01 | AD01 | FH02 | Yes
25-AI-63032-01E01 | AD01 | FL01 | Yes
50-AI-63034-01E01 | AD01 | FL02 | Yes
50-AI-63035-01E01 | AD01 | GN01 | No
25-AI-63036-01E01 | AD01 | GN02 | No
50-AI-63037-01E01 | AD01 | OL01 | No
50-AI-63038-01E01 | AD01 | PF01 | Yes
25-AI-63039-01E01 | AD01 | PF02 | No
50-AI-63040-01E01 | AD01 | PF03 | No
50-AI-63044-01E01 | AD01 | PF04 | No
50-AI-63450-01E01 | AD01 | PG01 | Yes
1"-AI-XXXXX-01E01 | AD01 | PG02 | No
50-AI-63001-01S01 | AD02 | PG03 | Yes
0100-AS-63L9001-AS20-00 | AD02 | PG04 | Yes
0100-AS-63L9002-AS20-00 | AD02 | PG05 | Yes
0200-AI-63L9003-AS20-00 | AD02 | PG06 | Yes
0100-AI-63L9004-AS20-00 | AD02 | PG07 | No
0100-AS-63L9005-AS20-00 | AD02 | PG08 | Yes
50-CG-38005-01C02 | CG01 | PG09 | Yes
50-CG-38006-01C02 | CG01 | PG10 | No
50-CG-38007-01C02 | CG01 | PL01 | Yes
50-CG-38008-01C02 | CG01 | PL02 | Yes
50-CG-39009-01C02 | CG01 | PL03 | Yes
50-CG-24002-09C02 | CG01 | PL04 | No
50-CG-38009-01C02 | CG01 | PW01 | Yes
50-CG-38463-01C02 | CG01 | PW02 | Yes
50-CG-38467-01C02 | CG01 | PW03 | Yes
50-CG-38490-09C02 | CG01 | RP01 | No
50-CG-38491-09C02 | CG01 | SD01 | No
50-CG-38492-01C02 | CG01 | SD02 | No
50-CG-38500-01C02 | CG01 | VA01 | Yes
50-CG-38300-01C02-P | CG02 | VA02 | No
50-CG-38301-01C02-P | CG02 | WC01 | Yes
50-CG-38302-01C02-P | CG02 | WC02 | Yes
50-CG-24003-09C02 | CG02 | WD01 | No
50-CG-38001-09C02 | CG02 | WD02 | No
50-CG-38466-01C02 | CG02 | WD03 | No
50-CG-38472-01C02 | CG02 | WD04 | No
25-CG-38478-01C02 | CG02 | WF01 | No
25-CG-38481-01C02 | CG02 | WF02 | No
25-CG-38482-01C02 | CG02 | WS01 | No
25-CG-38483-01C02 | CG02 | WS02 | No
25-CG-38493-01C02 | CG02 | Marine | No
25-CG-38494-01C02 | CG02
25-CG-38495-01C02 | CG02
50-CG-38002-09C02-P | CG03
50-CG-38456-01C02-H | CG03
50-CG-38457-01C02-P | CG03
50-CG-38458-01C02-P | CG03
80-CG-38459-09C02-P | CG03
80-CG-38486-09C02-P | CG03
50-CG-38487-09C02-P | CG03
50-CG-38488-09C02-P | CG03
50-CG-38489-01C02-P | CG03
50-CG-38451-09C02-P | CG04
50-CG-38452-09C02-P | CG04
50-CG-38470-01C02-P | CG04
50-CG-38471-01C02-P | CG04
50-CG-38474-01C02-P | CG04
50-CG-38475-01C02-P | CG04
50-CG-38476-01C02-H | CG04
50-CG-38477-01C02-P | CG04
50-CG-38484-01C02-P | CG04
50-CG-38485-01C02-P | CG04
50-CG-38454-01C02-H | CG05
50-CG-38455-01C02-H | CG05
80-CG-38460-01C02-P | CG05
50-FL-43450-01C02-P | FL01
100-FL-43455-01C02-P | FL02
50-CI-42040-01S01 | CI01
50-CI-42041-01S01 | CI01
50-CI-42042-01S01 | CI01
50-CI-42043-01S01 | CI01
50-CI-42044-01S01 | CI01
50-CI-42045-01S01 | CI01
50-CI-42046-01S01 | CI01
50-CI-42047-01S01 | CI01
25-CI-42301-01S01 | CI01
50-CI-42304-01S01 | CI01
50-CI-42305-01S01 | CI01
50-CI-42306-01S01 | CI01
50-CI-42307-01S01 | CI01
50-CI-42308-01S01 | CI01
40-CI-42309-01S01 | CI01
40-CI-42310-01S01 | CI01
40-CI-42311-01S01 | CI01
40-CI-42312-01S01 | CI01
40-CI-42313-01S01 | CI01
50-CI-42314-01S01 | CI01
50-CI-42315-01S01 | CI01
50-CI-42316-01S01 | CI01
50-CI-42317-01S01 | CI01
80-DC-57001-01C02 | DC01
80-DC-57002-01C02 | DC01
80-DC-57003-01C02 | DC01
80-DC-57004-01C02 | DC01
80-DC-57005-01C02 | DC01
80-DC-57006-01C02 | DC01
80-DC-57007-01C02 | DC01
80-DC-57008-01C02 | DC01
50-DC-57009-01C02 | DC01
50-DC-57010-01C02 | DC01
50-DC-57011-01C02 | DC01
50-DC-57012-01C02 | DC01
50-DC-57013-01C02 | DC01
50-DC-57014-01C02 | DC01
50-DC-57015-01C02 | DC01
50-DC-57016-01C02 | DC01
20-DC-57017-01C02 | DC01
50-DC-57019-01C02 | DC01
50-DC-57020-01C02 | DC01
50-DC-57024-01C02 | DC01
50-DC-57025-01C02 | DC01
50-DC-57027-01C02 | DC01
50-DC-57028-01C02 | DC01
50-DC-57029-01C02 | DC01
50-DC-57030-01C02 | DC01
50-DC-57031-01C02 | DC01
100-DC-57035-01C02 | DC01
100-DC-57036-01C02 | DC01
100-DC-57037-01C02 | DC01
100-DC-57038-01C02 | DC01
150-DC-57041-01C02 | DC01
50-DC-57042-01C02 | DC01
50-DC-57043-01C02 | DC01
50-DC-57044-01C02 | DC01
50-DC-57048-03C02 | DC01
50-DC-57051-01C02 | DC01
50-DC-57056-03C02 | DC01
50-DC-57058-06C02 | DC01
50-DC-57059-25C02 | DC01
50-DC-57063-01C02 | DC01
250-DC-57064-01C02 | DC01
250-DC-57065-01C02 | DC01
50-DC-57067-01C02 | DC01
50-DC-57068-01C02 | DC01
50-DC-57069-01C02 | DC01
100-DC-57075-01C02 | DC01
50-DC-57076-25C02 | DC01
50-DC-57077-15C02 | DC01
50-DC-57300-01C02 | DC01
50-DC-57301-01C02 | DC01
50-DC-57310-01C02 | DC01
25-DC-57311-01C02-P | DC01
25-DC-57312-01C02-P | DC01
25-DC-57313-01C02-P | DC01
25-DC-57314-01C02-P | DC01
25-DC-57315-01C02-P | DC01
50-DC-57316-01C02-P | DC01
50-DC-57317-01C02-P | DC01
25-DC-57318-01C02-P | DC01
25-DC-57319-01C02-P | DC01
25-DC-57320-01C02-P | DC01
25-DC-57321-01C02-P | DC01
80-DC-57322-01C02-P | DC01
150-PL-43303-01C02 | DC01
150-PL-43304-01C02 | DC01
150-PL-43305-01C02 | DC01
150-PL-43309-01C02 | DC01
250-PL-43310-01C02 | DC01
50-CG-38462-01C02 | DC01
50-CG-38464-01C02 | DC01
50-CG-38465-01C02 | DC01
50-DC-57450-01C02-P | DC01
50-DC-57451-01C02-P | DC01
0200-DC-57L9006-AC21-00 | DC01
0600-DH-56L9000-AC21M-00 | DC01
0200-DH-56L9003-AC21M-00 | DC01
50-DC-XXXXX-09C03 | DC02
50-DC-XXXXX-03C03 | DC02
50-DC-XXXXX-03C03 | DC02
80-DC-XXXXX-03C03-P | DC02
20-DC-57303-03C03 | DC02
20-DC-57304-06C03 | DC02
25-DC-57305-09C03 | DC02
100-DC-57307-01C03 | DC02
150-DC-57308-01C03 | DC02
150-DC-57309-01C03 | DC02
50-DC-57400-01C03 | DC02
50-DC-57400-01C03 | DC02
50-DC-57403-01C03 | DC02
50-DC-57404-01C03 | DC02
0100-DC-57L9001-AS20-00 | DC03
0100-DC-57L9002-AS20-00 | DC03
0100-DC-57L9003-AS20-00 | DC03
0200-DC-57L9008-AS20-00 | DC03
0100-DC-57L9002-AS20-E-25 | DC03
0100-DC-57L9005-AS20-E-25 | DC03
0200-DC-57L9008-AS20-E-25 | DC03
80-DH-56001-01C02 | DH01
80-DH-56002-01C02 | DH01
80-DH-56003-01C02 | DH01
80-DH-56004-01C02 | DH01
80-DH-56005-01C02 | DH01
80-DH-56006-01C02 | DH01
80-DH-56007-01C02 | DH01
80-DH-56008-01C02 | DH01
100-DH-56009-01C02 | DH01
50-DH-56010-01C02 | DH01
50-DH-56011-01C02 | DH01
80-DH-56012-01C02 | DH01
50-DH-56013-01C02 | DH01
50-DH-56014-01C02 | DH01
50-DH-56015-01C02 | DH01
80-DH-56018-01C02 | DH01
80-DH-56019-01C02 | DH01
80-DH-56021-01C02 | DH01
80-DH-56022-01C02 | DH01
80-DH-56023-01C02 | DH01
80-DH-56024-01C02 | DH01
80-DH-56025-01C02 | DH01
80-DH-56026-01C02 | DH01
80-DH-56027-01C02 | DH01
80-DH-56028-01C02 | DH01
80-DH-56029-01C02 | DH01
80-DH-56030-01C02 | DH01
80-DH-56032-01C02 | DH01
80-DH-56033-01C02 | DH01
80-DH-56034-01C02 | DH01
80-DH-56039-01C02 | DH01
80-DH-56040-01C02 | DH01
80-DH-56041-01C02 | DH01
80-DH-56042-01C02 | DH01
80-DH-56043-01C02 | DH01
80-DH-56044-01C02 | DH01
80-DH-56045-01C02 | DH01
80-DH-56045-01C02 | DH01
80-DH-56046-01C02 | DH01
80-DH-56051-01C02 | DH01
50-DH-56052-01C02 | DH01
80-DH-56053-01C02 | DH01
80-DH-56054-01C02 | DH01
50-DH-56056-01C02 | DH01
50-DH-56057-01C02 | DH01
50-DH-56058-01C02 | DH01
50-DH-56059-01C02 | DH01
50-DH-56060-01C02 | DH01
50-DH-56061-01C02 | DH01
50-DH-56062-01C02 | DH01
50-DH-56063-01C02 | DH01
50-DH-56064-01C02 | DH01
50-DH-56065-01C02 | DH01
50-DH-56066-01C02 | DH01
50-DH-56067-01C02 | DH01
50-DH-56068-01C02 | DH01
50-DH-56069-01C02 | DH01
50-DH-56070-01C02 | DH01
50-DH-56071-01C02 | DH01
80-DH-56074-01C02 | DH01
150-DH-56080-01C02 | DH01
100-DH-56082-01C02 | DH01
100-DH-56083-01C02 | DH01
100-DH-56084-01C02 | DH01
100-DH-56086-01C02 | DH01
100-DH-56087-01C02 | DH01
100-DH-56088-01C02 | DH01
80-DH-56091-01C02 | DH01
80-DH-56092-01C02 | DH01
50-DH-56102-01C02 | DH01
50-DH-56103-01C02 | DH01
50-DH-56104-01C02 | DH01
50-DH-56105-01C02 | DH01
80-DH-56106-01C02 | DH01
80-DH-56107-01C02 | DH01
50-DH-56108-01C02 | DH01
50-DH-56109-01C02 | DH01
50-DH-56110-01C02 | DH01
50-DH-56111-01C02 | DH01
50-DH-56112-01C02 | DH01
50-DH-56113-01C02 | DH01
50-DH-56114-01C02 | DH01
50-DH-56115-01C02 | DH01
50-DH-56116-01C02 | DH01
50-DH-56116A-01C02 | DH01
50-DH-56117-01C02 | DH01
50-DH-56118-01C02 | DH01
50-DH-56119-01C02 | DH01
50-DH-56119A-01C02 | DH01
50-DH-56120-01C02 | DH01
50-DH-56121-01C02 | DH01
50-DH-56122-01C02 | DH01
50-DH-56123-01C02 | DH01
80-DH-56126-01C02 | DH01
80-DH-56127-01C02 | DH01
80-DH-56128-01C02 | DH01
50-DH-56129-01C02 | DH01
50-DH-56130-01C02 | DH01
50-DH-56131-01C02 | DH01
50-DH-56137-01C02 | DH01
50-DH-56138-01C02 | DH01
50-DH-56139-01C02 | DH01
80-DH-56140-01C02 | DH01
80-DH-56140-01C02 | DH01
50-DH-56141-01C02 | DH01
50-DH-56141-01C02 | DH01
25-DH-56142-01C02 | DH01
25-DH-56143-01C02 | DH01
50-DH-56300-01C02 | DH01
50-DH-56302-01C02 | DH01
50-DH-56303-01C02 | DH01
50-DH-56305-01C02 | DH01
50-DH-56306-01C02 | DH01
50-DH-56308-01C02 | DH01
50-DH-56309-01C02 | DH01
50-DH-56310-01C02 | DH01
50-DH-56317-01C02 | DH01
50-DH-56554-01C02 | DH01
50-DH-56555-01C02 | DH01
50-DH-56556-01C02 | DH01
50-DH-56557-01C02 | DH01
50-DH-56558-01C02 | DH01
50-DH-56559-01C02 | DH01
100-DH-56561-01C02 | DH01
50-DH-56564-01C02 | DH01
50-DH-56401-01C02 | DH01
25-DH-58451-01S01 | DH02
25-DH-58451-01S01 | DH02
50-DN-56075-01C02 | DN01
100-DN-56089-01C02 | DN01
50-DN-56094-01C02 | DN01
50-DN-56095-01C02 | DN01
50-DN-56096-01C02 | DN01
50-DN-56097-01C02 | DN01
50-DN-56098-01C02 | DN01
50-DN-56099-01C02 | DN01
50-DN-56100-01C02 | DN01
50-DN-56101-01C02 | DN01
50-DN-56133-01C02 | DN01
50-DN-56134-01C02 | DN01
50-DN-56135-01C02 | DN01
50-DN-56313-01C02 | DN01
50-DN-56314-01C02 | DN01
0200-DN-56L9004-AC21M-00 | DN01
50-DO-62001-01C02 | DO01
50-DO-62003-01C02 | DO01
50-DO-62005-01C02 | DO01
50-DO-62002-01S01 | DO02
50-DO-62004-01S01 | DO02
50-DO-62006-01S01 | DO02
25-DO-62007-15S01 | DO02
25-DO-62008-15S01 | DO02
100-FG-45022-01C02 | FG01
50-FG-45023-01C02 | FG01
50-FG-45024-01C02 | FG01
100-FG-45041-01C02 | FG01
50-FG-45044-03C02 | FG01
50-FG-45048-03C02 | FG01
50-FG-45300-01C02 | FG01
50-FG-45301-01C02 | FG01
50-FG-45302-01C02 | FG01
50-FG-45501-01C02 | FG01
50-FG-45503-01C02 | FG01
150-FG-45505-01C02 | FG01
150-FG-45005-03C02-E | FG02
100-FG-45006-03C02-E | FG02
100-FG-45007-03C02-E | FG02
100-FG-45008-03C02-E | FG02
150-FG-45009-01C02-E | FG02
50-FG-45014-01C02-E | FG02
80-FG-45028-03C02-E | FG02
50-FG-45042-03C02-E | FG02
100-FG-45043-03C02-E | FG02
80-FG-45046-03C02-E | FG02
100-FG-45047-03C02-E | FG02
80-FG-45050-03C02-E | FG02
80-FG-45053-03C02-E | FG02
80-FG-45058-03C02-E | FG02
50-FG-45502-01C02-E | FG02
100-FG-45504-03C02-E | FG02
100-FG-45507-03C02-E | FG02
25-FG-45450-01C02-E | FG02
50-FG-45451-01C02-E | FG02
25-FG-45455-01C02-E | FG02
80-FG-45045-06S01-E | FG03
50-FG-45049-06S01-E | FG03
50-FG-45054-06S01-E | FG03
50-FG-45055-06S01-E | FG03
50-FG-45056-06S01-E | FG03
150-FG-45003-03C02 | FG04
150-FG-45004-03C02 | FG04
100-FG-45017-03C02 | FG04
50-FG-45018-03C02 | FG04
50-FG-45019-03C02 | FG04
50-FG-45020-03C02 | FG04
50-FG-45021-03C02 | FG04
100-FG-45032-03C02 | FG04
25-FG-45033-03C02 | FG04
25-FG-45034-03C02 | FG04
50-FG-45035-03C02 | FG04
50-FG-45036-03C02 | FG04
150-FG-45038-03C02 | FG04
25-FG-45039-03C02 | FG04
25-FG-45040-03C02 | FG04
150-FG-45051-03C02 | FG04
150-FG-45052-03C02 | FG04
50-FG-45452-01C02-H | FG05
50-FG-45454-01C02-E | FG05
150-FG-45002-03C02 | FG06
100-FG-45304-03C02 | FG06
100-FG-45305-03C02 | FG06
80-FG-45453-01C02-P | FG06
80-FG-XXXXX-03C03 | FG07
300-FH-43001-01C02 | FH01
300-FH-43002-01C02 | FH01
200-FH-43003-01C02 | FH01
200-FH-43004-01C02 | FH01
80-FH-43005-01C02 | FH01
80-FH-43007-01C02 | FH01
80-FH-43009-01C02 | FH01
50-FH-43011-01C02 | FH01
200-FH-43012-01C02 | FH01
50-FH-43016-01C02 | FH01
150-FH-43017-01C02 | FH01
80-FH-43019-01C02 | FH01
80-FH-43020-01C02 | FH01
80-FH-43021-01C02 | FH01
50-FH-43023-01C02 | FH01
200-FH-43025-01C02 | FH01
150-FH-43026-01C02 | FH01
150-FH-43027-01C02 | FH01
400-FH-43029-01C02 | FH01
400-FH-43030-01C02 | FH01
100-FH-43035-01C02 | FH01
100-FH-43036-01C02 | FH01
200-FH-43037-01C02 | FH01
200-FH-43038-01C02 | FH01
100-FH-43075-01C02 | FH01
80-FH-43081-01C02 | FH01
100-FH-43100-01C02 | FH01
100-FH-43101-01C02 | FH01
100-FH-43102-01C02 | FH01
300-FH-43103-01C02 | FH01
100-FH-43104-01C02 | FH01
100-FH-43105-01C02 | FH01
100-FH-43106-01C02 | FH01
300-FH-43107-01C02 | FH01
200-FH-43108-01C02 | FH01
200-FH-43109-01C02 | FH01
200-FH-43110-01C02 | FH01
80-FH-43111-01C02 | FH01
80-FH-43112-01C02 | FH01
80-FH-43113-01C02 | FH01
200-FH-43114-01C02 | FH01
80-FH-43115-01C02 | FH01
150-FH-43116-01C02 | FH01
50-FH-43117-01C02 | FH01
50-FH-43118-01C02 | FH01
80-FH-43119-01C02 | FH01
200-FH-43120-01C02 | FH01
150-FH-43121-01C02 | FH01
50-FH-43122-01C02 | FH01
50-FH-43123-01C02 | FH01
80-FH-43124-01C02 | FH01
200-FH-43125-01C02 | FH01
100-FH-43126-01C02 | FH01
150-FH-43127-01C02 | FH01
50-FH-43128-01C02 | FH01
50-FH-43129-01C02 | FH01
200-FH-43131-01C02 | FH01
50-FH-43132-01C02 | FH01
50-FH-43133-01C02 | FH01
200-FH-43135-01C02 | FH01
150-FH-43136-01C02 | FH01
50-FH-43137-01C02 | FH01
50-FH-43138-01C02 | FH01
50-FH-43140-01C02 | FH01
150-FH-43141-01C02 | FH01
100-FH-43142-01C02 | FH01
100-FH-43144-01C02 | FH01
80-FH-43146-01C02 | FH01
100-FH-43147-01C02 | FH01
80-FH-43150-01C02 | FH01
80-FH-43151-01C02 | FH01
80-FH-43155-01C02 | FH01
80-FH-43156-01C02 | FH01
150-FH-43157-01C02 | FH01
80-FH-43158-01C02 | FH01
80-FH-43179-01C02 | FH01
250-FH-43302-01C02 | FH01
250-FH-43303-01C02 | FH01
200-FH-43304-01C02 | FH01
80-FH-43306-01C02 | FH01
80-FH-43307-01C02 | FH01
200-FH-43311-01C02 | FH01
50-FH-43315-01C02 | FH01
400-FH-43500-01C02 | FH01
150-FH-43502-01C02 | FH01
200-FH-43503-01C02 | FH01
200-FH-43504-01C02 | FH01
150-FH-43505-01C02 | FH01
100-FH-43507-01C02 | FH01
400-FH-43508-01C02 | FH01
300-FH-43510-01C02 | FH01
200-FH-43515-01C02 | FH01
200-FH-43516-01C02 | FH01
150-FH-43517-01C02 | FH01
150-FH-43518-01C02 | FH01
50-PG-23061-25C02-P | FH01
50-PG-23074-01C02-P | FH01
25-PW-44026-01C02 | FH01
25-PW-44028-01C02 | FH01
50-FH-43450-01C02 | FH01
50-FH-43451-01C02 | FH01
50-FH-43406-01C02 | FH01
150-FH-43407-01C02 | FH01
150-FH-43148-01S01 | FH02
150-FH-43149-01S01 | FH02
150-FH-43300-25S01-P | FH02
150-FH-43301-01S01 | FH02
150-FH-43313-01S01-P | FH02
50-PG-23062-25S01 | FH02
80-FH-XXXXX-03C03-P | FH03
50-FG-XXXXX-03C02-E | FH04
250-FL-43014-01C02 | FL01
80-FL-43015-01C02 | FL01
300-FL-43070-01C02 | FL01
50-FL-43071-01C02 | FL01
50-FL-43072-01C02 | FL01
50-FL-43074-01C02 | FL01
150-FL-43076-01C02 | FL01
50-FL-43079-01C02 | FL01
300-FL-43080-01C02 | FL01
150-FL-43084-01C02 | FL01
350-FL-43085-01C02 | FL01
350-FL-43086-01C02 | FL01
80-FL-43091-01C02 | FL01
100-FL-43154-01C02 | FL01
250-FL-43170-01C02 | FL01
80-FL-43171-01C02 | FL01
150-FL-43174-01C02 | FL01
150-FL-43175-01C02 | FL01
300-FL-43176-01C02 | FL01
50-FL-43300-01C02 | FL01
50-FL-43301-01C02 | FL01
50-FL-43302-01C02 | FL01
50-FL-43303-01C02 | FL01
150-FL-43304-01C02 | FL01
50-FL-43316-01C02 | FL01
300-FL-43509-01C02 | FL01
300-FL-43510-01C02 | FL01
350-FL-43511-01C02 | FL01
350-FL-43512-01C02 | FL01
50-FL-43513-01C02 | FL01
150-FL-43514-01C02 | FL01
200-VA-23055-01C02 | FL01
50-CG-38478-01C02-P | FL01
150-FL-43451-01C02 | FL01
150-FL-43453-01C02 | FL01
150-FL-43458-01C02 | FL01
80-FL-43460-01C02 | FL01
150-FL-43452-01C02 | FL02
50-FL-43454-01C02-P | FL02
50-GN-67001-01E01 | GN01
50-GN-67002-01E01 | GN01
50-GN-67003-01E01 | GN01
50-GN-67004-01E01 | GN01
50-GN-67005-01E01 | GN01
50-GN-67006-01E01 | GN01
50-GN-67007-01E01 | GN01
50-GN-67008-01E01 | GN01
50-GN-67009-01E01 | GN01
50-GN-67010-01E01 | GN01
50-GN-67011-01E01 | GN01
25-GN-67300-01E01 | GN01
25-GN-67301-01E01 | GN01
0100-GN-67L9000-AS20-00 | GN02
100-OL-69001-01S01 | OL01
100-OL-69002-01S01 | OL01
80-OL-69003-01S01 | OL01
80-OL-69004-01S01 | OL01
50-OL-69005-01S01 | OL01
50-OL-69006-01S01 | OL01
300-PF-20001-03C03-P | PF01
300-PF-20002-03C03-P | PF01
300-PF-20003-03C03-P | PF01
50-PF-20300-03C03-P | PF01
50-PF-20301-03C03-P | PF01
300-PF-20500-03C03-P | PF01
300-PF-20501-03C03-P | PF01
50-PF-20503-03C03-P | PF01
50-PF-20504-03C03-P | PF01
300-PF-20508-03C03-P | PF01
300-PF-20509-03C03-P | PF01
50-PF-20063-03S01-P | PF02
50-PF-20064-03S01-P | PF02
300-PL-13L9004-BC11X-P-50 | PF03
300-PL-13L9005-BC11X-P-50 | PF03
250-PL-13L9000-DD20-P-50 | PF04
250-PL-13L9001-BD20X-P-50 | PF04
250-PL-13L9002-DD20-P-50 | PF04
250-PL-13L9003-BD20X-P-50 | PF04
1000-PL-13L9006-BD20X-P-50 | PF04
50-PG-44022-01C03-P | PG01
250-PW-44010-01C03-P | PG01
250-PW-44023-01C03-P | PG01
300-PG-20004-03C03-P | PG01
300-PG-20005-03C03-P | PG01
150-PG-20009-01C03-P | PG01
80-PG-20026-03C03-P | PG01
80-PG-20027-03C03-P | PG01
50-PG-20030-01C03-P | PG01
150-PG-20031-01C03-P | PG01
250-PG-20036-01C03-P | PG01
80-PG-20044-03C03-P | PG01
80-PG-20045-03C03-P | PG01
80-PG-20046-03C03-P | PG01
80-PG-20047-03C03-P | PG01
300-PG-20048-03C03-P | PG01
300-PG-20049-03C03-P | PG01
80-PG-20053-01C03-P | PG01
150-PG-20054-01C03-P | PG01
150-PG-20055-01C03-P | PG01
100-PG-20056-01C03-P | PG01
80-PG-20061-01C03-P | PG01
150-PG-20062-01C03-P | PG01
250-PG-20062-01C03-P | PG01
200-PG-20071-01C03-P | PG01
200-PG-20300-03C03-P | PG01
200-PG-20301-03C03-P | PG01
200-PG-20302-03C03-P | PG01
200-PG-20303-03C03-P | PG01
300-PG-20502-01C03-P | PG01
300-PG-20506-03C03-P | PG01
150-PG-20507-01C03-P | PG01
300-PG-23001-03C03 | PG01
250-PG-23005-06C03 | PG01
50-PG-23024-03C03 | PG01
80-PG-23025-06C03 | PG01
50-PG-23044-03C03 | PG01
80-PG-23046-06C03 | PG01
300-PG-23070-01C03-P | PG01
100-PG-23071-01C03 | PG01
100-PG-23072-03C03 | PG01
300-PG-20025-03D01-P | PG02
300-PG-20028-03D01-P | PG02
250-PG-20042-01D01-P | PG02
150-PG-20043-01D01-P | PG02
250-PG-23039-06D01 | PG02
200-PG-23066-15S01 | PG02
200-PG-23066-15D01 | PG02
200-PG-23504-15S01 | PG02
80-FG-45303-03C03-P | PG03
80-FG-45306-03C03-P | PG03
300-PG-20037-03C03-PA | PG03
300-PG-23001-03C03-A | PG03
300-PG-23002-03C03-A | PG03
250-PG-23004-06C03-A | PG03
250-PG-23005-06C03-A | PG03
200-PG-23007-09C03-PA | PG03
200-PG-23013-09C03-A | PG03
200-PG-23014-09C03-A | PG03
250-PG-23015-06C03-A | PG03
250-PG-23016-06C03-A | PG03
250-PG-23017-03C03-A | PG03
200-PG-23018-09C03-A | PG03
300-PG-23019-09C03-A | PG03
200-PG-23035-09C03-A | PG03
100-PG-23503-03C03-A | PG03
150-PG-23026-09C02-P | PG04
50-PG-23030-09C02-P | PG04
150-PG-23043-06C02-P | PG04
150-PG-23045-06C02-P | PG04
150-PG-23047-09C02-P | PG04
50-PG-23048-09C02 | PG04
250-PG-23003-06C02-PA | PG05
200-PG-23006-09C02-PA | PG05
200-PG-23008-15S01-A | PG06
300-PG-23038-03D01-A | PG06
150-PG-23L9008-GD20-P-50 | PG07
100-FG-45001-09C02 | PG08
200-PG-23009-09C02 | PG08
100-PG-23028-25C02-P | PG08
80-PG-23029-25C02-P | PG08
100-PG-23049-25C02-P | PG08
80-PG-23050-25C02-P | PG08
50-PG-23063-09C02 | PG08
50-PG-23064-09C02 | PG08
25-PG-23300-25C02 | PG08
150-PG-23506-25C02 | PG08
50-PG-23508-25C02 | PG08
200-PG-24001-09C02 | PG08
150-PG-23010-25C02-PA | PG09
150-PG-23011-25C02-A | PG09
150-PG-23012-25C02-A | PG09
150-PG-23037-25C02-A | PG09
200-PG-23051-09C02-A | PG09
200-PG-23065-09C02-A | PG09
200-PG-23505-09C02-A | PG09
150-PG-23L9009-GD20-P-50 | PG10
250-PL-20006-01C02-P | PL01
250-PL-20007-01C02-P | PL01
200-PL-20010-01C02-P | PL01
300-PL-20011-01C02-P | PL01
200-PL-20012-01C02-P | PL01
200-PL-20013-01C02-P | PL01
200-PL-20014-01C02-P | PL01
200-PL-20015-01C02-P | PL01
200-PL-20016-01C02-P | PL01
200-PL-20017-01C02-P | PL01
200-PL-20018-01C02-P | PL01
200-PL-20019-01C02 | PL01
200-PL-20020-01C02-P | PL01
150-PL-20029-01C02-P | PL01
50-PL-20033-01C02 | PL01
200-PL-20034-03C02-P | PL01
200-PL-20035-03C02-P | PL01
150-PL-20050-01C02-P | PL01
150-PL-20051-01C02-P | PL01
200-PL-20052-01C02-P | PL01
200-PL-20059-01C02 | PL01
50-PL-20060-01C02 | PL01
150-PL-20065-01C02-P | PL01
150-PL-20066-01C02-P | PL01
150-PL-20067-01C02-P | PL01
100-PL-20068-01C02-P | PL01
100-PL-20069-01C02-P | PL01
100-PL-20070-01C02-P | PL01
50-PL-24036-09C02 | PL01
80-PL-44008-01C02 | PL01
80-PL-44513-01C02 | PL01
50-PL-24003-09C02 | PL01
200-PL-20008-01C02-H | PL02
200-PL-43300-01C02-E | PL02
200-PL-43301-01C02-E | PL02
200-PL-43302-01C02-E | PL02
200-PL-43306-01C02-E | PL02
200-PL-43307-01C02-E | PL02
200-PL-43308-01C02-E | PL02
50-PL-23020-01C03 | PL03
50-PL-23021-03C03 | PL03
50-PL-23022-03C03 | PL03
50-PL-23023-03C03 | PL03
50-PL-23032-01C03 | PL03
50-PL-23033-03C03 | PL03
50-PL-23034-01C03 | PL03
50-PL-23040-03C03 | PL03
50-PL-23041-06C03 | PL03
50-PL-23042-09C03 | PL03
50-PL-23052-09C03 | PL03
50-PL-23300-09C03 | PL03
50-PL-23514-01C03 | PL03
50-PL-23515-01C03 | PL03
50-PL-23516-03C03 | PL03
50-PL-45015-03C03 | PL03
50-PL-45016-03C03 | PL03
50-PL-45030-03C03 | PL03
50-PL-45031-03C03 | PL03
50-PL-57066-01C03 | PL03
50-PL-57406-01C03 | PL03
80-PL-44017-01X01 | PL04
80-PL-44031-01X01 | PL04
100-PW-20021-01C02-P | PW01
100-PW-20057-01C02-P | PW01
80-PW-44001-01C02-P | PW01
250-PW-44004-01C02 | PW01
80-PW-44016-01C02-P | PW01
250-PW-44029-01C02 | PW01
250-PW-44030-01C02 | PW01
80-PW-44032-01C02-P | PW01
80-PW-44033-01C02-P | PW01
80-PW-44034-01C02-P | PW01
80-PW-44035-01C02-P | PW01
80-PW-44036-01C02-P | PW01
50-PW-44040-01C02 | PW01
250-PW-20022-01C03-P | PW02
250-PW-20023-01C03-P | PW02
80-PW-20024-01C03-P | PW02
250-PW-20039-01C03-P | PW02
250-PW-20040-03C03-P | PW02
250-PW-20041-03C03-P | PW02
300-PW-44003-01C03 | PW02
50-PW-44009-01C03-P | PW02
300-PW-44037-01C03 | PW02
250-PW-44509-01C03-P | PW02
250-PW-XXXXX-03C03-P | PW02
250-PW-XXXXX-03C03-P | PW02
300-PW-44002-01X01-P | PW03
250-PW-44004-01X01 | PW03
250-PW-44006-01X01 | PW03
250-PW-44007-01X01 | PW03
80-PW-44011-01X01-P | PW03
50-PW-44012-01X01 | PW03
50-PW-44013-01X01 | PW03
50-PW-44014-01X01 | PW03
50-PW-44015-01X01 | PW03
200-PW-44018-01X01 | PW03
200-PW-44019-01X01 | PW03
200-PW-44020-01X01 | PW03
200-PW-44021-01X01 | PW03
80-PW-44024-01X01-P | PW03
50-PW-44025-01X01 | PW03
50-PW-44027-01X01 | PW03
50-FH-43308-01C02 | RP01
50-FH-43309-01C02 | RP01
50-WC-40063-01C02-P | RP01
50-WC-40071-01C02 | RP01
50-DC-57401-01C03 | RP01
50-DC-57402-01C03 | RP01
80-FH-43402-01C02 | RP01
300-PG-23400-01C03-P | RP01
250-PG-23401-01D03-PA | RP01
150-PG-23402-01C02-PA | RP01
150-PG-23403-01C03-A | RP01
150-PG-23404-01D03-A | RP01
100-PG-23405-03C02-P | RP01
100-PG-23406-03C03 | RP01
50-PG-23407-01C03-P | RP01
50-PG-23408-01C02-P | RP01
100-PG-23409-01C03 | RP01
100-PG-23410-01C03 | RP01
50-PG-23411-03C02-P | RP01
50-PG-23412-03C03 | RP01
100-PG-23413-01C03-A | RP01
50-PG-23414-03C03 | RP01
100-PG-23415-01C03 | RP01
50-PG-23416-03C03 | RP01
50-PL-57403-01C03 | RP01
50-WC-40406-01C02 | RP01
150-SL-55001-01C02-H | SD01
80-SC-55002-01C02-P | SD02
50-SL-55003-01C02-P | SD02
50-SL-55006-01C02-P | SD02
25-VA-23054-01C02 | VA01
50-VA-23056-01C02 | VA01
200-VA-23057-01C02 | VA01
200-VA-23058-01C02 | VA01
80-VA-23060-01C02 | VA01
50-VA-80001-01C02 | VA01
100-VA-80002-01C02 | VA01
150-VA-80003-01C02 | VA01
50-VA-80005-01C02 | VA01
100-VA-80006-01C02 | VA01
150-VA-80007-01C02 | VA01
50-VA-43519-01C02 | VA01
0200-VA-43L9000-AC21-00 | VA01
0200-VA-43L9004-AC21-00 | VA01
50-VA-80009-01S01 | VA02
50-VA-80010-01S01 | VA02
50-VA-80011-01S01 | VA02
50-VA-80012-01S01 | VA02
50-VA-80013-01S01 | VA02
50-VA-80014-01S01 | VA02
80-VA-80015-01S01 | VA02
50-VA-80300-01S01 | VA02
25-VA-XXXXX-01S01 | VA02
25-VA-XXXXX-01S01 | VA02
50-VA-XXXXX-01S01 | VA02
0100-VA-43L9001-AS20-00 | VA02
0100-VA-43L9002-AS20-00 | VA02
150-WC-40001-01C02 | WC01
150-WC-40002-01C02 | WC01
150-WC-40003-01C02 | WC01
150-WC-40004-01C02 | WC01
150-WC-40005-01C02 | WC01
150-WC-40006-01C02 | WC01
200-WC-40007-01C02 | WC01
200-WC-40008-01C02-P | WC01
200-WC-40009-01C02 | WC01
200-WC-40010-01C02 | WC01
50-WC-40011-01C02 | WC01
50-WC-40013-01C02 | WC01
50-WC-40014-01C02 | WC01
250-WC-40016-01C02 | WC01
250-WC-40017-01C02 | WC01
50-WC-40018-01C02 | WC01
100-WC-40020-01C02 | WC01
50-WC-40021-01C02 | WC01
400-WC-40022-01C02 | WC01
50-WC-40023-01C02 | WC01
400-WC-40024-01C02 | WC01
400-WC-40025-01C02 | WC01
250-WC-40026-01C02 | WC01
100-WC-40027-01C02 | WC01
50-WC-40028-01C02 | WC01
50-WC-40029-01C02 | WC01
150-WC-40030-01C02 | WC01
50-WC-40031-01C02 | WC01
50-WC-40032-01C02 | WC01
300-WC-40033-01C02 | WC01
100-WC-40034-01C02 | WC01
100-WC-40035-01C02 | WC01
200-WC-40036-01C02 | WC01
200-WC-40038-01C02 | WC01
300-WC-40040-01C02 | WC01
300-WC-40043-01C02 | WC01
300-WC-40044-01C02 | WC01
300-WC-40045-01C02 | WC01
300-WC-40046-01C02 | WC01
50-WC-40047-01C02 | WC01
50-WC-40048-01C02 | WC01
50-WC-40049-01C02 | WC01
50-WC-40050-01C02 | WC01
50-WC-40051-01C02 | WC01
50-WC-40052-01C02 | WC01
50-WC-40053-01C02 | WC01
50-WC-40054-01C02 | WC01
50-WC-40055-01C02 | WC01
150-WC-40056-01C02 | WC01
100-WC-40057-01C02 | WC01
100-WC-40057-01C02 | WC01
80-WC-40058-01C02 | WC01
80-WC-40059-01C02 | WC01
400-WC-40060-01C02 | WC01
400-WC-40061-01C02 | WC01
100-WC-40062-01C02 | WC01
80-WC-40064-01C02 | WC01
50-WC-40065-01C02 | WC01
50-WC-40066-01C02 | WC01
100-WC-40067-01C02 | WC01
80-WC-40068-01C02 | WC01
100-WC-40069-01C02 | WC01
150-WC-40070-01C02 | WC01
50-WC-40450-01C02 | WC01
50-WC-40451-01C02 | WC01
50-WC-40452-01C02 | WC01
200-WC-40401-01C02 | WC01
100-WC-40402-01C02 | WC01
100-WC-40403-01C02 | WC01
150-WC-40404-01C02 | WC01
150-WC-40405-01C02 | WC01
100-WC-4057-1CG | WC02
300-WC-40500-1CG | WC02
400-WC-40500-1CG | WC02
300-WC-40501-1CG | WC02
400-WC-40501-1CG | WC02
250-WC-40502-1CG | WC02
150-WC-40503-1CG | WC02
150-WC-40504-1CG | WC02
250-WC-40505-1CG | WC02
250-WC-40506-1CG | WC02
200-WC-40507-1CG | WC02
200-WC-40508-1CG | WC02
150-WC-40509-1CG | WC02
100-WC-40510-1CG | WC02
300-WC-40511-1CG | WC02
150-WC-40512-1CG | WC02
300-WC-40513-1CG | WC02
50-WC-40514-1CG | WC02
50-WC-40515-1CG | WC02
100-WC-40516-1CG | WC02
50-WC-XXXXX-01E01 | WC02
50-WD-53003-01E01 | WD01
50-WD-53007-01E01 | WD01
50-WD-53008-01E01 | WD01
50-WD-53009-01E01 | WD01
50-WD-53010-01E01 | WD01
50-WD-53011-01E01 | WD01
50-WD-53012-01E01 | WD01
50-WD-53013-01E01 | WD01
50-WD-53014-01E01 | WD01
50-WD-53015-01E01 | WD01
50-WD-53016-01E01 | WD01
25-WD-53018-01E01-C | WD02
25-WD-53019-01E01-C | WD02
25-WD-53020-01E01-C | WD02
25-WD-53021-01E01-C | WD02
25-WD-53022-01E01-C | WD02
25-WD-53023-01E01-C | WD02
25-WD-53024-01E01-C | WD02
15-WD-53025-01E01-C | WD02
0200-WZ-53L9000-AS20-00 | WD03
0100-WZ-53L9001-AS20-00 | WD03
0100-WZ-53L9002-AS20-00 | WD03
32-WZ-53813-1SS-CC | WD04
20-WZ-53814-1SS-CC | WD04
25-WZ-53815-1SS-CC | WD04
15-WZ-53816-1SS-CC | WD04
25-WZ-53817-1SS-CC | WD04
15-WZ-53818-1SS-CC | WD04
25-WZ-53819-1SS-CC | WD04
15-WZ-53820-1SS-CC | WD04
25-WD-53854-1SS-CC | WD04
15-WZ-53855-1SS-CC | WD04
250-WF-71306-01K01 | WF01
200-WF-71306-01K01 | WF01
80-WF-71306-01K01 | WF01
50-WF-71306-01K01 | WF01
100-WF-71308-01K01 | WF01
100-WF-71309-01K01 | WF01
80-WF-71310-01K01 | WF01
150-WF-71310-01K01 | WF01
80-WF-71311-01K01 | WF01
50-WF-71312-01K01 | WF01
40-WF-71313-01K01 | WF01
150-WF-71315-01K01 | WF01
100-WF-71315-01K01 | WF01
50-WF-71316-01K01 | WF01
50-WF-71317-01K01 | WF01
50-WF-71318-01K01 | WF01
100-WF-71319-01K01 | WF01
80-WF-71319-01K01 | WF01
80-WF-71320-01K01 | WF01
100-WF-71321-01K01 | WF01
80-WF-71321-01K01 | WF01
80-WF-71322-01K01 | WF01
150-WF-71323-01K01 | WF01
80-WF-71324-01K01 | WF01
50-WF-71325-01K01 | WF01
100-WF-71326-01K01 | WF01
100-WF-71327-01K01 | WF01
100-WF-71328-01K01 | WF01
50-WF-71329-01K01 | WF01
40-WF-71331-01K01 | WF01
40-WF-71332-01K01 | WF01
50-WF-71333-01K01 | WF01
50-WF-71333-01K01 | WF01
200-WF-71334-01K01 | WF01
40-WF-71334-01K01 | WF01
150-WF-71335-01K01 | WF01
100-WF-71336-01K01 | WF01
40-WF-71337-01K01 | WF01
100-WF-71337-01K01 | WF01
80-WF-71338-01K01 | WF01
50-WF-71339-01K01 | WF01
100-WF-71340-01K01 | WF01
80-WF-71340-01K01 | WF01
50-WF-71340-01K01 | WF01
80-WF-71341-01K01 | WF01
80-WF-71342-01K01 | WF01
50-WF-71342-01K01 | WF01
50-WF-71343-01K01 | WF01
40-WF-71344-01K01 | WF01
150-WF-71345-01K01 | WF01
200-WF-71346-01K01 | WF01
150-WF-71346-01K01 | WF01
150-WF-71347-01K01 | WF01
50-WF-71348-01K01 | WF01
25-WF-71349-01K01 | WF01
50-WF-71350-01K01 | WF01
50-WF-71351-01K01 | WF01
100-WF-71352-01K01 | WF01
50-WF-71353-01K01 | WF01
40-WF-71354-01K01 | WF01
40-WF-71355-01K01 | WF01
40-WF-71356-01K01 | WF01
25-WF-71357-01K01 | WF01
50-WF-71358-01K01 | WF01
100-WF-71359-01K01 | WF01
40-WF-71360-01K01 | WF01
40-WF-71361-01K01 | WF01
50-WF-71362-01K01 | WF01
50-WF-71363-01K01 | WF01
80-WF-71400-01K01 | WF01
0600-WF-XXXXXXX-AK11-00 | WF01
6" FIREWATER INLET 1 | WF01
6" FIREWATER INLET 2 | WF01
6" FIREWATER | WF01
1.5" AFFF | WF02
6" FIREWATER/AFFF OUTLET | WF01
4" TEST/DRAIN | WF01
0600-WF-71L9000-AK11-00 | WF01
0400-WF-71L9001-AK11-00 | WF01
0300-WF-71L9002-AK11-00 | WF01
0300-WF-71L9003-AK11-00 | WF01
0300-WF-71L9004-AK11-00 | WF01
0100-WF-71L9005-AK11-00 | WF01
450-WS-50001-01G02 | WS01
450-WS-50002-01G02 | WS01
50-WS-50003-01G02 | WS01
50-WS-50004-01G02 | WS01
300-WS-50016-01G02 | WS01
300-WS-50017-01G02 | WS01
300-WS-50018-01G02 | WS01
300-WS-50019-01G02 | WS01
50-WS-50020-01G02 | WS01
50-WS-50021-01G02 | WS01
0200-WS-50L9000-AG70-00 | WS02
0200-WS-50L9001-AG70-00 | WS02
150-WF-71371-01K01 | WF01
250-WF-71373-01K01 | WF01
0100-AI-63L9003-AS20-00 | RP01
100-DH-56085-01C02 | RP01
100-DH-56089-01C02 | RP01
150-FL-43456-01C02 | RP01
15-CI-42001-T | RP01
200-WC-40400-01C02 | RP01
100-WF-71967-1CG | Marine
150-WF-71372-01K01 | Marine
150-WF-71374-01K01 | Marine
150-WF-71517-01F01 | Marine
25-DH-56451-01S01 | RP01
25-DH-56452-01S01 | RP01
25-DO-62300-01C02 | Marine
25-DO-62301-01C02 | Marine
25-DO-62302-01C02 | Marine
50-WS-50839-1CG | Marine
25-WS-50840-1LC | Marine
300-WS-50805-1LC | Marine
300-WS-50806-1LC | Marine
500-WS-50801-1LC | Marine
500-WS-50802-1LC | Marine
500-WS-50803-1LC | Marine
500-WS-50812-1LC | Marine
500-WS-50813-1LC | Marine
50-CH-98806-1CG | Marine
50-CH-98808-1CG | Marine
50-DC-57046-01C02 | RP01
50-FL-43306-01C02 | RP01
50-DC-57052-01C02 | RP01
50-PG-23073-01C03-P | RP01
50-PL-45037-03C03 | RP01
50-PL-45517-03C03 | RP01
50-PW-44041-01C02 | RP01
50-WC-40081-01C02 | RP01
80-VA-23301-01C02 | VA01
80-VA-23302-01C02 | VA01
80-WF-71370-01K01 | Marine
80-WS-50810-1LC | Marine
80-WS-50811-1LC | Marine