## Pipe Wall Thickness (Events)
Corrosion Loop ID | Asset Location.Full Location | Loop In 2020 Scope? | Asset Location.Full Location | Asset Location.Full Location | Asset Location.Full Location | Asset Location.Full Location |  | Scope Inspection? | Workpack | Event | Event | Commentary | Last Inspection Date | Event | Finding | Anomaly | Reviewed | Reviewed | Reviewed | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | GVI | Insulation Condition Report | Insulation Condition Report | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Pipe Wall Thickness | Std Deviation | Normal | Normal | Isometric? | Date | UT Reading | UT Reading | UT Reading | UT Reading | Nominal Thickness | Notes
[9 empty] | Name | Event Type | Event Number | Notes |  | End Clock | Reason | Anomaly Number | Personnel | Date and Time | Description | Date of Inspection | External thinning | Flange external coating | Flanges Corrosion Pitting | Handle Instrumentation | Inspector | Instruments External Coating | Instruments External Corrosion Pitting | Insulation Instrumentation | Insulation Piping | Mechanical failure | Overall | Penetrations | Piping corrosion pitting | Piping external coating | Stud Nuts Bolting Corrosion Pitting | Studs Nuts Bolting External Coating | Supports Corrosion pitting | Supports external coating | Supports in Piping | Temporary repair joints clamps condition | Valves External coating | Valves External Corrosion Pitting | Vendor Ref | Vibration in Piping | Vibration Instrumentation | Welds Corrosion Pitting | Welds external coating | Inspector | Vendor Ref | Alarm Breach? | Average Wall Thickness | CML ID | CML Type | Corrosion Allowance | Date for MAWT | Date for T(alarm) | Date of Inspection | High Alarm | Historical Corrosion Rate | Historical CR Location | Inspector | Low Alarm | MAWT | Medium Alarm | Minimum Wall Thickness | Minimum WT Position | Nominal Diameter | Nominal Wall Thickness | Parent Piping | Pipe Schedule | Reading Location 1 | Reading Location 2 | Reading Location 3 | Reading Location 4 | Remaining to MAWT | STCR | Thickness 1 | Thickness 2 | Thickness 3 | Thickness 4 | Vendor Ref | Start - Elevation | End - Elevation |  |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45003-03C02 | CML-7 | 150-FG-45003-03C02 CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24373 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-7 | CML: Elbow | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 4.11 | 2.5 | 3.305 |  | 9 O'Clock | 150 | 7.11 | 150-FG-45003-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45003-03C02 | CML-6 | 150-FG-45003-03C02 CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24372 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-6 | CML: Elbow | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 4.11 | 2.5 | 3.305 |  | 9 O'Clock | 150 | 7.11 | 150-FG-45003-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45003-03C02 | CML-5 | 150-FG-45003-03C02 CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24371 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-5 | CML: Pipe Length | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 4.11 | 2.5 | 3.305 |  | 9 O'Clock | 20 | 7.11 | 150-FG-45003-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9004-AK11-00 | CML-1 | 0300-WF-71L9004-AK11-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22554 | Rope Access / Physical damage to Nozzle | 2015-04-24 07:00 | 2015-04-24 15:00 | Pi | [34 empty] | High alarm breach | 1.6 | CML-1 | CML: Reducing Tee | 0.5 | 2011-02-07 | 2013-06-29 | 2015-04-24 07:00 | 2.5 | 0.26125 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 1.4 | 6 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -1.1 |  | 1.8 | 1.7 | 1.4 | 1.5 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9004-AK11-00 | CML-12 | 0300-WF-71L9004-AK11-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22565 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [35 empty] | High alarm breach | 1.45 | CML-12 | CML: Reducing Tee | 0.5 | 2011-02-07 | 2013-06-29 | 2015-04-24 07:00 | 2.5 | 0.26125 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 1.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -1.1 |  | 1.4 | 1.5 | 1.5 | 1.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-1 | 250-WF-71373-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6879 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.65 | CML-1 | CML: type TBC | 0.5 | 2014-04-17 | 2014-01-27 | 2015-04-05 07:00 | 3.5 | 1.1384 | A2: Right Quadrant |  | 4 | 3.5 | 3.75 | 2.4 | 3 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -1.1 |  | 2.6 | 2.4 | 2.5 | 3.1 | 0.31091
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML3 | 100-WF-71326-01K01 CML3 |  | FPSO 2015 | Pipe Wall Thickness | 7535 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.4 | CML3 | CML: type TBC | 0.5 | 2014-02-18 | 2014-02-18 | 2015-04-14 07:00 | 2.5 | 0.69545 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 1.7 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.8 |  | 2.4 | 1.7 | 2.4 | 3.1 | 0.57155
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-12 | 150-WF-71345-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6686 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.625 | CML-12 | CML: type TBC | 0.5 | 2014-03-08 | 2014-03-08 | 2015-04-04 07:00 | 2.5 | 0.6515 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 1.8 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.7 |  | 3.8 | 2.5 | 1.8 | 2.4 | 0.84212
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-38 | 150-WF-71345-01K01 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 6712 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-38 | CML: type TBC | 0.5 | 2014-03-08 | 2014-03-08 | 2015-04-04 07:00 | 2.5 | 0.6515 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 1.8 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.7 |  | 2.4 | 2.4 | 1.8 | 3 | 0.4899
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML57 | 100-WF-71309-01K01 CML57 |  | FPSO 2015 | Pipe Wall Thickness | 7396 |  | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-26 16:19 | [31 empty] | High alarm breach | 2.675 | CML57 | CML: type TBC | 0.5 | 2014-04-05 | 2014-04-05 | 2015-04-11 07:00 | 2.5 | 0.59106 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 1.9 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.6 |  | 2.6 | 1.9 | 2.6 | 3.6 | 0.6994
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML6 | 80-WF-71311-01K01 CML6 |  | FPSO 2015 | Pipe Wall Thickness | 7251 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 17:37 | [31 empty] | High alarm breach | 2.625 | CML6 | CML: type TBC | 0.5 | 2013-06-01 | 2014-03-10 | 2015-04-09 07:00 | 2.5 | 0.32335 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 1.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.6 |  | 1.9 | 2.5 | 3.6 | 2.5 | 0.70887
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML45 | 80-WF-71338-01K01 CML45 |  | FPSO 2015 | Pipe Wall Thickness | 7091 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.55 | CML45 | CML: type TBC | 0.5 | 2013-06-01 | 2014-03-09 | 2015-04-07 07:00 | 2.5 | 0.3243 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 1.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.6 |  | 1.9 | 2.4 | 3.3 | 2.6 | 0.58023
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-102 | 150-WF-71345-01K01 CML-102 |  | FPSO 2015 | Pipe Wall Thickness | 6776 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.45 | CML-102 | CML: type TBC | 0.5 | 2014-04-02 | 2014-04-02 | 2015-04-04 07:00 | 2.5 | 0.59721 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 1.9 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.6 |  | 2.5 | 3 | 2.4 | 1.9 | 0.45092
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-44 | 150-WF-71345-01K01 CML-44 |  | FPSO 2015 | Pipe Wall Thickness | 6718 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.525 | CML-44 | CML: type TBC | 0.5 | 2014-04-02 | 2014-04-02 | 2015-04-04 07:00 | 2.5 | 0.59721 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 1.9 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.6 |  | 2.4 | 1.9 | 2.2 | 3.6 | 0.74554
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 15 | 0300-WF-71L9003-AK11-00 CML - 15 |  | FPSO 2015 | Pipe Wall Thickness | 22624 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.3 | CML - 15 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2 | 6 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.5 | 2.3 | 2 | 2.4 | 0.21602
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-91 | 80-WF-71340-01K01 CML-91 |  | FPSO 2015 | Pipe Wall Thickness | 22462 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.025 | CML-91 | CML: Reducer | 0.5 | 2013-06-01 | 2014-05-10 | 2015-04-19 07:00 | 2.5 | 0.26553 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2 | 6 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2 | 2 | 2.1 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-79 | 80-WF-71340-01K01 CML-79 |  | FPSO 2015 | Pipe Wall Thickness | 22450 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.275 | CML-79 | CML: Elbow | 0.5 | 2013-06-01 | 2014-05-10 | 2015-04-19 07:00 | 2.5 | 0.26553 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.3 | 2.4 | 2.4 | 2 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-50 | 50-WF-71340-01K01 CML-50 |  | FPSO 2015 | Pipe Wall Thickness | 22421 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.625 | CML-50 | CML: Elbow | 0.5 | 2013-06-01 | 2014-05-10 | 2015-04-19 07:00 | 2.5 | 0.26553 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2 | 3 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.5 | 2 | 2.6 | 3.4 | 0.57951
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-22 | 100-WF-71340-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 22393 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.125 | CML-22 | CML: Reducer | 0.5 | 2014-05-10 | 2014-05-10 | 2015-04-19 07:00 | 2.5 | 0.53107 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.3 | 2.1 | 2.1 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-19 | 100-WF-71340-01K01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 22390 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-19 | CML: Elbow | 0.5 | 2014-05-10 | 2014-05-10 | 2015-04-19 07:00 | 2.5 | 0.53107 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.5 | 3 | 2.5 | 0.40825
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-2 | 100-WF-71340-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22373 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 3.75 | CML-2 | CML: Reducing Tee | 0.5 | 2014-05-10 | 2014-05-10 | 2015-04-19 07:00 | 2.5 | 0.53107 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 4 | 4.2 | 2 | 4.8 | 1.2152
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML59 | 100-WF-71326-01K01 CML59 |  | FPSO 2015 | Pipe Wall Thickness | 7591 |  | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 17:09 | [31 empty] | High alarm breach | 2.325 | CML59 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.1 | 2 | 2.2 | 3 | 0.45735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML48 | 100-WF-71326-01K01 CML48 |  | FPSO 2015 | Pipe Wall Thickness | 7580 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.65 | CML48 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.5 | 3.4 | 2.7 | 0.58023
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML43 | 100-WF-71326-01K01 CML43 |  | FPSO 2015 | Pipe Wall Thickness | 7575 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.125 | CML43 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.2 | 2.3 | 2 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML32 | 100-WF-71326-01K01 CML32 |  | FPSO 2015 | Pipe Wall Thickness | 7564 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.325 | CML32 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.4 | 2.5 | 2.4 | 2 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML63 | 100-WF-71326-01K01 CML63 |  | FPSO 2015 | Pipe Wall Thickness | 7595 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.55 | CML63 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 3 | 3.1 | 2 | 2.1 | 0.58023
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML26 | 100-WF-71326-01K01 CML26 |  | FPSO 2015 | Pipe Wall Thickness | 7558 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.375 | CML26 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.2 | 2.6 | 2.7 | 2 | 0.3304
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML24 | 100-WF-71326-01K01 CML24 |  | FPSO 2015 | Pipe Wall Thickness | 7556 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.275 | CML24 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.6 | 2.4 | 2.1 | 2 | 0.27538
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML14 | 100-WF-71326-01K01 CML14 |  | FPSO 2015 | Pipe Wall Thickness | 7546 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.15 | CML14 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.1 | 2.3 | 2.2 | 2 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML11 | 100-WF-71326-01K01 CML11 |  | FPSO 2015 | Pipe Wall Thickness | 7543 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.525 | CML11 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 3.2 | 2.6 | 2 | 2.3 | 0.51235
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML9 | 100-WF-71326-01K01 CML9 |  | FPSO 2015 | Pipe Wall Thickness | 7541 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.075 | CML9 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2 | 2.3 | 2 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML4 | 100-WF-71326-01K01 CML4 |  | FPSO 2015 | Pipe Wall Thickness | 7536 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.85 | CML4 | CML: type TBC | 0.5 | 2014-05-08 | 2014-05-08 | 2015-04-14 07:00 | 2.5 | 0.53496 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 3.5 | 3.3 | 2 | 2.6 | 0.68557
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML130 | 100-WF-71309-01K01 CML130 |  | FPSO 2015 | Pipe Wall Thickness | 7469 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.5 | CML130 | CML: type TBC | 0.5 | 2014-05-06 | 2014-05-06 | 2015-04-11 07:00 | 2.5 | 0.53732 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.4 | 3.2 | 2.4 | 0.50332
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML59 | 100-WF-71309-01K01 CML59 |  | FPSO 2015 | Pipe Wall Thickness | 7398 |  | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-26 16:19 | [31 empty] | High alarm breach | 2.625 | CML59 | CML: type TBC | 0.5 | 2014-05-06 | 2014-05-06 | 2015-04-11 07:00 | 2.5 | 0.53732 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.5 | 2 | 2.5 | 3.5 | 0.62915
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML58 | 100-WF-71309-01K01 CML58 |  | FPSO 2015 | Pipe Wall Thickness | 7397 |  | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-26 16:19 | [31 empty] | High alarm breach | 2.55 | CML58 | CML: type TBC | 0.5 | 2014-05-06 | 2014-05-06 | 2015-04-11 07:00 | 2.5 | 0.53732 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.3 | 2 | 2.4 | 3.5 | 0.65574
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML53 | 100-WF-71309-01K01 CML53 |  | FPSO 2015 | Pipe Wall Thickness | 7392 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.575 | CML53 | CML: type TBC | 0.5 | 2014-05-06 | 2014-05-06 | 2015-04-11 07:00 | 2.5 | 0.53732 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.6 | 2 | 2.4 | 3.3 | 0.54391
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML52 | 100-WF-71309-01K01 CML52 |  | FPSO 2015 | Pipe Wall Thickness | 7391 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.225 | CML52 | CML: type TBC | 0.5 | 2014-05-06 | 2014-05-06 | 2015-04-11 07:00 | 2.5 | 0.53732 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.4 | 2 | 2 | 2.5 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML27 | 100-WF-71309-01K01 CML27 |  | FPSO 2015 | Pipe Wall Thickness | 7366 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.025 | CML27 | CML: type TBC | 0.5 | 2014-05-06 | 2014-05-06 | 2015-04-11 07:00 | 2.5 | 0.53732 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.1 | 2 | 2 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML6 | 100-WF-71309-01K01 CML6 |  | FPSO 2015 | Pipe Wall Thickness | 7345 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.225 | CML6 | CML: type TBC | 0.5 | 2014-05-06 | 2014-05-06 | 2015-04-11 07:00 | 2.5 | 0.53732 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.6 | 2 | 2.1 | 2.2 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML4 | 100-WF-71309-01K01 CML4 |  | FPSO 2015 | Pipe Wall Thickness | 7343 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.55 | CML4 | CML: type TBC | 0.5 | 2014-05-06 | 2014-05-06 | 2015-04-11 07:00 | 2.5 | 0.53732 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.4 | 3.3 | 2.5 | 0.54467
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML9 | 80-WF-71311-01K01 CML9 |  | FPSO 2015 | Pipe Wall Thickness | 7254 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 17:40 | [31 empty] | High alarm breach | 2.575 | CML9 | CML: type TBC | 0.5 | 2013-06-01 | 2014-05-05 | 2015-04-09 07:00 | 2.5 | 0.26946 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 3.4 | 2.5 | 2 | 2.4 | 0.5909
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML7 | 80-WF-71311-01K01 CML7 |  | FPSO 2015 | Pipe Wall Thickness | 7252 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 17:39 | [31 empty] | High alarm breach | 2.55 | CML7 | CML: type TBC | 0.5 | 2013-06-01 | 2014-05-05 | 2015-04-09 07:00 | 2.5 | 0.26946 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.4 | 3.3 | 2.5 | 0.54467
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML3 | 80-WF-71311-01K01 CML3 |  | FPSO 2015 | Pipe Wall Thickness | 7248 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 08:54 | [31 empty] | High alarm breach | 2.65 | CML3 | CML: type TBC | 0.5 | 2013-06-01 | 2014-05-05 | 2015-04-09 07:00 | 2.5 | 0.26946 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 3.4 | 2.6 | 2 | 2.6 | 0.57446
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML50 | 80-WF-71320-01K01 CML50 |  | FPSO 2015 | Pipe Wall Thickness | 7239 |  | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:38 | [31 empty] | High alarm breach | 2.2 | CML50 | CML: type TBC | 0.5 | 2013-06-01 | 2014-05-05 | 2015-04-08 07:00 | 2.5 | 0.26985 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2 | 12 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.1 | 2.3 | 2.4 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML17 | 80-WF-71320-01K01 CML17 |  | FPSO 2015 | Pipe Wall Thickness | 7206 |  | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 11:16 | [31 empty] | High alarm breach | 2.35 | CML17 | CML: type TBC | 0.5 | 2013-06-01 | 2014-05-05 | 2015-04-08 07:00 | 2.5 | 0.26985 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.5 | 2 | 2.5 | 2.4 | 0.23805
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML127 | 80-WF-71338-01K01 CML127 |  | FPSO 2015 | Pipe Wall Thickness | 7173 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.525 | CML127 | CML: type TBC | 0.5 | 2013-06-01 | 2014-05-04 | 2015-04-07 07:00 | 2.5 | 0.27025 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 3.1 | 2.5 | 2.5 | 0.45
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML10 | 80-WF-71338-01K01 CML10 |  | FPSO 2015 | Pipe Wall Thickness | 7056 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML10 | CML: type TBC | 0.5 | 2013-06-01 | 2014-05-04 | 2015-04-07 07:00 | 2.5 | 0.27025 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.6 | 3 | 2.3 | 2 | 0.4272
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML5 | 100-WF-71308-01K01 CML5 |  | FPSO 2015 | Pipe Wall Thickness | 6923 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.925 | CML5 | CML: type TBC | 0.5 | 2014-05-04 | 2014-05-04 | 2015-04-06 07:00 | 2.5 | 0.54131 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 3.2 | 3 | 2 | 3.5 | 0.65
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-159 | 150-WF-71345-01K01 CML-159 |  | FPSO 2015 | Pipe Wall Thickness | 6833 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.3 | CML-159 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.3 | 2.4 | 2.5 | 0.21602
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-111 | 150-WF-71345-01K01 CML-111 |  | FPSO 2015 | Pipe Wall Thickness | 6785 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.75 | CML-111 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 3.7 | 2.7 | 2 | 2.6 | 0.70475
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-107 | 150-WF-71345-01K01 CML-107 |  | FPSO 2015 | Pipe Wall Thickness | 6781 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.575 | CML-107 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.5 | 2 | 2.6 | 3.2 | 0.49244
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-104 | 150-WF-71345-01K01 CML-104 |  | FPSO 2015 | Pipe Wall Thickness | 6778 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.5 | CML-104 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2 | 2.5 | 3 | 2.5 | 0.40825
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-103 | 150-WF-71345-01K01 CML-103 |  | FPSO 2015 | Pipe Wall Thickness | 6777 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.5 | CML-103 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 3 | 2.5 | 2.5 | 2 | 0.40825
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-101 | 150-WF-71345-01K01 CML-101 |  | FPSO 2015 | Pipe Wall Thickness | 6775 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-101 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 3 | 2.4 | 2 | 2.5 | 0.4113
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-27 | 150-WF-71345-01K01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6701 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.575 | CML-27 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.8 | 2.5 | 3 | 2 | 0.43493
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-26 | 150-WF-71345-01K01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6700 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 3.15 | CML-26 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 4.1 | 3 | 3.5 | 2 | 0.88882
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-50 | 150-WF-71345-01K01 CML-50 |  | FPSO 2015 | Pipe Wall Thickness | 6724 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.25 | CML-50 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.4 | 2 | 2.1 | 2.5 | 0.23805
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-43 | 150-WF-71345-01K01 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 6717 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.625 | CML-43 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.6 | 2 | 2.4 | 3.5 | 0.63443
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-65 | 150-WF-71345-01K01 CML-65 |  | FPSO 2015 | Pipe Wall Thickness | 6739 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.325 | CML-65 | CML: type TBC | 0.5 | 2014-05-03 | 2014-05-03 | 2015-04-04 07:00 | 2.5 | 0.54292 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.5 |  | 2.7 | 2 | 2.4 | 2.2 | 0.29861
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 27 | 0300-WF-71L9003-AK11-00 CML - 27 |  | FPSO 2015 | Pipe Wall Thickness | 22636 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.35 | CML - 27 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.1 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.3 | 2.1 | 2.2 | 2.8 | 0.31091
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 34 | 0300-WF-71L9002-AK11-00 CML - 34 |  | FPSO 2015 | Pipe Wall Thickness | 22603 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.425 | CML - 34 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.1 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.3 | 2.8 | 2.5 | 2.1 | 0.29861
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 14 | 0300-WF-71L9002-AK11-00 CML - 14 |  | FPSO 2015 | Pipe Wall Thickness | 22583 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.425 | CML - 14 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.1 | 6 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.5 | 2.7 | 2.1 | 2.4 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 9 | 0300-WF-71L9002-AK11-00 CML - 9 |  | FPSO 2015 | Pipe Wall Thickness | 22578 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.25 | CML - 9 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.1 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.3 | 2.1 | 2.4 | 2.2 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-111 | 80-WF-71340-01K01 CML-111 |  | FPSO 2015 | Pipe Wall Thickness | 22482 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.35 | CML-111 | CML: Reducer | 0.5 | 2013-06-01 | 2014-08-04 | 2015-04-19 07:00 | 2.5 | 0.21243 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 3 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.4 | 2.1 | 2.2 | 2.7 | 0.26458
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-74 | 80-WF-71340-01K01 CML-74 |  | FPSO 2015 | Pipe Wall Thickness | 22445 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.275 | CML-74 | CML: Reducer | 0.5 | 2013-06-01 | 2014-08-04 | 2015-04-19 07:00 | 2.5 | 0.21243 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 3 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.2 | 2.1 | 2.2 | 2.6 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-71 | 80-WF-71340-01K01 CML-71 |  | FPSO 2015 | Pipe Wall Thickness | 22442 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.375 | CML-71 | CML: Elbow | 0.5 | 2013-06-01 | 2014-08-04 | 2015-04-19 07:00 | 2.5 | 0.21243 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.5 | 2.3 | 2.6 | 2.1 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-25 | 100-WF-71340-01K01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 22396 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.525 | CML-25 | CML: Reducing Tee | 0.5 | 2014-06-17 | 2014-06-17 | 2015-04-19 07:00 | 2.5 | 0.47796 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 3 | 2.5 | 2.1 | 2.5 | 0.36856
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-21 | 100-WF-71340-01K01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 22392 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-21 | CML: Elbow | 0.5 | 2014-06-17 | 2014-06-17 | 2015-04-19 07:00 | 2.5 | 0.47796 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.5 | 3 | 2.3 | 0.38622
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-3 | 100-WF-71340-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22374 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.575 | CML-3 | CML: Elbow | 0.5 | 2014-06-17 | 2014-06-17 | 2015-04-19 07:00 | 2.5 | 0.47796 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.7 | 3.2 | 2.3 | 2.1 | 0.48563
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML3 | 40-WF-71354-01K01 CML3 |  | FPSO 2015 | Pipe Wall Thickness | 7598 |  | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.375 | CML3 | CML: type TBC | 0.5 | 2013-06-01 | 2014-08-02 | 2015-04-15 07:00 | 2.5 | 0.21367 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 12 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.5 | 2.4 | 2.5 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML23 | 100-WF-71326-01K01 CML23 |  | FPSO 2015 | Pipe Wall Thickness | 7555 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.325 | CML23 | CML: type TBC | 0.5 | 2014-06-15 | 2014-06-15 | 2015-04-14 07:00 | 2.5 | 0.48147 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.5 | 2.6 | 2.1 | 2.1 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML8 | 100-WF-71326-01K01 CML8 |  | FPSO 2015 | Pipe Wall Thickness | 7540 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.225 | CML8 | CML: type TBC | 0.5 | 2014-06-15 | 2014-06-15 | 2015-04-14 07:00 | 2.5 | 0.48147 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.5 | 2.1 | 2.2 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML129 | 100-WF-71309-01K01 CML129 |  | FPSO 2015 | Pipe Wall Thickness | 7468 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.625 | CML129 | CML: type TBC | 0.5 | 2014-06-13 | 2014-06-13 | 2015-04-11 07:00 | 2.5 | 0.48359 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.6 | 3.3 | 2.5 | 0.49917
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML128 | 100-WF-71309-01K01 CML128 |  | FPSO 2015 | Pipe Wall Thickness | 7467 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.55 | CML128 | CML: type TBC | 0.5 | 2014-06-13 | 2014-06-13 | 2015-04-11 07:00 | 2.5 | 0.48359 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.4 | 2.1 | 2.5 | 3.2 | 0.46547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML118 | 100-WF-71309-01K01 CML118 |  | FPSO 2015 | Pipe Wall Thickness | 7457 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.175 | CML118 | CML: type TBC | 0.5 | 2014-06-13 | 2014-06-13 | 2015-04-11 07:00 | 2.5 | 0.48359 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.2 | 2.1 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML93 | 100-WF-71309-01K01 CML93 |  | FPSO 2015 | Pipe Wall Thickness | 7432 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.175 | CML93 | CML: type TBC | 0.5 | 2014-06-13 | 2014-06-13 | 2015-04-11 07:00 | 2.5 | 0.48359 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.2 | 2.1 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML61 | 100-WF-71309-01K01 CML61 |  | FPSO 2015 | Pipe Wall Thickness | 7400 |  | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-26 16:19 | [31 empty] | High alarm breach | 2.275 | CML61 | CML: type TBC | 0.5 | 2014-06-13 | 2014-06-13 | 2015-04-11 07:00 | 2.5 | 0.48359 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.4 | 2.2 | 2.4 | 2.1 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML60 | 100-WF-71309-01K01 CML60 |  | FPSO 2015 | Pipe Wall Thickness | 7399 |  | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-26 16:19 | [31 empty] | High alarm breach | 2.675 | CML60 | CML: type TBC | 0.5 | 2014-06-13 | 2014-06-13 | 2015-04-11 07:00 | 2.5 | 0.48359 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.5 | 2.1 | 2.6 | 3.5 | 0.5909
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML3 | 100-WF-71309-01K01 CML3 |  | FPSO 2015 | Pipe Wall Thickness | 7342 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.675 | CML3 | CML: type TBC | 0.5 | 2014-06-13 | 2014-06-13 | 2015-04-11 07:00 | 2.5 | 0.48359 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.6 | 2.5 | 3.5 | 0.5909
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML26 | 80-WF-71311-01K01 CML26 |  | FPSO 2015 | Pipe Wall Thickness | 7271 |  | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.375 | CML26 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-29 | 2015-04-09 07:00 | 2.5 | 0.21556 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.4 | 2.5 | 2.5 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML23 | 80-WF-71311-01K01 CML23 |  | FPSO 2015 | Pipe Wall Thickness | 7268 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.775 | CML23 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-29 | 2015-04-09 07:00 | 2.5 | 0.21556 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.9 | 2.9 | 3.2 | 2.1 | 0.4717
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML16 | 80-WF-71311-01K01 CML16 |  | FPSO 2015 | Pipe Wall Thickness | 7261 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 16:41 | [31 empty] | High alarm breach | 2.35 | CML16 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-29 | 2015-04-09 07:00 | 2.5 | 0.21556 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.4 | 2.6 | 2.1 | 2.3 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML14 | 80-WF-71311-01K01 CML14 |  | FPSO 2015 | Pipe Wall Thickness | 7259 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 16:43 | [31 empty] | High alarm breach | 2.45 | CML14 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-29 | 2015-04-09 07:00 | 2.5 | 0.21556 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.6 | 2.6 | 2.1 | 2.5 | 0.23805
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML13 | 80-WF-71311-01K01 CML13 |  | FPSO 2015 | Pipe Wall Thickness | 7258 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 09:15 | [31 empty] | High alarm breach | 2.375 | CML13 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-29 | 2015-04-09 07:00 | 2.5 | 0.21556 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.4 | 2.5 | 2.5 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML5 | 80-WF-71311-01K01 CML5 |  | FPSO 2015 | Pipe Wall Thickness | 7250 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 08:56 | [31 empty] | High alarm breach | 2.1 | CML5 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-29 | 2015-04-09 07:00 | 2.5 | 0.21556 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.1 | 2.1 | 2.1 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML18 | 80-WF-71311-01K01 CML18 |  | FPSO 2015 | Pipe Wall Thickness | 7263 |  | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.325 | CML18 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-29 | 2015-04-09 07:00 | 2.5 | 0.21556 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.4 | 2.3 | 2.1 | 2.5 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML45 | 80-WF-71320-01K01 CML45 |  | FPSO 2015 | Pipe Wall Thickness | 7234 |  | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:37 | [31 empty] | High alarm breach | 2.65 | CML45 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-08 07:00 | 2.5 | 0.21588 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.6 | 2.1 | 3.2 | 2.7 | 0.45092
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML23 | 80-WF-71320-01K01 CML23 |  | FPSO 2015 | Pipe Wall Thickness | 7212 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.95 | CML23 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-08 07:00 | 2.5 | 0.21588 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.5 | 2.1 | 2.9 | 4.3 | 0.95743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML22 | 80-WF-71320-01K01 CML22 |  | FPSO 2015 | Pipe Wall Thickness | 7211 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.45 | CML22 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-08 07:00 | 2.5 | 0.21588 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.5 | 2.7 | 2.5 | 2.1 | 0.25166
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML1 | 80-WF-71320-01K01 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 7190 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.575 | CML1 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-08 07:00 | 2.5 | 0.21588 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 3.1 | 2.7 | 2.1 | 2.4 | 0.4272
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML101 | 80-WF-71338-01K01 CML101 |  | FPSO 2015 | Pipe Wall Thickness | 7147 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML101 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-07 07:00 | 2.5 | 0.2162 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.4 | 2.4 | 2.8 | 2.1 | 0.28723
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML87 | 80-WF-71338-01K01 CML87 |  | FPSO 2015 | Pipe Wall Thickness | 7133 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.325 | CML87 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-07 07:00 | 2.5 | 0.2162 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.4 | 2.4 | 2.4 | 2.1 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML86 | 80-WF-71338-01K01 CML86 |  | FPSO 2015 | Pipe Wall Thickness | 7132 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML86 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-07 07:00 | 2.5 | 0.2162 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.6 | 2.1 | 2.6 | 2.4 | 0.23629
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML84 | 80-WF-71338-01K01 CML84 |  | FPSO 2015 | Pipe Wall Thickness | 7130 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML84 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-07 07:00 | 2.5 | 0.2162 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.6 | 2.1 | 2.7 | 2.3 | 0.27538
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML67 | 80-WF-71338-01K01 CML67 |  | FPSO 2015 | Pipe Wall Thickness | 7113 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.525 | CML67 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-07 07:00 | 2.5 | 0.2162 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.5 | 2.5 | 3 | 0.36856
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML32 | 80-WF-71338-01K01 CML32 |  | FPSO 2015 | Pipe Wall Thickness | 7078 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.3 | CML32 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-07 07:00 | 2.5 | 0.2162 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.2 | 2.3 | 2.6 | 2.1 | 0.21602
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML9 | 80-WF-71338-01K01 CML9 |  | FPSO 2015 | Pipe Wall Thickness | 7055 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.4 | CML9 | CML: type TBC | 0.5 | 2013-06-01 | 2014-07-28 | 2015-04-07 07:00 | 2.5 | 0.2162 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.1 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.4 | 2.9 | 2.2 | 0.3559
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML33 | 100-WF-71308-01K01 CML33 |  | FPSO 2015 | Pipe Wall Thickness | 6951 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.275 | CML33 | CML: type TBC | 0.5 | 2014-06-10 | 2014-06-10 | 2015-04-06 07:00 | 2.5 | 0.48718 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.1 | 2.3 | 2.4 | 2.3 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML17 | 100-WF-71308-01K01 CML17 |  | FPSO 2015 | Pipe Wall Thickness | 6935 |  | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-27 15:58 | [31 empty] | High alarm breach | 2.3 | CML17 | CML: type TBC | 0.5 | 2014-06-10 | 2014-06-10 | 2015-04-06 07:00 | 2.5 | 0.48718 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.3 | 2.5 | 2.3 | 2.1 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML9 | 100-WF-71308-01K01 CML9 |  | FPSO 2015 | Pipe Wall Thickness | 6927 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.25 | CML9 | CML: type TBC | 0.5 | 2014-06-10 | 2014-06-10 | 2015-04-06 07:00 | 2.5 | 0.48718 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.5 | 2.1 | 2.1 | 2.3 | 0.19149
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-20 | 150-WF-71345-01K01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6694 |  | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 14:49 | [31 empty] | High alarm breach | 2.275 | CML-20 | CML: type TBC | 0.5 | 2014-06-09 | 2014-06-09 | 2015-04-04 07:00 | 2.5 | 0.48863 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.4 | 2.4 | 2.1 | 2.2 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-39 | 150-WF-71345-01K01 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 6713 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-39 | CML: type TBC | 0.5 | 2014-06-09 | 2014-06-09 | 2015-04-04 07:00 | 2.5 | 0.48863 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.4 | 2.4 | 2.1 | 2.7 | 0.24495
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71352-01K01 | CML-11 | 100-WF-71352-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6121 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [35 empty] | High alarm breach | 2.425 | CML-11 | CML: type TBC | 0.5 | 2014-05-30 | 2014-05-30 | 2015-03-17 07:00 | 2.5 | 0.50207 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.1 | 6 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.4 |  | 2.7 | 2.6 | 2.1 | 2.3 | 0.27538
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45051-03C02 | CML-2 | 150-FG-45051-03C02 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24376 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-2 | CML: Fitting | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 4.11 | 2.5 | 3.305 |  | 9 O'Clock | 150 | 7.11 | 150-FG-45051-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 22 | 0300-WF-71L9003-AK11-00 CML - 22 |  | FPSO 2015 | Pipe Wall Thickness | 22631 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 22 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.2 | 12 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.3 | 2.4 | 2.7 | 0.21602
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 17 | 0300-WF-71L9003-AK11-00 CML - 17 |  | FPSO 2015 | Pipe Wall Thickness | 22626 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.45 | CML - 17 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.2 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.8 | 2.4 | 2.2 | 0.25166
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 6 | 0300-WF-71L9003-AK11-00 CML - 6 |  | FPSO 2015 | Pipe Wall Thickness | 22615 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 6 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.2 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.3 | 2.2 | 2.5 | 2.5 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 31 | 0300-WF-71L9002-AK11-00 CML - 31 |  | FPSO 2015 | Pipe Wall Thickness | 22600 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.45 | CML - 31 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.2 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 2.2 | 2.5 | 2.6 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 13 | 0300-WF-71L9002-AK11-00 CML - 13 |  | FPSO 2015 | Pipe Wall Thickness | 22582 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 13 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.2 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.6 | 2.3 | 2.5 | 2.2 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 11 | 0300-WF-71L9002-AK11-00 CML - 11 |  | FPSO 2015 | Pipe Wall Thickness | 22580 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 11 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.2 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.6 | 2.3 | 2.4 | 2.2 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 7 | 0300-WF-71L9002-AK11-00 CML - 7 |  | FPSO 2015 | Pipe Wall Thickness | 22576 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 7 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.2 | 6 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.4 | 2.2 | 2.6 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-72 | 80-WF-71340-01K01 CML-72 |  | FPSO 2015 | Pipe Wall Thickness | 22443 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.7 | CML-72 | CML: Elbow | 0.5 | 2013-06-01 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.15932 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 3.5 | 2.6 | 2.2 | 0.55976
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-35 | 100-WF-71340-01K01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 22406 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.625 | CML-35 | CML: Reducer | 0.5 | 2014-08-04 | 2014-08-04 | 2015-04-19 07:00 | 2.5 | 0.42486 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.7 | 2.8 | 2.2 | 2.8 | 0.28723
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-31 | 100-WF-71340-01K01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 22402 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.6 | CML-31 | CML: Reducing Tee | 0.5 | 2014-08-04 | 2014-08-04 | 2015-04-19 07:00 | 2.5 | 0.42486 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 3.2 | 2.5 | 2.2 | 2.5 | 0.42426
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-18 | 100-WF-71340-01K01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 22389 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.6 | CML-18 | CML: Elbow | 0.5 | 2014-08-04 | 2014-08-04 | 2015-04-19 07:00 | 2.5 | 0.42486 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 3.2 | 2.5 | 2.2 | 2.5 | 0.42426
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-5 | 100-WF-71340-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22376 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.325 | CML-5 | CML: Reducer | 0.5 | 2014-08-04 | 2014-08-04 | 2015-04-19 07:00 | 2.5 | 0.42486 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.3 | 2.3 | 2.5 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML54 | 100-WF-71326-01K01 CML54 |  | FPSO 2015 | Pipe Wall Thickness | 7586 |  | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 17:07 | [31 empty] | High alarm breach | 2.475 | CML54 | CML: type TBC | 0.5 | 2014-08-01 | 2014-08-01 | 2015-04-14 07:00 | 2.5 | 0.42797 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.6 | 2.7 | 2.2 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML51 | 100-WF-71326-01K01 CML51 |  | FPSO 2015 | Pipe Wall Thickness | 7583 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 16:27 | [31 empty] | High alarm breach | 2.425 | CML51 | CML: type TBC | 0.5 | 2014-08-01 | 2014-08-01 | 2015-04-14 07:00 | 2.5 | 0.42797 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 2.2 | 2.5 | 2.5 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML42 | 100-WF-71326-01K01 CML42 |  | FPSO 2015 | Pipe Wall Thickness | 7574 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.45 | CML42 | CML: type TBC | 0.5 | 2014-08-01 | 2014-08-01 | 2015-04-14 07:00 | 2.5 | 0.42797 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.7 | 2.5 | 2.2 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML41 | 100-WF-71326-01K01 CML41 |  | FPSO 2015 | Pipe Wall Thickness | 7573 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.275 | CML41 | CML: type TBC | 0.5 | 2014-08-01 | 2014-08-01 | 2015-04-14 07:00 | 2.5 | 0.42797 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 2.2 | 2.2 | 2.2 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML131 | 100-WF-71309-01K01 CML131 |  | FPSO 2015 | Pipe Wall Thickness | 7470 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML131 | CML: type TBC | 0.5 | 2014-07-30 | 2014-07-30 | 2015-04-11 07:00 | 2.5 | 0.42986 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.6 | 2.2 | 2.6 | 2.5 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML99 | 100-WF-71309-01K01 CML99 |  | FPSO 2015 | Pipe Wall Thickness | 7438 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.35 | CML99 | CML: type TBC | 0.5 | 2014-07-30 | 2014-07-30 | 2015-04-11 07:00 | 2.5 | 0.42986 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.4 | 2.3 | 2.5 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML95 | 100-WF-71309-01K01 CML95 |  | FPSO 2015 | Pipe Wall Thickness | 7434 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.3 | CML95 | CML: type TBC | 0.5 | 2014-07-30 | 2014-07-30 | 2015-04-11 07:00 | 2.5 | 0.42986 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.3 | 2.2 | 2.4 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML62 | 100-WF-71309-01K01 CML62 |  | FPSO 2015 | Pipe Wall Thickness | 7401 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-26 16:19 | [31 empty] | High alarm breach | 2.35 | CML62 | CML: type TBC | 0.5 | 2014-07-30 | 2014-07-30 | 2015-04-11 07:00 | 2.5 | 0.42986 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.4 | 2.2 | 2.4 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML38 | 100-WF-71309-01K01 CML38 |  | FPSO 2015 | Pipe Wall Thickness | 7377 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.325 | CML38 | CML: type TBC | 0.5 | 2014-07-30 | 2014-07-30 | 2015-04-11 07:00 | 2.5 | 0.42986 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.3 | 2.2 | 2.4 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML24 | 100-WF-71309-01K01 CML24 |  | FPSO 2015 | Pipe Wall Thickness | 7363 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML24 | CML: type TBC | 0.5 | 2014-07-30 | 2014-07-30 | 2015-04-11 07:00 | 2.5 | 0.42986 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.5 | 2.7 | 2.5 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML19 | 100-WF-71309-01K01 CML19 |  | FPSO 2015 | Pipe Wall Thickness | 7358 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.35 | CML19 | CML: type TBC | 0.5 | 2014-07-30 | 2014-07-30 | 2015-04-11 07:00 | 2.5 | 0.42986 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.4 | 2.4 | 2.4 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML48 | 80-WF-71311-01K01 CML48 |  | FPSO 2015 | Pipe Wall Thickness | 7293 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-24 10:27 | [31 empty] | High alarm breach | 2.35 | CML48 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-17 | 2015-04-09 07:00 | 2.5 | 0.16167 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.4 | 2.4 | 2.2 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML12 | 80-WF-71311-01K01 CML12 |  | FPSO 2015 | Pipe Wall Thickness | 7257 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 09:11 | [31 empty] | High alarm breach | 2.4 | CML12 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-17 | 2015-04-09 07:00 | 2.5 | 0.16167 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.6 | 2.2 | 2.4 | 2.4 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML8 | 80-WF-71311-01K01 CML8 |  | FPSO 2015 | Pipe Wall Thickness | 7253 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 17:40 | [31 empty] | High alarm breach | 2.675 | CML8 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-17 | 2015-04-09 07:00 | 2.5 | 0.16167 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 3.4 | 2.7 | 2.4 | 2.2 | 0.5252
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML31 | 80-WF-71320-01K01 CML31 |  | FPSO 2015 | Pipe Wall Thickness | 7220 |  | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-20 11:25 | [31 empty] | High alarm breach | 2.375 | CML31 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-16 | 2015-04-08 07:00 | 2.5 | 0.16191 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.6 | 2.2 | 2.2 | 2.5 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML132 | 80-WF-71338-01K01 CML132 |  | FPSO 2015 | Pipe Wall Thickness | 7178 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.45 | CML132 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-15 | 2015-04-07 07:00 | 2.5 | 0.16215 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.9 | 2.4 | 2.3 | 0.31091
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML100 | 80-WF-71338-01K01 CML100 |  | FPSO 2015 | Pipe Wall Thickness | 7146 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML100 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-15 | 2015-04-07 07:00 | 2.5 | 0.16215 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 2.2 | 2.7 | 2.5 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML98 | 80-WF-71338-01K01 CML98 |  | FPSO 2015 | Pipe Wall Thickness | 7144 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.45 | CML98 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-15 | 2015-04-07 07:00 | 2.5 | 0.16215 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.3 | 2.2 | 2.7 | 2.6 | 0.23805
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML83 | 80-WF-71338-01K01 CML83 |  | FPSO 2015 | Pipe Wall Thickness | 7129 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 16:18 | [31 empty] | High alarm breach | 2.6 | CML83 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-15 | 2015-04-07 07:00 | 2.5 | 0.16215 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.7 | 2.8 | 2.7 | 2.2 | 0.2708
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML68 | 80-WF-71338-01K01 CML68 |  | FPSO 2015 | Pipe Wall Thickness | 7114 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.85 | CML68 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-15 | 2015-04-07 07:00 | 2.5 | 0.16215 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.4 | 2.8 | 4 | 0.80623
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML66 | 80-WF-71338-01K01 CML66 |  | FPSO 2015 | Pipe Wall Thickness | 7112 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.7 | CML66 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-15 | 2015-04-07 07:00 | 2.5 | 0.16215 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.6 | 2.2 | 2.7 | 3.3 | 0.45461
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML7 | 80-WF-71338-01K01 CML7 |  | FPSO 2015 | Pipe Wall Thickness | 7053 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.325 | CML7 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-15 | 2015-04-07 07:00 | 2.5 | 0.16215 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.4 | 2.3 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML3 | 80-WF-71338-01K01 CML3 |  | FPSO 2015 | Pipe Wall Thickness | 7049 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML3 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-15 | 2015-04-07 07:00 | 2.5 | 0.16215 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.4 | 2.5 | 2.6 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML1 | 80-WF-71338-01K01 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 7047 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.575 | CML1 | CML: type TBC | 0.5 | 2013-06-01 | 2014-12-15 | 2015-04-07 07:00 | 2.5 | 0.16215 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.2 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 2.2 | 2.7 | 2.9 | 0.29861
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML114 | 100-WF-71308-01K01 CML114 |  | FPSO 2015 | Pipe Wall Thickness | 7032 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.375 | CML114 | CML: type TBC | 0.5 | 2014-07-27 | 2014-07-27 | 2015-04-06 07:00 | 2.5 | 0.43305 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 2.4 | 2.4 | 2.2 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML112 | 100-WF-71308-01K01 CML112 |  | FPSO 2015 | Pipe Wall Thickness | 7030 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.3 | CML112 | CML: type TBC | 0.5 | 2014-07-27 | 2014-07-27 | 2015-04-06 07:00 | 2.5 | 0.43305 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.2 | 2.4 | 2.2 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML92 | 100-WF-71308-01K01 CML92 |  | FPSO 2015 | Pipe Wall Thickness | 7010 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML92 | CML: type TBC | 0.5 | 2014-07-27 | 2014-07-27 | 2015-04-06 07:00 | 2.5 | 0.43305 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.6 | 2.2 | 2.3 | 2.5 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML83 | 100-WF-71308-01K01 CML83 |  | FPSO 2015 | Pipe Wall Thickness | 7001 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML83 | CML: type TBC | 0.5 | 2014-07-27 | 2014-07-27 | 2015-04-06 07:00 | 2.5 | 0.43305 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.2 | 2.6 | 2.5 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML78 | 100-WF-71308-01K01 CML78 |  | FPSO 2015 | Pipe Wall Thickness | 6996 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML78 | CML: type TBC | 0.5 | 2014-07-27 | 2014-07-27 | 2015-04-06 07:00 | 2.5 | 0.43305 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.3 | 2.2 | 2.9 | 2.3 | 0.32016
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML62 | 100-WF-71308-01K01 CML62 |  | FPSO 2015 | Pipe Wall Thickness | 6980 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.35 | CML62 | CML: type TBC | 0.5 | 2014-07-27 | 2014-07-27 | 2015-04-06 07:00 | 2.5 | 0.43305 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.2 | 2.3 | 2.5 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML54 | 100-WF-71308-01K01 CML54 |  | FPSO 2015 | Pipe Wall Thickness | 6972 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.375 | CML54 | CML: type TBC | 0.5 | 2014-07-27 | 2014-07-27 | 2015-04-06 07:00 | 2.5 | 0.43305 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.5 | 2.4 | 2.2 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML44 | 100-WF-71308-01K01 CML44 |  | FPSO 2015 | Pipe Wall Thickness | 6962 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.325 | CML44 | CML: type TBC | 0.5 | 2014-07-27 | 2014-07-27 | 2015-04-06 07:00 | 2.5 | 0.43305 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.3 | 2.4 | 2.2 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-126 | 150-WF-71345-01K01 CML-126 |  | FPSO 2015 | Pipe Wall Thickness | 6800 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 17:36 | [31 empty] | High alarm breach | 2.325 | CML-126 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.3 | 2.2 | 2.4 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-117 | 150-WF-71345-01K01 CML-117 |  | FPSO 2015 | Pipe Wall Thickness | 6791 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.35 | CML-117 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.3 | 2.2 | 2.5 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-94 | 150-WF-71345-01K01 CML-94 |  | FPSO 2015 | Pipe Wall Thickness | 6768 |  | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 15:00 | [31 empty] | High alarm breach | 2.3 | CML-94 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.4 | 2.3 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-84 | 150-WF-71345-01K01 CML-84 |  | FPSO 2015 | Pipe Wall Thickness | 6758 |  | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 16:39 | [31 empty] | High alarm breach | 2.25 | CML-84 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.3 | 2.2 | 2.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-90 | 150-WF-71345-01K01 CML-90 |  | FPSO 2015 | Pipe Wall Thickness | 6764 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.35 | CML-90 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.3 | 2.2 | 2.5 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-29 | 150-WF-71345-01K01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6703 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.275 | CML-29 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.3 | 2.3 | 2.2 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-14 | 150-WF-71345-01K01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6688 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.35 | CML-14 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 2.3 | 2.4 | 2.2 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-56 | 150-WF-71345-01K01 CML-56 |  | FPSO 2015 | Pipe Wall Thickness | 6730 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.25 | CML-56 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.3 | 2.2 | 2.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-55 | 150-WF-71345-01K01 CML-55 |  | FPSO 2015 | Pipe Wall Thickness | 6729 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.35 | CML-55 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 2.4 | 2.3 | 2.2 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-52 | 150-WF-71345-01K01 CML-52 |  | FPSO 2015 | Pipe Wall Thickness | 6726 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.325 | CML-52 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.4 | 2.4 | 2.3 | 2.2 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-46 | 150-WF-71345-01K01 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 6720 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-46 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.2 | 2.8 | 2.5 | 0.28723
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-42 | 150-WF-71345-01K01 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 6716 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.5 | CML-42 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.5 | 3 | 2.3 | 2.2 | 0.3559
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-70 | 150-WF-71345-01K01 CML-70 |  | FPSO 2015 | Pipe Wall Thickness | 6744 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.45 | CML-70 | CML: type TBC | 0.5 | 2014-07-26 | 2014-07-26 | 2015-04-04 07:00 | 2.5 | 0.43434 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.2 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.2 | 2.7 | 2.5 | 2.4 | 0.20817
WD03 | Montara_Topside | No | Potable Water (53) | Pipework | 0200-WZ-53L9000-AS20-00 | CML-5 | 0200-WZ-53L9000-AS20-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5104 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | High alarm breach | 2.7 | CML-5 | CML: type TBC | 0 | 2014-01-14 | 2014-03-08 | 2015-03-06 07:00 | 2.5 | 0.26359 | A2: Right Quadrant |  | 2.77 | 2.5 | 2.4619 | 2.2 | 3 O'Clock | 50 | 2.77 | 0200-WZ-53L9000-AS20-00 | 10S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 2.9 | 2.2 | 2.9 | 2.8 | 0.33665
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45051-03C02 | CML-3 | 150-FG-45051-03C02 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24377 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-3 | CML: Pipe Length | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 4.11 | 2.5 | 3.305 |  | 9 O'Clock | 20 | 7.11 | 150-FG-45051-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45051-03C02 | CML-4 | 150-FG-45051-03C02 CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24378 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-4 | CML: Elbow | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 4.11 | 2.5 | 3.305 |  | 9 O'Clock | 150 | 7.11 | 150-FG-45051-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45051-03C02 | CML-5 | 150-FG-45051-03C02 CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24379 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-5 | CML: Elbow | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 4.11 | 2.5 | 3.305 |  | 9 O'Clock | 150 | 7.11 | 150-FG-45051-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 34 | 0300-WF-71L9003-AK11-00 CML - 34 |  | FPSO 2015 | Pipe Wall Thickness | 22643 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 34 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.5 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 31 | 0300-WF-71L9003-AK11-00 CML - 31 |  | FPSO 2015 | Pipe Wall Thickness | 22640 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.5 | CML - 31 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.5 | 2.7 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 30 | 0300-WF-71L9003-AK11-00 CML - 30 |  | FPSO 2015 | Pipe Wall Thickness | 22639 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.525 | CML - 30 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.7 | 2.6 | 2.3 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 29 | 0300-WF-71L9003-AK11-00 CML - 29 |  | FPSO 2015 | Pipe Wall Thickness | 22638 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.5 | CML - 29 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.6 | 2.6 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 25 | 0300-WF-71L9003-AK11-00 CML - 25 |  | FPSO 2015 | Pipe Wall Thickness | 22634 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.525 | CML - 25 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 2.3 | 2.9 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 21 | 0300-WF-71L9003-AK11-00 CML - 21 |  | FPSO 2015 | Pipe Wall Thickness | 22630 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 21 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 20 | 0300-WF-71L9003-AK11-00 CML - 20 |  | FPSO 2015 | Pipe Wall Thickness | 22629 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 20 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.6 | 2.3 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 19 | 0300-WF-71L9003-AK11-00 CML - 19 |  | FPSO 2015 | Pipe Wall Thickness | 22628 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.575 | CML - 19 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.7 | 2.3 | 2.7 | 2.6 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 18 | 0300-WF-71L9003-AK11-00 CML - 18 |  | FPSO 2015 | Pipe Wall Thickness | 22627 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 18 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 14 | 0300-WF-71L9003-AK11-00 CML - 14 |  | FPSO 2015 | Pipe Wall Thickness | 22623 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.55 | CML - 14 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.6 | 2.8 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 13 | 0300-WF-71L9003-AK11-00 CML - 13 |  | FPSO 2015 | Pipe Wall Thickness | 22622 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.775 | CML - 13 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 3.1 | 3.3 | 2.4 | 2.3 | 0.49917
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 11 | 0300-WF-71L9003-AK11-00 CML - 11 |  | FPSO 2015 | Pipe Wall Thickness | 22620 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 11 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.5 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 9 | 0300-WF-71L9003-AK11-00 CML - 9 |  | FPSO 2015 | Pipe Wall Thickness | 22618 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 9 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 7 | 0300-WF-71L9003-AK11-00 CML - 7 |  | FPSO 2015 | Pipe Wall Thickness | 22616 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.35 | CML - 7 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 5 | 0300-WF-71L9003-AK11-00 CML - 5 |  | FPSO 2015 | Pipe Wall Thickness | 22614 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 5 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 4 | 0300-WF-71L9003-AK11-00 CML - 4 |  | FPSO 2015 | Pipe Wall Thickness | 22613 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.425 | CML - 4 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.6 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 3 | 0300-WF-71L9003-AK11-00 CML - 3 |  | FPSO 2015 | Pipe Wall Thickness | 22612 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 3 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 39 | 0300-WF-71L9002-AK11-00 CML - 39 |  | FPSO 2015 | Pipe Wall Thickness | 22608 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 39 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 37 | 0300-WF-71L9002-AK11-00 CML - 37 |  | FPSO 2015 | Pipe Wall Thickness | 22606 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 37 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 12 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 36 | 0300-WF-71L9002-AK11-00 CML - 36 |  | FPSO 2015 | Pipe Wall Thickness | 22605 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.35 | CML - 36 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 33 | 0300-WF-71L9002-AK11-00 CML - 33 |  | FPSO 2015 | Pipe Wall Thickness | 22602 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.35 | CML - 33 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.3 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 27 | 0300-WF-71L9002-AK11-00 CML - 27 |  | FPSO 2015 | Pipe Wall Thickness | 22596 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 27 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 26 | 0300-WF-71L9002-AK11-00 CML - 26 |  | FPSO 2015 | Pipe Wall Thickness | 22595 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.425 | CML - 26 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 23 | 0300-WF-71L9002-AK11-00 CML - 23 |  | FPSO 2015 | Pipe Wall Thickness | 22592 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 23 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.3 | 2.6 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 21 | 0300-WF-71L9002-AK11-00 CML - 21 |  | FPSO 2015 | Pipe Wall Thickness | 22590 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 21 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 19 | 0300-WF-71L9002-AK11-00 CML - 19 |  | FPSO 2015 | Pipe Wall Thickness | 22588 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.425 | CML - 19 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.6 | 2.5 | 2.3 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 17 | 0300-WF-71L9002-AK11-00 CML - 17 |  | FPSO 2015 | Pipe Wall Thickness | 22586 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.525 | CML - 17 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.6 | 2.6 | 2.3 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 16 | 0300-WF-71L9002-AK11-00 CML - 16 |  | FPSO 2015 | Pipe Wall Thickness | 22585 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.325 | CML - 16 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 15 | 0300-WF-71L9002-AK11-00 CML - 15 |  | FPSO 2015 | Pipe Wall Thickness | 22584 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.525 | CML - 15 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.6 | 2.7 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 12 | 0300-WF-71L9002-AK11-00 CML - 12 |  | FPSO 2015 | Pipe Wall Thickness | 22581 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.45 | CML - 12 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 12 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.5 | 2.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 10 | 0300-WF-71L9002-AK11-00 CML - 10 |  | FPSO 2015 | Pipe Wall Thickness | 22579 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.375 | CML - 10 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 12 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 8 | 0300-WF-71L9002-AK11-00 CML - 8 |  | FPSO 2015 | Pipe Wall Thickness | 22577 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.35 | CML - 8 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 6 | 0300-WF-71L9002-AK11-00 CML - 6 |  | FPSO 2015 | Pipe Wall Thickness | 22575 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.35 | CML - 6 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 5 | 0300-WF-71L9002-AK11-00 CML - 5 |  | FPSO 2015 | Pipe Wall Thickness | 22574 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.625 | CML - 5 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 3 | 2.7 | 0.29861
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 1 | 0300-WF-71L9002-AK11-00 CML - 1 |  | FPSO 2015 | Pipe Wall Thickness | 22570 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.575 | CML - 1 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.9 | 2.5 | 2.3 | 2.6 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9004-AK11-00 | CML-8 | 0300-WF-71L9004-AK11-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22561 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [35 empty] | High alarm breach | 2.55 | CML-8 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.6 | 2.8 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9004-AK11-00 | CML-6 | 0300-WF-71L9004-AK11-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22559 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [35 empty] | High alarm breach | 2.575 | CML-6 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.3 | 2.7 | 2.7 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9004-AK11-00 | CML-5 | 0300-WF-71L9004-AK11-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22558 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [35 empty] | High alarm breach | 2.525 | CML-5 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.3 | 2.4 | 2.8 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9004-AK11-00 | CML-3 | 0300-WF-71L9004-AK11-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22556 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [35 empty] | High alarm breach | 2.325 | CML-3 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.3 | 9 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.3 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-94 | 50-WF-71340-01K01 CML-94 |  | FPSO 2015 | Pipe Wall Thickness | 22465 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.4 | CML-94 | CML: Elbow | 0.5 | 2013-06-01 | 2015-10-08 | 2015-04-19 07:00 | 2.5 | 0.10621 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 9 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.4 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-89 | 80-WF-71340-01K01 CML-89 |  | FPSO 2015 | Pipe Wall Thickness | 22460 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.425 | CML-89 | CML: Equal Tee | 0.5 | 2013-06-01 | 2015-10-08 | 2015-04-19 07:00 | 2.5 | 0.10621 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 12 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-88 | 80-WF-71340-01K01 CML-88 |  | FPSO 2015 | Pipe Wall Thickness | 22459 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-88 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2015-10-08 | 2015-04-19 07:00 | 2.5 | 0.10621 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 12 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.5 | 2.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-84 | 80-WF-71340-01K01 CML-84 |  | FPSO 2015 | Pipe Wall Thickness | 22455 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.425 | CML-84 | CML: Reducer | 0.5 | 2013-06-01 | 2015-10-08 | 2015-04-19 07:00 | 2.5 | 0.10621 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.6 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-83 | 80-WF-71340-01K01 CML-83 |  | FPSO 2015 | Pipe Wall Thickness | 22454 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.4 | CML-83 | CML: Equal Tee | 0.5 | 2013-06-01 | 2015-10-08 | 2015-04-19 07:00 | 2.5 | 0.10621 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 2.3 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-77 | 80-WF-71340-01K01 CML-77 |  | FPSO 2015 | Pipe Wall Thickness | 22448 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.425 | CML-77 | CML: Elbow | 0.5 | 2013-06-01 | 2015-10-08 | 2015-04-19 07:00 | 2.5 | 0.10621 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 12 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-61 | 50-WF-71340-01K01 CML-61 |  | FPSO 2015 | Pipe Wall Thickness | 22432 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.525 | CML-61 | CML: Reducer | 0.5 | 2013-06-01 | 2015-10-08 | 2015-04-19 07:00 | 2.5 | 0.10621 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.7 | 2.7 | 2.3 | 2.4 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-59 | 50-WF-71340-01K01 CML-59 |  | FPSO 2015 | Pipe Wall Thickness | 22430 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-59 | CML: Reducer | 0.5 | 2013-06-01 | 2015-10-08 | 2015-04-19 07:00 | 2.5 | 0.10621 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 12 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.6 | 2.4 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-42 | 100-WF-71340-01K01 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 22413 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.525 | CML-42 | CML: Reducer | 0.5 | 2014-10-04 | 2014-10-04 | 2015-04-19 07:00 | 2.5 | 0.37175 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.8 | 2.3 | 2.4 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-40 | 100-WF-71340-01K01 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 22411 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.425 | CML-40 | CML: Elbow | 0.5 | 2014-10-04 | 2014-10-04 | 2015-04-19 07:00 | 2.5 | 0.37175 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.5 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML1 | 150-WF-71371-01K01 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 7762 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [35 empty] | High alarm breach | 2.575 | CML1 | CML: type TBC | 0.5 | 2014-10-04 | 2014-10-04 | 2015-04-18 07:00 | 2.5 | 0.37229 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.8 | 2.3 | 2.4 | 2.8 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML13 | 40-WF-71354-01K01 CML13 |  | FPSO 2015 | Pipe Wall Thickness | 7608 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.4 | CML13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-10-03 | 2015-04-15 07:00 | 2.5 | 0.10684 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 12 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML12 | 40-WF-71354-01K01 CML12 |  | FPSO 2015 | Pipe Wall Thickness | 7607 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.4 | CML12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-10-03 | 2015-04-15 07:00 | 2.5 | 0.10684 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 3 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.4 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML7 | 40-WF-71354-01K01 CML7 |  | FPSO 2015 | Pipe Wall Thickness | 7602 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.4 | CML7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-10-03 | 2015-04-15 07:00 | 2.5 | 0.10684 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 3 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.4 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML6 | 40-WF-71354-01K01 CML6 |  | FPSO 2015 | Pipe Wall Thickness | 7601 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.4 | CML6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-10-03 | 2015-04-15 07:00 | 2.5 | 0.10684 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 12 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.5 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML53 | 100-WF-71326-01K01 CML53 |  | FPSO 2015 | Pipe Wall Thickness | 7585 |  | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 17:07 | [31 empty] | High alarm breach | 2.575 | CML53 | CML: type TBC | 0.5 | 2014-10-01 | 2014-10-01 | 2015-04-14 07:00 | 2.5 | 0.37447 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.8 | 2.4 | 2.3 | 2.8 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML37 | 100-WF-71326-01K01 CML37 |  | FPSO 2015 | Pipe Wall Thickness | 7569 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.4 | CML37 | CML: type TBC | 0.5 | 2014-10-01 | 2014-10-01 | 2015-04-14 07:00 | 2.5 | 0.37447 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML33 | 100-WF-71326-01K01 CML33 |  | FPSO 2015 | Pipe Wall Thickness | 7565 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.4 | CML33 | CML: type TBC | 0.5 | 2014-10-01 | 2014-10-01 | 2015-04-14 07:00 | 2.5 | 0.37447 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.5 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML31 | 100-WF-71326-01K01 CML31 |  | FPSO 2015 | Pipe Wall Thickness | 7563 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.425 | CML31 | CML: type TBC | 0.5 | 2014-10-01 | 2014-10-01 | 2015-04-14 07:00 | 2.5 | 0.37447 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.5 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML30 | 100-WF-71326-01K01 CML30 |  | FPSO 2015 | Pipe Wall Thickness | 7562 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.425 | CML30 | CML: type TBC | 0.5 | 2014-10-01 | 2014-10-01 | 2015-04-14 07:00 | 2.5 | 0.37447 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.8 | 2.3 | 2.3 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML25 | 100-WF-71326-01K01 CML25 |  | FPSO 2015 | Pipe Wall Thickness | 7557 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.375 | CML25 | CML: type TBC | 0.5 | 2014-10-01 | 2014-10-01 | 2015-04-14 07:00 | 2.5 | 0.37447 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML22 | 100-WF-71326-01K01 CML22 |  | FPSO 2015 | Pipe Wall Thickness | 7554 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.675 | CML22 | CML: type TBC | 0.5 | 2014-10-01 | 2014-10-01 | 2015-04-14 07:00 | 2.5 | 0.37447 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.9 | 3.1 | 2.3 | 2.4 | 0.38622
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML13 | 100-WF-71326-01K01 CML13 |  | FPSO 2015 | Pipe Wall Thickness | 7545 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.425 | CML13 | CML: type TBC | 0.5 | 2014-10-01 | 2014-10-01 | 2015-04-14 07:00 | 2.5 | 0.37447 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.4 | 2.3 | 2.4 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML7 | 100-WF-71326-01K01 CML7 |  | FPSO 2015 | Pipe Wall Thickness | 7539 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.5 | CML7 | CML: type TBC | 0.5 | 2014-10-01 | 2014-10-01 | 2015-04-14 07:00 | 2.5 | 0.37447 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.7 | 2.6 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML127 | 100-WF-71309-01K01 CML127 |  | FPSO 2015 | Pipe Wall Thickness | 7466 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.625 | CML127 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.3 | 3.1 | 2.5 | 0.34034
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML122 | 100-WF-71309-01K01 CML122 |  | FPSO 2015 | Pipe Wall Thickness | 7461 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML122 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML114 | 100-WF-71309-01K01 CML114 |  | FPSO 2015 | Pipe Wall Thickness | 7453 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.35 | CML114 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.3 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML113 | 100-WF-71309-01K01 CML113 |  | FPSO 2015 | Pipe Wall Thickness | 7452 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.35 | CML113 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.3 | 2.3 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML106 | 100-WF-71309-01K01 CML106 |  | FPSO 2015 | Pipe Wall Thickness | 7445 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML106 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML103 | 100-WF-71309-01K01 CML103 |  | FPSO 2015 | Pipe Wall Thickness | 7442 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML103 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML101 | 100-WF-71309-01K01 CML101 |  | FPSO 2015 | Pipe Wall Thickness | 7440 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML101 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.5 | 2.4 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML97 | 100-WF-71309-01K01 CML97 |  | FPSO 2015 | Pipe Wall Thickness | 7436 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML97 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.5 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML78 | 100-WF-71309-01K01 CML78 |  | FPSO 2015 | Pipe Wall Thickness | 7417 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.5 | CML78 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.5 | 2.7 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML74 | 100-WF-71309-01K01 CML74 |  | FPSO 2015 | Pipe Wall Thickness | 7413 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML74 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.4 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML73 | 100-WF-71309-01K01 CML73 |  | FPSO 2015 | Pipe Wall Thickness | 7412 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML73 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.3 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML72 | 100-WF-71309-01K01 CML72 |  | FPSO 2015 | Pipe Wall Thickness | 7411 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML72 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 2.3 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML67 | 100-WF-71309-01K01 CML67 |  | FPSO 2015 | Pipe Wall Thickness | 7406 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML67 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.5 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML49 | 100-WF-71309-01K01 CML49 |  | FPSO 2015 | Pipe Wall Thickness | 7388 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.35 | CML49 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML48 | 100-WF-71309-01K01 CML48 |  | FPSO 2015 | Pipe Wall Thickness | 7387 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML48 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML46 | 100-WF-71309-01K01 CML46 |  | FPSO 2015 | Pipe Wall Thickness | 7385 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML46 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML44 | 100-WF-71309-01K01 CML44 |  | FPSO 2015 | Pipe Wall Thickness | 7383 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML44 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML43 | 100-WF-71309-01K01 CML43 |  | FPSO 2015 | Pipe Wall Thickness | 7382 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML43 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 2.3 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML36 | 100-WF-71309-01K01 CML36 |  | FPSO 2015 | Pipe Wall Thickness | 7375 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML36 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.4 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML35 | 100-WF-71309-01K01 CML35 |  | FPSO 2015 | Pipe Wall Thickness | 7374 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML35 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 2.3 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML30 | 100-WF-71309-01K01 CML30 |  | FPSO 2015 | Pipe Wall Thickness | 7369 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML30 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML29 | 100-WF-71309-01K01 CML29 |  | FPSO 2015 | Pipe Wall Thickness | 7368 |  | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-24 09:03 | [31 empty] | High alarm breach | 2.575 | CML29 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 3 | 2.5 | 2.5 | 0.29861
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML21 | 100-WF-71309-01K01 CML21 |  | FPSO 2015 | Pipe Wall Thickness | 7360 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-24 09:49 | [31 empty] | High alarm breach | 2.45 | CML21 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.5 | 2.3 | 2.4 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML20 | 100-WF-71309-01K01 CML20 |  | FPSO 2015 | Pipe Wall Thickness | 7359 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-24 09:49 | [31 empty] | High alarm breach | 2.4 | CML20 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML16 | 100-WF-71309-01K01 CML16 |  | FPSO 2015 | Pipe Wall Thickness | 7355 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML16 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML13 | 100-WF-71309-01K01 CML13 |  | FPSO 2015 | Pipe Wall Thickness | 7352 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML13 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML12 | 100-WF-71309-01K01 CML12 |  | FPSO 2015 | Pipe Wall Thickness | 7351 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.375 | CML12 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML11 | 100-WF-71309-01K01 CML11 |  | FPSO 2015 | Pipe Wall Thickness | 7350 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.35 | CML11 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.3 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML9 | 100-WF-71309-01K01 CML9 |  | FPSO 2015 | Pipe Wall Thickness | 7348 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML9 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML8 | 100-WF-71309-01K01 CML8 |  | FPSO 2015 | Pipe Wall Thickness | 7347 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML8 | CML: type TBC | 0.5 | 2014-09-29 | 2014-09-29 | 2015-04-11 07:00 | 2.5 | 0.37613 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.6 | 2.4 | 2.3 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML94 | 80-WF-71311-01K01 CML94 |  | FPSO 2015 | Pipe Wall Thickness | 7339 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.425 | CML94 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-25 | 2015-04-09 07:00 | 2.5 | 0.10778 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.6 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML91 | 80-WF-71311-01K01 CML91 |  | FPSO 2015 | Pipe Wall Thickness | 7336 |  | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.375 | CML91 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-25 | 2015-04-09 07:00 | 2.5 | 0.10778 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.3 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML83 | 80-WF-71311-01K01 CML83 |  | FPSO 2015 | Pipe Wall Thickness | 7328 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.45 | CML83 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-25 | 2015-04-09 07:00 | 2.5 | 0.10778 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.5 | 2.6 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML76 | 80-WF-71311-01K01 CML76 |  | FPSO 2015 | Pipe Wall Thickness | 7321 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.45 | CML76 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-25 | 2015-04-09 07:00 | 2.5 | 0.10778 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.4 | 2.6 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML56 | 80-WF-71311-01K01 CML56 |  | FPSO 2015 | Pipe Wall Thickness | 7301 |  | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.45 | CML56 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-25 | 2015-04-09 07:00 | 2.5 | 0.10778 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.5 | 2.5 | 2.3 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML52 | 80-WF-71311-01K01 CML52 |  | FPSO 2015 | Pipe Wall Thickness | 7297 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML52 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-25 | 2015-04-09 07:00 | 2.5 | 0.10778 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.5 | 2.6 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML30 | 80-WF-71311-01K01 CML30 |  | FPSO 2015 | Pipe Wall Thickness | 7275 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-25 | 2015-04-09 07:00 | 2.5 | 0.10778 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.4 | 2.6 | 2.3 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML56 | 80-WF-71320-01K01 CML56 |  | FPSO 2015 | Pipe Wall Thickness | 7245 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-20 16:37 | [31 empty] | High alarm breach | 2.425 | CML56 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-24 | 2015-04-08 07:00 | 2.5 | 0.10794 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.5 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML49 | 80-WF-71320-01K01 CML49 |  | FPSO 2015 | Pipe Wall Thickness | 7238 |  | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:38 | [31 empty] | High alarm breach | 2.475 | CML49 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-24 | 2015-04-08 07:00 | 2.5 | 0.10794 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.6 | 2.4 | 2.3 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML28 | 80-WF-71320-01K01 CML28 |  | FPSO 2015 | Pipe Wall Thickness | 7217 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 11:57 | [31 empty] | High alarm breach | 2.4 | CML28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-24 | 2015-04-08 07:00 | 2.5 | 0.10794 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 12 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.5 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML24 | 80-WF-71320-01K01 CML24 |  | FPSO 2015 | Pipe Wall Thickness | 7213 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.5 | CML24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-24 | 2015-04-08 07:00 | 2.5 | 0.10794 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.8 | 2.4 | 2.3 | 0.21602
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML5 | 80-WF-71320-01K01 CML5 |  | FPSO 2015 | Pipe Wall Thickness | 7194 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.5 | CML5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-24 | 2015-04-08 07:00 | 2.5 | 0.10794 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.7 | 2.6 | 2.3 | 2.4 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML135 | 80-WF-71338-01K01 CML135 |  | FPSO 2015 | Pipe Wall Thickness | 7181 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.375 | CML135 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML133 | 80-WF-71338-01K01 CML133 |  | FPSO 2015 | Pipe Wall Thickness | 7179 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.35 | CML133 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML128 | 80-WF-71338-01K01 CML128 |  | FPSO 2015 | Pipe Wall Thickness | 7174 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML128 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.5 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML122 | 80-WF-71338-01K01 CML122 |  | FPSO 2015 | Pipe Wall Thickness | 7168 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.55 | CML122 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.7 | 2.7 | 2.3 | 2.5 | 0.19149
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML118 | 80-WF-71338-01K01 CML118 |  | FPSO 2015 | Pipe Wall Thickness | 7164 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.375 | CML118 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML114 | 80-WF-71338-01K01 CML114 |  | FPSO 2015 | Pipe Wall Thickness | 7160 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.525 | CML114 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 3 | 2.4 | 2.3 | 2.4 | 0.32016
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML97 | 80-WF-71338-01K01 CML97 |  | FPSO 2015 | Pipe Wall Thickness | 7143 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML97 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.5 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML89 | 80-WF-71338-01K01 CML89 |  | FPSO 2015 | Pipe Wall Thickness | 7135 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML89 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.5 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML88 | 80-WF-71338-01K01 CML88 |  | FPSO 2015 | Pipe Wall Thickness | 7134 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.45 | CML88 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.5 | 2.3 | 2.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML73 | 80-WF-71338-01K01 CML73 |  | FPSO 2015 | Pipe Wall Thickness | 7119 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.4 | CML73 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 2.3 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML62 | 80-WF-71338-01K01 CML62 |  | FPSO 2015 | Pipe Wall Thickness | 7108 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML62 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 2.3 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML44 | 80-WF-71338-01K01 CML44 |  | FPSO 2015 | Pipe Wall Thickness | 7090 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML44 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.7 | 2.3 | 2.3 | 2.6 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML54 | 80-WF-71338-01K01 CML54 |  | FPSO 2015 | Pipe Wall Thickness | 7100 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.55 | CML54 | CML: type TBC | 0.5 | 2013-06-01 | 2015-09-23 | 2015-04-07 07:00 | 2.5 | 0.1081 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.7 | 2.7 | 2.3 | 0.19149
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML124 | 100-WF-71308-01K01 CML124 |  | FPSO 2015 | Pipe Wall Thickness | 7042 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML124 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.7 | 2.3 | 2.5 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML122 | 100-WF-71308-01K01 CML122 |  | FPSO 2015 | Pipe Wall Thickness | 7040 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.375 | CML122 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML121 | 100-WF-71308-01K01 CML121 |  | FPSO 2015 | Pipe Wall Thickness | 7039 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.375 | CML121 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML118 | 100-WF-71308-01K01 CML118 |  | FPSO 2015 | Pipe Wall Thickness | 7036 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML118 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.6 | 2.3 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML115 | 100-WF-71308-01K01 CML115 |  | FPSO 2015 | Pipe Wall Thickness | 7033 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-26 14:08 | [31 empty] | High alarm breach | 2.55 | CML115 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.9 | 2.5 | 2.5 | 2.3 | 0.25166
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML105 | 100-WF-71308-01K01 CML105 |  | FPSO 2015 | Pipe Wall Thickness | 7023 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML105 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.6 | 2.4 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML104 | 100-WF-71308-01K01 CML104 |  | FPSO 2015 | Pipe Wall Thickness | 7022 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML104 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.4 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML103 | 100-WF-71308-01K01 CML103 |  | FPSO 2015 | Pipe Wall Thickness | 7021 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML103 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.5 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML99 | 100-WF-71308-01K01 CML99 |  | FPSO 2015 | Pipe Wall Thickness | 7017 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.35 | CML99 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.3 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML98 | 100-WF-71308-01K01 CML98 |  | FPSO 2015 | Pipe Wall Thickness | 7016 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML98 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML94 | 100-WF-71308-01K01 CML94 |  | FPSO 2015 | Pipe Wall Thickness | 7012 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML94 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.7 | 2.3 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML91 | 100-WF-71308-01K01 CML91 |  | FPSO 2015 | Pipe Wall Thickness | 7009 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML91 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.5 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML90 | 100-WF-71308-01K01 CML90 |  | FPSO 2015 | Pipe Wall Thickness | 7008 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.375 | CML90 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.3 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML86 | 100-WF-71308-01K01 CML86 |  | FPSO 2015 | Pipe Wall Thickness | 7004 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.375 | CML86 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.3 | 2.3 | 2.3 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML85 | 100-WF-71308-01K01 CML85 |  | FPSO 2015 | Pipe Wall Thickness | 7003 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.375 | CML85 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML82 | 100-WF-71308-01K01 CML82 |  | FPSO 2015 | Pipe Wall Thickness | 7000 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML82 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.5 | 2.5 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML75 | 100-WF-71308-01K01 CML75 |  | FPSO 2015 | Pipe Wall Thickness | 6993 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.35 | CML75 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML74 | 100-WF-71308-01K01 CML74 |  | FPSO 2015 | Pipe Wall Thickness | 6992 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML74 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 2.3 | 2.6 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML61 | 100-WF-71308-01K01 CML61 |  | FPSO 2015 | Pipe Wall Thickness | 6979 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.85 | CML61 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.7 | 2.3 | 2.8 | 3.6 | 0.54467
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML58 | 100-WF-71308-01K01 CML58 |  | FPSO 2015 | Pipe Wall Thickness | 6976 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.375 | CML58 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML57 | 100-WF-71308-01K01 CML57 |  | FPSO 2015 | Pipe Wall Thickness | 6975 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML57 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.4 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML55 | 100-WF-71308-01K01 CML55 |  | FPSO 2015 | Pipe Wall Thickness | 6973 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML55 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.4 | 2.4 | 2.3 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML52 | 100-WF-71308-01K01 CML52 |  | FPSO 2015 | Pipe Wall Thickness | 6970 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML52 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.5 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML50 | 100-WF-71308-01K01 CML50 |  | FPSO 2015 | Pipe Wall Thickness | 6968 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-27 15:58 | [31 empty] | High alarm breach | 2.5 | CML50 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.6 | 2.3 | 2.6 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML30 | 100-WF-71308-01K01 CML30 |  | FPSO 2015 | Pipe Wall Thickness | 6948 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML30 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.4 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML27 | 100-WF-71308-01K01 CML27 |  | FPSO 2015 | Pipe Wall Thickness | 6945 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML27 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.8 | 2.3 | 0.23805
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML12 | 100-WF-71308-01K01 CML12 |  | FPSO 2015 | Pipe Wall Thickness | 6930 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML12 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML11 | 100-WF-71308-01K01 CML11 |  | FPSO 2015 | Pipe Wall Thickness | 6929 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML11 | CML: type TBC | 0.5 | 2014-09-25 | 2014-09-25 | 2015-04-06 07:00 | 2.5 | 0.37892 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.5 | 2.6 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-42 | 100-WF-71328-01K01 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 6875 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.4 | CML-42 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-39 | 100-WF-71328-01K01 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 6872 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-12-01 08:50 | [31 empty] | High alarm breach | 2.325 | CML-39 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-38 | 100-WF-71328-01K01 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 6871 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.4 | CML-38 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-37 | 100-WF-71328-01K01 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 6870 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.4 | CML-37 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-36 | 100-WF-71328-01K01 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 6869 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.425 | CML-36 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.5 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-35 | 100-WF-71328-01K01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 6868 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.425 | CML-35 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.5 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-32 | 100-WF-71328-01K01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6865 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.375 | CML-32 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-31 | 100-WF-71328-01K01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6864 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.4 | CML-31 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-30 | 100-WF-71328-01K01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6863 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-12-01 08:50 | [31 empty] | High alarm breach | 2.35 | CML-30 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.3 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-29 | 100-WF-71328-01K01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6862 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.35 | CML-29 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.3 | 2.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-28 | 100-WF-71328-01K01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6861 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.375 | CML-28 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-26 | 100-WF-71328-01K01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6859 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-12-01 08:53 | [31 empty] | High alarm breach | 2.45 | CML-26 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.5 | 2.7 | 0.19149
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-25 | 100-WF-71328-01K01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6858 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.375 | CML-25 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-24 | 100-WF-71328-01K01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6857 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.4 | CML-24 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-23 | 100-WF-71328-01K01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6856 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.375 | CML-23 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.5 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-21 | 100-WF-71328-01K01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6854 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.45 | CML-21 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.5 | 2.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-20 | 100-WF-71328-01K01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6853 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.35 | CML-20 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-19 | 100-WF-71328-01K01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6852 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.425 | CML-19 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.5 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-16 | 100-WF-71328-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6849 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.375 | CML-16 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.5 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-13 | 100-WF-71328-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6846 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.4 | CML-13 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-10 | 100-WF-71328-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6843 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.4 | CML-10 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-9 | 100-WF-71328-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6842 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.475 | CML-9 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.8 | 2.3 | 2.4 | 2.4 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-8 | 100-WF-71328-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6841 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-12-01 08:52 | [31 empty] | High alarm breach | 2.325 | CML-8 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.3 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-6 | 100-WF-71328-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6839 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.55 | CML-6 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 3 | 2.3 | 0.31091
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-5 | 100-WF-71328-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6838 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.45 | CML-5 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-05 07:00 | 2.5 | 0.37948 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.3 | 2.5 | 2.4 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-140 | 150-WF-71345-01K01 CML-140 |  | FPSO 2015 | Pipe Wall Thickness | 6814 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-140 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.4 | 2.7 | 2.3 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-137 | 150-WF-71345-01K01 CML-137 |  | FPSO 2015 | Pipe Wall Thickness | 6811 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.45 | CML-137 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.5 | 2.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-131 | 150-WF-71345-01K01 CML-131 |  | FPSO 2015 | Pipe Wall Thickness | 6805 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.45 | CML-131 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.5 | 2.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-130 | 150-WF-71345-01K01 CML-130 |  | FPSO 2015 | Pipe Wall Thickness | 6804 |  | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 17:15 | [31 empty] | High alarm breach | 2.375 | CML-130 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-127 | 150-WF-71345-01K01 CML-127 |  | FPSO 2015 | Pipe Wall Thickness | 6801 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-127 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.3 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-123 | 150-WF-71345-01K01 CML-123 |  | FPSO 2015 | Pipe Wall Thickness | 6797 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-123 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-122 | 150-WF-71345-01K01 CML-122 |  | FPSO 2015 | Pipe Wall Thickness | 6796 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-122 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-120 | 150-WF-71345-01K01 CML-120 |  | FPSO 2015 | Pipe Wall Thickness | 6794 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-120 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.4 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-119 | 150-WF-71345-01K01 CML-119 |  | FPSO 2015 | Pipe Wall Thickness | 6793 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-119 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-87 | 150-WF-71345-01K01 CML-87 |  | FPSO 2015 | Pipe Wall Thickness | 6761 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.525 | CML-87 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.6 | 2.6 | 2.3 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-85 | 150-WF-71345-01K01 CML-85 |  | FPSO 2015 | Pipe Wall Thickness | 6759 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-85 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-91 | 150-WF-71345-01K01 CML-91 |  | FPSO 2015 | Pipe Wall Thickness | 6765 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-91 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.5 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-89 | 150-WF-71345-01K01 CML-89 |  | FPSO 2015 | Pipe Wall Thickness | 6763 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-89 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.3 | 2.3 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-88 | 150-WF-71345-01K01 CML-88 |  | FPSO 2015 | Pipe Wall Thickness | 6762 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.35 | CML-88 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-93 | 150-WF-71345-01K01 CML-93 |  | FPSO 2015 | Pipe Wall Thickness | 6767 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.825 | CML-93 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 3.1 | 3 | 2.3 | 2.9 | 0.3594
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-142 | 150-WF-71345-01K01 CML-142 |  | FPSO 2015 | Pipe Wall Thickness | 6816 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-142 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.4 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-141 | 150-WF-71345-01K01 CML-141 |  | FPSO 2015 | Pipe Wall Thickness | 6815 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-141 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.5 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-149 | 150-WF-71345-01K01 CML-149 |  | FPSO 2015 | Pipe Wall Thickness | 6823 |  | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 17:39 | [31 empty] | High alarm breach | 2.5 | CML-149 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.8 | 2.4 | 2.5 | 2.3 | 0.21602
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-158 | 150-WF-71345-01K01 CML-158 |  | FPSO 2015 | Pipe Wall Thickness | 6832 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.525 | CML-158 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.5 | 2.8 | 2.3 | 2.5 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-157 | 150-WF-71345-01K01 CML-157 |  | FPSO 2015 | Pipe Wall Thickness | 6831 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.35 | CML-157 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-156 | 150-WF-71345-01K01 CML-156 |  | FPSO 2015 | Pipe Wall Thickness | 6830 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-156 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.5 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-154 | 150-WF-71345-01K01 CML-154 |  | FPSO 2015 | Pipe Wall Thickness | 6828 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 17:41 | [31 empty] | High alarm breach | 2.375 | CML-154 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.5 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-97 | 150-WF-71345-01K01 CML-97 |  | FPSO 2015 | Pipe Wall Thickness | 6771 |  | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 15:00 | [31 empty] | High alarm breach | 2.35 | CML-97 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-96 | 150-WF-71345-01K01 CML-96 |  | FPSO 2015 | Pipe Wall Thickness | 6770 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-96 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-95 | 150-WF-71345-01K01 CML-95 |  | FPSO 2015 | Pipe Wall Thickness | 6769 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.325 | CML-95 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.3 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-81 | 150-WF-71345-01K01 CML-81 |  | FPSO 2015 | Pipe Wall Thickness | 6755 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-81 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.6 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-31 | 150-WF-71345-01K01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6705 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-31 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-30 | 150-WF-71345-01K01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6704 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.35 | CML-30 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-22 | 150-WF-71345-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6696 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.35 | CML-22 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-9 | 150-WF-71345-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6683 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.75 | CML-9 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.9 | 2.9 | 2.9 | 2.3 | 0.3
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-61 | 150-WF-71345-01K01 CML-61 |  | FPSO 2015 | Pipe Wall Thickness | 6735 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-61 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-59 | 150-WF-71345-01K01 CML-59 |  | FPSO 2015 | Pipe Wall Thickness | 6733 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-59 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-57 | 150-WF-71345-01K01 CML-57 |  | FPSO 2015 | Pipe Wall Thickness | 6731 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-57 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.3 | 2.4 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-54 | 150-WF-71345-01K01 CML-54 |  | FPSO 2015 | Pipe Wall Thickness | 6728 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-54 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.4 | 2.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-35 | 150-WF-71345-01K01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 6709 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-35 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.6 | 2.4 | 2.3 | 2.4 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-34 | 150-WF-71345-01K01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 6708 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-34 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-32 | 150-WF-71345-01K01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6706 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-32 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.3 | 2.8 | 0.23629
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-78 | 150-WF-71345-01K01 CML-78 |  | FPSO 2015 | Pipe Wall Thickness | 6752 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-78 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.5 | 2.4 | 2.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-74 | 150-WF-71345-01K01 CML-74 |  | FPSO 2015 | Pipe Wall Thickness | 6748 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-74 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-73 | 150-WF-71345-01K01 CML-73 |  | FPSO 2015 | Pipe Wall Thickness | 6747 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.375 | CML-73 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-72 | 150-WF-71345-01K01 CML-72 |  | FPSO 2015 | Pipe Wall Thickness | 6746 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.45 | CML-72 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.3 | 2.6 | 2.5 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-69 | 150-WF-71345-01K01 CML-69 |  | FPSO 2015 | Pipe Wall Thickness | 6743 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-69 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.5 | 2.3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-68 | 150-WF-71345-01K01 CML-68 |  | FPSO 2015 | Pipe Wall Thickness | 6742 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-68 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.4 | 2.3 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-67 | 150-WF-71345-01K01 CML-67 |  | FPSO 2015 | Pipe Wall Thickness | 6741 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.35 | CML-67 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.3 | 2.4 | 2.4 | 2.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-66 | 150-WF-71345-01K01 CML-66 |  | FPSO 2015 | Pipe Wall Thickness | 6740 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.4 | CML-66 | CML: type TBC | 0.5 | 2014-09-24 | 2014-09-24 | 2015-04-04 07:00 | 2.5 | 0.38004 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 2.4 | 2.5 | 2.3 | 2.4 | 0.08165
WD03 | Montara_Topside | No | Potable Water (53) | Pipework | 0200-WZ-53L9000-AS20-00 | CML-2 | 0200-WZ-53L9000-AS20-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5101 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | High alarm breach | 2.625 | CML-2 | CML: type TBC | 0 | 2014-04-04 | 2014-06-07 | 2015-03-06 07:00 | 2.5 | 0.21735 | A3: Inside Quadrant |  | 2.77 | 2.5 | 2.4619 | 2.3 | 6 O'Clock | 50 | 2.77 | 0200-WZ-53L9000-AS20-00 | 10S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.2 |  | 3.2 | 2.4 | 2.3 | 2.6 | 0.40311
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 35 | 0300-WF-71L9003-AK11-00 CML - 35 |  | FPSO 2015 | Pipe Wall Thickness | 22644 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.45 | CML - 35 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 6 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.6 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 32 | 0300-WF-71L9003-AK11-00 CML - 32 |  | FPSO 2015 | Pipe Wall Thickness | 22641 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.55 | CML - 32 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.6 | 2.7 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 28 | 0300-WF-71L9003-AK11-00 CML - 28 |  | FPSO 2015 | Pipe Wall Thickness | 22637 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 28 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 26 | 0300-WF-71L9003-AK11-00 CML - 26 |  | FPSO 2015 | Pipe Wall Thickness | 22635 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 26 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 23 | 0300-WF-71L9003-AK11-00 CML - 23 |  | FPSO 2015 | Pipe Wall Thickness | 22632 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 23 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 16 | 0300-WF-71L9003-AK11-00 CML - 16 |  | FPSO 2015 | Pipe Wall Thickness | 22625 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.6 | CML - 16 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.6 | 2.8 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 10 | 0300-WF-71L9003-AK11-00 CML - 10 |  | FPSO 2015 | Pipe Wall Thickness | 22619 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.575 | CML - 10 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.7 | 2.6 | 2.4 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 40 | 0300-WF-71L9002-AK11-00 CML - 40 |  | FPSO 2015 | Pipe Wall Thickness | 22609 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.425 | CML - 40 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 35 | 0300-WF-71L9002-AK11-00 CML - 35 |  | FPSO 2015 | Pipe Wall Thickness | 22604 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.525 | CML - 35 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.7 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 30 | 0300-WF-71L9002-AK11-00 CML - 30 |  | FPSO 2015 | Pipe Wall Thickness | 22599 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.475 | CML - 30 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.6 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 29 | 0300-WF-71L9002-AK11-00 CML - 29 |  | FPSO 2015 | Pipe Wall Thickness | 22598 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 29 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 28 | 0300-WF-71L9002-AK11-00 CML - 28 |  | FPSO 2015 | Pipe Wall Thickness | 22597 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.55 | CML - 28 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 6 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.7 | 2.4 | 2.7 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 25 | 0300-WF-71L9002-AK11-00 CML - 25 |  | FPSO 2015 | Pipe Wall Thickness | 22594 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.5 | CML - 25 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 20 | 0300-WF-71L9002-AK11-00 CML - 20 |  | FPSO 2015 | Pipe Wall Thickness | 22589 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.575 | CML - 20 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.5 | 2.8 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 18 | 0300-WF-71L9002-AK11-00 CML - 18 |  | FPSO 2015 | Pipe Wall Thickness | 22587 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 18 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 3 | 0300-WF-71L9002-AK11-00 CML - 3 |  | FPSO 2015 | Pipe Wall Thickness | 22572 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [35 empty] | High alarm breach | 2.4 | CML - 3 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9004-AK11-00 | CML-10 | 0300-WF-71L9004-AK11-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22563 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [35 empty] | High alarm breach | 2.475 | CML-10 | CML: Reducing Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 6 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9004-AK11-00 | CML-7 | 0300-WF-71L9004-AK11-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22560 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [35 empty] | High alarm breach | 2.8 | CML-7 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.4 | 3 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 3.2 | 2.4 | 2.7 | 2.9 | 0.33665
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-112 | 80-WF-71340-01K01 CML-112 |  | FPSO 2015 | Pipe Wall Thickness | 22483 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-112 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-110 | 80-WF-71340-01K01 CML-110 |  | FPSO 2015 | Pipe Wall Thickness | 22481 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-110 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-109 | 80-WF-71340-01K01 CML-109 |  | FPSO 2015 | Pipe Wall Thickness | 22480 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-109 | CML: Equal Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-108 | 80-WF-71340-01K01 CML-108 |  | FPSO 2015 | Pipe Wall Thickness | 22479 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-108 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-106 | 80-WF-71340-01K01 CML-106 |  | FPSO 2015 | Pipe Wall Thickness | 22477 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-106 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-105 | 80-WF-71340-01K01 CML-105 |  | FPSO 2015 | Pipe Wall Thickness | 22476 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-105 | CML: Equal Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-102 | 50-WF-71340-01K01 CML-102 |  | FPSO 2015 | Pipe Wall Thickness | 22473 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-102 | CML: Reducer | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.6 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-101 | 50-WF-71340-01K01 CML-101 |  | FPSO 2015 | Pipe Wall Thickness | 22472 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-101 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-100 | 50-WF-71340-01K01 CML-100 |  | FPSO 2015 | Pipe Wall Thickness | 22471 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-100 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-99 | 50-WF-71340-01K01 CML-99 |  | FPSO 2015 | Pipe Wall Thickness | 22470 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.425 | CML-99 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-98 | 50-WF-71340-01K01 CML-98 |  | FPSO 2015 | Pipe Wall Thickness | 22469 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.675 | CML-98 | CML: Reducer | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.8 | 2.9 | 2.6 | 2.4 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-97 | 50-WF-71340-01K01 CML-97 |  | FPSO 2015 | Pipe Wall Thickness | 22468 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-97 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-95 | 50-WF-71340-01K01 CML-95 |  | FPSO 2015 | Pipe Wall Thickness | 22466 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-95 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-93 | 50-WF-71340-01K01 CML-93 |  | FPSO 2015 | Pipe Wall Thickness | 22464 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-93 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-92 | 80-WF-71340-01K01 CML-92 |  | FPSO 2015 | Pipe Wall Thickness | 22463 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-92 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-90 | 80-WF-71340-01K01 CML-90 |  | FPSO 2015 | Pipe Wall Thickness | 22461 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.575 | CML-90 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.8 | 2.4 | 2.5 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-86 | 80-WF-71340-01K01 CML-86 |  | FPSO 2015 | Pipe Wall Thickness | 22457 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-86 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-82 | 80-WF-71340-01K01 CML-82 |  | FPSO 2015 | Pipe Wall Thickness | 22453 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.425 | CML-82 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-78 | 80-WF-71340-01K01 CML-78 |  | FPSO 2015 | Pipe Wall Thickness | 22449 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-78 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-76 | 80-WF-71340-01K01 CML-76 |  | FPSO 2015 | Pipe Wall Thickness | 22447 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-76 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-68 | 80-WF-71340-01K01 CML-68 |  | FPSO 2015 | Pipe Wall Thickness | 22439 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-68 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-67 | 80-WF-71340-01K01 CML-67 |  | FPSO 2015 | Pipe Wall Thickness | 22438 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-67 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-65 | 80-WF-71340-01K01 CML-65 |  | FPSO 2015 | Pipe Wall Thickness | 22436 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-65 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-64 | 80-WF-71340-01K01 CML-64 |  | FPSO 2015 | Pipe Wall Thickness | 22435 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.425 | CML-64 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-62 | 80-WF-71340-01K01 CML-62 |  | FPSO 2015 | Pipe Wall Thickness | 22433 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.425 | CML-62 | CML: Equal Tee | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-60 | 50-WF-71340-01K01 CML-60 |  | FPSO 2015 | Pipe Wall Thickness | 22431 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.575 | CML-60 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.9 | 2.5 | 2.5 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-56 | 50-WF-71340-01K01 CML-56 |  | FPSO 2015 | Pipe Wall Thickness | 22427 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.55 | CML-56 | CML: Elbow | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.8 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-54 | 50-WF-71340-01K01 CML-54 |  | FPSO 2015 | Pipe Wall Thickness | 22425 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-54 | CML: Pipe Length | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.6 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-53 | 50-WF-71340-01K01 CML-53 |  | FPSO 2015 | Pipe Wall Thickness | 22424 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-53 | CML: Pipe Length | 0.5 | 2013-06-01 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.05311 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-48 | 100-WF-71340-01K01 CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 22419 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-48 | CML: Reducing Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-46 | 100-WF-71340-01K01 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 22417 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-46 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.5 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-45 | 100-WF-71340-01K01 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 22416 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-45 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-44 | 100-WF-71340-01K01 CML-44 |  | FPSO 2015 | Pipe Wall Thickness | 22415 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-44 | CML: Equal Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-43 | 100-WF-71340-01K01 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 22414 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-43 | CML: Reducing Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-41 | 100-WF-71340-01K01 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 22412 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-41 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-39 | 100-WF-71340-01K01 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 22410 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-39 | CML: Equal Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-38 | 100-WF-71340-01K01 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 22409 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-38 | CML: Reducing Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-36 | 100-WF-71340-01K01 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 22407 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.525 | CML-36 | CML: Reducing Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.6 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-33 | 100-WF-71340-01K01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 22404 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-33 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-32 | 100-WF-71340-01K01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 22403 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-32 | CML: Reducing Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-30 | 100-WF-71340-01K01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 22401 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.525 | CML-30 | CML: Reducing Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.5 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-29 | 100-WF-71340-01K01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 22400 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.575 | CML-29 | CML: Reducing Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.8 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-28 | 100-WF-71340-01K01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 22399 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.5 | CML-28 | CML: Reducing Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.5 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-27 | 100-WF-71340-01K01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 22398 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-27 | CML: Reducing Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-23 | 100-WF-71340-01K01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 22394 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.425 | CML-23 | CML: Equal Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-20 | 100-WF-71340-01K01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 22391 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-20 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.6 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-15 | 100-WF-71340-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 22386 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-15 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-14 | 100-WF-71340-01K01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 22385 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-14 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-13 | 100-WF-71340-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22384 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.45 | CML-13 | CML: Equal Tee | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-11 | 100-WF-71340-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22382 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-11 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-10 | 100-WF-71340-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22381 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.475 | CML-10 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-7 | 100-WF-71340-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22378 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.75 | CML-7 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.7 | 3 | 2.4 | 2.9 | 0.26458
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-4 | 100-WF-71340-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22375 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [35 empty] | High alarm breach | 2.6 | CML-4 | CML: Elbow | 0.5 | 2014-12-25 | 2014-12-25 | 2015-04-19 07:00 | 2.5 | 0.31864 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 3 | 2.5 | 2.4 | 2.5 | 0.2708
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML14 | 40-WF-71354-01K01 CML14 |  | FPSO 2015 | Pipe Wall Thickness | 7609 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.425 | CML14 | CML: type TBC | 0.5 | 2013-06-01 | 2018-02-03 | 2015-04-15 07:00 | 2.5 | 0.05342 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML11 | 40-WF-71354-01K01 CML11 |  | FPSO 2015 | Pipe Wall Thickness | 7606 |  | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.575 | CML11 | CML: type TBC | 0.5 | 2013-06-01 | 2018-02-03 | 2015-04-15 07:00 | 2.5 | 0.05342 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.7 | 2.5 | 2.4 | 2.7 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML10 | 40-WF-71354-01K01 CML10 |  | FPSO 2015 | Pipe Wall Thickness | 7605 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.525 | CML10 | CML: type TBC | 0.5 | 2013-06-01 | 2018-02-03 | 2015-04-15 07:00 | 2.5 | 0.05342 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.8 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML9 | 40-WF-71354-01K01 CML9 |  | FPSO 2015 | Pipe Wall Thickness | 7604 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.475 | CML9 | CML: type TBC | 0.5 | 2013-06-01 | 2018-02-03 | 2015-04-15 07:00 | 2.5 | 0.05342 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML1 | 40-WF-71354-01K01 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 7596 |  | 2015-04-15 07:00 | 2015-04-15 15:00 | [35 empty] | High alarm breach | 2.475 | CML1 | CML: type TBC | 0.5 | 2013-06-01 | 2018-02-03 | 2015-04-15 07:00 | 2.5 | 0.05342 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML62 | 100-WF-71326-01K01 CML62 |  | FPSO 2015 | Pipe Wall Thickness | 7594 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.4 | CML62 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML61 | 100-WF-71326-01K01 CML61 |  | FPSO 2015 | Pipe Wall Thickness | 7593 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 17:31 | [31 empty] | High alarm breach | 2.45 | CML61 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML60 | 100-WF-71326-01K01 CML60 |  | FPSO 2015 | Pipe Wall Thickness | 7592 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 17:10 | [31 empty] | High alarm breach | 2.4 | CML60 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML50 | 100-WF-71326-01K01 CML50 |  | FPSO 2015 | Pipe Wall Thickness | 7582 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 16:26 | [31 empty] | High alarm breach | 2.475 | CML50 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML36 | 100-WF-71326-01K01 CML36 |  | FPSO 2015 | Pipe Wall Thickness | 7568 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.45 | CML36 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML35 | 100-WF-71326-01K01 CML35 |  | FPSO 2015 | Pipe Wall Thickness | 7567 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.525 | CML35 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.6 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML34 | 100-WF-71326-01K01 CML34 |  | FPSO 2015 | Pipe Wall Thickness | 7566 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.475 | CML34 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML29 | 100-WF-71326-01K01 CML29 |  | FPSO 2015 | Pipe Wall Thickness | 7561 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.45 | CML29 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML28 | 100-WF-71326-01K01 CML28 |  | FPSO 2015 | Pipe Wall Thickness | 7560 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.45 | CML28 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML27 | 100-WF-71326-01K01 CML27 |  | FPSO 2015 | Pipe Wall Thickness | 7559 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.475 | CML27 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML19 | 100-WF-71326-01K01 CML19 |  | FPSO 2015 | Pipe Wall Thickness | 7551 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.575 | CML19 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.6 | 2.7 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML18 | 100-WF-71326-01K01 CML18 |  | FPSO 2015 | Pipe Wall Thickness | 7550 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.425 | CML18 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML12 | 100-WF-71326-01K01 CML12 |  | FPSO 2015 | Pipe Wall Thickness | 7544 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [35 empty] | High alarm breach | 2.45 | CML12 | CML: type TBC | 0.5 | 2014-12-21 | 2014-12-21 | 2015-04-14 07:00 | 2.5 | 0.32098 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML124 | 100-WF-71309-01K01 CML124 |  | FPSO 2015 | Pipe Wall Thickness | 7463 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML124 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML123 | 100-WF-71309-01K01 CML123 |  | FPSO 2015 | Pipe Wall Thickness | 7462 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML123 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML120 | 100-WF-71309-01K01 CML120 |  | FPSO 2015 | Pipe Wall Thickness | 7459 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML120 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML119 | 100-WF-71309-01K01 CML119 |  | FPSO 2015 | Pipe Wall Thickness | 7458 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML119 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML117 | 100-WF-71309-01K01 CML117 |  | FPSO 2015 | Pipe Wall Thickness | 7456 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML117 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML116 | 100-WF-71309-01K01 CML116 |  | FPSO 2015 | Pipe Wall Thickness | 7455 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML116 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.6 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML112 | 100-WF-71309-01K01 CML112 |  | FPSO 2015 | Pipe Wall Thickness | 7451 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML112 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML111 | 100-WF-71309-01K01 CML111 |  | FPSO 2015 | Pipe Wall Thickness | 7450 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML111 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML110 | 100-WF-71309-01K01 CML110 |  | FPSO 2015 | Pipe Wall Thickness | 7449 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML110 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML109 | 100-WF-71309-01K01 CML109 |  | FPSO 2015 | Pipe Wall Thickness | 7448 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML109 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML108 | 100-WF-71309-01K01 CML108 |  | FPSO 2015 | Pipe Wall Thickness | 7447 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML108 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML107 | 100-WF-71309-01K01 CML107 |  | FPSO 2015 | Pipe Wall Thickness | 7446 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML107 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML105 | 100-WF-71309-01K01 CML105 |  | FPSO 2015 | Pipe Wall Thickness | 7444 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML105 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML104 | 100-WF-71309-01K01 CML104 |  | FPSO 2015 | Pipe Wall Thickness | 7443 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML104 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML102 | 100-WF-71309-01K01 CML102 |  | FPSO 2015 | Pipe Wall Thickness | 7441 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML102 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML100 | 100-WF-71309-01K01 CML100 |  | FPSO 2015 | Pipe Wall Thickness | 7439 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML100 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML98 | 100-WF-71309-01K01 CML98 |  | FPSO 2015 | Pipe Wall Thickness | 7437 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML98 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML96 | 100-WF-71309-01K01 CML96 |  | FPSO 2015 | Pipe Wall Thickness | 7435 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML96 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML91 | 100-WF-71309-01K01 CML91 |  | FPSO 2015 | Pipe Wall Thickness | 7430 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.5 | CML91 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.5 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML86 | 100-WF-71309-01K01 CML86 |  | FPSO 2015 | Pipe Wall Thickness | 7425 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.5 | CML86 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML85 | 100-WF-71309-01K01 CML85 |  | FPSO 2015 | Pipe Wall Thickness | 7424 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML85 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML84 | 100-WF-71309-01K01 CML84 |  | FPSO 2015 | Pipe Wall Thickness | 7423 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML84 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML83 | 100-WF-71309-01K01 CML83 |  | FPSO 2015 | Pipe Wall Thickness | 7422 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML83 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML82 | 100-WF-71309-01K01 CML82 |  | FPSO 2015 | Pipe Wall Thickness | 7421 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML82 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML81 | 100-WF-71309-01K01 CML81 |  | FPSO 2015 | Pipe Wall Thickness | 7420 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML81 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML80 | 100-WF-71309-01K01 CML80 |  | FPSO 2015 | Pipe Wall Thickness | 7419 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML80 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML79 | 100-WF-71309-01K01 CML79 |  | FPSO 2015 | Pipe Wall Thickness | 7418 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.5 | CML79 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.5 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML77 | 100-WF-71309-01K01 CML77 |  | FPSO 2015 | Pipe Wall Thickness | 7416 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML77 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML76 | 100-WF-71309-01K01 CML76 |  | FPSO 2015 | Pipe Wall Thickness | 7415 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML76 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML75 | 100-WF-71309-01K01 CML75 |  | FPSO 2015 | Pipe Wall Thickness | 7414 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML75 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML70 | 100-WF-71309-01K01 CML70 |  | FPSO 2015 | Pipe Wall Thickness | 7409 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML70 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML69 | 100-WF-71309-01K01 CML69 |  | FPSO 2015 | Pipe Wall Thickness | 7408 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.525 | CML69 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.7 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML68 | 100-WF-71309-01K01 CML68 |  | FPSO 2015 | Pipe Wall Thickness | 7407 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML68 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML66 | 100-WF-71309-01K01 CML66 |  | FPSO 2015 | Pipe Wall Thickness | 7405 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML66 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML65 | 100-WF-71309-01K01 CML65 |  | FPSO 2015 | Pipe Wall Thickness | 7404 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML65 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML64 | 100-WF-71309-01K01 CML64 |  | FPSO 2015 | Pipe Wall Thickness | 7403 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-26 16:20 | [31 empty] | High alarm breach | 2.45 | CML64 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML63 | 100-WF-71309-01K01 CML63 |  | FPSO 2015 | Pipe Wall Thickness | 7402 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-26 16:20 | [31 empty] | High alarm breach | 2.45 | CML63 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML56 | 100-WF-71309-01K01 CML56 |  | FPSO 2015 | Pipe Wall Thickness | 7395 |  | 2015-04-11 07:00 | 2015-04-11 15:00 |  |  | Nestor | 2014-11-20 15:17 | [31 empty] | High alarm breach | 2.45 | CML56 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML55 | 100-WF-71309-01K01 CML55 |  | FPSO 2015 | Pipe Wall Thickness | 7394 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 3 | CML55 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.7 | 3.2 | 3.7 | 0.57155
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML50 | 100-WF-71309-01K01 CML50 |  | FPSO 2015 | Pipe Wall Thickness | 7389 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML50 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML47 | 100-WF-71309-01K01 CML47 |  | FPSO 2015 | Pipe Wall Thickness | 7386 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML47 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML45 | 100-WF-71309-01K01 CML45 |  | FPSO 2015 | Pipe Wall Thickness | 7384 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.5 | CML45 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.6 | 2.4 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML42 | 100-WF-71309-01K01 CML42 |  | FPSO 2015 | Pipe Wall Thickness | 7381 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML42 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML41 | 100-WF-71309-01K01 CML41 |  | FPSO 2015 | Pipe Wall Thickness | 7380 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML41 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML40 | 100-WF-71309-01K01 CML40 |  | FPSO 2015 | Pipe Wall Thickness | 7379 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML40 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML39 | 100-WF-71309-01K01 CML39 |  | FPSO 2015 | Pipe Wall Thickness | 7378 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML39 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML37 | 100-WF-71309-01K01 CML37 |  | FPSO 2015 | Pipe Wall Thickness | 7376 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML37 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML34 | 100-WF-71309-01K01 CML34 |  | FPSO 2015 | Pipe Wall Thickness | 7373 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML34 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML33 | 100-WF-71309-01K01 CML33 |  | FPSO 2015 | Pipe Wall Thickness | 7372 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML33 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML32 | 100-WF-71309-01K01 CML32 |  | FPSO 2015 | Pipe Wall Thickness | 7371 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML32 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML31 | 100-WF-71309-01K01 CML31 |  | FPSO 2015 | Pipe Wall Thickness | 7370 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML31 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML26 | 100-WF-71309-01K01 CML26 |  | FPSO 2015 | Pipe Wall Thickness | 7365 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.5 | CML26 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.5 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML25 | 100-WF-71309-01K01 CML25 |  | FPSO 2015 | Pipe Wall Thickness | 7364 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML25 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML23 | 100-WF-71309-01K01 CML23 |  | FPSO 2015 | Pipe Wall Thickness | 7362 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML23 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML22 | 100-WF-71309-01K01 CML22 |  | FPSO 2015 | Pipe Wall Thickness | 7361 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.475 | CML22 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.6 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML18 | 100-WF-71309-01K01 CML18 |  | FPSO 2015 | Pipe Wall Thickness | 7357 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML18 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML17 | 100-WF-71309-01K01 CML17 |  | FPSO 2015 | Pipe Wall Thickness | 7356 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.4 | CML17 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML15 | 100-WF-71309-01K01 CML15 |  | FPSO 2015 | Pipe Wall Thickness | 7354 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.45 | CML15 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML14 | 100-WF-71309-01K01 CML14 |  | FPSO 2015 | Pipe Wall Thickness | 7353 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML14 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML10 | 100-WF-71309-01K01 CML10 |  | FPSO 2015 | Pipe Wall Thickness | 7349 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.425 | CML10 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML2 | 100-WF-71309-01K01 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 7341 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [35 empty] | High alarm breach | 2.725 | CML2 | CML: type TBC | 0.5 | 2014-12-19 | 2014-12-19 | 2015-04-11 07:00 | 2.5 | 0.32239 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.9 | 2.7 | 2.9 | 2.4 | 0.23629
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML92 | 80-WF-71311-01K01 CML92 |  | FPSO 2015 | Pipe Wall Thickness | 7337 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML92 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.5 | 2.5 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML85 | 80-WF-71311-01K01 CML85 |  | FPSO 2015 | Pipe Wall Thickness | 7330 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.45 | CML85 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.4 | 2.4 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML84 | 80-WF-71311-01K01 CML84 |  | FPSO 2015 | Pipe Wall Thickness | 7329 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML84 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.6 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML82 | 80-WF-71311-01K01 CML82 |  | FPSO 2015 | Pipe Wall Thickness | 7327 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.575 | CML82 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.7 | 2.4 | 2.6 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML81 | 80-WF-71311-01K01 CML81 |  | FPSO 2015 | Pipe Wall Thickness | 7326 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML81 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML80 | 80-WF-71311-01K01 CML80 |  | FPSO 2015 | Pipe Wall Thickness | 7325 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML80 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.7 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML78 | 80-WF-71311-01K01 CML78 |  | FPSO 2015 | Pipe Wall Thickness | 7323 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.45 | CML78 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML77 | 80-WF-71311-01K01 CML77 |  | FPSO 2015 | Pipe Wall Thickness | 7322 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.525 | CML77 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.5 | 2.4 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML75 | 80-WF-71311-01K01 CML75 |  | FPSO 2015 | Pipe Wall Thickness | 7320 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML75 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML74 | 80-WF-71311-01K01 CML74 |  | FPSO 2015 | Pipe Wall Thickness | 7319 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML74 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML73 | 80-WF-71311-01K01 CML73 |  | FPSO 2015 | Pipe Wall Thickness | 7318 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML73 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML72 | 80-WF-71311-01K01 CML72 |  | FPSO 2015 | Pipe Wall Thickness | 7317 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.45 | CML72 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML71 | 80-WF-71311-01K01 CML71 |  | FPSO 2015 | Pipe Wall Thickness | 7316 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML71 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.4 | 2.6 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML70 | 80-WF-71311-01K01 CML70 |  | FPSO 2015 | Pipe Wall Thickness | 7315 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML70 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.5 | 2.5 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML69 | 80-WF-71311-01K01 CML69 |  | FPSO 2015 | Pipe Wall Thickness | 7314 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML69 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.6 | 2.6 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML68 | 80-WF-71311-01K01 CML68 |  | FPSO 2015 | Pipe Wall Thickness | 7313 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.425 | CML68 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML66 | 80-WF-71311-01K01 CML66 |  | FPSO 2015 | Pipe Wall Thickness | 7311 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 14:26 | [31 empty] | High alarm breach | 2.475 | CML66 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML65 | 80-WF-71311-01K01 CML65 |  | FPSO 2015 | Pipe Wall Thickness | 7310 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 14:25 | [31 empty] | High alarm breach | 2.475 | CML65 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML64 | 80-WF-71311-01K01 CML64 |  | FPSO 2015 | Pipe Wall Thickness | 7309 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 14:25 | [31 empty] | High alarm breach | 2.55 | CML64 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.8 | 2.4 | 2.5 | 2.5 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML55 | 80-WF-71311-01K01 CML55 |  | FPSO 2015 | Pipe Wall Thickness | 7300 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML55 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML54 | 80-WF-71311-01K01 CML54 |  | FPSO 2015 | Pipe Wall Thickness | 7299 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML54 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML53 | 80-WF-71311-01K01 CML53 |  | FPSO 2015 | Pipe Wall Thickness | 7298 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-24 10:29 | [31 empty] | High alarm breach | 2.475 | CML53 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML50 | 80-WF-71311-01K01 CML50 |  | FPSO 2015 | Pipe Wall Thickness | 7295 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML50 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML49 | 80-WF-71311-01K01 CML49 |  | FPSO 2015 | Pipe Wall Thickness | 7294 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.4 | CML49 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML45 | 80-WF-71311-01K01 CML45 |  | FPSO 2015 | Pipe Wall Thickness | 7290 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML45 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML44 | 80-WF-71311-01K01 CML44 |  | FPSO 2015 | Pipe Wall Thickness | 7289 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-24 10:28 | [31 empty] | High alarm breach | 2.45 | CML44 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML43 | 80-WF-71311-01K01 CML43 |  | FPSO 2015 | Pipe Wall Thickness | 7288 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-24 10:28 | [31 empty] | High alarm breach | 2.45 | CML43 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML42 | 80-WF-71311-01K01 CML42 |  | FPSO 2015 | Pipe Wall Thickness | 7287 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-24 10:28 | [31 empty] | High alarm breach | 2.45 | CML42 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML40 | 80-WF-71311-01K01 CML40 |  | FPSO 2015 | Pipe Wall Thickness | 7285 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML40 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML38 | 80-WF-71311-01K01 CML38 |  | FPSO 2015 | Pipe Wall Thickness | 7283 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-24 10:18 | [31 empty] | High alarm breach | 2.525 | CML38 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.6 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML37 | 80-WF-71311-01K01 CML37 |  | FPSO 2015 | Pipe Wall Thickness | 7282 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.45 | CML37 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML35 | 80-WF-71311-01K01 CML35 |  | FPSO 2015 | Pipe Wall Thickness | 7280 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.425 | CML35 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML34 | 80-WF-71311-01K01 CML34 |  | FPSO 2015 | Pipe Wall Thickness | 7279 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML34 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML33 | 80-WF-71311-01K01 CML33 |  | FPSO 2015 | Pipe Wall Thickness | 7278 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML33 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML31 | 80-WF-71311-01K01 CML31 |  | FPSO 2015 | Pipe Wall Thickness | 7276 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.6 | CML31 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.7 | 2.4 | 2.5 | 2.8 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML29 | 80-WF-71311-01K01 CML29 |  | FPSO 2015 | Pipe Wall Thickness | 7274 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML29 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML28 | 80-WF-71311-01K01 CML28 |  | FPSO 2015 | Pipe Wall Thickness | 7273 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML28 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.5 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML27 | 80-WF-71311-01K01 CML27 |  | FPSO 2015 | Pipe Wall Thickness | 7272 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.45 | CML27 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML24 | 80-WF-71311-01K01 CML24 |  | FPSO 2015 | Pipe Wall Thickness | 7269 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.475 | CML24 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML15 | 80-WF-71311-01K01 CML15 |  | FPSO 2015 | Pipe Wall Thickness | 7260 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 16:43 | [31 empty] | High alarm breach | 2.625 | CML15 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.8 | 2.6 | 2.4 | 2.7 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML22 | 80-WF-71311-01K01 CML22 |  | FPSO 2015 | Pipe Wall Thickness | 7267 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML22 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.6 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML21 | 80-WF-71311-01K01 CML21 |  | FPSO 2015 | Pipe Wall Thickness | 7266 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.5 | CML21 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML20 | 80-WF-71311-01K01 CML20 |  | FPSO 2015 | Pipe Wall Thickness | 7265 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [35 empty] | High alarm breach | 2.45 | CML20 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-19 | 2015-04-09 07:00 | 2.5 | 0.05389 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML34 | 80-WF-71320-01K01 CML34 |  | FPSO 2015 | Pipe Wall Thickness | 7223 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-20 11:27 | [31 empty] | High alarm breach | 2.475 | CML34 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML33 | 80-WF-71320-01K01 CML33 |  | FPSO 2015 | Pipe Wall Thickness | 7222 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-20 11:26 | [31 empty] | High alarm breach | 2.45 | CML33 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML32 | 80-WF-71320-01K01 CML32 |  | FPSO 2015 | Pipe Wall Thickness | 7221 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-20 11:26 | [31 empty] | High alarm breach | 2.5 | CML32 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.7 | 2.4 | 2.4 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML30 | 80-WF-71320-01K01 CML30 |  | FPSO 2015 | Pipe Wall Thickness | 7219 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-20 11:12 | [31 empty] | High alarm breach | 2.5 | CML30 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML36 | 80-WF-71320-01K01 CML36 |  | FPSO 2015 | Pipe Wall Thickness | 7225 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 17:42 | [31 empty] | High alarm breach | 2.45 | CML36 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML55 | 80-WF-71320-01K01 CML55 |  | FPSO 2015 | Pipe Wall Thickness | 7244 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-20 16:37 | [31 empty] | High alarm breach | 2.5 | CML55 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.6 | 2.4 | 2.4 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML54 | 80-WF-71320-01K01 CML54 |  | FPSO 2015 | Pipe Wall Thickness | 7243 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:39 | [31 empty] | High alarm breach | 2.4 | CML54 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML52 | 80-WF-71320-01K01 CML52 |  | FPSO 2015 | Pipe Wall Thickness | 7241 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:38 | [31 empty] | High alarm breach | 2.475 | CML52 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.4 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML51 | 80-WF-71320-01K01 CML51 |  | FPSO 2015 | Pipe Wall Thickness | 7240 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:38 | [31 empty] | High alarm breach | 2.45 | CML51 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML48 | 80-WF-71320-01K01 CML48 |  | FPSO 2015 | Pipe Wall Thickness | 7237 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:37 | [31 empty] | High alarm breach | 2.45 | CML48 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML47 | 80-WF-71320-01K01 CML47 |  | FPSO 2015 | Pipe Wall Thickness | 7236 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:37 | [31 empty] | High alarm breach | 2.475 | CML47 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML44 | 80-WF-71320-01K01 CML44 |  | FPSO 2015 | Pipe Wall Thickness | 7233 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:37 | [31 empty] | High alarm breach | 2.5 | CML44 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.7 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML43 | 80-WF-71320-01K01 CML43 |  | FPSO 2015 | Pipe Wall Thickness | 7232 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.5 | CML43 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.5 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML41 | 80-WF-71320-01K01 CML41 |  | FPSO 2015 | Pipe Wall Thickness | 7230 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.45 | CML41 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.6 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML40 | 80-WF-71320-01K01 CML40 |  | FPSO 2015 | Pipe Wall Thickness | 7229 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.425 | CML40 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML39 | 80-WF-71320-01K01 CML39 |  | FPSO 2015 | Pipe Wall Thickness | 7228 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-19 17:20 | [31 empty] | High alarm breach | 2.475 | CML39 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.4 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML38 | 80-WF-71320-01K01 CML38 |  | FPSO 2015 | Pipe Wall Thickness | 7227 |  | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-19 17:20 | [31 empty] | High alarm breach | 2.6 | CML38 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.7 | 2.6 | 2.7 | 2.4 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML37 | 80-WF-71320-01K01 CML37 |  | FPSO 2015 | Pipe Wall Thickness | 7226 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-19 17:18 | [31 empty] | High alarm breach | 2.45 | CML37 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML29 | 80-WF-71320-01K01 CML29 |  | FPSO 2015 | Pipe Wall Thickness | 7218 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-20 11:11 | [31 empty] | High alarm breach | 2.5 | CML29 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML27 | 80-WF-71320-01K01 CML27 |  | FPSO 2015 | Pipe Wall Thickness | 7216 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-26 15:03 | [31 empty] | High alarm breach | 2.45 | CML27 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML26 | 80-WF-71320-01K01 CML26 |  | FPSO 2015 | Pipe Wall Thickness | 7215 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-26 15:03 | [31 empty] | High alarm breach | 2.45 | CML26 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML25 | 80-WF-71320-01K01 CML25 |  | FPSO 2015 | Pipe Wall Thickness | 7214 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 11:56 | [31 empty] | High alarm breach | 2.45 | CML25 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML21 | 80-WF-71320-01K01 CML21 |  | FPSO 2015 | Pipe Wall Thickness | 7210 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.45 | CML21 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML20 | 80-WF-71320-01K01 CML20 |  | FPSO 2015 | Pipe Wall Thickness | 7209 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 11:40 | [31 empty] | High alarm breach | 2.45 | CML20 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML16 | 80-WF-71320-01K01 CML16 |  | FPSO 2015 | Pipe Wall Thickness | 7205 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.575 | CML16 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.6 | 2.7 | 2.4 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML15 | 80-WF-71320-01K01 CML15 |  | FPSO 2015 | Pipe Wall Thickness | 7204 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.55 | CML15 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.8 | 2.4 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML13 | 80-WF-71320-01K01 CML13 |  | FPSO 2015 | Pipe Wall Thickness | 7202 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 11:11 | [31 empty] | High alarm breach | 2.45 | CML13 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML11 | 80-WF-71320-01K01 CML11 |  | FPSO 2015 | Pipe Wall Thickness | 7200 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.55 | CML11 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.8 | 2.4 | 2.4 | 0.19149
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML10 | 80-WF-71320-01K01 CML10 |  | FPSO 2015 | Pipe Wall Thickness | 7199 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.45 | CML10 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML9 | 80-WF-71320-01K01 CML9 |  | FPSO 2015 | Pipe Wall Thickness | 7198 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.475 | CML9 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML7 | 80-WF-71320-01K01 CML7 |  | FPSO 2015 | Pipe Wall Thickness | 7196 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.5 | CML7 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.5 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML6 | 80-WF-71320-01K01 CML6 |  | FPSO 2015 | Pipe Wall Thickness | 7195 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.45 | CML6 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML3 | 80-WF-71320-01K01 CML3 |  | FPSO 2015 | Pipe Wall Thickness | 7192 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [35 empty] | High alarm breach | 2.5 | CML3 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-16 | 2015-04-08 07:00 | 2.5 | 0.05397 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.6 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML143 | 80-WF-71338-01K01 CML143 |  | FPSO 2015 | Pipe Wall Thickness | 7189 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML143 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML141 | 80-WF-71338-01K01 CML141 |  | FPSO 2015 | Pipe Wall Thickness | 7187 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML141 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML140 | 80-WF-71338-01K01 CML140 |  | FPSO 2015 | Pipe Wall Thickness | 7186 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML140 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML130 | 80-WF-71338-01K01 CML130 |  | FPSO 2015 | Pipe Wall Thickness | 7176 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.45 | CML130 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML129 | 80-WF-71338-01K01 CML129 |  | FPSO 2015 | Pipe Wall Thickness | 7175 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.625 | CML129 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 3 | 2.6 | 2.5 | 2.4 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML125 | 80-WF-71338-01K01 CML125 |  | FPSO 2015 | Pipe Wall Thickness | 7171 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML125 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML121 | 80-WF-71338-01K01 CML121 |  | FPSO 2015 | Pipe Wall Thickness | 7167 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.55 | CML121 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.8 | 2.4 | 2.6 | 0.19149
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML120 | 80-WF-71338-01K01 CML120 |  | FPSO 2015 | Pipe Wall Thickness | 7166 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.5 | CML120 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML119 | 80-WF-71338-01K01 CML119 |  | FPSO 2015 | Pipe Wall Thickness | 7165 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.75 | CML119 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 3.6 | 2.5 | 2.4 | 2.5 | 0.56862
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML116 | 80-WF-71338-01K01 CML116 |  | FPSO 2015 | Pipe Wall Thickness | 7162 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.525 | CML116 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.6 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML115 | 80-WF-71338-01K01 CML115 |  | FPSO 2015 | Pipe Wall Thickness | 7161 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.575 | CML115 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.7 | 2.5 | 2.7 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML112 | 80-WF-71338-01K01 CML112 |  | FPSO 2015 | Pipe Wall Thickness | 7158 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.45 | CML112 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML111 | 80-WF-71338-01K01 CML111 |  | FPSO 2015 | Pipe Wall Thickness | 7157 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.5 | CML111 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML110 | 80-WF-71338-01K01 CML110 |  | FPSO 2015 | Pipe Wall Thickness | 7156 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.5 | CML110 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.4 | 2.6 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML108 | 80-WF-71338-01K01 CML108 |  | FPSO 2015 | Pipe Wall Thickness | 7154 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML108 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML107 | 80-WF-71338-01K01 CML107 |  | FPSO 2015 | Pipe Wall Thickness | 7153 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 15:56 | [31 empty] | High alarm breach | 2.6 | CML107 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.7 | 2.7 | 2.4 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML106 | 80-WF-71338-01K01 CML106 |  | FPSO 2015 | Pipe Wall Thickness | 7152 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 15:57 | [31 empty] | High alarm breach | 2.45 | CML106 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML104 | 80-WF-71338-01K01 CML104 |  | FPSO 2015 | Pipe Wall Thickness | 7150 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 15:40 | [31 empty] | High alarm breach | 2.475 | CML104 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML103 | 80-WF-71338-01K01 CML103 |  | FPSO 2015 | Pipe Wall Thickness | 7149 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 15:39 | [31 empty] | High alarm breach | 2.45 | CML103 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML94 | 80-WF-71338-01K01 CML94 |  | FPSO 2015 | Pipe Wall Thickness | 7140 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.6 | CML94 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 3.1 | 2.5 | 2.4 | 2.4 | 0.33665
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML93 | 80-WF-71338-01K01 CML93 |  | FPSO 2015 | Pipe Wall Thickness | 7139 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.425 | CML93 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML92 | 80-WF-71338-01K01 CML92 |  | FPSO 2015 | Pipe Wall Thickness | 7138 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML92 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML91 | 80-WF-71338-01K01 CML91 |  | FPSO 2015 | Pipe Wall Thickness | 7137 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.5 | CML91 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.6 | 2.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML90 | 80-WF-71338-01K01 CML90 |  | FPSO 2015 | Pipe Wall Thickness | 7136 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML90 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML81 | 80-WF-71338-01K01 CML81 |  | FPSO 2015 | Pipe Wall Thickness | 7127 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 16:18 | [31 empty] | High alarm breach | 2.475 | CML81 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML75 | 80-WF-71338-01K01 CML75 |  | FPSO 2015 | Pipe Wall Thickness | 7121 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.45 | CML75 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML74 | 80-WF-71338-01K01 CML74 |  | FPSO 2015 | Pipe Wall Thickness | 7120 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.525 | CML74 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.7 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML72 | 80-WF-71338-01K01 CML72 |  | FPSO 2015 | Pipe Wall Thickness | 7118 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML72 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML71 | 80-WF-71338-01K01 CML71 |  | FPSO 2015 | Pipe Wall Thickness | 7117 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.5 | CML71 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML70 | 80-WF-71338-01K01 CML70 |  | FPSO 2015 | Pipe Wall Thickness | 7116 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML70 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML65 | 80-WF-71338-01K01 CML65 |  | FPSO 2015 | Pipe Wall Thickness | 7111 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.625 | CML65 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 3.1 | 2.5 | 2.4 | 0.32016
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML61 | 80-WF-71338-01K01 CML61 |  | FPSO 2015 | Pipe Wall Thickness | 7107 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.45 | CML61 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.6 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML60 | 80-WF-71338-01K01 CML60 |  | FPSO 2015 | Pipe Wall Thickness | 7106 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.45 | CML60 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML57 | 80-WF-71338-01K01 CML57 |  | FPSO 2015 | Pipe Wall Thickness | 7103 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML57 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML43 | 80-WF-71338-01K01 CML43 |  | FPSO 2015 | Pipe Wall Thickness | 7089 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.55 | CML43 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.6 | 2.6 | 2.4 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML40 | 80-WF-71338-01K01 CML40 |  | FPSO 2015 | Pipe Wall Thickness | 7086 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.525 | CML40 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.6 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML24 | 80-WF-71338-01K01 CML24 |  | FPSO 2015 | Pipe Wall Thickness | 7070 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML24 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML21 | 80-WF-71338-01K01 CML21 |  | FPSO 2015 | Pipe Wall Thickness | 7067 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML21 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML14 | 80-WF-71338-01K01 CML14 |  | FPSO 2015 | Pipe Wall Thickness | 7060 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.5 | CML14 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML53 | 80-WF-71338-01K01 CML53 |  | FPSO 2015 | Pipe Wall Thickness | 7099 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.475 | CML53 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML13 | 80-WF-71338-01K01 CML13 |  | FPSO 2015 | Pipe Wall Thickness | 7059 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.45 | CML13 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML12 | 80-WF-71338-01K01 CML12 |  | FPSO 2015 | Pipe Wall Thickness | 7058 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.575 | CML12 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.9 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML4 | 80-WF-71338-01K01 CML4 |  | FPSO 2015 | Pipe Wall Thickness | 7050 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [35 empty] | High alarm breach | 2.525 | CML4 | CML: type TBC | 0.5 | 2013-06-01 | 2018-01-14 | 2015-04-07 07:00 | 2.5 | 0.05405 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.4 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.6 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML127 | 100-WF-71308-01K01 CML127 |  | FPSO 2015 | Pipe Wall Thickness | 7045 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML127 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.7 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML123 | 100-WF-71308-01K01 CML123 |  | FPSO 2015 | Pipe Wall Thickness | 7041 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML123 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.6 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML120 | 100-WF-71308-01K01 CML120 |  | FPSO 2015 | Pipe Wall Thickness | 7038 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML120 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML119 | 100-WF-71308-01K01 CML119 |  | FPSO 2015 | Pipe Wall Thickness | 7037 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML119 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML117 | 100-WF-71308-01K01 CML117 |  | FPSO 2015 | Pipe Wall Thickness | 7035 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-26 14:08 | [31 empty] | High alarm breach | 2.4 | CML117 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML116 | 100-WF-71308-01K01 CML116 |  | FPSO 2015 | Pipe Wall Thickness | 7034 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML116 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.6 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML113 | 100-WF-71308-01K01 CML113 |  | FPSO 2015 | Pipe Wall Thickness | 7031 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML113 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML107 | 100-WF-71308-01K01 CML107 |  | FPSO 2015 | Pipe Wall Thickness | 7025 |  | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-24 08:45 | [31 empty] | High alarm breach | 2.475 | CML107 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML106 | 100-WF-71308-01K01 CML106 |  | FPSO 2015 | Pipe Wall Thickness | 7024 |  | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-24 08:45 | [31 empty] | High alarm breach | 2.475 | CML106 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML102 | 100-WF-71308-01K01 CML102 |  | FPSO 2015 | Pipe Wall Thickness | 7020 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML102 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML101 | 100-WF-71308-01K01 CML101 |  | FPSO 2015 | Pipe Wall Thickness | 7019 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML101 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML100 | 100-WF-71308-01K01 CML100 |  | FPSO 2015 | Pipe Wall Thickness | 7018 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML100 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.8 | 2.4 | 2.4 | 0.2
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML97 | 100-WF-71308-01K01 CML97 |  | FPSO 2015 | Pipe Wall Thickness | 7015 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML97 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML96 | 100-WF-71308-01K01 CML96 |  | FPSO 2015 | Pipe Wall Thickness | 7014 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML96 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.8 | 2.4 | 2.4 | 2.4 | 0.2
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML95 | 100-WF-71308-01K01 CML95 |  | FPSO 2015 | Pipe Wall Thickness | 7013 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.525 | CML95 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.8 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML93 | 100-WF-71308-01K01 CML93 |  | FPSO 2015 | Pipe Wall Thickness | 7011 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.55 | CML93 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.8 | 2.5 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML89 | 100-WF-71308-01K01 CML89 |  | FPSO 2015 | Pipe Wall Thickness | 7007 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML89 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML88 | 100-WF-71308-01K01 CML88 |  | FPSO 2015 | Pipe Wall Thickness | 7006 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML88 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.5 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML84 | 100-WF-71308-01K01 CML84 |  | FPSO 2015 | Pipe Wall Thickness | 7002 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML84 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML81 | 100-WF-71308-01K01 CML81 |  | FPSO 2015 | Pipe Wall Thickness | 6999 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML81 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML80 | 100-WF-71308-01K01 CML80 |  | FPSO 2015 | Pipe Wall Thickness | 6998 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML80 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML79 | 100-WF-71308-01K01 CML79 |  | FPSO 2015 | Pipe Wall Thickness | 6997 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML79 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.6 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML76 | 100-WF-71308-01K01 CML76 |  | FPSO 2015 | Pipe Wall Thickness | 6994 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML76 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML72 | 100-WF-71308-01K01 CML72 |  | FPSO 2015 | Pipe Wall Thickness | 6990 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.525 | CML72 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.6 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML71 | 100-WF-71308-01K01 CML71 |  | FPSO 2015 | Pipe Wall Thickness | 6989 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML71 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.7 | 2.4 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML69 | 100-WF-71308-01K01 CML69 |  | FPSO 2015 | Pipe Wall Thickness | 6987 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML69 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.5 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML68 | 100-WF-71308-01K01 CML68 |  | FPSO 2015 | Pipe Wall Thickness | 6986 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML68 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.6 | 2.6 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML65 | 100-WF-71308-01K01 CML65 |  | FPSO 2015 | Pipe Wall Thickness | 6983 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML65 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML64 | 100-WF-71308-01K01 CML64 |  | FPSO 2015 | Pipe Wall Thickness | 6982 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML64 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML56 | 100-WF-71308-01K01 CML56 |  | FPSO 2015 | Pipe Wall Thickness | 6974 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML56 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML51 | 100-WF-71308-01K01 CML51 |  | FPSO 2015 | Pipe Wall Thickness | 6969 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML51 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.5 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML49 | 100-WF-71308-01K01 CML49 |  | FPSO 2015 | Pipe Wall Thickness | 6967 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML49 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML48 | 100-WF-71308-01K01 CML48 |  | FPSO 2015 | Pipe Wall Thickness | 6966 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML48 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML47 | 100-WF-71308-01K01 CML47 |  | FPSO 2015 | Pipe Wall Thickness | 6965 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML47 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML46 | 100-WF-71308-01K01 CML46 |  | FPSO 2015 | Pipe Wall Thickness | 6964 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML46 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML45 | 100-WF-71308-01K01 CML45 |  | FPSO 2015 | Pipe Wall Thickness | 6963 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.525 | CML45 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.4 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML42 | 100-WF-71308-01K01 CML42 |  | FPSO 2015 | Pipe Wall Thickness | 6960 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML42 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.5 | 2.4 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML40 | 100-WF-71308-01K01 CML40 |  | FPSO 2015 | Pipe Wall Thickness | 6958 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML40 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML39 | 100-WF-71308-01K01 CML39 |  | FPSO 2015 | Pipe Wall Thickness | 6957 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML39 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML38 | 100-WF-71308-01K01 CML38 |  | FPSO 2015 | Pipe Wall Thickness | 6956 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.525 | CML38 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.9 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML37 | 100-WF-71308-01K01 CML37 |  | FPSO 2015 | Pipe Wall Thickness | 6955 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.625 | CML37 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.8 | 2.4 | 2.9 | 2.4 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML36 | 100-WF-71308-01K01 CML36 |  | FPSO 2015 | Pipe Wall Thickness | 6954 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.5 | CML36 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.5 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML35 | 100-WF-71308-01K01 CML35 |  | FPSO 2015 | Pipe Wall Thickness | 6953 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML35 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML34 | 100-WF-71308-01K01 CML34 |  | FPSO 2015 | Pipe Wall Thickness | 6952 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML34 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML32 | 100-WF-71308-01K01 CML32 |  | FPSO 2015 | Pipe Wall Thickness | 6950 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML32 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML31 | 100-WF-71308-01K01 CML31 |  | FPSO 2015 | Pipe Wall Thickness | 6949 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML31 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML29 | 100-WF-71308-01K01 CML29 |  | FPSO 2015 | Pipe Wall Thickness | 6947 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML29 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.5 | 2.4 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML28 | 100-WF-71308-01K01 CML28 |  | FPSO 2015 | Pipe Wall Thickness | 6946 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML28 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML26 | 100-WF-71308-01K01 CML26 |  | FPSO 2015 | Pipe Wall Thickness | 6944 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML26 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML25 | 100-WF-71308-01K01 CML25 |  | FPSO 2015 | Pipe Wall Thickness | 6943 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML25 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML24 | 100-WF-71308-01K01 CML24 |  | FPSO 2015 | Pipe Wall Thickness | 6942 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.425 | CML24 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML23 | 100-WF-71308-01K01 CML23 |  | FPSO 2015 | Pipe Wall Thickness | 6941 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML23 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML22 | 100-WF-71308-01K01 CML22 |  | FPSO 2015 | Pipe Wall Thickness | 6940 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML22 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML21 | 100-WF-71308-01K01 CML21 |  | FPSO 2015 | Pipe Wall Thickness | 6939 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.4 | CML21 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.4 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML16 | 100-WF-71308-01K01 CML16 |  | FPSO 2015 | Pipe Wall Thickness | 6934 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML16 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML15 | 100-WF-71308-01K01 CML15 |  | FPSO 2015 | Pipe Wall Thickness | 6933 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML15 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML14 | 100-WF-71308-01K01 CML14 |  | FPSO 2015 | Pipe Wall Thickness | 6932 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.575 | CML14 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.6 | 2.8 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML13 | 100-WF-71308-01K01 CML13 |  | FPSO 2015 | Pipe Wall Thickness | 6931 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.45 | CML13 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML10 | 100-WF-71308-01K01 CML10 |  | FPSO 2015 | Pipe Wall Thickness | 6928 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.475 | CML10 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML2 | 100-WF-71308-01K01 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 6920 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [35 empty] | High alarm breach | 2.65 | CML2 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-06 07:00 | 2.5 | 0.32479 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.7 | 2.9 | 2.6 | 2.4 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-43 | 100-WF-71328-01K01 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 6876 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.475 | CML-43 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.5 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-40 | 100-WF-71328-01K01 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 6873 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-12-01 08:53 | [31 empty] | High alarm breach | 2.425 | CML-40 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-33 | 100-WF-71328-01K01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 6866 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.45 | CML-33 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-27 | 100-WF-71328-01K01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6860 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.425 | CML-27 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-18 | 100-WF-71328-01K01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6851 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.425 | CML-18 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-17 | 100-WF-71328-01K01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6850 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-12-01 08:52 | [31 empty] | High alarm breach | 2.425 | CML-17 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-15 | 100-WF-71328-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6848 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-12-01 08:52 | [31 empty] | High alarm breach | 2.45 | CML-15 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-14 | 100-WF-71328-01K01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6847 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.5 | CML-14 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.7 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-12 | 100-WF-71328-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6845 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.575 | CML-12 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.6 | 2.7 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-11 | 100-WF-71328-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6844 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.475 | CML-11 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.6 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-7 | 100-WF-71328-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6840 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.55 | CML-7 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.6 | 2.7 | 2.4 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-1 | 100-WF-71328-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6834 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | High alarm breach | 2.925 | CML-1 | CML: type TBC | 0.5 | 2014-12-14 | 2014-12-14 | 2015-04-05 07:00 | 2.5 | 0.32527 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 3.3 | 2.4 | 2.7 | 3.3 | 0.45
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-151 | 150-WF-71345-01K01 CML-151 |  | FPSO 2015 | Pipe Wall Thickness | 6825 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-151 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-139 | 150-WF-71345-01K01 CML-139 |  | FPSO 2015 | Pipe Wall Thickness | 6813 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.5 | CML-139 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-138 | 150-WF-71345-01K01 CML-138 |  | FPSO 2015 | Pipe Wall Thickness | 6812 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-138 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-135 | 150-WF-71345-01K01 CML-135 |  | FPSO 2015 | Pipe Wall Thickness | 6809 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-135 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.7 | 2.4 | 2.4 | 2.4 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-134 | 150-WF-71345-01K01 CML-134 |  | FPSO 2015 | Pipe Wall Thickness | 6808 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.45 | CML-134 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-133 | 150-WF-71345-01K01 CML-133 |  | FPSO 2015 | Pipe Wall Thickness | 6807 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-133 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-125 | 150-WF-71345-01K01 CML-125 |  | FPSO 2015 | Pipe Wall Thickness | 6799 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.45 | CML-125 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-121 | 150-WF-71345-01K01 CML-121 |  | FPSO 2015 | Pipe Wall Thickness | 6795 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-121 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-118 | 150-WF-71345-01K01 CML-118 |  | FPSO 2015 | Pipe Wall Thickness | 6792 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-118 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-116 | 150-WF-71345-01K01 CML-116 |  | FPSO 2015 | Pipe Wall Thickness | 6790 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-116 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-86 | 150-WF-71345-01K01 CML-86 |  | FPSO 2015 | Pipe Wall Thickness | 6760 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 15:00 | [31 empty] | High alarm breach | 2.425 | CML-86 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-92 | 150-WF-71345-01K01 CML-92 |  | FPSO 2015 | Pipe Wall Thickness | 6766 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-92 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-145 | 150-WF-71345-01K01 CML-145 |  | FPSO 2015 | Pipe Wall Thickness | 6819 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 17:38 | [31 empty] | High alarm breach | 2.45 | CML-145 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-144 | 150-WF-71345-01K01 CML-144 |  | FPSO 2015 | Pipe Wall Thickness | 6818 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-144 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-150 | 150-WF-71345-01K01 CML-150 |  | FPSO 2015 | Pipe Wall Thickness | 6824 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.525 | CML-150 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.7 | 2.5 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-155 | 150-WF-71345-01K01 CML-155 |  | FPSO 2015 | Pipe Wall Thickness | 6829 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.575 | CML-155 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.9 | 2.4 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-152 | 150-WF-71345-01K01 CML-152 |  | FPSO 2015 | Pipe Wall Thickness | 6826 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-152 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-112 | 150-WF-71345-01K01 CML-112 |  | FPSO 2015 | Pipe Wall Thickness | 6786 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-112 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-109 | 150-WF-71345-01K01 CML-109 |  | FPSO 2015 | Pipe Wall Thickness | 6783 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-109 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-106 | 150-WF-71345-01K01 CML-106 |  | FPSO 2015 | Pipe Wall Thickness | 6780 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-106 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-98 | 150-WF-71345-01K01 CML-98 |  | FPSO 2015 | Pipe Wall Thickness | 6772 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-98 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-82 | 150-WF-71345-01K01 CML-82 |  | FPSO 2015 | Pipe Wall Thickness | 6756 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.575 | CML-82 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.7 | 2.7 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-80 | 150-WF-71345-01K01 CML-80 |  | FPSO 2015 | Pipe Wall Thickness | 6754 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-80 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-24 | 150-WF-71345-01K01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6698 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 3.05 | CML-24 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 3.8 | 3 | 3 | 2.4 | 0.57446
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-23 | 150-WF-71345-01K01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6697 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.55 | CML-23 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.6 | 2.6 | 2.6 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-21 | 150-WF-71345-01K01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6695 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 14:49 | [31 empty] | High alarm breach | 2.45 | CML-21 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.5 | 2.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-18 | 150-WF-71345-01K01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6692 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.6 | CML-18 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.8 | 2.8 | 0.23094
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-17 | 150-WF-71345-01K01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6691 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.6 | CML-17 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.8 | 2.5 | 2.4 | 2.7 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-16 | 150-WF-71345-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6690 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.775 | CML-16 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.8 | 3 | 2.9 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-15 | 150-WF-71345-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6689 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-15 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-10 | 150-WF-71345-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6684 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.925 | CML-10 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.7 | 3.9 | 2.7 | 0.66521
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-8 | 150-WF-71345-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6682 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.65 | CML-8 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.8 | 2.8 | 2.6 | 0.19149
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-2 | 150-WF-71345-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6676 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 3.025 | CML-2 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 3 | 2.4 | 3 | 3.7 | 0.53151
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-63 | 150-WF-71345-01K01 CML-63 |  | FPSO 2015 | Pipe Wall Thickness | 6737 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-63 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-62 | 150-WF-71345-01K01 CML-62 |  | FPSO 2015 | Pipe Wall Thickness | 6736 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-62 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.5 | 2.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-60 | 150-WF-71345-01K01 CML-60 |  | FPSO 2015 | Pipe Wall Thickness | 6734 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.5 | CML-60 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.8 | 2.4 | 2.4 | 2.4 | 0.2
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-58 | 150-WF-71345-01K01 CML-58 |  | FPSO 2015 | Pipe Wall Thickness | 6732 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.55 | CML-58 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.7 | 2.6 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-53 | 150-WF-71345-01K01 CML-53 |  | FPSO 2015 | Pipe Wall Thickness | 6727 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.55 | CML-53 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.8 | 2.4 | 0.19149
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-51 | 150-WF-71345-01K01 CML-51 |  | FPSO 2015 | Pipe Wall Thickness | 6725 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-51 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-49 | 150-WF-71345-01K01 CML-49 |  | FPSO 2015 | Pipe Wall Thickness | 6723 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.525 | CML-49 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.5 | 2.6 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-48 | 150-WF-71345-01K01 CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 6722 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-48 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.4 | 2.6 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-47 | 150-WF-71345-01K01 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 6721 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.45 | CML-47 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.4 | 2.4 | 2.4 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-45 | 150-WF-71345-01K01 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 6719 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.575 | CML-45 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.5 | 2.4 | 2.8 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-41 | 150-WF-71345-01K01 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 6715 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-41 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.5 | 2.4 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-40 | 150-WF-71345-01K01 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 6714 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-40 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.6 | 2.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-79 | 150-WF-71345-01K01 CML-79 |  | FPSO 2015 | Pipe Wall Thickness | 6753 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.475 | CML-79 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.5 | 2.4 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-76 | 150-WF-71345-01K01 CML-76 |  | FPSO 2015 | Pipe Wall Thickness | 6750 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.575 | CML-76 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.6 | 2.6 | 2.7 | 2.4 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-75 | 150-WF-71345-01K01 CML-75 |  | FPSO 2015 | Pipe Wall Thickness | 6749 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 | [35 empty] | High alarm breach | 2.425 | CML-75 | CML: type TBC | 0.5 | 2014-12-13 | 2014-12-13 | 2015-04-04 07:00 | 2.5 | 0.32575 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.4 | 2.4 | 0.05
WD03 | Montara_Topside | No | Potable Water (53) | Pipework | 0200-WZ-53L9000-AS20-00 | CML-3 | 0200-WZ-53L9000-AS20-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5102 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | High alarm breach | 2.6 | CML-3 | CML: type TBC | 0 | 2014-08-04 | 2014-10-25 | 2015-03-06 07:00 | 2.5 | 0.1711 | A1: Outside Quadrant |  | 2.77 | 2.5 | 2.4619 | 2.4 | 12 O'Clock | 50 | 2.77 | 0200-WZ-53L9000-AS20-00 | 10S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 2.4 | 2.5 | 2.8 | 2.7 | 0.18257
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-3 | 50-GN-67002-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 9062 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | All readings consistant through out 300mm section of pipe. Wrong Schedule??? | [34 empty] | High alarm breach | 2.8 | CML-3 | CML: type TBC | 3 | 2015-02-09 | 2015-04-16 | 2015-03-01 09:30 | 2.5 | 1.7953 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 2.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.1 |  | 3 | 3 | 2.8 | 2.4 | 0.28284
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43150-01C02 | CML-3 | 80-FH-43150-01C02 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24397 | Lagging removed -Location requires rope access ,not requested at this time | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-3 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2016-06-08 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.1519 |  | 9 O'Clock | 80 | 5.49 | 80-FH-43150-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 36 | 0300-WF-71L9003-AK11-00 CML - 36 |  | FPSO 2015 | Pipe Wall Thickness | 22645 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.6 | CML - 36 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.5 | 6 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.6 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 33 | 0300-WF-71L9003-AK11-00 CML - 33 |  | FPSO 2015 | Pipe Wall Thickness | 22642 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.575 | CML - 33 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.5 | 6 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.5 | 2.7 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 12 | 0300-WF-71L9003-AK11-00 CML - 12 |  | FPSO 2015 | Pipe Wall Thickness | 22621 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.9 | CML - 12 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.5 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.8 | 2.5 | 3.1 | 3.2 | 0.31623
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 8 | 0300-WF-71L9003-AK11-00 CML - 8 |  | FPSO 2015 | Pipe Wall Thickness | 22617 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.6 | CML - 8 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.5 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.5 | 2.6 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 38 | 0300-WF-71L9002-AK11-00 CML - 38 |  | FPSO 2015 | Pipe Wall Thickness | 22607 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.625 | CML - 38 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.5 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.5 | 2.7 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 32 | 0300-WF-71L9002-AK11-00 CML - 32 |  | FPSO 2015 | Pipe Wall Thickness | 22601 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.7 | CML - 32 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.5 | 12 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.7 | 2.7 | 2.9 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 24 | 0300-WF-71L9002-AK11-00 CML - 24 |  | FPSO 2015 | Pipe Wall Thickness | 22593 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.575 | CML - 24 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.5 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.8 | 2.5 | 2.5 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 22 | 0300-WF-71L9002-AK11-00 CML - 22 |  | FPSO 2015 | Pipe Wall Thickness | 22591 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.575 | CML - 22 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 2.5 | 3 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-WF-71L9000-AK11-00 | CML-1 | 0600-WF-71L9000-AK11-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22546 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [35 empty] | Low alarm breach | 3.55 | CML-1 | CML: Elbow | 0.5 | 2015-04-23 | 2015-07-04 | 2015-04-23 07:00 | 2.7 | 0.34874 | A1: Outside Quadrant |  | 3 | 2.7 | 2.6313 | 2.7 | 12 O'Clock | 150 | 3.5 | 0600-WF-71L9000-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 3.6 | 4.4 | 3.5 | 0.69522
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43150-01C02 | CML-2 | 80-FH-43150-01C02 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24396 | Lagging removed -Location requires rope access ,not requested at this time | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2016-06-08 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.1519 |  | 9 O'Clock | 80 | 5.49 | 80-FH-43150-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-107 | 80-WF-71340-01K01 CML-107 |  | FPSO 2015 | Pipe Wall Thickness | 22478 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.725 | CML-107 | CML: Reducer | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.8 | 2.5 | 3 | 2.6 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-96 | 50-WF-71340-01K01 CML-96 |  | FPSO 2015 | Pipe Wall Thickness | 22467 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.5 | CML-96 | CML: Elbow | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-87 | 80-WF-71340-01K01 CML-87 |  | FPSO 2015 | Pipe Wall Thickness | 22458 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.625 | CML-87 | CML: Elbow | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.9 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-85 | 80-WF-71340-01K01 CML-85 |  | FPSO 2015 | Pipe Wall Thickness | 22456 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.5 | CML-85 | CML: Elbow | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-75 | 80-WF-71340-01K01 CML-75 |  | FPSO 2015 | Pipe Wall Thickness | 22446 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.725 | CML-75 | CML: Elbow | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.8 | 2.8 | 2.8 | 2.5 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-73 | 80-WF-71340-01K01 CML-73 |  | FPSO 2015 | Pipe Wall Thickness | 22444 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.5 | CML-73 | CML: Pipe Length | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-70 | 80-WF-71340-01K01 CML-70 |  | FPSO 2015 | Pipe Wall Thickness | 22441 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.875 | CML-70 | CML: Reducer | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 3 | 2.5 | 3.2 | 2.8 | 0.29861
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-69 | 80-WF-71340-01K01 CML-69 |  | FPSO 2015 | Pipe Wall Thickness | 22440 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.525 | CML-69 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-58 | 50-WF-71340-01K01 CML-58 |  | FPSO 2015 | Pipe Wall Thickness | 22429 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.5 | CML-58 | CML: Elbow | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-55 | 50-WF-71340-01K01 CML-55 |  | FPSO 2015 | Pipe Wall Thickness | 22426 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.525 | CML-55 | CML: Pipe Length | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-52 | 50-WF-71340-01K01 CML-52 |  | FPSO 2015 | Pipe Wall Thickness | 22423 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.5 | CML-52 | CML: Pipe Length | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-51 | 50-WF-71340-01K01 CML-51 |  | FPSO 2015 | Pipe Wall Thickness | 22422 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.5 | CML-51 | CML: Pipe Length | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-47 | 100-WF-71340-01K01 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 22418 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.75 | CML-47 | CML: Reducer | 0.5 | 2015-04-19 | 2015-04-19 | 2015-04-19 07:00 | 2.5 | 0.26553 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.9 | 2.8 | 2.8 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-34 | 100-WF-71340-01K01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 22405 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.5 | CML-34 | CML: Elbow | 0.5 | 2015-04-19 | 2015-04-19 | 2015-04-19 07:00 | 2.5 | 0.26554 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-26 | 100-WF-71340-01K01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 22397 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.525 | CML-26 | CML: Reducing Tee | 0.5 | 2015-04-19 | 2015-04-19 | 2015-04-19 07:00 | 2.5 | 0.26554 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-17 | 100-WF-71340-01K01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 22388 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.55 | CML-17 | CML: Reducing Tee | 0.5 | 2015-04-19 | 2015-04-19 | 2015-04-19 07:00 | 2.5 | 0.26554 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-6 | 100-WF-71340-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22377 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 3.175 | CML-6 | CML: Elbow | 0.5 | 2015-04-19 | 2015-04-19 | 2015-04-19 07:00 | 2.5 | 0.26554 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 3 | 3.4 | 3.8 | 0.55603
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML19 | 150-WF-71371-01K01 CML19 |  | FPSO 2015 | Pipe Wall Thickness | 7780 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3.075 | CML19 | CML: type TBC | 0.5 | 2015-04-18 | 2015-04-18 | 2015-04-18 07:00 | 2.5 | 0.26592 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 3.4 | 3.1 | 2.5 | 3.3 | 0.40311
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML9 | 150-WF-71371-01K01 CML9 |  | FPSO 2015 | Pipe Wall Thickness | 7770 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3.075 | CML9 | CML: type TBC | 0.5 | 2015-04-18 | 2015-04-18 | 2015-04-18 07:00 | 2.5 | 0.26592 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 3.1 | 3.6 | 3.1 | 0.45
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML8 | 150-WF-71371-01K01 CML8 |  | FPSO 2015 | Pipe Wall Thickness | 7769 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3.025 | CML8 | CML: type TBC | 0.5 | 2015-04-18 | 2015-04-18 | 2015-04-18 07:00 | 2.5 | 0.26592 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 3.1 | 3.8 | 2.7 | 2.5 | 0.57373
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML58 | 100-WF-71326-01K01 CML58 |  | FPSO 2015 | Pipe Wall Thickness | 7590 |  | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 17:09 | [32 empty] | 2.575 | CML58 | CML: type TBC | 0.5 | 2015-04-14 | 2015-04-14 | 2015-04-14 07:00 | 2.5 | 0.26748 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.8 | 2.5 | 2.5 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML49 | 100-WF-71326-01K01 CML49 |  | FPSO 2015 | Pipe Wall Thickness | 7581 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 2.65 | CML49 | CML: type TBC | 0.5 | 2015-04-14 | 2015-04-14 | 2015-04-14 07:00 | 2.5 | 0.26748 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.7 | 2.7 | 2.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML47 | 100-WF-71326-01K01 CML47 |  | FPSO 2015 | Pipe Wall Thickness | 7579 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 2.6 | CML47 | CML: type TBC | 0.5 | 2015-04-14 | 2015-04-14 | 2015-04-14 07:00 | 2.5 | 0.26748 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.6 | 2.7 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML45 | 100-WF-71326-01K01 CML45 |  | FPSO 2015 | Pipe Wall Thickness | 7577 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 2.575 | CML45 | CML: type TBC | 0.5 | 2015-04-14 | 2015-04-14 | 2015-04-14 07:00 | 2.5 | 0.26748 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML21 | 100-WF-71326-01K01 CML21 |  | FPSO 2015 | Pipe Wall Thickness | 7553 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 2.6 | CML21 | CML: type TBC | 0.5 | 2015-04-14 | 2015-04-14 | 2015-04-14 07:00 | 2.5 | 0.26748 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.6 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML16 | 100-WF-71326-01K01 CML16 |  | FPSO 2015 | Pipe Wall Thickness | 7548 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 2.575 | CML16 | CML: type TBC | 0.5 | 2015-04-14 | 2015-04-14 | 2015-04-14 07:00 | 2.5 | 0.26748 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML126 | 100-WF-71309-01K01 CML126 |  | FPSO 2015 | Pipe Wall Thickness | 7465 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 2.625 | CML126 | CML: type TBC | 0.5 | 2015-04-11 | 2015-04-11 | 2015-04-11 07:00 | 2.5 | 0.26866 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.8 | 2.6 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML92 | 100-WF-71309-01K01 CML92 |  | FPSO 2015 | Pipe Wall Thickness | 7431 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 2.5 | CML92 | CML: type TBC | 0.5 | 2015-04-11 | 2015-04-11 | 2015-04-11 07:00 | 2.5 | 0.26866 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML87 | 100-WF-71309-01K01 CML87 |  | FPSO 2015 | Pipe Wall Thickness | 7426 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 2.525 | CML87 | CML: type TBC | 0.5 | 2015-04-11 | 2015-04-11 | 2015-04-11 07:00 | 2.5 | 0.26866 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML71 | 100-WF-71309-01K01 CML71 |  | FPSO 2015 | Pipe Wall Thickness | 7410 | Cast fitting, reading taken on adjacent pipework | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 2.6 | CML71 | CML: type TBC | 0.5 | 2015-04-11 | 2015-04-11 | 2015-04-11 07:00 | 2.5 | 0.26866 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.7 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML51 | 100-WF-71309-01K01 CML51 |  | FPSO 2015 | Pipe Wall Thickness | 7390 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 2.5 | CML51 | CML: type TBC | 0.5 | 2015-04-11 | 2015-04-11 | 2015-04-11 07:00 | 2.5 | 0.26866 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML7 | 100-WF-71309-01K01 CML7 |  | FPSO 2015 | Pipe Wall Thickness | 7346 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 2.5 | CML7 | CML: type TBC | 0.5 | 2015-04-11 | 2015-04-11 | 2015-04-11 07:00 | 2.5 | 0.26866 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML93 | 80-WF-71311-01K01 CML93 |  | FPSO 2015 | Pipe Wall Thickness | 7338 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.5 | CML93 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML89 | 80-WF-71311-01K01 CML89 |  | FPSO 2015 | Pipe Wall Thickness | 7334 |  | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.6 | CML89 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.7 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML88 | 80-WF-71311-01K01 CML88 |  | FPSO 2015 | Pipe Wall Thickness | 7333 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.525 | CML88 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML87 | 80-WF-71311-01K01 CML87 |  | FPSO 2015 | Pipe Wall Thickness | 7332 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.5 | CML87 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML79 | 80-WF-71311-01K01 CML79 |  | FPSO 2015 | Pipe Wall Thickness | 7324 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.525 | CML79 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML67 | 80-WF-71311-01K01 CML67 |  | FPSO 2015 | Pipe Wall Thickness | 7312 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.5 | CML67 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML63 | 80-WF-71311-01K01 CML63 |  | FPSO 2015 | Pipe Wall Thickness | 7308 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.55 | CML63 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML62 | 80-WF-71311-01K01 CML62 |  | FPSO 2015 | Pipe Wall Thickness | 7307 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-24 10:29 | [32 empty] | 2.55 | CML62 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML61 | 80-WF-71311-01K01 CML61 |  | FPSO 2015 | Pipe Wall Thickness | 7306 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-24 10:29 | [32 empty] | 2.525 | CML61 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML60 | 80-WF-71311-01K01 CML60 |  | FPSO 2015 | Pipe Wall Thickness | 7305 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.5 | CML60 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML59 | 80-WF-71311-01K01 CML59 |  | FPSO 2015 | Pipe Wall Thickness | 7304 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.525 | CML59 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML51 | 80-WF-71311-01K01 CML51 |  | FPSO 2015 | Pipe Wall Thickness | 7296 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.5 | CML51 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML41 | 80-WF-71311-01K01 CML41 |  | FPSO 2015 | Pipe Wall Thickness | 7286 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.525 | CML41 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML39 | 80-WF-71311-01K01 CML39 |  | FPSO 2015 | Pipe Wall Thickness | 7284 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.75 | CML39 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.9 | 3.1 | 0.3
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML36 | 80-WF-71311-01K01 CML36 |  | FPSO 2015 | Pipe Wall Thickness | 7281 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.5 | CML36 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML32 | 80-WF-71311-01K01 CML32 |  | FPSO 2015 | Pipe Wall Thickness | 7277 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.525 | CML32 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML25 | 80-WF-71311-01K01 CML25 |  | FPSO 2015 | Pipe Wall Thickness | 7270 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.525 | CML25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML11 | 80-WF-71311-01K01 CML11 |  | FPSO 2015 | Pipe Wall Thickness | 7256 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 09:11 | [32 empty] | 2.625 | CML11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.7 | 2.6 | 2.7 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML19 | 80-WF-71311-01K01 CML19 |  | FPSO 2015 | Pipe Wall Thickness | 7264 | Cast fitting, reading taken on adjacent pipework | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.5 | CML19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML53 | 80-WF-71320-01K01 CML53 |  | FPSO 2015 | Pipe Wall Thickness | 7242 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:39 | [32 empty] | 2.525 | CML53 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML14 | 80-WF-71320-01K01 CML14 |  | FPSO 2015 | Pipe Wall Thickness | 7203 | Cast fitting, reading taken on adjacent pipework | 2015-04-08 07:00 | 2015-04-08 15:00 | [36 empty] | 2.525 | CML14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML8 | 80-WF-71320-01K01 CML8 |  | FPSO 2015 | Pipe Wall Thickness | 7197 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [36 empty] | 2.7 | CML8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.9 | 2.5 | 2.6 | 2.8 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML142 | 80-WF-71338-01K01 CML142 |  | FPSO 2015 | Pipe Wall Thickness | 7188 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML142 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML139 | 80-WF-71338-01K01 CML139 |  | FPSO 2015 | Pipe Wall Thickness | 7185 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML139 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML138 | 80-WF-71338-01K01 CML138 |  | FPSO 2015 | Pipe Wall Thickness | 7184 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.575 | CML138 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.7 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML137 | 80-WF-71338-01K01 CML137 |  | FPSO 2015 | Pipe Wall Thickness | 7183 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML137 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.6 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML136 | 80-WF-71338-01K01 CML136 |  | FPSO 2015 | Pipe Wall Thickness | 7182 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.575 | CML136 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML131 | 80-WF-71338-01K01 CML131 |  | FPSO 2015 | Pipe Wall Thickness | 7177 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.5 | CML131 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML126 | 80-WF-71338-01K01 CML126 |  | FPSO 2015 | Pipe Wall Thickness | 7172 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.5 | CML126 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML124 | 80-WF-71338-01K01 CML124 |  | FPSO 2015 | Pipe Wall Thickness | 7170 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.7 | CML124 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.9 | 2.9 | 2.5 | 2.5 | 0.23094
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML123 | 80-WF-71338-01K01 CML123 |  | FPSO 2015 | Pipe Wall Thickness | 7169 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.65 | CML123 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.7 | 2.8 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML117 | 80-WF-71338-01K01 CML117 |  | FPSO 2015 | Pipe Wall Thickness | 7163 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML117 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.5 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML113 | 80-WF-71338-01K01 CML113 |  | FPSO 2015 | Pipe Wall Thickness | 7159 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML113 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML109 | 80-WF-71338-01K01 CML109 |  | FPSO 2015 | Pipe Wall Thickness | 7155 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML109 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.6 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML105 | 80-WF-71338-01K01 CML105 |  | FPSO 2015 | Pipe Wall Thickness | 7151 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 15:54 | [32 empty] | 2.575 | CML105 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.7 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML95 | 80-WF-71338-01K01 CML95 |  | FPSO 2015 | Pipe Wall Thickness | 7141 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.675 | CML95 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.5 | 2.7 | 2.8 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML82 | 80-WF-71338-01K01 CML82 |  | FPSO 2015 | Pipe Wall Thickness | 7128 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 16:17 | [32 empty] | 2.525 | CML82 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML80 | 80-WF-71338-01K01 CML80 |  | FPSO 2015 | Pipe Wall Thickness | 7126 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 16:11 | [32 empty] | 2.525 | CML80 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML79 | 80-WF-71338-01K01 CML79 |  | FPSO 2015 | Pipe Wall Thickness | 7125 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 16:14 | [32 empty] | 2.525 | CML79 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML78 | 80-WF-71338-01K01 CML78 |  | FPSO 2015 | Pipe Wall Thickness | 7124 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.5 | CML78 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML77 | 80-WF-71338-01K01 CML77 |  | FPSO 2015 | Pipe Wall Thickness | 7123 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.575 | CML77 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML76 | 80-WF-71338-01K01 CML76 |  | FPSO 2015 | Pipe Wall Thickness | 7122 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.6 | CML76 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.7 | 2.5 | 2.7 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML69 | 80-WF-71338-01K01 CML69 |  | FPSO 2015 | Pipe Wall Thickness | 7115 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.7 | CML69 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.8 | 2.7 | 2.8 | 2.5 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML64 | 80-WF-71338-01K01 CML64 |  | FPSO 2015 | Pipe Wall Thickness | 7110 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML64 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.5 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML63 | 80-WF-71338-01K01 CML63 |  | FPSO 2015 | Pipe Wall Thickness | 7109 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML63 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML59 | 80-WF-71338-01K01 CML59 |  | FPSO 2015 | Pipe Wall Thickness | 7105 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.5 | CML59 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML58 | 80-WF-71338-01K01 CML58 |  | FPSO 2015 | Pipe Wall Thickness | 7104 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.6 | CML58 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.9 | 2.5 | 0.2
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML42 | 80-WF-71338-01K01 CML42 |  | FPSO 2015 | Pipe Wall Thickness | 7088 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML42 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.6 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML39 | 80-WF-71338-01K01 CML39 |  | FPSO 2015 | Pipe Wall Thickness | 7085 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML39 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML38 | 80-WF-71338-01K01 CML38 |  | FPSO 2015 | Pipe Wall Thickness | 7084 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML38 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML35 | 80-WF-71338-01K01 CML35 |  | FPSO 2015 | Pipe Wall Thickness | 7081 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML35 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML34 | 80-WF-71338-01K01 CML34 |  | FPSO 2015 | Pipe Wall Thickness | 7080 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.575 | CML34 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML31 | 80-WF-71338-01K01 CML31 |  | FPSO 2015 | Pipe Wall Thickness | 7077 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML31 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML30 | 80-WF-71338-01K01 CML30 |  | FPSO 2015 | Pipe Wall Thickness | 7076 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.6 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML28 | 80-WF-71338-01K01 CML28 |  | FPSO 2015 | Pipe Wall Thickness | 7074 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML27 | 80-WF-71338-01K01 CML27 |  | FPSO 2015 | Pipe Wall Thickness | 7073 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML26 | 80-WF-71338-01K01 CML26 |  | FPSO 2015 | Pipe Wall Thickness | 7072 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.65 | CML26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.6 | 2.9 | 2.5 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML23 | 80-WF-71338-01K01 CML23 |  | FPSO 2015 | Pipe Wall Thickness | 7069 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.5 | CML23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML22 | 80-WF-71338-01K01 CML22 |  | FPSO 2015 | Pipe Wall Thickness | 7068 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.55 | CML22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML20 | 80-WF-71338-01K01 CML20 |  | FPSO 2015 | Pipe Wall Thickness | 7066 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.5 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML19 | 80-WF-71338-01K01 CML19 |  | FPSO 2015 | Pipe Wall Thickness | 7065 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.5 | CML19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML17 | 80-WF-71338-01K01 CML17 |  | FPSO 2015 | Pipe Wall Thickness | 7063 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML16 | 80-WF-71338-01K01 CML16 |  | FPSO 2015 | Pipe Wall Thickness | 7062 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML47 | 80-WF-71338-01K01 CML47 |  | FPSO 2015 | Pipe Wall Thickness | 7093 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML47 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML56 | 80-WF-71338-01K01 CML56 |  | FPSO 2015 | Pipe Wall Thickness | 7102 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.775 | CML56 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 3 | 2.9 | 2.5 | 2.7 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML52 | 80-WF-71338-01K01 CML52 |  | FPSO 2015 | Pipe Wall Thickness | 7098 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.6 | CML52 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.6 | 2.5 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML51 | 80-WF-71338-01K01 CML51 |  | FPSO 2015 | Pipe Wall Thickness | 7097 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.5 | CML51 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML50 | 80-WF-71338-01K01 CML50 |  | FPSO 2015 | Pipe Wall Thickness | 7096 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.5 | CML50 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML8 | 80-WF-71338-01K01 CML8 |  | FPSO 2015 | Pipe Wall Thickness | 7054 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.575 | CML8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.7 | 2.5 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML5 | 80-WF-71338-01K01 CML5 |  | FPSO 2015 | Pipe Wall Thickness | 7051 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.525 | CML5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.5 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML126 | 100-WF-71308-01K01 CML126 |  | FPSO 2015 | Pipe Wall Thickness | 7044 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.55 | CML126 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.7 | 2.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML125 | 100-WF-71308-01K01 CML125 |  | FPSO 2015 | Pipe Wall Thickness | 7043 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.5 | CML125 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML110 | 100-WF-71308-01K01 CML110 |  | FPSO 2015 | Pipe Wall Thickness | 7028 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 3.075 | CML110 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 3 | 3.9 | 2.9 | 0.5909
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML87 | 100-WF-71308-01K01 CML87 |  | FPSO 2015 | Pipe Wall Thickness | 7005 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.55 | CML87 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.6 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML77 | 100-WF-71308-01K01 CML77 |  | FPSO 2015 | Pipe Wall Thickness | 6995 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.675 | CML77 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.9 | 2.7 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML73 | 100-WF-71308-01K01 CML73 |  | FPSO 2015 | Pipe Wall Thickness | 6991 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.625 | CML73 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.7 | 2.7 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML70 | 100-WF-71308-01K01 CML70 |  | FPSO 2015 | Pipe Wall Thickness | 6988 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.525 | CML70 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML66 | 100-WF-71308-01K01 CML66 |  | FPSO 2015 | Pipe Wall Thickness | 6984 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.7 | CML66 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.7 | 2.9 | 2.7 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML53 | 100-WF-71308-01K01 CML53 |  | FPSO 2015 | Pipe Wall Thickness | 6971 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.525 | CML53 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML43 | 100-WF-71308-01K01 CML43 |  | FPSO 2015 | Pipe Wall Thickness | 6961 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.65 | CML43 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 3 | 2.5 | 0.23805
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML41 | 100-WF-71308-01K01 CML41 |  | FPSO 2015 | Pipe Wall Thickness | 6959 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.75 | CML41 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 3 | 3 | 2.5 | 0.28868
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML20 | 100-WF-71308-01K01 CML20 |  | FPSO 2015 | Pipe Wall Thickness | 6938 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.6 | CML20 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.8 | 2.5 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML19 | 100-WF-71308-01K01 CML19 |  | FPSO 2015 | Pipe Wall Thickness | 6937 |  | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-27 15:58 | [32 empty] | 2.65 | CML19 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.7 | 2.5 | 2.7 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML18 | 100-WF-71308-01K01 CML18 |  | FPSO 2015 | Pipe Wall Thickness | 6936 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.55 | CML18 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.5 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML6 | 100-WF-71308-01K01 CML6 |  | FPSO 2015 | Pipe Wall Thickness | 6924 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 3.4 | CML6 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 3.8 | 3.9 | 3.4 | 2.5 | 0.6377
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML4 | 100-WF-71308-01K01 CML4 |  | FPSO 2015 | Pipe Wall Thickness | 6922 |  | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-27 15:57 | [32 empty] | 2.65 | CML4 | CML: type TBC | 0.5 | 2015-04-06 | 2015-04-06 | 2015-04-06 07:00 | 2.5 | 0.27065 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.8 | 2.5 | 2.5 | 2.8 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-34 | 250-WF-71373-01K01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 6912 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | Medium alarm breach | 4.325 | CML-34 | CML: type TBC | 0.5 | 2015-04-05 | 2014-10-18 | 2015-04-05 07:00 | 3.5 | 0.54211 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 3.5 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 3.5 | 4.5 | 5.1 | 4.2 | 0.66521
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-22 | 100-WF-71328-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6855 | Cast fitting, reading taken on adjacent pipework | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 2.5 | CML-22 | CML: type TBC | 0.5 | 2015-04-05 | 2015-04-05 | 2015-04-05 07:00 | 2.5 | 0.27106 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-124 | 150-WF-71345-01K01 CML-124 |  | FPSO 2015 | Pipe Wall Thickness | 6798 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.55 | CML-124 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.6 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-113 | 150-WF-71345-01K01 CML-113 |  | FPSO 2015 | Pipe Wall Thickness | 6787 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.5 | CML-113 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-143 | 150-WF-71345-01K01 CML-143 |  | FPSO 2015 | Pipe Wall Thickness | 6817 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.6 | CML-143 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.8 | 2.5 | 2.6 | 2.5 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-153 | 150-WF-71345-01K01 CML-153 |  | FPSO 2015 | Pipe Wall Thickness | 6827 | Cast fitting, reading taken on adjacent pipework | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 17:40 | [32 empty] | 2.6 | CML-153 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.8 | 2.5 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-108 | 150-WF-71345-01K01 CML-108 |  | FPSO 2015 | Pipe Wall Thickness | 6782 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.625 | CML-108 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.8 | 2.5 | 2.5 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-105 | 150-WF-71345-01K01 CML-105 |  | FPSO 2015 | Pipe Wall Thickness | 6779 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.5 | CML-105 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.5 | 2.5 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-100 | 150-WF-71345-01K01 CML-100 |  | FPSO 2015 | Pipe Wall Thickness | 6774 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.875 | CML-100 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 3.1 | 3 | 2.9 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-7 | 150-WF-71345-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6681 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.75 | CML-7 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 3 | 2.8 | 2.5 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-1 | 150-WF-71345-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6675 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.825 | CML-1 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.9 | 2.9 | 2.5 | 3 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-36 | 150-WF-71345-01K01 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 6710 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.55 | CML-36 | CML: type TBC | 0.5 | 2015-04-04 | 2015-04-04 | 2015-04-04 07:00 | 2.5 | 0.27146 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.6 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-21 | 50-WF-71350-01K01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6064 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.65 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.7 | 2.8 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-18 | 50-WF-71350-01K01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6061 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.625 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.7 | 2.8 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-2 | 50-WF-71350-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6045 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.875 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 3 | 3 | 3 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-1 | 50-WF-71350-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6044 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 3.4 | 2.5 | 3.3 | 2.9 | 0.4113
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-33 | 50-WF-71351-01K01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 6108 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.6 | CML-33 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.7 | 2.5 | 2.6 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71352-01K01 | CML-1 | 100-WF-71352-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6111 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.625 | CML-1 | CML: type TBC | 0.5 | 2015-03-17 | 2015-03-17 | 2015-03-17 07:00 | 2.5 | 0.27893 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.5 | 12 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 4 | 4.3 | 3.7 | 0.78899
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-15 | 50-WF-71351-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6090 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.625 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.7 | 2.7 | 2.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-8 | 50-WF-71351-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6083 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.625 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.7 | 2.7 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-7 | 50-WF-71351-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6082 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.6 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.7 | 2.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-4 | 50-WF-71351-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6079 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.625 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.7 | 2.7 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-26 | 50-WF-71350-01K01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6069 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.55 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-25 | 50-WF-71350-01K01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6068 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.55 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.6 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-22 | 50-WF-71350-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6065 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.65 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.7 | 2.8 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-10 | 80-WF-71310-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5495 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.7 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.7 | 2.9 | 2.7 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-9 | 80-WF-71310-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5494 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.75 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.8 | 3 | 2.7 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-68 | 80-WF-71310-01K01 CML-68 |  | FPSO 2015 | Pipe Wall Thickness | 5553 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.6 | CML-68 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.6 | 2.7 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-63 | 80-WF-71310-01K01 CML-63 |  | FPSO 2015 | Pipe Wall Thickness | 5548 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.55 | CML-63 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.6 | 2.5 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-62 | 80-WF-71310-01K01 CML-62 |  | FPSO 2015 | Pipe Wall Thickness | 5547 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-62 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.7 | 2.7 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-60 | 80-WF-71310-01K01 CML-60 |  | FPSO 2015 | Pipe Wall Thickness | 5545 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-60 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.7 | 2.7 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-58 | 80-WF-71310-01K01 CML-58 |  | FPSO 2015 | Pipe Wall Thickness | 5543 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.65 | CML-58 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.8 | 2.8 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-55 | 80-WF-71310-01K01 CML-55 |  | FPSO 2015 | Pipe Wall Thickness | 5540 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.75 | CML-55 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.7 | 3.2 | 0.31091
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-54 | 80-WF-71310-01K01 CML-54 |  | FPSO 2015 | Pipe Wall Thickness | 5539 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.65 | CML-54 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.8 | 2.7 | 2.5 | 2.6 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-53 | 80-WF-71310-01K01 CML-53 |  | FPSO 2015 | Pipe Wall Thickness | 5538 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.6 | CML-53 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.8 | 2.6 | 2.5 | 2.5 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-74 | 80-WF-71310-01K01 CML-74 |  | FPSO 2015 | Pipe Wall Thickness | 5559 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.775 | CML-74 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.8 | 2.5 | 2.7 | 3.1 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-72 | 80-WF-71310-01K01 CML-72 |  | FPSO 2015 | Pipe Wall Thickness | 5557 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.6 | CML-72 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.7 | 2.6 | 2.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-79 | 80-WF-71310-01K01 CML-79 |  | FPSO 2015 | Pipe Wall Thickness | 5564 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-79 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.6 | 2.5 | 2.7 | 2.7 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-8 | 80-WF-71310-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5493 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.725 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.7 | 3 | 2.7 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-50 | 80-WF-71310-01K01 CML-50 |  | FPSO 2015 | Pipe Wall Thickness | 5535 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.575 | CML-50 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.5 | 3 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.5 | 2.7 | 2.6 | 0.095743
WD03 | Montara_Topside | No | Potable Water (53) | Pipework | 0100-WZ-53L9001-AS20-00 | CML-9 | 0100-WZ-53L9001-AS20-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5113 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Medium alarm breach | 3.025 | CML-9 | CML: type TBC | 0 | 2015-03-06 | 2014-08-13 | 2015-03-06 07:00 | 2.5 | 0.40695 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.5 | 3 O'Clock | 25 | 3.38 | 0100-WZ-53L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 3.1 | 2.5 | 3.5 | 3 | 0.4113
WD03 | Montara_Topside | No | Potable Water (53) | Pipework | 0200-WZ-53L9000-AS20-00 | CML-1 | 0200-WZ-53L9000-AS20-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5100 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 2.625 | CML-1 | CML: type TBC | 0 | 2015-03-06 | 2015-06-25 | 2015-03-06 07:00 | 2.5 | 0.12486 | A1: Outside Quadrant |  | 2.77 | 2.5 | 2.4619 | 2.5 | 12 O'Clock | 50 | 2.77 | 0200-WZ-53L9000-AS20-00 | 10S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 2.5 | 2.6 | 2.8 | 2.6 | 0.12583
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9002-AS20-00 | CML-7 | 0100-DC-57L9002-AS20-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5084 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Check Corrosion Rate of 0.407mm/ yr | [34 empty] | Medium alarm breach | 3.225 | CML-7 | CML: type TBC | 0 | 2015-03-06 | 2014-08-13 | 2015-03-06 07:00 | 2.5 | 0.40695 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.5 | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 3.6 | 4 | 2.8 | 2.5 | 0.69462
RP01 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9003-AS20-00 | CML2 | 0100-AI-63L9003-AS20-00 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 7472 |  | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 3.75 | CML2 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-04-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.7 | 3 O'Clock | 25 | 3.38 | 0100-AI-63L9003-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.7 | 3.8 | 3.8 | 0.057735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-10 | 80-FH-43111-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12808 | Inspection not carried due to location access | 2014-02-01 07:00 | 2014-02-01 09:00 | [37 empty] | CML-10 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-02-01 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.1519 |  | 9 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9003-AK11-00 | CML - 24 | 0300-WF-71L9003-AK11-00 CML - 24 |  | FPSO 2015 | Pipe Wall Thickness | 22633 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.6 | CML - 24 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.6 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.6 | 2.6 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9002-AK11-00 | CML - 4 | 0300-WF-71L9002-AK11-00 CML - 4 |  | FPSO 2015 | Pipe Wall Thickness | 22573 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 2.625 | CML - 4 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.6 | 9 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0300-WF-71L9004-AK11-00 | CML-9 | 0300-WF-71L9004-AK11-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22562 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [36 empty] | 2.725 | CML-9 | CML: Elbow | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 2.6 | 6 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.7 | 2.6 | 2.9 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-104 | 80-WF-71340-01K01 CML-104 |  | FPSO 2015 | Pipe Wall Thickness | 22475 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.725 | CML-104 | CML: Reducing Tee | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 12 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.7 | 2.9 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-16 | 100-WF-71340-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 22387 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.65 | CML-16 | CML: Reducer | 0.5 | 2015-10-08 | 2015-10-08 | 2015-04-19 07:00 | 2.5 | 0.21243 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.6 | 2.7 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML24 | 150-WF-71371-01K01 CML24 |  | FPSO 2015 | Pipe Wall Thickness | 7785 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3.05 | CML24 | CML: type TBC | 0.5 | 2015-10-06 | 2015-10-06 | 2015-04-18 07:00 | 2.5 | 0.21274 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 6 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3.5 | 3.3 | 2.6 | 2.8 | 0.42032
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML27 | 150-WF-71371-01K01 CML27 |  | FPSO 2015 | Pipe Wall Thickness | 7788 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3.075 | CML27 | CML: type TBC | 0.5 | 2015-10-06 | 2015-10-06 | 2015-04-18 07:00 | 2.5 | 0.21274 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 6 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3.7 | 3 | 2.6 | 3 | 0.45735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML56 | 100-WF-71326-01K01 CML56 |  | FPSO 2015 | Pipe Wall Thickness | 7588 |  | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 17:08 | [32 empty] | 2.675 | CML56 | CML: type TBC | 0.5 | 2015-10-01 | 2015-10-01 | 2015-04-14 07:00 | 2.5 | 0.21398 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.7 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML58 | 80-WF-71311-01K01 CML58 |  | FPSO 2015 | Pipe Wall Thickness | 7303 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-24 10:29 | [32 empty] | 2.675 | CML58 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.8 | 2.7 | 2.6 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML46 | 80-WF-71311-01K01 CML46 |  | FPSO 2015 | Pipe Wall Thickness | 7291 |  | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 2.65 | CML46 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.6 | 2.7 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML41 | 80-WF-71338-01K01 CML41 |  | FPSO 2015 | Pipe Wall Thickness | 7087 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.625 | CML41 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML49 | 80-WF-71338-01K01 CML49 |  | FPSO 2015 | Pipe Wall Thickness | 7095 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.925 | CML49 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.9 | 3.2 | 3 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML108 | 100-WF-71308-01K01 CML108 |  | FPSO 2015 | Pipe Wall Thickness | 7026 |  | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-24 08:45 | [32 empty] | 3.225 | CML108 | CML: type TBC | 0.5 | 2015-09-21 | 2015-09-21 | 2015-04-06 07:00 | 2.5 | 0.21652 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3.4 | 3.5 | 3.4 | 2.6 | 0.41932
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML7 | 100-WF-71308-01K01 CML7 |  | FPSO 2015 | Pipe Wall Thickness | 6925 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 3.15 | CML7 | CML: type TBC | 0.5 | 2015-09-21 | 2015-09-21 | 2015-04-06 07:00 | 2.5 | 0.21652 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3.9 | 3 | 3.1 | 2.6 | 0.54467
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML3 | 100-WF-71308-01K01 CML3 |  | FPSO 2015 | Pipe Wall Thickness | 6921 |  | 2015-04-06 07:00 | 2015-04-06 15:00 |  |  | Nestor | 2014-11-27 15:57 | [32 empty] | 3.075 | CML3 | CML: type TBC | 0.5 | 2015-09-21 | 2015-09-21 | 2015-04-06 07:00 | 2.5 | 0.21652 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 4 | 2.8 | 2.6 | 2.9 | 0.62915
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-8 | 250-WF-71373-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6886 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | Medium alarm breach | 4.175 | CML-8 | CML: type TBC | 0.5 | 2015-06-19 | 2014-12-14 | 2015-04-05 07:00 | 3.5 | 0.4879 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 3.6 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3.6 | 4.2 | 4.6 | 4.3 | 0.41932
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-44 | 100-WF-71328-01K01 CML-44 |  | FPSO 2015 | Pipe Wall Thickness | 6877 |  | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-11-27 16:33 | [32 empty] | 2.725 | CML-44 | CML: type TBC | 0.5 | 2015-09-20 | 2015-09-20 | 2015-04-05 07:00 | 2.5 | 0.21685 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.8 | 2.9 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-41 | 100-WF-71328-01K01 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 6874 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 2.725 | CML-41 | CML: type TBC | 0.5 | 2015-09-20 | 2015-09-20 | 2015-04-05 07:00 | 2.5 | 0.21685 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.7 | 3 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-114 | 150-WF-71345-01K01 CML-114 |  | FPSO 2015 | Pipe Wall Thickness | 6788 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.175 | CML-114 | CML: type TBC | 0.5 | 2015-09-19 | 2015-09-19 | 2015-04-04 07:00 | 2.5 | 0.21717 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.6 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3.1 | 3.8 | 3.2 | 2.6 | 0.49244
RP01 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9003-AS20-00 | CML1 | 0100-AI-63L9003-AS20-00 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 7471 |  | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 3.725 | CML1 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-04-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.7 | 9 O'Clock | 25 | 3.38 | 0100-AI-63L9003-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.7 | 3.8 | 3.7 | 0.05
RP01 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9003-AS20-00 | CML3 | 0100-AI-63L9003-AS20-00 CML3 |  | FPSO 2015 | Pipe Wall Thickness | 7473 |  | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 5.95 | CML3 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-04-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 5.9 | 9 O'Clock | 25 | 3.38 | 0100-AI-63L9003-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 6 | 5.9 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-19 | 50-WF-71350-01K01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6062 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.675 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 3 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.6 | 2.7 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-17 | 50-WF-71350-01K01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6060 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.65 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 3 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.7 | 2.7 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-13 | 50-WF-71350-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6056 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.65 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.6 | 2.6 | 2.7 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-9 | 50-WF-71350-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6052 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.625 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.6 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-5 | 50-WF-71350-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6048 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.7 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 12 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.8 | 2.7 | 2.7 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-34 | 50-WF-71351-01K01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 6109 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.675 | CML-34 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.7 | 2.7 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-13 | 50-WF-71351-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6088 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.675 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.7 | 2.6 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-12 | 50-WF-71351-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6087 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.65 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.7 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-9 | 50-WF-71351-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6084 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.675 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.7 | 2.6 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-5 | 50-WF-71351-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6080 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.65 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.6 | 2.6 | 2.7 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-3 | 50-WF-71351-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6078 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.65 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.7 | 2.6 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-29 | 50-WF-71350-01K01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6072 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.65 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.7 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-27 | 50-WF-71350-01K01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6070 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.65 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.6 | 2.7 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-13 | 80-WF-71310-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5498 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.775 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.8 | 3 | 2.7 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-67 | 80-WF-71310-01K01 CML-67 |  | FPSO 2015 | Pipe Wall Thickness | 5552 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-67 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-66 | 80-WF-71310-01K01 CML-66 |  | FPSO 2015 | Pipe Wall Thickness | 5551 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.6 | CML-66 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.6 | 2.6 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-65 | 80-WF-71310-01K01 CML-65 |  | FPSO 2015 | Pipe Wall Thickness | 5550 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-65 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-64 | 80-WF-71310-01K01 CML-64 |  | FPSO 2015 | Pipe Wall Thickness | 5549 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.65 | CML-64 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.7 | 2.6 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-61 | 80-WF-71310-01K01 CML-61 |  | FPSO 2015 | Pipe Wall Thickness | 5546 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.675 | CML-61 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.7 | 2.6 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-57 | 80-WF-71310-01K01 CML-57 |  | FPSO 2015 | Pipe Wall Thickness | 5542 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-57 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.7 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-73 | 80-WF-71310-01K01 CML-73 |  | FPSO 2015 | Pipe Wall Thickness | 5558 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.85 | CML-73 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3 | 2.9 | 2.6 | 2.9 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-71 | 80-WF-71310-01K01 CML-71 |  | FPSO 2015 | Pipe Wall Thickness | 5556 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.6 | CML-71 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.6 | 2.6 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-69 | 80-WF-71310-01K01 CML-69 |  | FPSO 2015 | Pipe Wall Thickness | 5554 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-69 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.6 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-78 | 80-WF-71310-01K01 CML-78 |  | FPSO 2015 | Pipe Wall Thickness | 5563 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-78 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-77 | 80-WF-71310-01K01 CML-77 |  | FPSO 2015 | Pipe Wall Thickness | 5562 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-77 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-81 | 80-WF-71310-01K01 CML-81 |  | FPSO 2015 | Pipe Wall Thickness | 5566 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.65 | CML-81 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.7 | 2.6 | 2.6 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-52 | 80-WF-71310-01K01 CML-52 |  | FPSO 2015 | Pipe Wall Thickness | 5537 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-52 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.7 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-51 | 80-WF-71310-01K01 CML-51 |  | FPSO 2015 | Pipe Wall Thickness | 5536 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-51 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.6 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-47 | 80-WF-71310-01K01 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 5532 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-47 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.6 | 2.6 | 2.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-45 | 80-WF-71310-01K01 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 5530 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.625 | CML-45 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.6 | 2.6 | 2.6 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71312-01K01 | CML-7 | 50-WF-71312-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5325 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.075 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.6 | 6 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3.9 | 2.8 | 2.6 | 3 | 0.57373
WD03 | Montara_Topside | No | Potable Water (53) | Pipework | 0200-WZ-53L9000-AS20-00 | CML-4 | 0200-WZ-53L9000-AS20-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5103 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 2.725 | CML-4 | CML: type TBC | 0 | 2016-06-12 | 2016-12-06 | 2015-03-06 07:00 | 2.5 | 0.07861 | A2: Right Quadrant |  | 2.77 | 2.5 | 2.4619 | 2.6 | 9 O'Clock | 50 | 2.77 | 0200-WZ-53L9000-AS20-00 | 10S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 2.7 | 2.6 | 3 | 2.6 | 0.1893
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9001-AS20-00 | CML-4 | 0100-DC-57L9001-AS20-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5060 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Check Corrosion Rate of 0.361mm/ yr | [34 empty] | Medium alarm breach | 3.025 | CML-4 | CML: type TBC | 0 | 2015-06-15 | 2014-10-27 | 2015-03-06 07:00 | 2.5 | 0.3607 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.6 | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3.2 | 3.4 | 2.9 | 2.6 | 0.35
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0400-WF-71L9001-AK11-00 | CML-2 | 0400-WF-71L9001-AK11-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22567 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [36 empty] | 3 | CML-2 | CML: Elbow | 0.5 | 2013-01-06 | 2017-01-28 | 2015-04-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.0938 | 2.7 | 12 O'Clock | 100 | 2.5 | 0400-WF-71L9001-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.8 | 3.4 | 3.1 | 0.31623
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0400-WF-71L9001-AK11-00 | CML-1 | 0400-WF-71L9001-AK11-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22566 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [36 empty] | 2.85 | CML-1 | CML: Elbow | 0.5 | 2013-01-06 | 2017-01-28 | 2015-04-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.0938 | 2.7 | 6 O'Clock | 100 | 2.5 | 0400-WF-71L9001-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.1 | 2.8 | 2.7 | 2.8 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-80 | 80-WF-71340-01K01 CML-80 |  | FPSO 2015 | Pipe Wall Thickness | 22451 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.775 | CML-80 | CML: Equal Tee | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 12 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.8 | 2.8 | 2.8 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-12 | 100-WF-71340-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22383 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.95 | CML-12 | CML: Reducer | 0.5 | 2016-07-20 | 2016-07-20 | 2015-04-19 07:00 | 2.5 | 0.15932 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 3 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.7 | 3.2 | 3.2 | 0.28868
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML18 | 150-WF-71371-01K01 CML18 |  | FPSO 2015 | Pipe Wall Thickness | 7779 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.9 | CML18 | CML: type TBC | 0.5 | 2016-07-18 | 2016-07-18 | 2015-04-18 07:00 | 2.5 | 0.15955 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 12 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.8 | 3.1 | 3 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML15 | 150-WF-71371-01K01 CML15 |  | FPSO 2015 | Pipe Wall Thickness | 7776 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.8 | CML15 | CML: type TBC | 0.5 | 2016-07-18 | 2016-07-18 | 2015-04-18 07:00 | 2.5 | 0.15955 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 12 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.8 | 2.9 | 2.8 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML26 | 150-WF-71371-01K01 CML26 |  | FPSO 2015 | Pipe Wall Thickness | 7787 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3.125 | CML26 | CML: type TBC | 0.5 | 2016-07-18 | 2016-07-18 | 2015-04-18 07:00 | 2.5 | 0.15955 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 6 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.8 | 3 | 2.7 | 3 | 0.4717
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML25 | 150-WF-71371-01K01 CML25 |  | FPSO 2015 | Pipe Wall Thickness | 7786 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.95 | CML25 | CML: type TBC | 0.5 | 2016-07-18 | 2016-07-18 | 2015-04-18 07:00 | 2.5 | 0.15955 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 12 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 3 | 3.2 | 2.9 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML23 | 150-WF-71371-01K01 CML23 |  | FPSO 2015 | Pipe Wall Thickness | 7784 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.875 | CML23 | CML: type TBC | 0.5 | 2016-07-18 | 2016-07-18 | 2015-04-18 07:00 | 2.5 | 0.15955 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 3 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3 | 2.7 | 2.8 | 3 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML6 | 150-WF-71371-01K01 CML6 |  | FPSO 2015 | Pipe Wall Thickness | 7767 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 4.15 | CML6 | CML: type TBC | 0.5 | 2016-07-18 | 2016-07-18 | 2015-04-18 07:00 | 2.5 | 0.15955 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 12 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 4.5 | 4.9 | 4.5 | 0.98489
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71354-01K01 | CML8 | 40-WF-71354-01K01 CML8 |  | FPSO 2015 | Pipe Wall Thickness | 7603 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-15 07:00 | 2015-04-15 15:00 | [36 empty] | 2.8 | CML8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 3 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.7 | 2.9 | 2.9 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML2 | 100-WF-71326-01K01 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 7534 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 2.85 | CML2 | CML: type TBC | 0.5 | 2016-07-12 | 2016-07-12 | 2015-04-14 07:00 | 2.5 | 0.16049 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.7 | 3 | 3 | 0.17321
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML94 | 100-WF-71309-01K01 CML94 |  | FPSO 2015 | Pipe Wall Thickness | 7433 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 2.875 | CML94 | CML: type TBC | 0.5 | 2016-07-07 | 2016-07-07 | 2015-04-11 07:00 | 2.5 | 0.1612 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.9 | 2.9 | 3 | 2.7 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML90 | 100-WF-71309-01K01 CML90 |  | FPSO 2015 | Pipe Wall Thickness | 7429 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 3.2 | CML90 | CML: type TBC | 0.5 | 2016-07-07 | 2016-07-07 | 2015-04-11 07:00 | 2.5 | 0.1612 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.5 | 3.7 | 2.9 | 2.7 | 0.4761
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML1 | 80-WF-71311-01K01 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 7246 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 16:37 | [32 empty] | 2.725 | CML1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.8 | 2.7 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML35 | 80-WF-71320-01K01 CML35 |  | FPSO 2015 | Pipe Wall Thickness | 7224 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [36 empty] | 2.9 | CML35 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 6 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3 | 2.9 | 2.7 | 3 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71320-01K01 | CML42 | 80-WF-71320-01K01 CML42 |  | FPSO 2015 | Pipe Wall Thickness | 7231 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [36 empty] | 3.375 | CML42 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.9 | 2.7 | 4.1 | 3.8 | 0.68007
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML29 | 80-WF-71338-01K01 CML29 |  | FPSO 2015 | Pipe Wall Thickness | 7075 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.75 | CML29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.8 | 2.7 | 2.8 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML48 | 80-WF-71338-01K01 CML48 |  | FPSO 2015 | Pipe Wall Thickness | 7094 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.775 | CML48 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.8 | 2.7 | 2.7 | 2.9 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML111 | 100-WF-71308-01K01 CML111 |  | FPSO 2015 | Pipe Wall Thickness | 7029 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 3.125 | CML111 | CML: type TBC | 0.5 | 2016-06-28 | 2016-06-28 | 2015-04-06 07:00 | 2.5 | 0.16239 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.8 | 3 | 2.7 | 3 | 0.4717
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML59 | 100-WF-71308-01K01 CML59 |  | FPSO 2015 | Pipe Wall Thickness | 6977 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.9 | CML59 | CML: type TBC | 0.5 | 2016-06-28 | 2016-06-28 | 2015-04-06 07:00 | 2.5 | 0.16239 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.9 | 2.7 | 3 | 3 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-39 | 250-WF-71373-01K01 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 6917 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | Medium alarm breach | 4.575 | CML-39 | CML: type TBC | 0.5 | 2015-09-20 | 2015-02-22 | 2015-04-05 07:00 | 3.5 | 0.43369 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 3.7 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.7 | 4.9 | 5.2 | 4.5 | 0.65
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-10 | 250-WF-71373-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6888 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | Medium alarm breach | 4.4 | CML-10 | CML: type TBC | 0.5 | 2015-09-20 | 2015-02-22 | 2015-04-05 07:00 | 3.5 | 0.43369 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 3.7 | 3 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.7 | 3.7 | 5.6 | 4.6 | 0.90554
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-4 | 250-WF-71373-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6882 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | Medium alarm breach | 4.4 | CML-4 | CML: type TBC | 0.5 | 2015-09-20 | 2015-02-22 | 2015-04-05 07:00 | 3.5 | 0.43369 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 3.7 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.7 | 4.3 | 5.3 | 4.3 | 0.66332
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-4 | 100-WF-71328-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6837 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 2.875 | CML-4 | CML: type TBC | 0.5 | 2016-06-27 | 2016-06-27 | 2015-04-05 07:00 | 2.5 | 0.16263 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 6 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3 | 3 | 2.7 | 2.8 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-136 | 150-WF-71345-01K01 CML-136 |  | FPSO 2015 | Pipe Wall Thickness | 6810 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.85 | CML-136 | CML: type TBC | 0.5 | 2016-06-25 | 2016-06-25 | 2015-04-04 07:00 | 2.5 | 0.16288 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3 | 2.9 | 2.7 | 2.8 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-19 | 150-WF-71345-01K01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6693 |  | 2015-04-04 07:00 | 2015-04-04 15:00 |  |  | Nestor | 2014-11-27 14:49 | [32 empty] | 2.925 | CML-19 | CML: type TBC | 0.5 | 2016-06-25 | 2016-06-25 | 2015-04-04 07:00 | 2.5 | 0.16288 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.7 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3 | 3 | 3 | 2.7 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71341-01K01 | CML-1 | 80-WF-71341-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6280 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.1 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 12 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 3.1 | 3.3 | 3.3 | 0.28284
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71333-01K01 | CML-9 | 50-WF-71333-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6236 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.075 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 6 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.5 | 3 | 2.7 | 3.1 | 0.3304
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71363-01K01 | CML-1 | 50-WF-71363-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6194 | Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.05 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 12 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 3.1 | 3.3 | 3.1 | 0.25166
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-12 | 50-WF-71350-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6055 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.75 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 3 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.7 | 2.8 | 2.8 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-11 | 50-WF-71350-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6054 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.7 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.7 | 2.7 | 2.7 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-8 | 50-WF-71350-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6051 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.725 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.8 | 2.7 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-7 | 50-WF-71350-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6050 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.7 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.7 | 2.7 | 2.7 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-6 | 50-WF-71350-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6049 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.9 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 12 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.9 | 3 | 3 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-4 | 50-WF-71350-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6047 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.775 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.7 | 3 | 2.7 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-3 | 50-WF-71350-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6046 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.75 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.8 | 2.8 | 2.7 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 25-WF-71349-01K01 | CML-5 | 25-WF-71349-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6042 | CAST Fitting. Readings taken on piping adjacent to fitting. | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.7 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 25 | 2.5 | 25-WF-71349-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.7 | 2.7 | 2.7 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 25-WF-71349-01K01 | CML-3 | 25-WF-71349-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6040 | CAST Fitting. Readings taken on piping adjacent to fitting. | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.85 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 25 | 2.5 | 25-WF-71349-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.2 | 2.7 | 2.8 | 2.7 | 0.23805
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 25-WF-71349-01K01 | CML-1 | 25-WF-71349-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6038 | CAST Fitting. Readings taken on piping adjacent to fitting. | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.775 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 25 | 2.5 | 25-WF-71349-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.8 | 2.8 | 2.8 | 2.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-11 | 50-WF-71351-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6086 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.925 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.1 | 3.2 | 2.7 | 2.7 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-23 | 50-WF-71350-01K01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6066 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.7 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 2.7 | 2.7 | 2.7 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71325-01K01 | CML-2 | 50-WF-71325-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5973 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 12 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 3.2 | 2.9 | 3.1 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71324-01K01 | CML-1 | 80-WF-71324-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5954 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 12 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 3 | 3.4 | 2.8 | 0.30957
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-2 | 80-WF-71310-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5487 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.95 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.9 | 3.2 | 3 | 2.7 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-1 | 80-WF-71310-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5486 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.05 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 3 | 3.2 | 3.3 | 0.26458
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-76 | 80-WF-71310-01K01 CML-76 |  | FPSO 2015 | Pipe Wall Thickness | 5561 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.775 | CML-76 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.7 | 6 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.8 | 2.8 | 2.7 | 2.8 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 200-WF-71306-01K01 | CML-6 | 200-WF-71306-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5192 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [35 empty] | Medium alarm breach | 3.05 | CML-6 | CML: type TBC | 0.5 | 2015-07-20 | 2014-12-04 | 2015-03-12 07:00 | 2.8 | 0.56215 | A1: Outside Quadrant |  | 3.5 | 2.8 | 3.15 | 3 | 3 O'Clock | 200 | 4 | 200-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3 | 3 | 3.1 | 3.1 | 0.057735
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9001-AS20-00 | CML-5 | 0100-DC-57L9001-AS20-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5061 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Check Corrosion Rate of 0.314mm/ yr | [34 empty] | Medium alarm breach | 2.925 | CML-5 | CML: type TBC | 0 | 2015-10-24 | 2015-01-31 | 2015-03-06 07:00 | 2.5 | 0.31446 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.7 | 6 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 3.2 | 2.8 | 2.7 | 3 | 0.22174
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9001-AS20-00 | CML-14 | 0100-AS-63L9001-AS20-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5023 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Check Corrosion Rate of 0.315mm/ yr | [34 empty] | Medium alarm breach | 2.975 | CML-14 | CML: type TBC | 0 | 2015-10-21 | 2015-01-30 | 2015-03-04 07:00 | 2.5 | 0.31526 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.7 | 12 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.2 |  | 2.7 | 3 | 3.2 | 3 | 0.20616
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9005-AS20-E-25 | CML-1 | 0100-DC-57L9005-AS20-E-25 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5071 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.25 | CML-1 | CML: type TBC | 0 | 2018-01-07 | 2016-09-19 | 2015-03-06 07:00 | 2.5 | 0.17573 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9005-AS20-E-25 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.4 | 3.5 | 3.1 | 3 | 0.23805
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71340-01K01 | CML-63 | 80-WF-71340-01K01 CML-63 |  | FPSO 2015 | Pipe Wall Thickness | 22434 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.925 | CML-63 | CML: Reducer | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.9 | 3 | 3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71340-01K01 | CML-49 | 50-WF-71340-01K01 CML-49 |  | FPSO 2015 | Pipe Wall Thickness | 22420 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.975 | CML-49 | CML: Reducer | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 3 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 2.8 | 2.9 | 3.1 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-37 | 100-WF-71340-01K01 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 22408 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 3.025 | CML-37 | CML: Reducer | 0.5 | 2018-02-13 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.10621 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 3.4 | 2.8 | 2.8 | 0.28723
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-24 | 100-WF-71340-01K01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 22395 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 3 | CML-24 | CML: Reducer | 0.5 | 2018-02-13 | 2018-02-13 | 2015-04-19 07:00 | 2.5 | 0.10621 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 3.1 | 2.8 | 3.1 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML21 | 150-WF-71371-01K01 CML21 |  | FPSO 2015 | Pipe Wall Thickness | 7782 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.875 | CML21 | CML: type TBC | 0.5 | 2018-02-10 | 2018-02-10 | 2015-04-18 07:00 | 2.5 | 0.10637 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3 | 2.8 | 2.9 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML16 | 150-WF-71371-01K01 CML16 |  | FPSO 2015 | Pipe Wall Thickness | 7777 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.9 | CML16 | CML: type TBC | 0.5 | 2018-02-10 | 2018-02-10 | 2015-04-18 07:00 | 2.5 | 0.10637 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 3 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 2.8 | 3 | 2.9 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML14 | 150-WF-71371-01K01 CML14 |  | FPSO 2015 | Pipe Wall Thickness | 7775 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.875 | CML14 | CML: type TBC | 0.5 | 2018-02-10 | 2018-02-10 | 2015-04-18 07:00 | 2.5 | 0.10637 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 9 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 2.9 | 2.9 | 2.8 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71371-01K01 | CML10 | 150-WF-71371-01K01 CML10 |  | FPSO 2015 | Pipe Wall Thickness | 7771 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.875 | CML10 | CML: type TBC | 0.5 | 2018-02-10 | 2018-02-10 | 2015-04-18 07:00 | 2.5 | 0.10637 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 3 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.8 | 3 | 2.9 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML15 | 100-WF-71326-01K01 CML15 |  | FPSO 2015 | Pipe Wall Thickness | 7547 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 3.275 | CML15 | CML: type TBC | 0.5 | 2018-01-31 | 2018-01-31 | 2015-04-14 07:00 | 2.5 | 0.10699 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 3.8 | 2.8 | 3.4 | 0.4272
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML134 | 80-WF-71338-01K01 CML134 |  | FPSO 2015 | Pipe Wall Thickness | 7180 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.85 | CML134 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 2.8 | 2.9 | 2.8 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML25 | 80-WF-71338-01K01 CML25 |  | FPSO 2015 | Pipe Wall Thickness | 7071 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.975 | CML25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 3 | 3.1 | 2.8 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML18 | 80-WF-71338-01K01 CML18 |  | FPSO 2015 | Pipe Wall Thickness | 7064 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.9 | CML18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 2.9 | 2.9 | 2.8 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML15 | 80-WF-71338-01K01 CML15 |  | FPSO 2015 | Pipe Wall Thickness | 7061 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.925 | CML15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.9 | 3 | 3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML46 | 80-WF-71338-01K01 CML46 |  | FPSO 2015 | Pipe Wall Thickness | 7092 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 3.325 | CML46 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.4 | 2.8 | 3.5 | 3.6 | 0.3594
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML67 | 100-WF-71308-01K01 CML67 |  | FPSO 2015 | Pipe Wall Thickness | 6985 | Cast fitting, reading taken on adjacent pipework | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.925 | CML67 | CML: type TBC | 0.5 | 2018-01-11 | 2018-01-11 | 2015-04-06 07:00 | 2.5 | 0.10826 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 3.2 | 2.8 | 2.8 | 0.1893
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML63 | 100-WF-71308-01K01 CML63 |  | FPSO 2015 | Pipe Wall Thickness | 6981 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 2.825 | CML63 | CML: type TBC | 0.5 | 2018-01-11 | 2018-01-11 | 2015-04-06 07:00 | 2.5 | 0.10826 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.8 | 2.8 | 2.9 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-18 | 250-WF-71373-01K01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6896 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | Low alarm breach | 4.375 | CML-18 | CML: type TBC | 0.5 | 2016-01-18 | 2015-05-23 | 2015-04-05 07:00 | 3.5 | 0.37948 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 3.8 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.8 | 4 | 4.5 | 5.2 | 0.62383
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71328-01K01 | CML-34 | 100-WF-71328-01K01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 6867 |  | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-12-01 08:53 | [32 empty] | 2.925 | CML-34 | CML: type TBC | 0.5 | 2018-01-09 | 2018-01-09 | 2015-04-05 07:00 | 2.5 | 0.10842 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 3 | 2.8 | 2.9 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-132 | 150-WF-71345-01K01 CML-132 |  | FPSO 2015 | Pipe Wall Thickness | 6806 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.925 | CML-132 | CML: type TBC | 0.5 | 2018-01-06 | 2018-01-06 | 2015-04-04 07:00 | 2.5 | 0.10858 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 3 | 2.9 | 2.8 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-3 | 150-WF-71345-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6677 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.85 | CML-3 | CML: type TBC | 0.5 | 2018-01-06 | 2018-01-06 | 2015-04-04 07:00 | 2.5 | 0.10858 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.8 | 2.8 | 3 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-13 | 150-WF-71345-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6687 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.55 | CML-13 | CML: type TBC | 0.5 | 2018-01-06 | 2018-01-06 | 2015-04-04 07:00 | 2.5 | 0.10858 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3.9 | 3.5 | 4 | 0.54467
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-4 | 150-WF-71345-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6678 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.225 | CML-4 | CML: type TBC | 0.5 | 2018-01-06 | 2018-01-06 | 2015-04-04 07:00 | 2.5 | 0.10858 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 4 | 3.1 | 3 | 2.8 | 0.53151
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-77 | 150-WF-71345-01K01 CML-77 |  | FPSO 2015 | Pipe Wall Thickness | 6751 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 2.875 | CML-77 | CML: type TBC | 0.5 | 2018-01-06 | 2018-01-06 | 2015-04-04 07:00 | 2.5 | 0.10858 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 2.8 | 2.8 | 2.9 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71343-01K01 | CML-15 | 50-WF-71343-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6631 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.075 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 9 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 3.3 | 3.1 | 2.8 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71336-01K01 | CML-12 | 100-WF-71336-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6421 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.125 | CML-12 | CML: type TBC | 0.5 | 2017-12-02 | 2017-12-02 | 2015-03-21 07:00 | 2.5 | 0.11089 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 2.8 | 3.2 | 3.5 | 0.29861
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71336-01K01 | CML-29 | 100-WF-71336-01K01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6438 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.925 | CML-29 | CML: type TBC | 0.5 | 2017-12-02 | 2017-12-02 | 2015-03-21 07:00 | 2.5 | 0.11089 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 3 | 2.8 | 3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71336-01K01 | CML-27 | 100-WF-71336-01K01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6436 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.95 | CML-27 | CML: type TBC | 0.5 | 2017-12-02 | 2017-12-02 | 2015-03-21 07:00 | 2.5 | 0.11089 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 3 | 3.1 | 2.8 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71336-01K01 | CML-35 | 100-WF-71336-01K01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 6444 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3 | CML-35 | CML: type TBC | 0.5 | 2017-12-02 | 2017-12-02 | 2015-03-21 07:00 | 2.5 | 0.11089 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 3.1 | 2.8 | 3 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71336-01K01 | CML-32 | 100-WF-71336-01K01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6441 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.9 | CML-32 | CML: type TBC | 0.5 | 2017-12-02 | 2017-12-02 | 2015-03-21 07:00 | 2.5 | 0.11089 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.8 | 3 | 3 | 0.11547
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9005-AS20-E-25 | CML-6 | 0100-DC-57L9005-AS20-E-25 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5076 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.45 | CML-6 | CML: type TBC | 0 | 2019-10-22 | 2018-01-15 | 2015-03-06 07:00 | 2.5 | 0.12948 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.1 | 6 O'Clock | 25 | 3.38 | 0100-DC-57L9005-AS20-E-25 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.7 | 3.4 | 3.1 | 3.6 | 0.26458
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9005-AS20-E-25 | CML-7 | 0100-DC-57L9005-AS20-E-25 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5077 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.525 | CML-7 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.4 | 12 O'Clock | 25 | 3.38 | 0100-DC-57L9005-AS20-E-25 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.6 | 3.6 | 3.5 | 0.095743
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9005-AS20-E-25 | CML-5 | 0100-DC-57L9005-AS20-E-25 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5075 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.75 | CML-5 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.5 | 12 O'Clock | 25 | 3.38 | 0100-DC-57L9005-AS20-E-25 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.5 | 3.8 | 3.8 | 3.9 | 0.17321
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9005-AS20-E-25 | CML-4 | 0100-DC-57L9005-AS20-E-25 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5074 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.65 | CML-4 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.5 | 6 O'Clock | 25 | 3.38 | 0100-DC-57L9005-AS20-E-25 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.6 | 3.8 | 3.5 | 3.7 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71334-01K01 | CML-4 | 40-WF-71334-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6353 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 6 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 3.1 | 2.8 | 3 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71334-01K01 | CML-2 | 40-WF-71334-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6351 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.95 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 3 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 2.8 | 3 | 3.1 | 0.1291
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9005-AS20-E-25 | CML-3 | 0100-DC-57L9005-AS20-E-25 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5073 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 5.95 | CML-3 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 5.6 | 6 O'Clock | 25 | 3.38 | 0100-DC-57L9005-AS20-E-25 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 6 | 5.6 | 6 | 0.25166
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9005-AS20-E-25 | CML-2 | 0100-DC-57L9005-AS20-E-25 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5072 | Does not exist. Modified | 2015-03-06 07:00 | 2015-03-06 15:00 | [37 empty] | CML-2 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 |  |  | 3.38 | 2.5 | 2.7287 |  | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9005-AS20-E-25 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71360-01K01 | CML-29 | 40-WF-71360-01K01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6192 | CAST Fitting. Readings taken on piping adjacent to fitting | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.975 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 40 | 2.5 | 40-WF-71360-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.9 | 3.2 | 3 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 25-WF-71349-01K01 | CML-2 | 25-WF-71349-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6039 | CAST Fitting. Readings taken on piping adjacent to fitting. | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.8 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 9 O'Clock | 25 | 2.5 | 25-WF-71349-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.8 | 2.8 | 2.8 | 0
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71352-01K01 | CML-4 | 100-WF-71352-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6114 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.475 | CML-4 | CML: type TBC | 0.5 | 2017-11-22 | 2017-11-22 | 2015-03-17 07:00 | 2.5 | 0.11157 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 12 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3.4 | 3.9 | 3.8 | 0.49917
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71352-01K01 | CML-3 | 100-WF-71352-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6113 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.3 | CML-3 | CML: type TBC | 0.5 | 2017-11-22 | 2017-11-22 | 2015-03-17 07:00 | 2.5 | 0.11157 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 12 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3.3 | 4 | 3.1 | 0.5099
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-16 | 50-WF-71351-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6091 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 3.1 | 2.8 | 3.2 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-1 | 50-WF-71351-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6076 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.35 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.9 | 3.9 | 2.8 | 2.8 | 0.63509
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71322-01K01 | CML-36 | 80-WF-71322-01K01 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 6022 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.975 | CML-36 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 3 | 2.8 | 3 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71322-01K01 | CML-31 | 80-WF-71322-01K01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6017 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.175 | CML-31 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 3.9 | 2.8 | 2.9 | 0.49917
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71322-01K01 | CML-25 | 80-WF-71322-01K01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6011 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.925 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 3 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.8 | 3 | 3.1 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71325-01K01 | CML-9 | 50-WF-71325-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5980 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 6 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 3.1 | 2.8 | 3 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71325-01K01 | CML-6 | 50-WF-71325-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5977 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.025 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3 | 3.3 | 3 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71325-01K01 | CML-1 | 50-WF-71325-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5972 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.025 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3 | 3.3 | 3 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71324-01K01 | CML-10 | 80-WF-71324-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5963 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.075 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3 | 3.4 | 3.1 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71324-01K01 | CML-8 | 80-WF-71324-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5961 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.025 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3.1 | 3.3 | 2.9 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71324-01K01 | CML-4 | 80-WF-71324-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5957 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.075 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 6 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.4 | 3.1 | 2.8 | 3 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71327-01K01 | CML-33 | 100-WF-71327-01K01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 5950 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-33 | CML: type TBC | 0.5 | 2017-11-20 | 2017-11-20 | 2015-03-16 07:00 | 2.5 | 0.11174 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 3.1 | 2.9 | 2.8 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71327-01K01 | CML-27 | 100-WF-71327-01K01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 5944 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-27 | CML: type TBC | 0.5 | 2017-11-20 | 2017-11-20 | 2015-03-16 07:00 | 2.5 | 0.11174 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 3 | 2.8 | 2.9 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71327-01K01 | CML-15 | 100-WF-71327-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5932 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-15 | CML: type TBC | 0.5 | 2017-11-20 | 2017-11-20 | 2015-03-16 07:00 | 2.5 | 0.11174 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.8 | 6 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.1 | 3 | 2.8 | 3 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71318-01K01 | CML-34 | 50-WF-71318-01K01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 5916 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.925 | CML-34 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3 | 3 | 2.9 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71316-01K01 | CML-19 | 50-WF-71316-01K01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 5397 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.925 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.9 | 3.1 | 2.9 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71316-01K01 | CML-7 | 50-WF-71316-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5385 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.925 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 3 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 2.8 | 3 | 3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71316-01K01 | CML-1 | 50-WF-71316-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5379 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.075 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3.1 | 3.3 | 3.1 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71312-01K01 | CML-9 | 50-WF-71312-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5327 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 2.9 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 6 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 2.9 | 2.8 | 2.9 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71312-01K01 | CML-5 | 50-WF-71312-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5323 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.15 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 6 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 3.9 | 2.8 | 2.9 | 0.50662
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71312-01K01 | CML-3 | 50-WF-71312-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5321 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 2.9 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.9 | 2.9 | 3 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-7 | 80-WF-71400-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5252 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.025 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.2 | 3 | 2.8 | 3.1 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-5 | 80-WF-71400-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5250 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.15 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3.1 | 3.5 | 3.2 | 0.28868
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-4 | 80-WF-71400-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5249 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.05 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3 | 3.3 | 3.1 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-3 | 80-WF-71400-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5248 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.275 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 3 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.6 | 2.8 | 3.4 | 3.3 | 0.34034
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-1 | 80-WF-71400-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5246 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.2 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 2.9 | 3.2 | 3.9 | 0.49666
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-20 | 80-WF-71400-01K01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 5265 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 3 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 2.8 | 3.1 | 3.1 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-49 | 80-WF-71400-01K01 CML-49 |  | FPSO 2015 | Pipe Wall Thickness | 5294 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.9 | CML-49 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.9 | 2.9 | 3 | 2.8 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-66 | 80-WF-71400-01K01 CML-66 |  | FPSO 2015 | Pipe Wall Thickness | 5311 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.9 | CML-66 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 2.8 | 3.1 | 2.9 | 2.8 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-61 | 80-WF-71400-01K01 CML-61 |  | FPSO 2015 | Pipe Wall Thickness | 5306 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-61 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.8 | 3 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3 | 2.8 | 2.9 | 3.1 | 0.1291
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9001-AS20-00 | CML-10 | 0100-DC-57L9001-AS20-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5066 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.2 | CML-10 | CML: type TBC | 0 | 2016-04-17 | 2015-06-11 | 2015-03-06 07:00 | 2.5 | 0.26822 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.8 | 3 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 3.5 | 2.8 | 3.1 | 3.4 | 0.31623
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-16 | 80-SC-55002-01C02-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8846 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 3.675 | CML-16 | CML: type TBC | 3 | 2015-05-05 | 2015-07-26 | 2015-02-24 07:00 | 2.5 | 1.5504 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 2.8 | 9 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 4.4 | 4.7 | 2.8 | 2.8 | 1.0178
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-9 | 80-FH-43111-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12807 | Inspection not carried due to location access | 2014-02-01 07:00 | 2014-02-01 09:00 | [37 empty] | CML-9 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-02-01 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.1519 |  | 9 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-8 | 80-FH-43111-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12806 | Inspection not carried due to location access | 2014-02-01 07:00 | 2014-02-01 09:00 | [37 empty] | CML-8 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-02-01 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.1519 |  | 9 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-10 | 0600-DH-56L9000-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5040 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [35 empty] | Low alarm breach | 8.675 | CML-10 | CML: type TBC | 3 | 2018-10-13 | 2017-05-21 | 2015-03-05 07:00 | 2.5 | 1.4678 | A1: Outside Quadrant |  | 7.97 | 2.5 | 4.5494 | 7.8 | 12 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.4 | 9.2 | 9.3 | 0.70887
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-103 | 0600-DH-56L9000-AC21M-00 CML-103 |  | FPSO 2015 | Pipe Wall Thickness | 22474 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.95 | CML-103 | CML: Reducer | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-66 | 0600-DH-56L9000-AC21M-00 CML-66 |  | FPSO 2015 | Pipe Wall Thickness | 22437 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 2.975 | CML-66 | CML: Reducer | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-57 | 0600-DH-56L9000-AC21M-00 CML-57 |  | FPSO 2015 | Pipe Wall Thickness | 22428 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 3.275 | CML-57 | CML: Elbow | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.3 | 3.6 | 3.3 | 2.9 | 0.28723
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML17 | 0600-DH-56L9000-AC21M-00 CML17 |  | FPSO 2015 | Pipe Wall Thickness | 7778 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.95 | CML17 | CML: type TBC | 0.5 | 2022-10-23 | 2022-10-23 | 2015-04-18 07:00 | 2.5 | 0.05318 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML13 | 0600-DH-56L9000-AC21M-00 CML13 |  | FPSO 2015 | Pipe Wall Thickness | 7774 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.975 | CML13 | CML: type TBC | 0.5 | 2022-10-23 | 2022-10-23 | 2015-04-18 07:00 | 2.5 | 0.05318 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML12 | 0600-DH-56L9000-AC21M-00 CML12 |  | FPSO 2015 | Pipe Wall Thickness | 7773 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.975 | CML12 | CML: type TBC | 0.5 | 2022-10-23 | 2022-10-23 | 2015-04-18 07:00 | 2.5 | 0.05318 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 2.9 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML11 | 0600-DH-56L9000-AC21M-00 CML11 |  | FPSO 2015 | Pipe Wall Thickness | 7772 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.925 | CML11 | CML: type TBC | 0.5 | 2022-10-23 | 2022-10-23 | 2015-04-18 07:00 | 2.5 | 0.05318 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML7 | 0600-DH-56L9000-AC21M-00 CML7 |  | FPSO 2015 | Pipe Wall Thickness | 7768 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.95 | CML7 | CML: type TBC | 0.5 | 2022-10-23 | 2022-10-23 | 2015-04-18 07:00 | 2.5 | 0.05318 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML5 | 0600-DH-56L9000-AC21M-00 CML5 |  | FPSO 2015 | Pipe Wall Thickness | 7766 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3 | CML5 | CML: type TBC | 0.5 | 2022-10-23 | 2022-10-23 | 2015-04-18 07:00 | 2.5 | 0.05318 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 6 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.2 | 2.9 | 3 | 0.14142
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML4 | 0600-DH-56L9000-AC21M-00 CML4 |  | FPSO 2015 | Pipe Wall Thickness | 7765 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3.15 | CML4 | CML: type TBC | 0.5 | 2022-10-23 | 2022-10-23 | 2015-04-18 07:00 | 2.5 | 0.05318 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3.8 | 3 | 0.43589
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML2 | 0600-DH-56L9000-AC21M-00 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 7763 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 2.925 | CML2 | CML: type TBC | 0.5 | 2022-10-23 | 2022-10-23 | 2015-04-18 07:00 | 2.5 | 0.05318 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 6 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML57 | 0600-DH-56L9000-AC21M-00 CML57 |  | FPSO 2015 | Pipe Wall Thickness | 7302 |  | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 3.425 | CML57 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 4 | 3 | 3.8 | 2.9 | 0.55603
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML47 | 0600-DH-56L9000-AC21M-00 CML47 |  | FPSO 2015 | Pipe Wall Thickness | 7292 |  | 2015-04-09 07:00 | 2015-04-09 15:00 | [36 empty] | 3.225 | CML47 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.2 | 3 | 3.8 | 0.40311
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML102 | 0600-DH-56L9000-AC21M-00 CML102 |  | FPSO 2015 | Pipe Wall Thickness | 7148 |  | 2015-04-07 07:00 | 2015-04-07 15:00 |  |  | Nestor | 2014-11-20 15:37 | [32 empty] | 3.175 | CML102 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.2 | 2.9 | 3.2 | 3.4 | 0.20616
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML96 | 0600-DH-56L9000-AC21M-00 CML96 |  | FPSO 2015 | Pipe Wall Thickness | 7142 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 3.025 | CML96 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.1 | 3 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML33 | 0600-DH-56L9000-AC21M-00 CML33 |  | FPSO 2015 | Pipe Wall Thickness | 7079 | Cast fitting, reading taken on adjacent pipework | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 2.925 | CML33 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-40 | 0600-DH-56L9000-AC21M-00 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 6918 |  | 2015-04-05 07:00 | 2015-04-05 15:00 |  |  | Nestor | 2014-11-27 15:48 | [31 empty] | Low alarm breach | 4.3 | CML-40 | CML: type TBC | 0.5 | 2016-06-27 | 2015-09-20 | 2015-04-05 07:00 | 3.5 | 0.32527 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 3.9 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.9 | 4.5 | 4.7 | 4.1 | 0.36515
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-33 | 0600-DH-56L9000-AC21M-00 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 6911 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | Low alarm breach | 4.275 | CML-33 | CML: type TBC | 0.5 | 2016-06-27 | 2015-09-20 | 2015-04-05 07:00 | 3.5 | 0.32527 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 3.9 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.9 | 4.1 | 4.6 | 4.5 | 0.3304
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-31 | 0600-DH-56L9000-AC21M-00 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6909 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | Low alarm breach | 4.55 | CML-31 | CML: type TBC | 0.5 | 2016-06-27 | 2015-09-20 | 2015-04-05 07:00 | 3.5 | 0.32527 | A3: Inside Quadrant |  | 4 | 3.5 | 3.75 | 3.9 | 6 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 4.5 | 5.2 | 3.9 | 4.6 | 0.53229
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-28 | 0600-DH-56L9000-AC21M-00 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6906 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [35 empty] | Low alarm breach | 4.475 | CML-28 | CML: type TBC | 0.5 | 2016-06-27 | 2015-09-20 | 2015-04-05 07:00 | 3.5 | 0.32527 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 3.9 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.9 | 4.5 | 4.6 | 4.9 | 0.41932
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-128 | 0600-DH-56L9000-AC21M-00 CML-128 |  | FPSO 2015 | Pipe Wall Thickness | 6802 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3 | CML-128 | CML: type TBC | 0.5 | 2022-08-14 | 2022-08-14 | 2015-04-04 07:00 | 2.5 | 0.05429 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3.1 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-71 | 0600-DH-56L9000-AC21M-00 CML-71 |  | FPSO 2015 | Pipe Wall Thickness | 6745 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3 | CML-71 | CML: type TBC | 0.5 | 2022-08-14 | 2022-08-14 | 2015-04-04 07:00 | 2.5 | 0.05429 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 3 | 2.9 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-83 | 0600-DH-56L9000-AC21M-00 CML-83 |  | FPSO 2015 | Pipe Wall Thickness | 6757 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.025 | CML-83 | CML: type TBC | 0.5 | 2022-08-14 | 2022-08-14 | 2015-04-04 07:00 | 2.5 | 0.05429 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.1 | 3.1 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-22 | 0600-DH-56L9000-AC21M-00 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6655 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 2.975 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-30 | 0600-DH-56L9000-AC21M-00 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6663 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 11:59 | [32 empty] | 3 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3.1 | 2.9 | 2.9 | 0.11547
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-29 | 0600-DH-56L9000-AC21M-00 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6662 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 11:38 | [32 empty] | 2.95 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-27 | 0600-DH-56L9000-AC21M-00 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6660 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 11:43 | [32 empty] | 3 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 2.9 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-24 | 0600-DH-56L9000-AC21M-00 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6657 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 11:41 | [32 empty] | 2.975 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-23 | 0600-DH-56L9000-AC21M-00 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6656 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.05 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 3.2 | 2.9 | 0.1291
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-21 | 0600-DH-56L9000-AC21M-00 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6654 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 2.975 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-15 | 0600-DH-56L9000-AC21M-00 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6648 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:23 | [32 empty] | 2.95 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6645 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:22 | [32 empty] | 3 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6640 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:10 | [32 empty] | 2.95 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6639 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:09 | [32 empty] | 3.025 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3.1 | 2.9 | 3 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-16 | 0600-DH-56L9000-AC21M-00 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6632 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.125 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.4 | 3.1 | 0.20616
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-4 | 0600-DH-56L9000-AC21M-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6608 |  | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.15 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71342-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.4 | 3.1 | 2.9 | 3.2 | 0.20817
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6422 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.05 | CML-13 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.2 | 3.1 | 2.9 | 0.1291
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6409 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.925 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71356-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6408 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.975 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71356-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6407 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.975 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71356-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.1 | 2.9 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-28 | 0600-DH-56L9000-AC21M-00 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6437 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.025 | CML-28 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 12 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.1 | 3.1 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-26 | 0600-DH-56L9000-AC21M-00 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6435 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.9 | CML-26 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 2.9 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-22 | 0600-DH-56L9000-AC21M-00 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6431 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.95 | CML-22 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-21 | 0600-DH-56L9000-AC21M-00 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6430 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.975 | CML-21 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-20 | 0600-DH-56L9000-AC21M-00 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6429 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.975 | CML-20 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 6 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-19 | 0600-DH-56L9000-AC21M-00 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6428 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.95 | CML-19 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-18 | 0600-DH-56L9000-AC21M-00 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6427 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.975 | CML-18 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-17 | 0600-DH-56L9000-AC21M-00 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6426 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.95 | CML-17 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6423 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.1 | CML-14 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.3 | 3.2 | 2.9 | 0.18257
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-36 | 0600-DH-56L9000-AC21M-00 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 6445 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.95 | CML-36 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-34 | 0600-DH-56L9000-AC21M-00 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 6443 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.975 | CML-34 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-33 | 0600-DH-56L9000-AC21M-00 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 6442 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.975 | CML-33 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 12 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-31 | 0600-DH-56L9000-AC21M-00 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6440 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.95 | CML-31 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3.1 | 2.9 | 0.1
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-30 | 0600-DH-56L9000-AC21M-00 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6439 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 2.9 | CML-30 | CML: type TBC | 0.5 | 2022-06-05 | 2022-06-05 | 2015-03-21 07:00 | 2.5 | 0.05545 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 2.9 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-9 | 0600-DH-56L9000-AC21M-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6288 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.925 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-8 | 0600-DH-56L9000-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6287 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6286 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.95 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6285 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3.1 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6284 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.95 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6281 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.1 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.3 | 3.1 | 0.1633
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6291 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-9 | 0600-DH-56L9000-AC21M-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5039 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [36 empty] | 10.475 | CML-9 | CML: type TBC | 3 | 2031-11-11 | 2027-04-20 | 2015-03-05 07:00 | 2.5 | 0.44914 | A4: Left Quadrant |  | 7.97 | 2.5 | 4.5494 | 10 | 9 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.8 | 10.9 | 10.2 | 10 | 0.44253
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-8 | 0600-DH-56L9000-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5038 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [36 empty] | 10.3 | CML-8 | CML: type TBC | 3 | 2031-11-11 | 2027-04-20 | 2015-03-05 07:00 | 2.5 | 0.44914 | A1: Outside Quadrant |  | 7.97 | 2.5 | 4.5494 | 10 | 12 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 10.8 | 10.1 | 10.3 | 0.3559
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5032 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [36 empty] | 10.6 | CML-2 | CML: type TBC | 3 | 2034-01-10 | 2028-12-10 | 2015-03-05 07:00 | 2.5 | 0.40283 | A1: Outside Quadrant |  | 7.97 | 2.5 | 4.5494 | 10.1 | 12 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.1 | 10.6 | 11.3 | 10.4 | 0.5099
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-4 | 0600-DH-56L9000-AC21M-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5034 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [36 empty] | 10.675 | CML-4 | CML: type TBC | 3 | 2040-04-19 | 2033-09-12 | 2015-03-05 07:00 | 2.5 | 0.31023 | A3: Inside Quadrant |  | 7.97 | 2.5 | 4.5494 | 10.3 | 6 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.8 | 10.9 | 10.3 | 10.7 | 0.263
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5037 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [36 empty] | 10.75 | CML-7 | CML: type TBC | 3 | 2051-11-29 | 2042-07-01 | 2015-03-05 07:00 | 2.5 | 0.21762 | A2: Right Quadrant |  | 7.97 | 2.5 | 4.5494 | 10.5 | 3 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.6 | 10.5 | 10.6 | 11.3 | 0.36968
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6363 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6362 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.95 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6352 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.025 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3.1 | 2.9 | 3 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6350 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5035 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [36 empty] | 10.675 | CML-5 | CML: type TBC | 3 | 2051-11-29 | 2042-07-01 | 2015-03-05 07:00 | 2.5 | 0.21762 | A3: Inside Quadrant |  | 7.97 | 2.5 | 4.5494 | 10.5 | 6 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.6 | 10.8 | 10.5 | 10.8 | 0.15
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5033 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [36 empty] | 10.775 | CML-3 | CML: type TBC | 3 | 2062-06-03 | 2050-06-20 | 2015-03-05 07:00 | 2.5 | 0.17132 | A1: Outside Quadrant |  | 7.97 | 2.5 | 4.5494 | 10.6 | 12 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.6 | 10.8 | 10.8 | 10.9 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6386 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.05 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.2 | 3 | 2.9 | 3.1 | 0.1291
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6382 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6373 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.2 | 3.2 | 0.15
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6390 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.2 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 40 | 2.5 | 40-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.3 | 3.5 | 3.1 | 0.2582
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6389 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.95 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6387 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.95 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-31 | 0600-DH-56L9000-AC21M-00 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6310 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-31 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-29 | 0600-DH-56L9000-AC21M-00 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6308 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-36 | 0600-DH-56L9000-AC21M-00 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 6315 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-36 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-25 | 0600-DH-56L9000-AC21M-00 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6304 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.925 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-21 | 0600-DH-56L9000-AC21M-00 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6300 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-16 | 0600-DH-56L9000-AC21M-00 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6295 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 2.975 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6253 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 3 | 2.9 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6246 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.025 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 40 | 2.5 | 40-WF-71331-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.1 | 3 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-4 | 0600-DH-56L9000-AC21M-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6245 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.05 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 40 | 2.5 | 40-WF-71331-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.1 | 3.2 | 0.1291
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6264 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3.1 | 2.9 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6254 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.025 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3.1 | 3 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6275 | Cast Fitting, Reading taken on adjacent piping. | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 2.975 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 25 | 2.5 | 25-WF-71357-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6230 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.025 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3.2 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6227 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.075 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71348-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.4 | 3 | 0.22174
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6226 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.15 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71348-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.4 | 3.2 | 2.9 | 3.1 | 0.20817
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6223 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.3 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71348-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.2 | 3.3 | 3.8 | 0.37417
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-15 | 0600-DH-56L9000-AC21M-00 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6208 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.975 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6207 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.95 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6206 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.975 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6205 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.95 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6204 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.95 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-10 | 0600-DH-56L9000-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6203 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.975 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-9 | 0600-DH-56L9000-AC21M-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6202 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.975 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6200 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.95 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-30 | 0600-DH-56L9000-AC21M-00 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6193 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71360-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3.1 | 2.9 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-28 | 0600-DH-56L9000-AC21M-00 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6191 | CAST Fitting. Readings taken on piping adjacent to fitting | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.975 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 40 | 2.5 | 40-WF-71360-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3.1 | 3 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-27 | 0600-DH-56L9000-AC21M-00 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6190 | CAST Fitting. Readings taken on piping adjacent to fitting | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.975 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 40 | 2.5 | 40-WF-71360-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-26 | 0600-DH-56L9000-AC21M-00 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6189 | CAST Fitting. Readings taken on piping adjacent to fitting | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.95 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71360-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-25 | 0600-DH-56L9000-AC21M-00 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6188 | CAST Fitting. Readings taken on piping adjacent to fitting | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.95 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71360-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-24 | 0600-DH-56L9000-AC21M-00 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6187 | CAST Fitting. Readings taken on piping adjacent to fitting | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.95 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71360-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-23 | 0600-DH-56L9000-AC21M-00 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6186 | CAST Fitting. Readings taken on piping adjacent to fitting | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 2.95 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71360-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5991 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.075 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.2 | 3.1 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5988 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.125 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.2 | 3.4 | 3 | 0.22174
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5987 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.075 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.2 | 3.2 | 2.9 | 0.15
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5993 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.925 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-51 | 0600-DH-56L9000-AC21M-00 CML-51 |  | FPSO 2015 | Pipe Wall Thickness | 6037 | CAST Fitting. Readings taken on piping adjacent to fitting. | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.95 | CML-51 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-50 | 0600-DH-56L9000-AC21M-00 CML-50 |  | FPSO 2015 | Pipe Wall Thickness | 6036 | CAST Fitting. Readings taken on piping adjacent to fitting. | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.975 | CML-50 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-49 | 0600-DH-56L9000-AC21M-00 CML-49 |  | FPSO 2015 | Pipe Wall Thickness | 6035 | CAST Fitting. Readings taken on piping adjacent to fitting. | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.95 | CML-49 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-47 | 0600-DH-56L9000-AC21M-00 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 6033 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.975 | CML-47 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-32 | 0600-DH-56L9000-AC21M-00 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6107 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.975 | CML-32 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-31 | 0600-DH-56L9000-AC21M-00 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6106 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3 | CML-31 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 3 | 2.9 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-25 | 0600-DH-56L9000-AC21M-00 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6100 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 2.9 | 3.1 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6112 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.45 | CML-2 | CML: type TBC | 0.5 | 2022-05-16 | 2022-05-16 | 2015-03-17 07:00 | 2.5 | 0.05579 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 4.1 | 3.4 | 3.4 | 2.9 | 0.49329
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-35 | 0600-DH-56L9000-AC21M-00 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 6110 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.925 | CML-35 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6122 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.15 | CML-12 | CML: type TBC | 0.5 | 2022-05-16 | 2022-05-16 | 2015-03-17 07:00 | 2.5 | 0.05579 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 12 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.4 | 3 | 3.3 | 0.23805
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-40 | 0600-DH-56L9000-AC21M-00 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 6026 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.975 | CML-40 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-35 | 0600-DH-56L9000-AC21M-00 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 6021 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.975 | CML-35 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-34 | 0600-DH-56L9000-AC21M-00 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 6020 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.95 | CML-34 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-33 | 0600-DH-56L9000-AC21M-00 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 6019 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.95 | CML-33 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-32 | 0600-DH-56L9000-AC21M-00 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6018 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.075 | CML-32 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3.3 | 2.9 | 3 | 0.17078
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-27 | 0600-DH-56L9000-AC21M-00 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6013 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.975 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-26 | 0600-DH-56L9000-AC21M-00 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6012 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.1 | 3.1 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-23 | 0600-DH-56L9000-AC21M-00 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6009 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.975 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-20 | 0600-DH-56L9000-AC21M-00 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6006 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.125 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.2 | 3.3 | 3.1 | 0.17078
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-19 | 0600-DH-56L9000-AC21M-00 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6005 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.95 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-18 | 0600-DH-56L9000-AC21M-00 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6004 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.925 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-17 | 0600-DH-56L9000-AC21M-00 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6003 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.975 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5999 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.925 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5998 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 2.95 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-9 | 0600-DH-56L9000-AC21M-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5995 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.1 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.3 | 3.1 | 0.1633
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5984 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5982 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-4 | 0600-DH-56L9000-AC21M-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5975 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.025 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3.2 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-16 | 0600-DH-56L9000-AC21M-00 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 5969 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5967 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3.1 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-9 | 0600-DH-56L9000-AC21M-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5962 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.175 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.5 | 3.1 | 2.9 | 3.2 | 0.25
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5960 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.45 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 4 | 2.9 | 3.2 | 3.7 | 0.49329
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5959 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-36 | 0600-DH-56L9000-AC21M-00 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 5953 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-36 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.1 | 3 | 2.9 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-35 | 0600-DH-56L9000-AC21M-00 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 5952 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-35 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 12 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-34 | 0600-DH-56L9000-AC21M-00 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 5951 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-34 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 6 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-32 | 0600-DH-56L9000-AC21M-00 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 5949 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-32 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 6 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-31 | 0600-DH-56L9000-AC21M-00 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 5948 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-31 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 6 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-30 | 0600-DH-56L9000-AC21M-00 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 5947 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-30 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 6 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-29 | 0600-DH-56L9000-AC21M-00 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 5946 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-29 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3.1 | 3 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-26 | 0600-DH-56L9000-AC21M-00 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 5943 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.925 | CML-26 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-24 | 0600-DH-56L9000-AC21M-00 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 5941 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-24 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-22 | 0600-DH-56L9000-AC21M-00 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 5939 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-22 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-20 | 0600-DH-56L9000-AC21M-00 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 5937 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-20 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 3 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-19 | 0600-DH-56L9000-AC21M-00 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 5936 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-19 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-18 | 0600-DH-56L9000-AC21M-00 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5935 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-18 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 6 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5931 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-14 | CML: type TBC | 0.5 | 2022-05-11 | 2022-05-11 | 2015-03-16 07:00 | 2.5 | 0.05587 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-32 | 0600-DH-56L9000-AC21M-00 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 5914 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-32 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-31 | 0600-DH-56L9000-AC21M-00 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 5913 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-31 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-29 | 0600-DH-56L9000-AC21M-00 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 5911 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-28 | 0600-DH-56L9000-AC21M-00 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 5910 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3.1 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-27 | 0600-DH-56L9000-AC21M-00 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 5909 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 3.1 | 0.1
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-25 | 0600-DH-56L9000-AC21M-00 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 5907 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-24 | 0600-DH-56L9000-AC21M-00 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 5906 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-21 | 0600-DH-56L9000-AC21M-00 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 5903 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-20 | 0600-DH-56L9000-AC21M-00 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 5902 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-18 | 0600-DH-56L9000-AC21M-00 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5900 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.925 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-17 | 0600-DH-56L9000-AC21M-00 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5899 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-33 | 0600-DH-56L9000-AC21M-00 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 5915 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-33 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3.1 | 3 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-16 | 0600-DH-56L9000-AC21M-00 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 5898 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-15 | 0600-DH-56L9000-AC21M-00 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5897 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5896 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5893 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.95 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-10 | 0600-DH-56L9000-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5892 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5885 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.125 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.2 | 3.4 | 3 | 2.9 | 0.22174
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5888 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 2.975 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5490 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.15 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.4 | 3.2 | 0.20817
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5491 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.175 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.3 | 2.9 | 3 | 3.5 | 0.27538
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-49 | 0600-DH-56L9000-AC21M-00 CML-49 |  | FPSO 2015 | Pipe Wall Thickness | 5534 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 2.975 | CML-49 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 2.9 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-46 | 0600-DH-56L9000-AC21M-00 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 5531 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.5 | CML-46 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.6 | 3.7 | 3.8 | 0.40825
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-24 | 0600-DH-56L9000-AC21M-00 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 5402 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.925 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-23 | 0600-DH-56L9000-AC21M-00 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 5401 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-22 | 0600-DH-56L9000-AC21M-00 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 5400 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-20 | 0600-DH-56L9000-AC21M-00 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 5398 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-17 | 0600-DH-56L9000-AC21M-00 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5395 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.975 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.1 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-27 | 0600-DH-56L9000-AC21M-00 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 5405 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3.1 | 2.9 | 2.9 | 0.11547
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-25 | 0600-DH-56L9000-AC21M-00 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 5403 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.975 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-30 | 0600-DH-56L9000-AC21M-00 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 5408 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.975 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-16 | 0600-DH-56L9000-AC21M-00 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 5394 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-15 | 0600-DH-56L9000-AC21M-00 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5393 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.025 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 2.9 | 3.1 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5392 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.975 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-10 | 0600-DH-56L9000-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5388 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 2.9 | 2.9 | 0.1
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-9 | 0600-DH-56L9000-AC21M-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5387 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-8 | 0600-DH-56L9000-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5386 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.025 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.1 | 3.1 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5381 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.075 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.2 | 3.1 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5380 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.125 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.4 | 3.1 | 2.9 | 3.1 | 0.20616
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5431 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.975 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-8 | 0600-DH-56L9000-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5428 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.925 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5425 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-4 | 0600-DH-56L9000-AC21M-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5424 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5422 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3.1 | 2.9 | 0.1
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-42 | 0600-DH-56L9000-AC21M-00 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 5420 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.975 | CML-42 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3.1 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-40 | 0600-DH-56L9000-AC21M-00 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 5418 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.975 | CML-40 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-20 | 0600-DH-56L9000-AC21M-00 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 5440 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.925 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-17 | 0600-DH-56L9000-AC21M-00 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5437 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5434 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.975 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-39 | 0600-DH-56L9000-AC21M-00 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 5417 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3 | CML-39 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 2.9 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-38 | 0600-DH-56L9000-AC21M-00 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 5416 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3 | CML-38 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 2.9 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-36 | 0600-DH-56L9000-AC21M-00 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 5414 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.975 | CML-36 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-34 | 0600-DH-56L9000-AC21M-00 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 5412 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-34 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-33 | 0600-DH-56L9000-AC21M-00 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 5411 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 2.95 | CML-33 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-31 | 0600-DH-56L9000-AC21M-00 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 5409 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3 | CML-31 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3.1 | 2.9 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-32 | 0600-DH-56L9000-AC21M-00 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 5410 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3 | CML-32 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 3 | 2.9 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-18 | 0600-DH-56L9000-AC21M-00 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5179 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-15 | 0600-DH-56L9000-AC21M-00 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5260 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5259 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5258 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5257 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3.1 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5256 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.1 | 2.9 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-10 | 0600-DH-56L9000-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5255 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.1 | 2.9 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5251 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.075 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3.3 | 3 | 2.9 | 0.17078
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5247 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.1 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.3 | 3.1 | 2.9 | 3.1 | 0.1633
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-29 | 0600-DH-56L9000-AC21M-00 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 5274 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.925 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-28 | 0600-DH-56L9000-AC21M-00 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 5273 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-27 | 0600-DH-56L9000-AC21M-00 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 5272 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.925 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-26 | 0600-DH-56L9000-AC21M-00 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 5271 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-24 | 0600-DH-56L9000-AC21M-00 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 5269 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.1 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-18 | 0600-DH-56L9000-AC21M-00 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5263 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-17 | 0600-DH-56L9000-AC21M-00 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5262 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.1 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-16 | 0600-DH-56L9000-AC21M-00 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 5261 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-41 | 0600-DH-56L9000-AC21M-00 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 5286 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-41 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-39 | 0600-DH-56L9000-AC21M-00 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 5284 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.925 | CML-39 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-37 | 0600-DH-56L9000-AC21M-00 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 5282 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.9 | CML-37 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 2.9 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-33 | 0600-DH-56L9000-AC21M-00 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 5278 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-33 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-35 | 0600-DH-56L9000-AC21M-00 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 5280 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-35 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-60 | 0600-DH-56L9000-AC21M-00 CML-60 |  | FPSO 2015 | Pipe Wall Thickness | 5305 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-60 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-59 | 0600-DH-56L9000-AC21M-00 CML-59 |  | FPSO 2015 | Pipe Wall Thickness | 5304 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.1 | CML-59 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.3 | 3.1 | 0.1633
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-57 | 0600-DH-56L9000-AC21M-00 CML-57 |  | FPSO 2015 | Pipe Wall Thickness | 5302 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.05 | CML-57 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3.3 | 3.1 | 0.19149
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-52 | 0600-DH-56L9000-AC21M-00 CML-52 |  | FPSO 2015 | Pipe Wall Thickness | 5297 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-52 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-51 | 0600-DH-56L9000-AC21M-00 CML-51 |  | FPSO 2015 | Pipe Wall Thickness | 5296 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-51 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-50 | 0600-DH-56L9000-AC21M-00 CML-50 |  | FPSO 2015 | Pipe Wall Thickness | 5295 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-50 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-48 | 0600-DH-56L9000-AC21M-00 CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 5293 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.925 | CML-48 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-47 | 0600-DH-56L9000-AC21M-00 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 5292 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-47 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 2.9 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-46 | 0600-DH-56L9000-AC21M-00 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 5291 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-46 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.1 | 2.9 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-65 | 0600-DH-56L9000-AC21M-00 CML-65 |  | FPSO 2015 | Pipe Wall Thickness | 5310 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-65 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-63 | 0600-DH-56L9000-AC21M-00 CML-63 |  | FPSO 2015 | Pipe Wall Thickness | 5308 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-63 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-62 | 0600-DH-56L9000-AC21M-00 CML-62 |  | FPSO 2015 | Pipe Wall Thickness | 5307 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.925 | CML-62 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 2.9 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5175 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.1 | 3 | 2.9 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5174 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5172 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-10 | 0600-DH-56L9000-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5171 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 3 | 2.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-8 | 0600-DH-56L9000-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5169 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5168 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3 | 2.9 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5166 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3.1 | 2.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-4 | 0600-DH-56L9000-AC21M-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5165 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 9 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 2.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5164 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5163 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.95 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5162 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 2.975 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 2.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 2.9 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Potable Water (53) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-8 | 0600-DH-56L9000-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5112 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 3.425 | CML-8 | CML: type TBC | 0 | 2016-12-23 | 2015-12-12 | 2015-03-06 07:00 | 2.5 | 0.22197 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.9 | 12 O'Clock | 25 | 3.38 | 0100-WZ-53L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.5 | 3.6 | 3.7 | 0.3594
DC01 | Montara_Topside | No | Potable Water (53) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5111 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 3 | CML-7 | CML: type TBC | 0 | 2016-12-23 | 2015-12-12 | 2015-03-06 07:00 | 2.5 | 0.22197 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.9 | 9 O'Clock | 25 | 3.38 | 0100-WZ-53L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3 | 3.1 | 3 | 2.9 | 0.08165
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-8 | 0600-DH-56L9000-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5085 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.35 | CML-8 | CML: type TBC | 0 | 2016-12-23 | 2015-12-12 | 2015-03-06 07:00 | 2.5 | 0.22197 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.9 | 6 O'Clock | 25 | 3.38 | 0100-DC-57L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.6 | 3.5 | 2.9 | 3.4 | 0.31091
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5062 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.225 | CML-6 | CML: type TBC | 0 | 2016-12-23 | 2015-12-12 | 2015-03-06 07:00 | 2.5 | 0.22197 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.9 | 3 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.3 | 2.9 | 3.2 | 3.5 | 0.25
DC01 | Montara_Topside | No | Compressed Air (63) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5021 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.225 | CML-12 | CML: type TBC | 0 | 2016-12-19 | 2015-12-10 | 2015-03-04 07:00 | 2.5 | 0.22254 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.9 | 12 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.1 | 3.7 | 3.2 | 0.34034
DC01 | Montara_Topside | No | Compressed Air (63) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5020 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.275 | CML-11 | CML: type TBC | 0 | 2016-12-19 | 2015-12-10 | 2015-03-04 07:00 | 2.5 | 0.22254 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.9 | 3 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.2 | 2.9 | 3.3 | 3.7 | 0.3304
DC01 | Montara_Topside | No | Compressed Air (63) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-9 | 0600-DH-56L9000-AC21M-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5018 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.025 | CML-9 | CML: type TBC | 0 | 2016-12-19 | 2015-12-10 | 2015-03-04 07:00 | 2.5 | 0.22254 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.9 | 3 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 2.9 | 3.3 | 3 | 0.1893
DC01 | Montara_Topside | No | Compressed Air (63) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5014 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.175 | CML-5 | CML: type TBC | 0 | 2016-12-19 | 2015-12-10 | 2015-03-04 07:00 | 2.5 | 0.22254 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 2.9 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 3.2 | 3.6 | 3 | 2.9 | 0.30957
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8537 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 3.2 | CML-3 | CML: type TBC | 0.5 | 2021-10-23 | 2021-10-23 | 2015-02-04 07:30 | 2.5 | 0.05951 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 12 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.3 | 3.3 | 3.3 | 0.2
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8536 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 3.425 | CML-2 | CML: type TBC | 0.5 | 2021-10-23 | 2021-10-23 | 2015-02-04 07:30 | 2.5 | 0.05951 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 12 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.4 | 4 | 3.4 | 0.45
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8535 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 3.35 | CML-1 | CML: type TBC | 0.5 | 2021-10-23 | 2021-10-23 | 2015-02-04 07:30 | 2.5 | 0.05951 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 2.9 | 12 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 2.9 | 3.4 | 3.9 | 3.2 | 0.42032
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 | High Priority | FPSO 2016 | Pipe Wall Thickness | 24498 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.4 | CML-13 | CML: Elbow | 3 | 2017-02-17 | 2017-07-13 | 2016-07-09 07:00 | 2.5 | 0.81734 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 | 0.68887 | 3.7 | 3.6 | 3.3 | 3 | 0.31623
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 | High Priority | FPSO 2016 | Pipe Wall Thickness | 24497 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.375 | CML-12 | CML: Elbow | 3 | 2017-02-17 | 2017-07-13 | 2016-07-09 07:00 | 2.5 | 0.81734 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 | 0.09841 | 3.2 | 3.6 | 3.7 | 3 | 0.3304
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML - 2 | 0600-DH-56L9000-AC21M-00 CML - 2 |  | FPSO 2015 | Pipe Wall Thickness | 22611 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 3.2 | CML - 2 | CML: Reducer | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 3 | 3 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.3 | 3.4 | 0.18257
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5031 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [36 empty] | 10.775 | CML-1 | CML: type TBC | 3 | 2062-06-03 | 2050-06-20 | 2015-03-05 07:00 | 2.5 | 0.17132 | A1: Outside Quadrant |  | 7.97 | 2.5 | 4.5494 | 10.6 | 12 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.6 | 10.8 | 10.8 | 10.9 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-113 | 0600-DH-56L9000-AC21M-00 CML-113 |  | FPSO 2015 | Pipe Wall Thickness | 22484 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 3.075 | CML-113 | CML: Reducer | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 12 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3.1 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-81 | 0600-DH-56L9000-AC21M-00 CML-81 |  | FPSO 2015 | Pipe Wall Thickness | 22452 | Cast fitting. Reading taken adjacent to fitting. | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 3.25 | CML-81 | CML: Reducer | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 80 | 2.5 | 80-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.3 | 3.6 | 3.1 | 0.26458
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22372 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 3.375 | CML-1 | CML: Elbow | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 4 | 3.1 | 3.4 | 3 | 0.45
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML22 | 0600-DH-56L9000-AC21M-00 CML22 |  | FPSO 2015 | Pipe Wall Thickness | 7783 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3 | CML22 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML20 | 0600-DH-56L9000-AC21M-00 CML20 |  | FPSO 2015 | Pipe Wall Thickness | 7781 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 3 | CML20 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML38 | 0600-DH-56L9000-AC21M-00 CML38 |  | FPSO 2015 | Pipe Wall Thickness | 7570 | Cast fitting. Readings taken adjacent to fitting. | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 3.05 | CML38 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3.1 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML20 | 0600-DH-56L9000-AC21M-00 CML20 |  | FPSO 2015 | Pipe Wall Thickness | 7552 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 3.6 | CML20 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.8 | 3 | 4 | 3.6 | 0.43205
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML10 | 0600-DH-56L9000-AC21M-00 CML10 |  | FPSO 2015 | Pipe Wall Thickness | 7542 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 3.1 | CML10 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.2 | 3 | 3.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-32 | 0600-DH-56L9000-AC21M-00 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6910 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.4 | CML-32 | CML: type TBC | 0.5 | 2017-02-06 | 2016-03-06 | 2015-04-05 07:00 | 3.5 | 0.27106 | A3: Inside Quadrant |  | 4 | 3.5 | 3.75 | 4 | 6 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 5 | 4.1 | 4 | 4.5 | 0.45461
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-21 | 0600-DH-56L9000-AC21M-00 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6899 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.375 | CML-21 | CML: type TBC | 0.5 | 2017-02-06 | 2016-03-06 | 2015-04-05 07:00 | 3.5 | 0.27106 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 4 | 4.5 | 4.5 | 4.5 | 0.25
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-9 | 0600-DH-56L9000-AC21M-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6887 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.5 | CML-9 | CML: type TBC | 0.5 | 2017-02-06 | 2016-03-06 | 2015-04-05 07:00 | 3.5 | 0.27106 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 4.3 | 4.4 | 5.3 | 4 | 0.55976
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6884 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.3 | CML-6 | CML: type TBC | 0.5 | 2017-02-06 | 2016-03-06 | 2015-04-05 07:00 | 3.5 | 0.27106 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 4 | 4.3 | 4.6 | 4.3 | 0.24495
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6835 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 3.4 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 12 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.3 | 3.3 | 4 | 0.42426
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6680 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.2 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.5 | 3 | 3.3 | 3 | 0.24495
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-37 | 0600-DH-56L9000-AC21M-00 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 6711 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.025 | CML-37 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3.1 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-33 | 0600-DH-56L9000-AC21M-00 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 6707 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.05 | CML-33 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-28 | 0600-DH-56L9000-AC21M-00 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6661 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 11:43 | [32 empty] | 3 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-26 | 0600-DH-56L9000-AC21M-00 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6659 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 11:42 | [32 empty] | 3.025 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-20 | 0600-DH-56L9000-AC21M-00 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6653 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:26 | [32 empty] | 3 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-18 | 0600-DH-56L9000-AC21M-00 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6651 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:24 | [32 empty] | 3 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-16 | 0600-DH-56L9000-AC21M-00 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6649 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:23 | [32 empty] | 3.025 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6647 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:22 | [32 empty] | 3.05 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3.1 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6646 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:22 | [32 empty] | 3.025 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-10 | 0600-DH-56L9000-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6643 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:14 | [32 empty] | 3.05 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-8 | 0600-DH-56L9000-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6641 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:13 | [32 empty] | 3.025 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6638 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:07 | [32 empty] | 3.05 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.2 | 3 | 3 | 0.1
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-4 | 0600-DH-56L9000-AC21M-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6637 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:07 | [32 empty] | 3.1 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.2 | 3.1 | 3.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-12 | 0600-DH-56L9000-AC21M-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6628 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.1 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.2 | 3.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-10 | 0600-DH-56L9000-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6626 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.075 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3.1 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-8 | 0600-DH-56L9000-AC21M-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6624 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.1 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.2 | 3.1 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6623 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.075 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3.1 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6621 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.075 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.1 | 3.1 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-4 | 0600-DH-56L9000-AC21M-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6612 | Cast fitting, reading taken on adjacent pipework | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.05 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 40 | 2.5 | 40-WF-71344-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3.1 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-2 | 0600-DH-56L9000-AC21M-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6610 | Cast fitting, reading taken on adjacent pipework | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.1 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 40 | 2.5 | 40-WF-71344-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.2 | 3.1 | 3 | 3.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-7 | 0600-DH-56L9000-AC21M-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6615 | Cast fitting, reading taken on adjacent pipework | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.075 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 40 | 2.5 | 40-WF-71344-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3.1 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-5 | 0600-DH-56L9000-AC21M-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6613 | Cast fitting, reading taken on adjacent pipework | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.075 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 40 | 2.5 | 40-WF-71344-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3.1 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6420 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.1 | CML-11 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.2 | 3.2 | 3 | 3 | 0.11547
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-10 | 0600-DH-56L9000-AC21M-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6419 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.1 | CML-10 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.2 | 3.1 | 3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-1 | 0600-DH-56L9000-AC21M-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6410 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.825 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 6 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 4.4 | 4.3 | 3 | 3.6 | 0.65511
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-24 | 0600-DH-56L9000-AC21M-00 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6433 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.075 | CML-24 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3.1 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-23 | 0600-DH-56L9000-AC21M-00 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6432 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.075 | CML-23 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3.1 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-16 | 0600-DH-56L9000-AC21M-00 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6425 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3 | CML-16 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-15 | 0600-DH-56L9000-AC21M-00 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6424 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3 | CML-15 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-3 | 0600-DH-56L9000-AC21M-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6282 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.2 | 3.1 | 3 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-13 | 0600-DH-56L9000-AC21M-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6292 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.025 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-11 | 0600-DH-56L9000-AC21M-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6290 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-14 | 0600-DH-56L9000-AC21M-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6293 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 0600-DH-56L9000-AC21M-00 | CML-6 | 0600-DH-56L9000-AC21M-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5036 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | [36 empty] | 11.2 | CML-6 | CML: type TBC | 3 | 2120-07-19 | 2094-07-12 | 2015-03-05 07:00 | 2.5 | 0.07871 | A1: Outside Quadrant |  | 7.97 | 2.5 | 4.5494 | 10.8 | 12 O'Clock | 150 | 10.97 | 0600-DN-56L9000-AC21M-00 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 11.1 | 11.7 | 11.2 | 0.37417
PG07 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9008-GD20-P-50 | CML-3 | 150-PG-23L9008-GD20-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6470 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [35 empty] | Low alarm breach | 21.15 | CML-3 | CML: Elbow | 0 | 2022-10-07 | 2018-12-22 | 2014-07-22 07:30 | 9.6 | 1.2658 | A4: Left Quadrant |  | 21.95 | 9.6 | 14.4031 | 20 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9008-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 21.5 | 21.1 | 22 | 20 | 0.85049
PG07 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9008-GD20-P-50 | CML-1 | 150-PG-23L9008-GD20-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6468 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [35 empty] | Low alarm breach | 21.55 | CML-1 | CML: Elbow | 0 | 2028-03-23 | 2022-04-23 | 2014-07-22 07:30 | 9.6 | 0.81138 | A4: Left Quadrant |  | 21.95 | 9.6 | 14.4031 | 20.7 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9008-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 23.3 | 21.1 | 21.1 | 20.7 | 1.1818
PG07 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9008-GD20-P-50 | CML-5 | 150-PG-23L9008-GD20-P-50 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6472 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [35 empty] | Low alarm breach | 21.1 | CML-5 | CML: Equal Tee | 0 | 2035-05-21 | 2026-09-07 | 2014-07-22 07:30 | 9.6 | 0.55174 | A1: Outside Quadrant |  | 21.95 | 9.6 | 14.4031 | 21.1 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9008-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 21.1 | 21.1 | 21.1 | 21.1 | 0
PG07 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9008-GD20-P-50 | CML-2 | 150-PG-23L9008-GD20-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6469 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [35 empty] | Low alarm breach | 21.8 | CML-2 | CML: Reducer | 0 | 2035-05-21 | 2026-09-07 | 2014-07-22 07:30 | 9.6 | 0.55174 | A4: Left Quadrant |  | 21.95 | 9.6 | 14.4031 | 21.1 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9008-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 21.2 | 21.6 | 23.3 | 21.1 | 1.0231
PG07 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9008-GD20-P-50 | CML-4 | 150-PG-23L9008-GD20-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6471 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 22.325 | CML-4 | CML: Equal Tee | 0 | 2136-07-05 | 2088-06-24 | 2014-07-22 07:30 | 9.6 | 0 | A1: Outside Quadrant |  | 21.95 | 9.6 | 14.4031 | 22 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9008-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.4 |  | 22 | 22.7 | 22.6 | 22 | 0.37749
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-3 | 150-PG-23L9009-GD20-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6499 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | Low alarm WT breach | [34 empty] | Low alarm breach | 20.75 | CML-3 | CML: Elbow | 0 | 2026-02-24 | 2021-01-15 | 2014-07-23 07:30 | 9.6 | 0.93953 | A1: Outside Quadrant |  | 21.95 | 9.6 | 14.4031 | 20.5 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 20.5 | 21 | 21 | 20.5 | 0.28868
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-21 | 150-PG-23L9009-GD20-P-50 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6370 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-20 | 150-PG-23L9009-GD20-P-50 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6369 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-19 | 150-PG-23L9009-GD20-P-50 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6368 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-16 | 150-PG-23L9009-GD20-P-50 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6365 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.025 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-11 | 150-PG-23L9009-GD20-P-50 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6360 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-9 | 150-PG-23L9009-GD20-P-50 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6358 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-6 | 150-PG-23L9009-GD20-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6355 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.1 | 3.1 | 0.05
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-8 | 150-PG-23L9009-GD20-P-50 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 6504 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [35 empty] | Low alarm breach | 20.975 | CML-8 | CML: Elbow | 0 | 2027-02-15 | 2021-08-21 | 2014-07-23 07:30 | 9.6 | 0.87474 | A4: Left Quadrant |  | 21.95 | 9.6 | 14.4031 | 20.6 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11 |  | 21.1 | 21.1 | 21.1 | 20.6 | 0.25
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-4 | 150-PG-23L9009-GD20-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6500 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [35 empty] | Low alarm breach | 21.3 | CML-4 | CML: Elbow | 0 | 2033-01-24 | 2025-04-07 | 2014-07-23 07:30 | 9.6 | 0.61556 | A3: Inside Quadrant |  | 21.95 | 9.6 | 14.4031 | 21 | 6 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.4 |  | 22 | 21.1 | 21 | 21.1 | 0.46904
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-10 | 150-PG-23L9009-GD20-P-50 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 6506 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [35 empty] | Low alarm breach | 21.1 | CML-10 | CML: Elbow | 0 | 2035-06-04 | 2026-09-16 | 2014-07-23 07:30 | 9.6 | 0.55076 | A1: Outside Quadrant |  | 21.95 | 9.6 | 14.4031 | 21.1 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 21.1 | 21.1 | 21.1 | 21.1 | 0
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-9 | 150-PG-23L9009-GD20-P-50 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 6505 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [35 empty] | Low alarm breach | 21.1 | CML-9 | CML: Elbow | 0 | 2035-06-04 | 2026-09-16 | 2014-07-23 07:30 | 9.6 | 0.55076 | A1: Outside Quadrant |  | 21.95 | 9.6 | 14.4031 | 21.1 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 21.1 | 21.1 | 21.1 | 21.1 | 0
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-7 | 150-PG-23L9009-GD20-P-50 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 6503 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [35 empty] | Low alarm breach | 21.2 | CML-7 | CML: Elbow | 0 | 2035-06-04 | 2026-09-16 | 2014-07-23 07:30 | 9.6 | 0.55076 | A1: Outside Quadrant |  | 21.95 | 9.6 | 14.4031 | 21.1 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 21.1 | 21.3 | 21.3 | 21.1 | 0.11547
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-12 | 150-PG-23L9009-GD20-P-50 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6383 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-10 | 150-PG-23L9009-GD20-P-50 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6381 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.025 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-8 | 150-PG-23L9009-GD20-P-50 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6379 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-7 | 150-PG-23L9009-GD20-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6378 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.025 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-3 | 150-PG-23L9009-GD20-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6374 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-1 | 150-PG-23L9009-GD20-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6372 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-4 | 150-PG-23L9009-GD20-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6375 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.125 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.2 | 3.2 | 3.1 | 0.095743
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-7 | 150-PG-23L9009-GD20-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6391 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-34 | 150-PG-23L9009-GD20-P-50 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 6313 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-34 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.1 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-33 | 150-PG-23L9009-GD20-P-50 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 6312 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.075 | CML-33 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.2 | 3 | 0.095743
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-30 | 150-PG-23L9009-GD20-P-50 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6309 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.025 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-27 | 150-PG-23L9009-GD20-P-50 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6306 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.25 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.7 | 3 | 3.3 | 3 | 0.33166
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-6 | 150-PG-23L9009-GD20-P-50 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 6502 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [35 empty] | Low alarm breach | 21.2 | CML-6 | CML: Pipe Length | 0 | 2035-06-04 | 2026-09-16 | 2014-07-23 07:30 | 9.6 | 0.55076 | A1: Outside Quadrant |  | 21.95 | 9.6 | 14.4031 | 21.1 | 6 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 21.1 | 21.3 | 21.1 | 21.3 | 0.11547
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-24 | 150-PG-23L9009-GD20-P-50 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6303 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-23 | 150-PG-23L9009-GD20-P-50 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6302 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-20 | 150-PG-23L9009-GD20-P-50 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6299 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.025 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-19 | 150-PG-23L9009-GD20-P-50 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6298 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-18 | 150-PG-23L9009-GD20-P-50 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6297 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.05 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3.1 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-8 | 150-PG-23L9009-GD20-P-50 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6249 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.075 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71331-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-7 | 150-PG-23L9009-GD20-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6248 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.075 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71331-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.2 | 3.1 | 3 | 0.095743
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-6 | 150-PG-23L9009-GD20-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6247 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.1 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 40 | 2.5 | 40-WF-71331-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.2 | 3.1 | 0.08165
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-3 | 150-PG-23L9009-GD20-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6244 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.075 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 40 | 2.5 | 40-WF-71331-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.2 | 3 | 3 | 3.1 | 0.095743
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-2 | 150-PG-23L9009-GD20-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6243 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.125 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 40 | 2.5 | 40-WF-71331-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.3 | 3.1 | 3 | 3.1 | 0.12583
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-11 | 150-PG-23L9009-GD20-P-50 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6238 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.05 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3.1 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-11 | 150-PG-23L9009-GD20-P-50 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6263 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.025 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-10 | 150-PG-23L9009-GD20-P-50 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6262 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.05 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-5 | 150-PG-23L9009-GD20-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6257 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.075 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.2 | 3 | 3 | 0.095743
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-4 | 150-PG-23L9009-GD20-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6256 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.1 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3.2 | 0.08165
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-3 | 150-PG-23L9009-GD20-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6255 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.075 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-6 | 150-PG-23L9009-GD20-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6258 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.075 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3.2 | 0.095743
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-4 | 150-PG-23L9009-GD20-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6278 | Cast Fitting, Reading taken on adjacent piping. | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 25 | 2.5 | 25-WF-71357-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-3 | 150-PG-23L9009-GD20-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6277 | Cast Fitting, Reading taken on adjacent piping. | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 25 | 2.5 | 25-WF-71357-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-2 | 150-PG-23L9009-GD20-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6276 | Cast Fitting, Reading taken on adjacent piping. | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.025 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 25 | 2.5 | 25-WF-71357-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-21 | 150-PG-23L9009-GD20-P-50 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6273 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.025 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-20 | 150-PG-23L9009-GD20-P-50 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6272 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.025 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-19 | 150-PG-23L9009-GD20-P-50 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6271 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.025 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-18 | 150-PG-23L9009-GD20-P-50 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6270 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.1 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.2 | 3.1 | 0.08165
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-16 | 150-PG-23L9009-GD20-P-50 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6268 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.05 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.1 | 3 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-15 | 150-PG-23L9009-GD20-P-50 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6267 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.05 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-14 | 150-PG-23L9009-GD20-P-50 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6266 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.05 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-10 | 150-PG-23L9009-GD20-P-50 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6237 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.2 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.5 | 3.2 | 3.1 | 0.21602
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-8 | 150-PG-23L9009-GD20-P-50 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6235 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.1 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.3 | 3.1 | 0.14142
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-5 | 150-PG-23L9009-GD20-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6232 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.075 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-6 | 150-PG-23L9009-GD20-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6233 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.075 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.2 | 3.1 | 3 | 0.095743
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-5 | 150-PG-23L9009-GD20-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6225 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.075 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71348-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-2 | 150-PG-23L9009-GD20-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6222 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.125 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71348-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3.3 | 0.12583
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-8 | 150-PG-23L9009-GD20-P-50 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6201 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-5 | 150-PG-23L9009-GD20-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6198 | Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.075 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-4 | 150-PG-23L9009-GD20-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6197 | Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.1 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.1 | 3.2 | 0.08165
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-3 | 150-PG-23L9009-GD20-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6196 | Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.075 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.1 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-22 | 150-PG-23L9009-GD20-P-50 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6185 | CAST Fitting. Readings taken on piping adjacent to fitting | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71360-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-20 | 150-PG-23L9009-GD20-P-50 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6063 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-10 | 150-PG-23L9009-GD20-P-50 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6053 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-6 | 150-PG-23L9009-GD20-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6043 | CAST Fitting. Readings taken on piping adjacent to fitting. | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.1 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 25 | 2.5 | 25-WF-71349-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.2 | 3.1 | 3 | 0.08165
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-46 | 150-PG-23L9009-GD20-P-50 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 6032 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-46 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-45 | 150-PG-23L9009-GD20-P-50 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 6031 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.05 | CML-45 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-43 | 150-PG-23L9009-GD20-P-50 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 6029 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.05 | CML-43 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-30 | 150-PG-23L9009-GD20-P-50 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6105 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.05 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-28 | 150-PG-23L9009-GD20-P-50 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6103 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.075 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.1 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-27 | 150-PG-23L9009-GD20-P-50 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6102 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-27 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-9 | 150-PG-23L9009-GD20-P-50 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6119 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.65 | CML-9 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 12 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 4.1 | 4.1 | 3.4 | 0.54467
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-20 | 150-PG-23L9009-GD20-P-50 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6095 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.1 | CML-20 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3.2 | 0.08165
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-23 | 150-PG-23L9009-GD20-P-50 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6098 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.05 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.1 | 3 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-18 | 150-PG-23L9009-GD20-P-50 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6093 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-17 | 150-PG-23L9009-GD20-P-50 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6092 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.075 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-14 | 150-PG-23L9009-GD20-P-50 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6089 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.075 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.2 | 3.1 | 3 | 3 | 0.095743
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-10 | 150-PG-23L9009-GD20-P-50 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6085 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-6 | 150-PG-23L9009-GD20-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6081 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-32 | 150-PG-23L9009-GD20-P-50 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6075 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.175 | CML-32 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 12 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.4 | 3.2 | 0.17078
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-28 | 150-PG-23L9009-GD20-P-50 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6071 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.075 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-41 | 150-PG-23L9009-GD20-P-50 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 6027 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3 | CML-41 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-38 | 150-PG-23L9009-GD20-P-50 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 6024 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.075 | CML-38 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.1 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-37 | 150-PG-23L9009-GD20-P-50 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 6023 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.1 | CML-37 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3.2 | 3.1 | 3 | 0.08165
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-28 | 150-PG-23L9009-GD20-P-50 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6014 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-24 | 150-PG-23L9009-GD20-P-50 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6010 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-15 | 150-PG-23L9009-GD20-P-50 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6001 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-14 | 150-PG-23L9009-GD20-P-50 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6000 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.025 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-14 | 150-PG-23L9009-GD20-P-50 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5985 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.025 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-10 | 150-PG-23L9009-GD20-P-50 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5981 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.05 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3.1 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-7 | 150-PG-23L9009-GD20-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5978 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.125 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.1 | 3.3 | 0.12583
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-17 | 150-PG-23L9009-GD20-P-50 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5970 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-13 | 150-PG-23L9009-GD20-P-50 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5966 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.025 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-12 | 150-PG-23L9009-GD20-P-50 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5965 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-5 | 150-PG-23L9009-GD20-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5958 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.05 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 3 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3.1 | 3.1 | 0.057735
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-25 | 150-PG-23L9009-GD20-P-50 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 5942 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.025 | CML-25 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-23 | 150-PG-23L9009-GD20-P-50 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 5940 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-23 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-21 | 150-PG-23L9009-GD20-P-50 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 5938 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-21 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-17 | 150-PG-23L9009-GD20-P-50 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5934 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-17 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-16 | 150-PG-23L9009-GD20-P-50 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 5933 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-16 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-26 | 150-PG-23L9009-GD20-P-50 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 5908 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-19 | 150-PG-23L9009-GD20-P-50 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 5901 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-8 | 150-PG-23L9009-GD20-P-50 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5890 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-7 | 150-PG-23L9009-GD20-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5889 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-12 | 150-PG-23L9009-GD20-P-50 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5497 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.075 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.2 | 3.1 | 3 | 3 | 0.095743
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-28 | 150-PG-23L9009-GD20-P-50 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 5406 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.3 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.6 | 3.6 | 3 | 3 | 0.34641
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-13 | 150-PG-23L9009-GD20-P-50 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5391 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.025 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3.1 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-12 | 150-PG-23L9009-GD20-P-50 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5390 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-3 | 150-PG-23L9009-GD20-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5423 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-35 | 150-PG-23L9009-GD20-P-50 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 5413 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3 | CML-35 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-5 | 150-PG-23L9009-GD20-P-50 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6501 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [35 empty] | Low alarm breach | 21.325 | CML-5 | CML: Elbow | 0 | 2035-06-04 | 2026-09-16 | 2014-07-23 07:30 | 9.6 | 0.55076 | A2: Right Quadrant |  | 21.95 | 9.6 | 14.4031 | 21.1 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 22 | 21.1 | 21.1 | 21.1 | 0.45
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-2 | 150-PG-23L9009-GD20-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6498 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [35 empty] | Low alarm breach | 21.1 | CML-2 | CML: Elbow | 0 | 2035-06-04 | 2026-09-16 | 2014-07-23 07:30 | 9.6 | 0.55076 | A1: Outside Quadrant |  | 21.95 | 9.6 | 14.4031 | 21.1 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 21.1 | 21.1 | 21.1 | 21.1 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-12 | 150-PG-23L9009-GD20-P-50 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5330 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.2 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.7 | 3 | 3.1 | 3 | 0.33665
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-11 | 150-PG-23L9009-GD20-P-50 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5329 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.025 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-2 | 150-PG-23L9009-GD20-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5320 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.45 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.9 | 3 | 3.9 | 0.51962
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-31 | 150-PG-23L9009-GD20-P-50 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 5276 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3 | CML-31 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-30 | 150-PG-23L9009-GD20-P-50 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 5275 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-25 | 150-PG-23L9009-GD20-P-50 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 5270 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-19 | 150-PG-23L9009-GD20-P-50 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 5264 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.025 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3 | 3 | 0.05
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-64 | 150-PG-23L9009-GD20-P-50 CML-64 |  | FPSO 2015 | Pipe Wall Thickness | 5309 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3 | CML-64 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-17 | 150-PG-23L9009-GD20-P-50 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5178 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.1 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3 | 6 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.2 | 3 | 3 | 3.2 | 0.11547
PG10 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-9 | 150-PG-23L9009-GD20-P-50 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5170 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3 | 9 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
PG10 | Montara_Topside | No | Potable Water (53) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-3 | 150-PG-23L9009-GD20-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5107 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 3.1 | CML-3 | CML: type TBC | 0 | 2018-01-07 | 2016-09-19 | 2015-03-06 07:00 | 2.5 | 0.17573 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 12 O'Clock | 25 | 3.38 | 0100-WZ-53L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.2 | 3.1 | 0.08165
PG10 | Montara_Topside | No | Potable Water (53) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-2 | 150-PG-23L9009-GD20-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5106 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 3.1 | CML-2 | CML: type TBC | 0 | 2018-01-07 | 2016-09-19 | 2015-03-06 07:00 | 2.5 | 0.17573 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 12 O'Clock | 25 | 3.38 | 0100-WZ-53L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.2 | 3.1 | 3.1 | 0.08165
PG10 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23L9009-GD20-P-50 | CML-1 | 150-PG-23L9009-GD20-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6497 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [35 empty] | Low alarm breach | 21.175 | CML-1 | CML: Elbow | 0 | 2035-06-04 | 2026-09-16 | 2014-07-23 07:30 | 9.6 | 0.55076 | A4: Left Quadrant |  | 21.95 | 9.6 | 14.4031 | 21.1 | 9 O'Clock | 150 | 21.95 | 0600-PG-23L9009-GD20-P-50 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 21.2 | 21.2 | 21.2 | 21.1 | 0.05
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9001-AS20-00 | CML-11 | 0100-DC-57L9001-AS20-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5067 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.6 | CML-11 | CML: type TBC | 0 | 2018-01-07 | 2016-09-19 | 2015-03-06 07:00 | 2.5 | 0.17573 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 6 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 4.6 | 3.6 | 3 | 3.2 | 0.71181
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9001-AS20-00 | CML-7 | 0100-DC-57L9001-AS20-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5063 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.375 | CML-7 | CML: type TBC | 0 | 2018-01-07 | 2016-09-19 | 2015-03-06 07:00 | 2.5 | 0.17573 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 6 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.5 | 3.6 | 3 | 3.4 | 0.263
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9001-AS20-00 | CML-2 | 0100-DC-57L9001-AS20-00 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5058 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.525 | CML-2 | CML: type TBC | 0 | 2018-01-07 | 2016-09-19 | 2015-03-06 07:00 | 2.5 | 0.17573 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 3 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.6 | 3 | 3.8 | 3.7 | 0.3594
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9001-AS20-00 | CML-17 | 0100-AS-63L9001-AS20-00 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5026 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.3 | CML-17 | CML: type TBC | 0 | 2018-01-03 | 2016-09-16 | 2015-03-04 07:00 | 2.5 | 0.17617 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 3 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.2 | 3 | 3.4 | 3.6 | 0.2582
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9001-AS20-00 | CML-15 | 0100-AS-63L9001-AS20-00 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5024 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.2 | CML-15 | CML: type TBC | 0 | 2018-01-03 | 2016-09-16 | 2015-03-04 07:00 | 2.5 | 0.17617 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 12 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.3 | 3.3 | 3.2 | 0.14142
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9001-AS20-00 | CML-13 | 0100-AS-63L9001-AS20-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5022 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.35 | CML-13 | CML: type TBC | 0 | 2018-01-03 | 2016-09-16 | 2015-03-04 07:00 | 2.5 | 0.17617 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 12 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.4 | 3.6 | 3.4 | 0.25166
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9001-AS20-00 | CML-8 | 0100-AS-63L9001-AS20-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5017 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.4 | CML-8 | CML: type TBC | 0 | 2018-01-03 | 2016-09-16 | 2015-03-04 07:00 | 2.5 | 0.17617 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.4 | 3.7 | 3.5 | 3 | 0.29439
GN02 | Montara_Topside | No | Nitrogen (67) | Pipework | 0100-GN-67L9000-AS20-00 | CML-5 | 0100-GN-67L9000-AS20-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5004 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [35 empty] | Low alarm breach | 3.15 | CML-5 | CML: type TBC | 0 | 2017-12-31 | 2016-09-14 | 2015-03-03 07:00 | 2.5 | 0.1764 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 3 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.1 | 3 | 3.2 | 3.3 | 0.1291
GN02 | Montara_Topside | No | Nitrogen (67) | Pipework | 0100-GN-67L9000-AS20-00 | CML-4 | 0100-GN-67L9000-AS20-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5003 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [35 empty] | Low alarm breach | 3.175 | CML-4 | CML: type TBC | 0 | 2017-12-31 | 2016-09-14 | 2015-03-03 07:00 | 2.5 | 0.1764 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3 | 12 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.1 | 3.3 | 3.3 | 0.15
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-3 | 80-SC-55002-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8833 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 3.85 | CML-3 | CML: type TBC | 3 | 2015-07-01 | 2015-09-27 | 2015-02-24 07:00 | 2.5 | 1.4351 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 3 | 3 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 4.4 | 3 | 4.2 | 3.8 | 0.61914
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71321-01K01 | CML-5 | 100-WF-71321-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8539 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 3.375 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-02-04 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 6 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3.5 | 3 | 3 | 4 | 0.47871
VA02 | Montara_Topside | No | Main Power (80) | Pipework | 50-VA-80012-01S01 | CML-1 | 50-VA-80012-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8513 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [35 empty] | Medium alarm breach | 3.55 | CML-1 | CML: type TBC | 1 | 2015-06-03 | 2014-12-23 | 2015-02-03 07:30 | 2.5 | 1.5141 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3 | 12 O'Clock | 50 | 5.54 | 50-VA-80012-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.3 | 3.7 | 4.2 | 0.51962
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-22 | 50-WC-40451-01C02 CML-22 | yes | FPSO 2013 | Pipe Wall Thickness | 10162 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 3.038mm/ yr | [35 empty] | 4.725 | CML-22 | CML: type TBC | 3 | 2014-06-01 | 2014-07-10 | 2013-11-09 | 2.5 | 3.0379 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.6 | 4.5 | 5.6 | 0.60759
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9000-DD20-P-50 | CML-2 | 250-PL-13L9000-DD20-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6448 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.275 | CML-2 | CML: Elbow | 0 | 2063-09-18 | 2044-02-27 | 2014-07-22 07:30 | 4.2 | 0 | A3: Inside Quadrant |  | 9.27 | 4.2 | 6.1556 | 10.9 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9000-DD20-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 11.7 | 11.6 | 10.9 | 10.9 | 0.43493
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9000-DD20-P-50 | CML-1 | 250-PL-13L9000-DD20-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6447 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.525 | CML-1 | CML: Elbow | 0 | 2063-09-18 | 2044-02-27 | 2014-07-22 07:30 | 4.2 | 0 | A4: Left Quadrant |  | 9.27 | 4.2 | 6.1556 | 11 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9000-DD20-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 12.2 | 11.1 | 11.8 | 11 | 0.57373
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-6 | 150-WC-40006-01C02 CML-6 | yes | FPSO 2013 | Pipe Wall Thickness | 20025 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.85 | CML-6 | CML: type TBC | 3 | 2014-06-19 | 2014-07-30 | 2013-11-17 | 2.5 | 2.8941 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 9 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.9 | 4.9 | 5.4 | 4.2 | 0.49329
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-6 | 250-PL-13L9001-BD20X-P-50 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 6454 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.4 | CML-6 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A4: Left Quadrant |  | 9.27 |  |  | 11.2 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9001-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.4 | 11.4 | 11.6 | 11.2 | 0.1633
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-4 | 250-PL-13L9001-BD20X-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22557 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [36 empty] | 3.225 | CML-4 | CML: Equal Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 3.1 | 6 O'Clock | 80 | 2 | 0300-WF-71L9004-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.5 | 3.1 | 3.2 | 0.1893
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-5 | 250-PL-13L9001-BD20X-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22550 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 3.525 | CML-5 | CML: Pipe Length | 0.5 | 2022-03-09 | 2022-12-21 | 2015-04-23 07:00 | 2.7 | 0.08719 | A3: Inside Quadrant |  | 3 | 2.7 | 2.6313 | 3.3 | 6 O'Clock | 150 | 3.5 | 0600-WF-71L9000-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.9 | 3.5 | 3.3 | 3.4 | 0.263
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-3 | 250-PL-13L9001-BD20X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22548 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 3.45 | CML-3 | CML: Pipe Length | 0.5 | 2022-03-09 | 2022-12-21 | 2015-04-23 07:00 | 2.7 | 0.08719 | A1: Outside Quadrant |  | 3 | 2.7 | 2.6313 | 3.3 | 12 O'Clock | 150 | 3.5 | 0600-WF-71L9000-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.3 | 3.6 | 3.5 | 3.4 | 0.1291
PF04 | Montara_Topside | No | Open Drain (56) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-1 | 250-PL-13L9001-BD20X-P-50 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 9088 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.025 | CML-1 | CML: type TBC | 3 | 2015-08-06 | 2015-10-30 | 2015-03-02 07:00 | 2.5 | 1.3931 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.1 | 12 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 4.6 | 5.1 | 3.3 | 0.97767
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-5 | 250-PL-13L9001-BD20X-P-50 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6453 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.675 | CML-5 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A1: Outside Quadrant |  | 9.27 |  |  | 11.6 | 12 O'Clock | 250 | 9.27 | 1000-PL-13L9001-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.6 | 11.7 | 11.7 | 11.7 | 0.05
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML88 | 250-PL-13L9001-BD20X-P-50 CML88 |  | FPSO 2015 | Pipe Wall Thickness | 7427 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 3.125 | CML88 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.1 | 3.1 | 0.05
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-35 | 250-PL-13L9001-BD20X-P-50 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 6913 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.3 | CML-35 | CML: type TBC | 0.5 | 2018-01-09 | 2016-11-14 | 2015-04-05 07:00 | 3.5 | 0.21685 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4.1 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.1 | 4.2 | 4.6 | 4.3 | 0.21602
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-27 | 250-PL-13L9001-BD20X-P-50 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 6905 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.425 | CML-27 | CML: type TBC | 0.5 | 2018-01-09 | 2016-11-14 | 2015-04-05 07:00 | 3.5 | 0.21685 | A2: Right Quadrant |  | 4 | 3.5 | 3.75 | 4.1 | 3 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.2 | 4.1 | 4.7 | 4.7 | 0.32016
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-25 | 250-PL-13L9001-BD20X-P-50 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6903 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.5 | CML-25 | CML: type TBC | 0.5 | 2018-01-09 | 2016-11-14 | 2015-04-05 07:00 | 3.5 | 0.21685 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4.1 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.1 | 4.4 | 4.4 | 5.1 | 0.42426
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-24 | 250-PL-13L9001-BD20X-P-50 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6902 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.4 | CML-24 | CML: type TBC | 0.5 | 2018-01-09 | 2016-11-14 | 2015-04-05 07:00 | 3.5 | 0.21685 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4.1 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.7 | 4.5 | 4.3 | 4.1 | 0.2582
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-19 | 250-PL-13L9001-BD20X-P-50 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6897 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.875 | CML-19 | CML: type TBC | 0.5 | 2018-01-09 | 2016-11-14 | 2015-04-05 07:00 | 3.5 | 0.21685 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4.1 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 5.7 | 4.9 | 4.8 | 4.1 | 0.65511
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-14 | 250-PL-13L9001-BD20X-P-50 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6892 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.425 | CML-14 | CML: type TBC | 0.5 | 2018-01-09 | 2016-11-14 | 2015-04-05 07:00 | 3.5 | 0.21685 | A3: Inside Quadrant |  | 4 | 3.5 | 3.75 | 4.1 | 6 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.7 | 4.4 | 4.1 | 4.5 | 0.25
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-13 | 250-PL-13L9001-BD20X-P-50 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6891 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.425 | CML-13 | CML: type TBC | 0.5 | 2018-01-09 | 2016-11-14 | 2015-04-05 07:00 | 3.5 | 0.21685 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4.1 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.7 | 4.5 | 4.4 | 4.1 | 0.25
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-17 | 250-PL-13L9001-BD20X-P-50 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6895 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.425 | CML-17 | CML: type TBC | 0.5 | 2018-01-09 | 2016-11-14 | 2015-04-05 07:00 | 3.5 | 0.21685 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4.1 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.6 | 4.5 | 4.5 | 4.1 | 0.22174
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-28 | 250-PL-13L9001-BD20X-P-50 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6702 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.425 | CML-28 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 4 | 3.3 | 3.3 | 0.39476
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-2 | 250-PL-13L9001-BD20X-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6674 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.15 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 6 O'Clock | 50 | 2.5 | 50-WF-71353-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.1 | 3.2 | 0.057735
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-25 | 250-PL-13L9001-BD20X-P-50 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6658 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 11:42 | [32 empty] | 3.175 | CML-25 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.2 | 3.3 | 3.1 | 0.095743
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-3 | 250-PL-13L9001-BD20X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6619 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.1 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.1 | 3.1 | 3.1 | 0
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-1 | 250-PL-13L9001-BD20X-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6617 | Cast fitting, reading taken on adjacent pipework | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.125 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.2 | 3.1 | 3.1 | 0.05
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-3 | 250-PL-13L9001-BD20X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6611 | Cast fitting, reading taken on adjacent pipework | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.125 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 6 O'Clock | 40 | 2.5 | 40-WF-71344-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.1 | 3.1 | 3.2 | 0.05
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-9 | 250-PL-13L9001-BD20X-P-50 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6418 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.125 | CML-9 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.1 | 3.1 | 0.05
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-8 | 250-PL-13L9001-BD20X-P-50 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6417 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.125 | CML-8 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 6 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.1 | 3.1 | 3.2 | 0.05
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-3 | 250-PL-13L9001-BD20X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6412 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.6 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 6 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.3 | 3.7 | 3.1 | 3.3 | 0.52915
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-37 | 250-PL-13L9001-BD20X-P-50 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 6446 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.175 | CML-37 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 6 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.1 | 3.1 | 3.4 | 0.15
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-4 | 250-PL-13L9001-BD20X-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6452 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 10.275 | CML-4 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A1: Outside Quadrant |  | 9.27 |  |  | 10.2 | 12 O'Clock | 250 | 9.27 | 1000-PL-13L9001-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.2 | 10.3 | 10.3 | 10.3 | 0.05
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-3 | 250-PL-13L9001-BD20X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6451 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.675 | CML-3 | CML: Fitting | 0 |  |  | 2014-07-22 07:30 |  | 0 | A1: Outside Quadrant |  | 9.27 |  |  | 11.5 | 12 O'Clock | 250 | 9.27 | 1000-PL-13L9001-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.5 | 11.6 | 11.9 | 11.7 | 0.17078
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-10 | 250-PL-13L9001-BD20X-P-50 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6359 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.1 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.1 | 3.1 | 3.1 | 0
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-5 | 250-PL-13L9001-BD20X-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6376 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.2 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 3 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.3 | 3.2 | 0.08165
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-9 | 250-PL-13L9001-BD20X-P-50 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6261 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.1 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.1 | 3.1 | 3.1 | 0
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-7 | 250-PL-13L9001-BD20X-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6259 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.1 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.1 | 3.1 | 3.1 | 0
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-24 | 250-PL-13L9001-BD20X-P-50 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6099 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.225 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.3 | 3.3 | 3.2 | 3.1 | 0.095743
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-24 | 250-PL-13L9001-BD20X-P-50 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 6067 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.15 | CML-24 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 6 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.1 | 3.2 | 0.057735
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-22 | 250-PL-13L9001-BD20X-P-50 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6008 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.2 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.3 | 3.2 | 3.1 | 0.08165
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-3 | 250-PL-13L9001-BD20X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5974 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.1 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.1 | 3.1 | 3.1 | 0
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-7 | 250-PL-13L9001-BD20X-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5492 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.35 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.9 | 3.1 | 3.3 | 3.1 | 0.37859
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-6 | 250-PL-13L9001-BD20X-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5384 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.25 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.3 | 3.3 | 3.1 | 3.3 | 0.1
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-1 | 250-PL-13L9001-BD20X-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5421 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.125 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.1 | 3.1 | 0.05
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-2 | 250-PL-13L9001-BD20X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6450 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.6 | CML-2 | CML: Equal Tee | 0 |  |  | 2014-07-22 07:30 |  | 0 | A1: Outside Quadrant |  | 9.27 |  |  | 11.6 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9001-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.6 | 11.6 | 11.6 | 11.6 | 0
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9001-BD20X-P-50 | CML-1 | 250-PL-13L9001-BD20X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6449 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.5 | CML-1 | CML: Fitting | 0 |  |  | 2014-07-22 07:30 |  | 0 | A1: Outside Quadrant |  | 9.27 |  |  | 11.5 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9001-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.5 | 11.5 | 11.5 | 11.5 | 0
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9002-DD20-P-50 | CML-1 | 250-PL-13L9002-DD20-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6455 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.025 | CML-1 | CML: Elbow | 0 | 2063-09-18 | 2044-02-27 | 2014-07-22 07:30 | 4.2 | 0 | A2: Right Quadrant |  | 9.27 | 4.2 | 6.1556 | 10.6 | 3 O'Clock | 250 | 9.27 | 1000-PL-13L9002-DD20-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10.9 | 10.6 | 11.2 | 11.4 | 0.35
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9002-DD20-P-50 | CML-2 | 250-PL-13L9002-DD20-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6456 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.35 | CML-2 | CML: Elbow | 0 | 2063-09-18 | 2044-02-27 | 2014-07-22 07:30 | 4.2 | 0 | A4: Left Quadrant |  | 9.27 | 4.2 | 6.1556 | 11 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9002-DD20-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 11.2 | 11.6 | 11.6 | 11 | 0.3
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-6 | 250-PL-13L9003-BD20X-P-50 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 6462 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.575 | CML-6 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A2: Right Quadrant |  | 9.27 |  |  | 11.4 | 3 O'Clock | 250 | 9.27 | 1000-PL-13L9003-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.5 | 11.4 | 11.9 | 11.5 | 0.22174
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-5 | 250-PL-13L9003-BD20X-P-50 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6461 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.6 | CML-5 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A1: Outside Quadrant |  | 9.27 |  |  | 11.3 | 12 O'Clock | 250 | 9.27 | 1000-PL-13L9003-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.3 | 12 | 11.4 | 11.7 | 0.31623
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-3 | 250-PL-13L9003-BD20X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5314 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.875 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 3 O'Clock | 150 | 3 | 150-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.7 | 3.1 | 4.1 | 4.6 | 0.63443
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-55 | 250-PL-13L9003-BD20X-P-50 CML-55 |  | FPSO 2015 | Pipe Wall Thickness | 5300 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.125 | CML-55 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.1 | 3.1 | 0.05
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-4 | 250-PL-13L9003-BD20X-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6460 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.2 | CML-4 | CML: Elbow | 0 |  |  | 2014-07-22 07:30 |  | 0 | A3: Inside Quadrant |  | 9.27 |  |  | 10.9 | 6 O'Clock | 250 | 9.27 | 1000-PL-13L9003-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.3 | 11.3 | 10.9 | 11.3 | 0.2
PF04 | Montara_Topside | No | Potable Water (53) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-2 | 250-PL-13L9003-BD20X-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5115 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 3.125 | CML-2 | CML: type TBC | 0 | 2019-10-22 | 2018-01-15 | 2015-03-06 07:00 | 2.5 | 0.12948 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.1 | 9 O'Clock | 25 | 3.38 | 0100-WZ-53L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.1 | 3.1 | 0.05
PF04 | Montara_Topside | No | Potable Water (53) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-1 | 250-PL-13L9003-BD20X-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5114 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 3.15 | CML-1 | CML: type TBC | 0 | 2019-10-22 | 2018-01-15 | 2015-03-06 07:00 | 2.5 | 0.12948 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.1 | 9 O'Clock | 25 | 3.38 | 0100-WZ-53L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.2 | 3.2 | 3.1 | 0.057735
PF04 | Montara_Topside | No | Potable Water (53) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-6 | 250-PL-13L9003-BD20X-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5110 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [35 empty] | Low alarm breach | 3.375 | CML-6 | CML: type TBC | 0 | 2019-10-22 | 2018-01-15 | 2015-03-06 07:00 | 2.5 | 0.12948 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.1 | 9 O'Clock | 25 | 3.38 | 0100-WZ-53L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.6 | 3.1 | 3.7 | 3.1 | 0.32016
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-3 | 250-PL-13L9003-BD20X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6459 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.3 | CML-3 | CML: Fitting | 0 |  |  | 2014-07-22 07:30 |  | 0 | A1: Outside Quadrant |  | 9.27 |  |  | 11.3 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9003-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.3 | 11.3 | 11.3 | 11.3 | 0
PF04 | Montara_Topside | No | Compressed Air (63) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-2 | 250-PL-13L9003-BD20X-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5029 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.725 | CML-2 | CML: type TBC | 0 | 2019-10-16 | 2018-01-11 | 2015-03-04 07:00 | 2.5 | 0.12981 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.1 | 3 O'Clock | 25 | 3.38 | 0100-AS-63L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.5 | 3.1 | 3.4 | 4.9 | 0.80156
PF04 | Montara_Topside | No | Compressed Air (63) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-1 | 250-PL-13L9003-BD20X-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5028 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.4 | CML-1 | CML: type TBC | 0 | 2019-10-16 | 2018-01-11 | 2015-03-04 07:00 | 2.5 | 0.12981 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.1 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.4 | 3.6 | 3.5 | 3.1 | 0.21602
PF04 | Montara_Topside | No | Compressed Air (63) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-7 | 250-PL-13L9003-BD20X-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5016 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.2 | CML-7 | CML: type TBC | 0 | 2019-10-16 | 2018-01-11 | 2015-03-04 07:00 | 2.5 | 0.12981 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.1 | 3 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.2 | 3.1 | 3.2 | 3.3 | 0.08165
PF04 | Montara_Topside | No | Compressed Air (63) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-4 | 250-PL-13L9003-BD20X-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5013 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.3 | CML-4 | CML: type TBC | 0 | 2019-10-16 | 2018-01-11 | 2015-03-04 07:00 | 2.5 | 0.12981 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.1 | 6 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.7 | 3.2 | 3.1 | 3.2 | 0.2708
PF04 | Montara_Topside | No | Nitrogen (67) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-3 | 250-PL-13L9003-BD20X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5002 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [35 empty] | Low alarm breach | 3.95 | CML-3 | CML: type TBC | 0 | 2019-10-13 | 2018-01-08 | 2015-03-03 07:00 | 2.5 | 0.12998 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.1 | 9 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 6.5 | 3.1 | 3.1 | 1.7
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-8 | 250-PL-13L9003-BD20X-P-50 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8542 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 3.575 | CML-8 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-02-04 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 9 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.3 | 3.9 | 4 | 3.1 | 0.44253
PF04 | Montara_Topside | No | Main Power (80) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-2 | 250-PL-13L9003-BD20X-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8520 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [35 empty] | Medium alarm breach | 4.625 | CML-2 | CML: type TBC | 1 | 2015-07-03 | 2015-01-15 | 2015-02-03 07:30 | 2.5 | 1.4545 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.1 | 12 O'Clock | 50 | 5.54 | 50-VA-80013-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 6.5 | 4 | 4.9 | 1.45
PF04 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-3 | 250-PL-13L9003-BD20X-P-50 CML-3 | Yes | FPSO 2016 | Pipe Wall Thickness | 24490 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.65 | CML-3 | CML: Fitting | 3 | 2017-06-13 | 2017-11-18 | 2016-07-09 07:00 | 2.5 | 0.75298 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.2 | 12 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 | 0.49205 | 3.2 | 3.9 | 4 | 3.5 | 0.36968
PF04 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-2 | 250-PL-13L9003-BD20X-P-50 CML-2 | Yes | FPSO 2016 | Pipe Wall Thickness | 24489 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.65 | CML-2 | CML: Elbow | 3 | 2017-06-13 | 2017-11-18 | 2016-07-09 07:00 | 2.5 | 0.75298 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.2 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 | 0.78728 | 3.9 | 3.7 | 3.2 | 3.8 | 0.31091
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML - 37 | 250-PL-13L9003-BD20X-P-50 CML - 37 |  | FPSO 2015 | Pipe Wall Thickness | 22646 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 3.225 | CML - 37 | CML: Reducer | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 1.5 | 2.5 | 1.875 | 3.2 | 9 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.3 | 3.2 | 3.2 | 3.2 | 0.05
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-3 | 250-PL-13L9003-BD20X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22568 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [36 empty] | 3.25 | CML-3 | CML: Equal Tee | 0.5 | 2013-01-06 | 2017-01-28 | 2015-04-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.0938 | 3.2 | 9 O'Clock | 100 | 2.5 | 0400-WF-71L9001-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.4 | 3.2 | 3.2 | 3.2 | 0.1
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-6 | 250-PL-13L9003-BD20X-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22551 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 3.5 | CML-6 | CML: Pipe Length | 0.5 | 2031-05-10 | 2032-12-05 | 2015-04-23 07:00 | 2.7 | 0.04359 | A1: Outside Quadrant |  | 3 | 2.7 | 2.6313 | 3.4 | 9 O'Clock | 150 | 3.5 | 0600-WF-71L9000-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.4 | 3.8 | 3.4 | 3.4 | 0.2
PF04 | Montara_Topside | No | Fire Water (71) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-4 | 250-PL-13L9003-BD20X-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22549 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 3.625 | CML-4 | CML: Pipe Length | 0.5 | 2031-05-10 | 2032-12-05 | 2015-04-23 07:00 | 2.7 | 0.04359 | A3: Inside Quadrant |  | 3 | 2.7 | 2.6313 | 3.4 | 6 O'Clock | 150 | 3.5 | 0600-WF-71L9000-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.7 | 3.6 | 3.4 | 3.8 | 0.17078
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-2 | 250-PL-13L9003-BD20X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6458 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.3 | CML-2 | CML: Equal Tee | 0 |  |  | 2014-07-22 07:30 |  | 0 | A1: Outside Quadrant |  | 9.27 |  |  | 11.3 | 9 O'Clock | 250 | 9.27 | 1000-PL-13L9003-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.3 | 11.3 | 11.3 | 11.3 | 0
PF04 | Montara_Topside | No | Separation (20) | Pipework | 250-PL-13L9003-BD20X-P-50 | CML-1 | 250-PL-13L9003-BD20X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6457 | Protective mesh removed/Rope Access | 2014-07-22 07:30 | 2014-07-22 14:00 | [36 empty] | 11.025 | CML-1 | CML: Fitting | 0 |  |  | 2014-07-22 07:30 |  | 0 | A3: Inside Quadrant |  | 9.27 |  |  | 10.6 | 6 O'Clock | 250 | 9.27 | 1000-PL-13L9003-BD20X-P-50 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11.5 | 10.7 | 10.6 | 11.3 | 0.44253
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML55 | 80-WF-71338-01K01 CML55 |  | FPSO 2015 | Pipe Wall Thickness | 7101 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 3.8 | CML55 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 3 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 4 | 3.2 | 4 | 4 | 0.4
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-22 | 250-WF-71373-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6900 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.45 | CML-22 | CML: type TBC | 0.5 | 2019-07-24 | 2018-01-09 | 2015-04-05 07:00 | 3.5 | 0.16263 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4.2 | 12 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 4.2 | 4.6 | 4.4 | 4.6 | 0.19149
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-20 | 250-WF-71373-01K01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 6898 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.425 | CML-20 | CML: type TBC | 0.5 | 2019-07-24 | 2018-01-09 | 2015-04-05 07:00 | 3.5 | 0.16263 | A2: Right Quadrant |  | 4 | 3.5 | 3.75 | 4.2 | 3 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 4.5 | 4.2 | 4.5 | 4.5 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-12 | 250-WF-71373-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6890 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.45 | CML-12 | CML: type TBC | 0.5 | 2019-07-24 | 2018-01-09 | 2015-04-05 07:00 | 3.5 | 0.16263 | A3: Inside Quadrant |  | 4 | 3.5 | 3.75 | 4.2 | 6 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 4.7 | 4.4 | 4.2 | 4.5 | 0.20817
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-7 | 250-WF-71373-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6885 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.25 | CML-7 | CML: type TBC | 0.5 | 2019-07-24 | 2018-01-09 | 2015-04-05 07:00 | 3.5 | 0.16263 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 4.2 | 6 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 4.2 | 4.2 | 4.2 | 4.4 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-5 | 250-WF-71373-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6883 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.6 | CML-5 | CML: type TBC | 0.5 | 2019-07-24 | 2018-01-09 | 2015-04-05 07:00 | 3.5 | 0.16263 | A2: Right Quadrant |  | 4 | 3.5 | 3.75 | 4.2 | 3 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 4.3 | 4.2 | 5.3 | 4.6 | 0.49666
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71373-01K01 | CML-3 | 250-WF-71373-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6881 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.375 | CML-3 | CML: type TBC | 0.5 | 2019-07-24 | 2018-01-09 | 2015-04-05 07:00 | 3.5 | 0.16263 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4.2 | 9 O'Clock | 250 | 4.5 | 250-WF-71373-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 4.4 | 4.5 | 4.4 | 4.2 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-115 | 150-WF-71345-01K01 CML-115 |  | FPSO 2015 | Pipe Wall Thickness | 6789 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.575 | CML-115 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 6 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 4 | 3.2 | 3.9 | 0.43493
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-110 | 150-WF-71345-01K01 CML-110 |  | FPSO 2015 | Pipe Wall Thickness | 6784 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 3.425 | CML-110 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.3 | 3.5 | 3.7 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71353-01K01 | CML-1 | 50-WF-71353-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6673 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.25 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 6 O'Clock | 50 | 2.5 | 50-WF-71353-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.3 | 3.2 | 3.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71361-01K01 | CML-11 | 40-WF-71361-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6644 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 13:59 | [32 empty] | 3.325 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 12 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.3 | 3.4 | 3.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71343-01K01 | CML-14 | 50-WF-71343-01K01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6630 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.25 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 6 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.2 | 3.2 | 3.4 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71344-01K01 | CML-1 | 40-WF-71344-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6609 |  | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.25 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 6 O'Clock | 40 | 2.5 | 40-WF-71344-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.3 | 3.2 | 3.2 | 3.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71336-01K01 | CML-4 | 100-WF-71336-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6413 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.5 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 6 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.6 | 3.6 | 3.2 | 3.6 | 0.2
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71341-01K01 | CML-15 | 80-WF-71341-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6294 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.4 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 3 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.4 | 3.2 | 3.5 | 3.5 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71359-01K01 | CML-8 | 100-WF-71359-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6217 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.575 | CML-8 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 6 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 4 | 3.5 | 3.2 | 3.6 | 0.3304
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-14 | 50-WF-71350-01K01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 6057 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.35 | CML-14 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 6 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.2 | 3.2 | 3.8 | 0.3
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 25-WF-71349-01K01 | CML-4 | 25-WF-71349-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6041 | CAST Fitting. Readings taken on piping adjacent to fitting. | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.4 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 9 O'Clock | 25 | 2.5 | 25-WF-71349-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.6 | 3.5 | 3.3 | 3.2 | 0.18257
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71322-01K01 | CML-16 | 80-WF-71322-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6002 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.225 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.2 | 3.3 | 3.2 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71322-01K01 | CML-11 | 80-WF-71322-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5997 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.25 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.3 | 3.3 | 3.2 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71327-01K01 | CML-9 | 100-WF-71327-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5926 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.325 | CML-9 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 3 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.4 | 3.2 | 3.3 | 3.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71327-01K01 | CML-1 | 100-WF-71327-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5918 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.675 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 12 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 4.1 | 3.5 | 3.9 | 0.40311
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-59 | 80-WF-71310-01K01 CML-59 |  | FPSO 2015 | Pipe Wall Thickness | 5544 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.275 | CML-59 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.3 | 3.3 | 3.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-56 | 80-WF-71310-01K01 CML-56 |  | FPSO 2015 | Pipe Wall Thickness | 5541 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.275 | CML-56 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 3 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.2 | 3.4 | 3.3 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-70 | 80-WF-71310-01K01 CML-70 |  | FPSO 2015 | Pipe Wall Thickness | 5555 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.225 | CML-70 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.3 | 3.2 | 3.2 | 0.05
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57309-01C03 | CML-5 | 150-DC-57309-01C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2340 |  | 2014-03-17 07:00 | 2014-03-17 08:00 | [36 empty] | 10.4 | CML-5 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 9.8 | 3 O'Clock | 100 | 8.56 | 100-DC-57309-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.6 | 9.8 | 10.2 | 11 | 0.5164
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57309-01C03 | CML-6 | 150-DC-57309-01C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2341 |  | 2014-03-17 07:00 | 2014-03-17 08:00 | [36 empty] | 11.1 | CML-6 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 10.8 | 12 O'Clock | 100 | 8.56 | 100-DC-57309-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 11.1 | 11.2 | 11.3 | 0.21602
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57309-01C03 | CML-1 | 150-DC-57309-01C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2336 |  | 2014-03-17 07:00 | 2014-03-17 08:00 | [36 empty] | 11.125 | CML-1 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 10.9 | 9 O'Clock | 100 | 8.56 | 100-DC-57309-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.2 | 11.4 | 11 | 10.9 | 0.22174
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57309-01C03 | CML-4 | 150-DC-57309-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2339 |  | 2014-03-17 07:00 | 2014-03-17 08:00 | [36 empty] | 11.3 | CML-4 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 11 | 12 O'Clock | 100 | 8.56 | 100-DC-57309-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11 | 11.2 | 11.7 | 11.3 | 0.29439
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57309-01C03 | CML-2 | 150-DC-57309-01C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2337 |  | 2014-03-17 07:00 | 2014-03-17 08:00 | [36 empty] | 11.675 | CML-2 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 11.2 | 6 O'Clock | 100 | 8.56 | 100-DC-57309-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.6 | 12.1 | 11.2 | 11.8 | 0.37749
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57309-01C03 | CML-3 | 150-DC-57309-01C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2338 |  | 2014-03-17 07:00 | 2014-03-17 08:00 | [36 empty] | 11.575 | CML-3 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 11.5 | 12 O'Clock | 100 | 8.56 | 100-DC-57309-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 11.5 | 11.6 | 11.6 | 11.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71306-01K01 | CML-15 | 50-WF-71306-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5176 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.3 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.2 | 6 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.3 | 3.3 | 3.2 | 3.4 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43140-01C02 | CML-1 | 50-FH-43140-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22690 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43140-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43138-01C02 | CML-1 | 50-FH-43138-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22687 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-10 | 50-FH-43137-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22684 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-10 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-1 | 50-PW-44014-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23146 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 4.55 | CML-1 | CML: Elbow | 3 | 2017-01-03 | 2017-05-24 | 2015-05-10 07:00 | 2.5 | 0.84513 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.9 | 9 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 | 0.98196 | 4.3 | 5.2 | 4.8 | 3.9 | 0.56862
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-38 | 250-PW-44006-01X01 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 23209 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.25 | CML-38 | CML: Elbow | 3 | 2016-06-19 | 2016-06-11 | 2015-05-11 07:00 | 2.5 | 1.2608 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 3.9 | 6 O'Clock | 50 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 | 4.6062 | 3.9 | 4.3 | 3.9 | 4.9 | 0.47258
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-2 | 250-PW-44007-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23135 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.675 | CML-2 | CML: Elbow | 3 | 2016-08-04 | 2016-07-26 | 2015-05-10 07:00 | 2.5 | 1.211 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4 | 6 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 1.6032 | 5.8 | 6.4 | 4 | 6.5 | 1.1587
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-5 | 50-PW-44014-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23150 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 4.875 | CML-5 | CML: Elbow | 3 | 2017-03-30 | 2017-08-27 | 2015-05-10 07:00 | 2.5 | 0.7936 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4 | 6 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 1.0712 | 5 | 5.1 | 4 | 5.4 | 0.60759
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-3 | 50-PW-44013-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22722 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 4.65 | CML-3 | CML: Elbow | 3 | 2017-03-06 | 2017-08-01 | 2015-04-28 07:00 | 2.5 | 0.80728 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 0.11784 | 4.8 | 4.6 | 4 | 5.2 | 0.5
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-8 | 50-FH-43137-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22682 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-8 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-6 | 50-FH-43137-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22680 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-6 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-3 | 50-FH-43137-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22677 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-3 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-1 | 50-FH-43137-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22675 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-9 | 25-FG-45455-01C02-E CML-9 |  | FPSO 2016 | Pipe Wall Thickness | 24354 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-9 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-8 | 25-FG-45455-01C02-E CML-8 |  | FPSO 2016 | Pipe Wall Thickness | 24353 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-7 | 25-FG-45455-01C02-E CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24352 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24351 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24350 | Lagging removal requires rope access, asked to leave these CML''''s by PTTEP | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-11 | 50-FH-43016-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22672 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-11 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-9 | 50-FH-43016-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22670 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-9 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-7 | 50-FH-43016-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22668 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-7 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-5 | 50-FH-43016-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22666 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-5 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-3 | 50-FH-43016-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22664 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-3 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-1 | 50-FH-43016-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22662 | Reading Not Required | 2015-04-27 07:00 | 2015-04-27 15:00 | [37 empty] | CML-1 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-10 | 300-FH-43001-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12522 | CML covered no inspection carried out | 2014-01-24 13:00 | 2014-01-24 15:00 | [37 empty] | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-24 13:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-11 | 300-FH-43001-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12523 | CML covered no inspection carried out | 2014-01-24 13:00 | 2014-01-24 15:00 | [37 empty] | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-24 13:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-11 | 200-FH-43114-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12819 | Inspection not carried due to location access | 2014-02-01 12:00 | 2014-02-01 14:00 | [37 empty] | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 12:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-12 | 200-FH-43114-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12820 | Inspection not carried due to location access | 2014-02-01 12:00 | 2014-02-01 14:00 | [37 empty] | CML-12 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 12:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-2 | 200-FH-43114-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12810 | Inspection not carried due to location access | 2014-02-01 12:00 | 2014-02-01 14:00 | [37 empty] | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 12:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-1 | 200-FH-43114-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12809 | Inspection not carried due to location access | 2014-02-01 12:00 | 2014-02-01 14:00 | [37 empty] | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 12:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-10 | 50-CG-38458-01C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23738 | DOES NOT EXIST - BLANKED | 2015-10-30 07:00 | 2015-10-30 15:00 | [37 empty] | CML-10 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 20 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71334-01K01 | CML-22 | 40-WF-71334-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6371 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.375 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 6 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.5 | 3.3 | 3.3 | 3.4 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71334-01K01 | CML-7 | 40-WF-71334-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6356 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.35 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.4 | 3.4 | 3.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71339-01K01 | CML-13 | 50-WF-71339-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6384 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.375 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 12 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.4 | 3.4 | 3.4 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71339-01K01 | CML-9 | 50-WF-71339-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6380 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.4 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 3 O'Clock | 50 | 2.5 | 50-WF-71339-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 3.3 | 3.4 | 3.5 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71341-01K01 | CML-28 | 80-WF-71341-01K01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6307 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.475 | CML-28 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 3 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 3.3 | 3.5 | 3.7 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71341-01K01 | CML-35 | 80-WF-71341-01K01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 6314 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.35 | CML-35 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.4 | 3.3 | 3.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71348-01K01 | CML-4 | 50-WF-71348-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6224 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.525 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 9 O'Clock | 50 | 2.5 | 50-WF-71348-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.5 | 3.8 | 3.5 | 3.3 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71359-01K01 | CML-6 | 100-WF-71359-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6215 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.6 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 6 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.9 | 3.6 | 3.3 | 3.6 | 0.24495
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71363-01K01 | CML-16 | 50-WF-71363-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6209 | Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.425 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 6 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 3.5 | 3.3 | 3.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71363-01K01 | CML-6 | 50-WF-71363-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6199 | Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.4 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 6 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 3.5 | 3.3 | 3.4 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-16 | 50-WF-71350-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 6059 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.5 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 9 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.7 | 3.5 | 3.5 | 3.3 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71352-01K01 | CML-10 | 100-WF-71352-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6120 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.4 | CML-10 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 3 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.3 | 3.6 | 3.4 | 0.14142
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-22 | 50-WF-71351-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 6097 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.35 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 6 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.4 | 3.3 | 3.4 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-19 | 50-WF-71351-01K01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 6094 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.375 | CML-19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 3.4 | 3.4 | 3.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71351-01K01 | CML-2 | 50-WF-71351-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6077 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 4.075 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 9 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.6 | 4.5 | 3.9 | 3.3 | 0.60208
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71350-01K01 | CML-30 | 50-WF-71350-01K01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6073 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.375 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 3 O'Clock | 50 | 2.5 | 50-WF-71350-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.3 | 3.4 | 3.5 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71322-01K01 | CML-42 | 80-WF-71322-01K01 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 6028 | CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.35 | CML-42 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 3.4 | 3.3 | 3.3 | 0.057735
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71322-01K01 | CML-30 | 80-WF-71322-01K01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6016 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.35 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.3 | 3.3 | 3.5 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71325-01K01 | CML-12 | 50-WF-71325-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5983 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.725 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 3 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4 | 3.3 | 3.6 | 4 | 0.34034
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71327-01K01 | CML-28 | 100-WF-71327-01K01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 5945 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.325 | CML-28 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.4 | 3.3 | 3.3 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71327-01K01 | CML-7 | 100-WF-71327-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5924 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.375 | CML-7 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.6 | 3.3 | 3.3 | 0.15
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71318-01K01 | CML-5 | 50-WF-71318-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5887 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.85 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.3 | 4.2 | 3.6 | 3.3 | 0.47958
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-4 | 80-WF-71310-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5489 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.475 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 3 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.7 | 3.3 | 3.4 | 3.5 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71316-01K01 | CML-11 | 50-WF-71316-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5389 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 3.85 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 6 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.3 | 4 | 3.3 | 3.8 | 0.42032
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 100-DH-56085-01C02 | CML-6 | 100-DH-56085-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3337 | Rope Access | 2014-05-08 09:30 | 2014-05-08 11:00 | [36 empty] | 5.625 | CML-6 | CML: type TBC | 3 | 2016-12-28 | 2017-02-09 | 2014-05-08 09:30 | 2.5 | 0.98361 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 12 O'Clock | 100 | 6.02 | 100-DH-56085-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 6 | 5.6 | 5.8 | 0.38622
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 100-DH-56085-01C02 | CML-3 | 100-DH-56085-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3334 | Rope Access | 2014-05-08 09:30 | 2014-05-08 11:00 | [36 empty] | 5.475 | CML-3 | CML: type TBC | 3 | 2018-09-21 | 2018-11-24 | 2014-05-08 09:30 | 2.5 | 0.66287 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 6 O'Clock | 100 | 6.02 | 100-DH-56085-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.6 | 5.4 | 5.5 | 0.095743
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 100-DH-56085-01C02 | CML-1 | 100-DH-56085-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3332 | Rope Access | 2014-05-08 09:30 | 2014-05-08 11:00 | [36 empty] | 6.55 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 9 O'Clock | 100 | 6.02 | 100-DH-56085-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7.2 | 6.8 | 6.1 | 6.1 | 0.54467
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 100-DH-56085-01C02 | CML-7 | 100-DH-56085-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3338 | Rope Access | 2014-05-08 09:30 | 2014-05-08 11:00 | [36 empty] | 7.65 | CML-7 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 12 O'Clock | 100 | 6.02 | 100-DH-56085-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 8.1 | 8.2 | 7.7 | 0.73258
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 100-DH-56085-01C02 | CML-4 | 100-DH-56085-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3335 | Rope Access | 2014-05-08 09:30 | 2014-05-08 11:00 | [36 empty] | 7.825 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.8 | 12 O'Clock | 100 | 6.02 | 100-DH-56085-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.4 | 8.3 | 8.8 | 0.89582
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 100-DH-56085-01C02 | CML-2 | 100-DH-56085-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3333 | Rope Access | 2014-05-08 09:30 | 2014-05-08 11:00 | [36 empty] | 7.65 | CML-2 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.4 | 12 O'Clock | 100 | 6.02 | 100-DH-56085-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.9 | 7.5 | 7.8 | 0.23805
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 100-DH-56085-01C02 | CML-5 | 100-DH-56085-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3336 | Rope Access | 2014-05-08 09:30 | 2014-05-08 11:00 | [36 empty] | 7.75 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.6 | 9 O'Clock | 100 | 6.02 | 100-DH-56085-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 7.9 | 7.9 | 7.6 | 0.17321
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 100-DH-56089-01C02 | CML-1 | 100-DH-56089-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8060 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 10.175 | CML-1 | CML: type TBC | 3 |  |  | 2015-01-22 07:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 9.4 | 6 O'Clock | 100 |  | 100-DH-56089-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.3 | 10.4 | 9.4 | 10.6 | 0.53151
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71310-01K01 | CML-2 | 150-WF-71310-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5313 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.75 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 9 O'Clock | 150 | 3 | 150-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.7 | 4.3 | 3.7 | 3.3 | 0.41231
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71310-01K01 | CML-1 | 150-WF-71310-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5312 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.525 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 9 O'Clock | 150 | 3 | 150-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.8 | 3.7 | 3.3 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-58 | 80-WF-71400-01K01 CML-58 |  | FPSO 2015 | Pipe Wall Thickness | 5303 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.55 | CML-58 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.6 | 3.6 | 3.3 | 3.7 | 0.17321
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45044-03C02 | CML-4 | 50-FG-45044-03C02 CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24401 | Lagging removed -Location requires rope access ,not requested at this time | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2043-08-12 | 2016-06-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.52 |  | 9 O'Clock | 50 | 5.54 | 50-FG-45044-03C02-E | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45044-03C02 | CML-3 | 50-FG-45044-03C02 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24400 | Lagging removed -Location requires rope access ,not requested at this time | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2043-08-12 | 2016-06-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.52 |  | 9 O'Clock | 50 | 5.54 | 50-FG-45044-03C02-E | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45044-03C02 | CML-2 | 50-FG-45044-03C02 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24399 | Lagging removed -Location requires rope access ,not requested at this time | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2043-08-12 | 2016-06-08 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.52 |  | 9 O'Clock | 50 | 5.54 | 50-FG-45044-03C02-E | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-1 | 50-PW-44013-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5725 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 4.575 | CML-1 | CML: Elbow | 3 | 2015-07-04 | 2015-09-23 | 2014-06-22 13:00 | 2.5 | 1.4542 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 6.6647 | 4.7 | 4 | 4.7 | 4.9 | 0.39476
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-10 | 50-PW-44014-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23155 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 4.5 | CML-10 | CML: Elbow | 3 | 2017-03-30 | 2017-08-27 | 2015-05-10 07:00 | 2.5 | 0.7936 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4 | 9 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 0.98196 | 4.8 | 4.6 | 4.6 | 4 | 0.34641
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-3 | 50-PW-44013-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5727 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 4.475 | CML-3 | CML: Elbow | 3 | 2015-08-26 | 2015-11-21 | 2014-06-22 13:00 | 2.5 | 1.3598 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.1 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 | 1.1379 | 4.4 | 4.7 | 4.1 | 4.7 | 0.28723
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-11 | 50-PW-44013-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5735 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 4.925 | CML-11 | CML: Elbow | 3 | 2015-10-25 | 2016-01-28 | 2014-06-22 13:00 | 2.5 | 1.2653 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 | 1.6255 | 4.2 | 4.8 | 5.1 | 5.6 | 0.58523
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-17 | 80-CG-38459-09C02-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23714 | DOES NOT EXIST ON SITE | 2015-10-30 07:00 | 2015-10-30 15:00 | [37 empty] | CML-17 | CML: Pipe Length | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.1519 |  | 9 O'Clock | 20 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45046-03C02-E | CML-1 | 80-FG-45046-03C02-E CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24407 | Lagging removed -Location requires rope access ,not requested at this time | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | No Readings to Review | [32 empty] | CML-1 | CML: Reducer | 3 | 2043-04-25 | 2043-05-13 | 2016-06-08 07:00 | 2.5 | 0 |  |  | 2.49 | 2.5 | 2.495 |  | 9 O'Clock | 100 | 5.49 | 80-FG-45046-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-2 | 300-PF-20003-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21740 | Lagged | 2014-10-01 07:00 | 2014-10-01 15:00 | [37 empty] | CML-2 | CML: Fitting | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-13 | 300-PF-20501-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21689 | Lagged | 2014-09-28 07:00 | 2014-09-28 15:00 | [37 empty] | CML-13 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-12 | 300-PF-20501-03C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21688 | Lagged | 2014-09-28 07:00 | 2014-09-28 15:00 | [37 empty] | CML-12 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-11 | 300-PF-20501-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21687 | Lagged | 2014-09-28 07:00 | 2014-09-28 15:00 | [37 empty] | CML-11 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-10 | 300-PF-20501-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21686 | Lagged | 2014-09-28 07:00 | 2014-09-28 15:00 | [37 empty] | CML-10 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-7 | 300-PF-20501-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21683 | Lagged | 2014-09-28 07:00 | 2014-09-28 15:00 | [37 empty] | CML-7 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-6 | 300-PF-20501-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21682 | Lagged | 2014-09-28 07:00 | 2014-09-28 15:00 | [37 empty] | CML-6 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-13 | 300-PF-20500-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21633 | Lagged | 2014-09-27 07:00 | 2014-09-27 15:00 | [37 empty] | CML-13 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-12 | 300-PF-20500-03C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21632 | Lagged | 2014-09-27 07:00 | 2014-09-27 15:00 | [37 empty] | CML-12 | CML: Fitting | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-11 | 300-PF-20500-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21631 | Lagged | 2014-09-27 07:00 | 2014-09-27 15:00 | [37 empty] | CML-11 | CML: Fitting | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-10 | 300-PF-20500-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21630 | Lagged | 2014-09-27 07:00 | 2014-09-27 15:00 | [37 empty] | CML-10 | CML: Fitting | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-7 | 300-PF-20500-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21627 | Lagged | 2014-09-27 07:00 | 2014-09-27 15:00 | [37 empty] | CML-7 | CML: Reducing Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-6 | 300-PF-20500-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21626 | Lagged | 2014-09-27 07:00 | 2014-09-27 15:00 | [37 empty] | CML-6 | CML: Fitting | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-2 | 300-PF-20001-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21140 | Lagged- no readings | 2014-07-16 07:30 | 2014-07-16 15:00 | [37 empty] | CML-2 | CML: Fitting | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 |  |  | 8.27 | 4.9 | 6.585 |  | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-8 | 100-DH-56561-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7940 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [37 empty] | CML-8 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2015-01-17 13:00 | 2.5 | 0 |  |  | 3.02 | 2.5 | 2.3838 |  | 9 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-19 | 80-PG-23025-06C03 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 13090 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | CML reading not in report | [36 empty] | CML-19 | CML: Elbow | 6 | 2096-09-16 | 2085-01-22 | 2014-02-07 11:00 | 2.8 | 0 |  |  | 5.13 | 2.8 | 3.965 |  | 9 O'Clock | 25 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-12 | 300-FL-43070-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12705 | CML location covered with Mesh | 2014-02-01 09:00 | 2014-02-01 12:00 | [37 empty] | CML-12 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-11 | 300-FL-43070-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12704 | CML location covered with Mesh | 2014-02-01 09:00 | 2014-02-01 12:00 | [37 empty] | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-10 | 300-FL-43070-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12703 | CML location covered with Mesh | 2014-02-01 09:00 | 2014-02-01 12:00 | [37 empty] | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-9 | 300-FL-43070-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12702 | CML location covered with Mesh | 2014-02-01 09:00 | 2014-02-01 12:00 | [37 empty] | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-8 | 300-FL-43070-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12701 | CML location covered with Mesh | 2014-02-01 09:00 | 2014-02-01 12:00 | [37 empty] | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-4 | 300-FL-43070-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12697 | CML location covered with Mesh | 2014-02-01 09:00 | 2014-02-01 12:00 | [37 empty] | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-3 | 300-FL-43070-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12696 | CML location covered with Mesh | 2014-02-01 09:00 | 2014-02-01 12:00 | [37 empty] | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-2 | 300-FL-43070-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12695 | CML location covered with Mesh | 2014-02-01 09:00 | 2014-02-01 12:00 | [37 empty] | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-1 | 300-FL-43070-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12694 | CML location covered with Mesh | 2014-02-01 09:00 | 2014-02-01 12:00 | [37 empty] | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-53 | 200-PL-20019-01C02 CML-53 | yes | FPSO 2015 | Pipe Wall Thickness | 23483 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 4.625 | CML-53 | CML: Pipe Length | 3 | 2016-12-05 | 2016-11-25 | 2015-07-24 07:00 | 2.5 | 1.0951 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 0.98316 | 4.8 | 4.9 | 4 | 4.8 | 0.41932
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-14 | 80-PL-44008-01C02 CML-14 | yes | FPSO 2015 | Pipe Wall Thickness | 23782 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.275 | CML-14 | CML: Elbow | 3 | 2018-02-19 | 2018-09-08 | 2015-04-18 07:00 | 2.5 | 0.63289 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.3 | 6 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 1.4614 | 6 | 5.4 | 4.3 | 5.4 | 0.70887
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-11 | 80-PL-44008-01C02 CML-11 | no | FPSO 2015 | Pipe Wall Thickness | 23779 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.2 | CML-11 | CML: Elbow | 3 | 2019-09-23 | 2020-06-18 | 2015-04-18 07:00 | 2.5 | 0.47334 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 6 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 1.0961 | 6 | 4.9 | 4.6 | 5.3 | 0.60553
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44513-01C02 | CML-8 | 80-PL-44513-01C02 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 7973 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:09 | [32 empty] | 4.8 | CML-8 | CML: Pipe Length | 3 | 2018-11-25 | 2019-07-17 | 2015-01-18 10:30 | 2.5 | 0.54465 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 12 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.8 | 4.9 | 4.9 | 0.14142
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44513-01C02 | CML-7 | 80-PL-44513-01C02 CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 7972 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:09 | [32 empty] | 4.775 | CML-7 | CML: Pipe Length | 3 | 2018-11-25 | 2019-07-17 | 2015-01-18 10:30 | 2.5 | 0.54465 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 9 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 4.8 | 4.8 | 4.6 | 0.12583
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44513-01C02 | CML-10 | 80-PL-44513-01C02 CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 7975 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:09 | [32 empty] | 4.625 | CML-10 | CML: Pipe Length | 3 | 2018-11-25 | 2019-07-17 | 2015-01-18 10:30 | 2.5 | 0.54465 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 9 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.7 | 4.6 | 4.6 | 4.6 | 0.05
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-25 | 250-PL-20006-01C02-P CML-25 | yes | FPSO 2014 | Pipe Wall Thickness | 13195 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.4 | CML-25 | CML: Elbow | 3 | 2016-08-12 | 2017-03-25 | 2014-01-21 13:00 | 3.61 | 0.85592 | A1: Outside Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.8 | 12 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.19 |  | 5.8 | 6.5 | 6.8 | 6.5 | 0.42426
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-11 | 250-PL-20006-01C02-P CML-11 | yes | FPSO 2014 | Pipe Wall Thickness | 13181 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.1 | CML-11 | CML: Tee | 3 | 2016-08-12 | 2017-03-25 | 2014-01-21 13:00 | 3.61 | 0.85592 | A1: Outside Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.8 | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.19 |  | 5.8 | 6.6 | 6.2 | 5.8 | 0.38297
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-11 | 250-PL-20006-01C02-P CML-11 | yes | FPSO 2014 | Pipe Wall Thickness | 21198 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 6.025 | CML-11 | CML: Tee | 3 | 2018-05-16 | 2019-04-29 | 2014-05-30 09:30 | 3.61 | 0.55243 | A1: Outside Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.8 | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.19 | 0 | 5.8 | 6.5 | 6 | 5.8 | 0.3304
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-10 | 250-PL-20006-01C02-P CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 21197 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 6.275 | CML-10 | CML: Tee | 3 | 2019-06-22 | 2020-08-21 | 2014-05-30 09:30 | 3.61 | 0.45199 | A1: Outside Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.9 | 12 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.29 | 0 | 5.9 | 6.6 | 6.3 | 6.3 | 0.28723
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-10 | 250-PL-20006-01C02-P CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 13180 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.275 | CML-10 | CML: Tee | 3 | 2017-04-29 | 2018-01-28 | 2014-01-21 13:00 | 3.61 | 0.7003 | A1: Outside Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.9 | 12 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.29 |  | 5.9 | 6.5 | 6.3 | 6.4 | 0.263
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-13 | 80-PL-44008-01C02 CML-13 | yes | FPSO 2015 | Pipe Wall Thickness | 23781 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.225 | CML-13 | CML: Elbow | 3 | 2021-07-22 | 2022-07-04 | 2015-04-18 07:00 | 2.5 | 0.36697 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 6 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 1.4614 | 5.7 | 5 | 4.8 | 5.4 | 0.40311
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-16 | 200-PL-20019-01C02 CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 21267 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 4.8 | CML-16 | CML: Pipe Length | 3 | 2016-09-20 | 2016-09-12 | 2014-09-30 07:00 | 2.5 | 1.1634 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.8 | 9 O'Clock | 15 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.8 | 4.8 | 4.8 | 0
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-53 | 200-PL-20019-01C02 CML-53 | yes | FPSO 2014 | Pipe Wall Thickness | 21304 | Reviewed on 27/11/14. FFS. recheck on Sep.15 | 2014-09-30 07:00 | 2014-09-30 15:00 |  |  | Nestor | 2014-11-27 15:58 | [32 empty] | 4.8 | CML-53 | CML: Pipe Length | 3 | 2016-09-20 | 2016-09-12 | 2014-09-30 07:00 | 2.5 | 1.1634 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.8 | 4.8 | 4.8 | 0
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20068-01C02-P | CML-2 | 100-PL-20068-01C02-P CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 23456 | Re-check on line / Selected CML''s as Per RBI 2014 Report cml 2 only | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 5.25 | CML-2 | CML: Elbow | 3 | 2020-02-23 | 2020-05-14 | 2015-07-23 07:00 | 2.5 | 0.52257 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 6 O'Clock | 100 | 6.02 | 100-PL-20068-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.19678 | 5.4 | 5.2 | 4.9 | 5.5 | 0.26458
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-8 | 50-FG-45023-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12994 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | No readings access restriction | [36 empty] | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-01-20 07:00 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-6 | 250-PG-23004-06C03-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13006 | No data | 2014-01-11 15:00 | 2014-01-11 18:00 | [37 empty] | CML-6 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-5 | 250-PG-23004-06C03-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13005 | No data | 2014-01-11 15:00 | 2014-01-11 18:00 | [37 empty] | CML-5 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-4 | 250-PG-23004-06C03-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13004 | No data | 2014-01-11 15:00 | 2014-01-11 18:00 | [37 empty] | CML-4 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-3 | 250-PG-23004-06C03-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13003 | No data | 2014-01-11 15:00 | 2014-01-11 18:00 | [37 empty] | CML-3 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-2 | 250-PG-23004-06C03-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13002 | No data | 2014-01-11 15:00 | 2014-01-11 18:00 | [37 empty] | CML-2 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-1 | 250-PG-23004-06C03-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13001 | No data | 2014-01-11 15:00 | 2014-01-11 18:00 | [37 empty] | CML-1 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-9 | 250-PG-23015-06C03-A CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 13041 | No data | 2014-01-11 13:00 | 2014-01-11 15:00 | [37 empty] | CML-9 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 13:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-8 | 250-PG-23015-06C03-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13040 | No data | 2014-01-11 13:00 | 2014-01-11 15:00 | [37 empty] | CML-8 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 13:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-7 | 250-PG-23015-06C03-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13039 | No data | 2014-01-11 13:00 | 2014-01-11 15:00 | [37 empty] | CML-7 | CML: Tee | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 13:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-6 | 250-PG-23015-06C03-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13038 | No data | 2014-01-11 13:00 | 2014-01-11 15:00 | [37 empty] | CML-6 | CML: Reducer | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 13:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23016-06C03-A | CML-2 | 250-PG-23016-06C03-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13053 |  | 2014-01-11 07:00 | 2014-01-11 09:00 | [37 empty] | CML-2 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 07:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23016-06C03-A | CML-1 | 250-PG-23016-06C03-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13052 |  | 2014-01-11 07:00 | 2014-01-11 09:00 | [37 empty] | CML-1 | CML: Reducer | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 07:00 | 8.55 | 0 |  |  | 12.26 | 8.55 | 10.405 |  | 9 O'Clock | 250 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23017-03C03-A | CML-5 | 250-PG-23017-03C03-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10979 | Rope Access | 2014-01-09 | 2014-01-09 | [37 empty] | CML-5 | CML: Elbow | 6 | 2096-05-30 | 2084-11-28 | 2014-01-09 | 4.4 | 0 |  |  | 6.7 | 4.4 | 5.55 |  | 9 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-39 | 300-PF-20501-03C03-P CML-39 | yes | FPSO 2014 | Pipe Wall Thickness | 21715 | Reviewed 01/12/14. Low values is considered a typo. To be rechecked | 2014-09-28 07:00 | 2014-09-28 15:00 |  |  | Nestor | 2014-12-01 08:50 | [31 empty] | High alarm breach | 12.075 | CML-39 | CML: type TBC | 6 | 2014-05-22 | 2014-03-19 | 2014-09-28 07:00 | 4.9 | 9.6245 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 1.5 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -3.4 |  | 16.1 | 14.7 | 1.5 | 16 | 7.0788
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-1 | 300-PG-20037-03C03-PA CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 23340 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | Check Corrosion Rate of 5.887mm/ yr | [34 empty] | High alarm breach | 10.95 | CML-1 | CML: Pipe Length | 6 | 2014-12-07 | 2014-09-07 | 2015-07-20 07:00 | 5.33 | 5.8875 | A2: Right Quadrant |  | 8.27 | 5.33 | 6.8 | 1.7 | 3 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -3.63 | 11.1653 | 14 | 1.7 | 13.5 | 14.6 | 6.183
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-24 | 300-PG-20506-03C03-P CML-24 | yes | FPSO 2014 | Pipe Wall Thickness | 13238 | Measured thickness below alarm thickness | 2014-02-04 15:00 | 2014-02-04 18:00 | [35 empty] | Low alarm breach | 12.825 | CML-24 | CML: type TBC | 6 | 2014-04-17 | 2014-02-18 | 2014-02-04 15:00 | 4.9 | 10.6729 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 7 | 3 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 9.9 | 7 | 16.4 | 18 | 5.2296
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-30 | 300-PF-20501-03C03-P CML-30 | yes | FPSO 2014 | Pipe Wall Thickness | 21706 | Reviewed 01/12/14. Low values is considered a typo. To be rechecked | 2014-09-28 07:00 | 2014-09-28 15:00 |  |  | Nestor | 2014-12-01 08:50 | [31 empty] | High alarm breach | 11.95 | CML-30 | CML: type TBC | 6 | 2014-09-13 | 2014-06-20 | 2014-09-28 07:00 | 4.9 | 7.2881 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 4.6 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.3 |  | 14.4 | 14.4 | 4.6 | 14.4 | 4.9
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-5 | 80-PG-23025-06C03 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 13076 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 15.05 | CML-5 | CML: Pipe Length | 6 | 2057-07-12 | 2051-05-12 | 2014-02-07 11:00 | 2.8 | 0.1887 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 11 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11 | 11.2 | 20.5 | 17.5 | 4.7233
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-3 | 250-PG-20036-01C03-P CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 21361 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 14.725 | CML-3 | CML: Equal Tee | 6 | 2081-02-10 | 2077-04-05 | 2014-07-14 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 11.7 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 12.5 | 21.1 | 11.7 | 13.6 | 4.3208
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-9 | 50-PW-44012-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23168 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.975 | CML-9 | CML: Pipe Length | 3 | 2017-10-27 | 2018-04-17 | 2015-05-11 07:00 | 2.5 | 0.68956 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 | 1.1576 | 5.2 | 5.2 | 4.2 | 5.3 | 0.51881
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 23371 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [35 empty] | Low alarm breach | 17.025 | CML-3 | CML: Pipe Length | 6 | 2016-06-25 | 2015-11-24 | 2015-07-21 07:00 | 8.55 | 3.1622 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 11.5 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.95 |  | 20.2 | 18.9 | 17.5 | 11.5 | 3.8448
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-18 | 200-PG-23013-09C03-A CML-18 | yes | FPSO 2014 | Pipe Wall Thickness | 20002 | Rope Access | 2014-01-10 | 2014-01-10 | [35 empty] | Low alarm breach | 17.975 | CML-18 | CML: type TBC | 6 | 2014-05-17 | 2014-03-04 | 2014-01-10 | 10.22 | 10.8354 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 14 | 12 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.78 |  | 14 | 15.6 | 21.1 | 21.2 | 3.7241
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-12 | 300-PF-20003-03C03-P CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 21750 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 17.925 | CML-12 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.6 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 20.9 | 15.4 | 20.8 | 14.6 | 3.3935
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-45 | 300-PF-20001-03C03-P CML-45 | yes | FPSO 2014 | Pipe Wall Thickness | 21183 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 16.75 | CML-45 | CML: Elbow | 6 | 2020-07-29 | 2019-04-16 | 2014-07-16 07:30 | 4.9 | 1.3077 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.8 | 3 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 16.2 | 12.8 | 17 | 21 | 3.368
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-46 | 300-PF-20001-03C03-P CML-46 | yes | FPSO 2014 | Pipe Wall Thickness | 21184 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.507mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:57 | [32 empty] | 16.075 | CML-46 | CML: Fitting | 6 | 2031-11-18 | 2028-07-24 | 2014-07-16 07:30 | 4.9 | 0.50705 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 14.8 | 21 | 14.8 | 13.7 | 3.324
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-30 | 300-PF-20003-03C03-P CML-30 | yes | FPSO 2014 | Pipe Wall Thickness | 21768 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 16.1 | CML-30 | CML: Elbow | 6 | 2035-05-07 | 2031-05-27 | 2014-10-01 07:00 | 4.9 | 0.42695 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 13.7 | 15.7 | 20.8 | 14.2 | 3.2465
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-1 | 200-PG-23008-15S01-A CML-1 | Yes | FPSO 2013 | Pipe Wall Thickness | 10087 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 23.075 | CML-1 | CML: Pipe Length | 1 | 2014-11-28 | 2014-03-31 | 2013-11-07 | 14.06 | 5.9915 | A3: Inside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 26.9 | 24.6 | 20.4 | 20.4 | 3.2284
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-16 | 300-PF-20500-03C03-P CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 21638 | Reviewed on Reading 300x150mm area to 10mm Outside Radius. It appears to be a material feature (e.g. a lamination) | 2014-09-27 07:00 | 2014-09-27 15:00 | Low alarm breach | 2 | Nestor | 2014-11-27 17:15 | [32 empty] | 14.75 | CML-16 | CML: Elbow | 6 | 2016-04-26 | 2015-10-18 | 2014-09-27 07:00 | 4.9 | 3.2249 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 10 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 16.8 | 15.7 | 10 | 16.5 | 3.2005
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-3 | 80-PG-20046-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21462 | Protective mesh removed | 2014-06-28 08:00 | 2014-06-28 09:00 | [36 empty] | 12.95 | CML-3 | CML: Equal Tee | 6 | 2041-07-04 | 2037-03-23 | 2014-06-28 08:00 | 2.5 | 0.30701 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.8 | 6 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 17.3 | 10.8 | 12.9 | 3.0643
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-1 | 80-PW-20024-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23045 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 5.925 | CML-1 | CML: Pipe Length | 6 | 2016-05-15 | 2015-12-03 | 2015-05-06 07:00 | 2.5 | 2.9177 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 5.5 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 5.9 | 5.5 | 6.4 | 0.36856
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-44 | 300-PF-20001-03C03-P CML-44 | Yes | FPSO 2014 | Pipe Wall Thickness | 21182 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 16.975 | CML-44 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.4 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 17.2 | 15.2 | 21.1 | 14.4 | 2.9915
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-27 | 300-PF-20003-03C03-P CML-27 | Yes | FPSO 2014 | Pipe Wall Thickness | 21765 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 16.825 | CML-27 | CML: Elbow | 6 | 2040-01-05 | 2035-03-25 | 2014-10-01 07:00 | 4.9 | 0.35205 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 3 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 20.8 | 13.8 | 15.8 | 16.9 | 2.9443
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-21 | 25-VA-23054-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21430 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 18.7 | CML-21 | CML: Reducer | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A1: Outside Quadrant |  | 6.7 | 4.1 | 5.4 | 14.7 | 12 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.6 |  | 14.7 | 18.5 | 20.8 | 20.8 | 2.8787
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-10 | 100-DH-56088-01C02 CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 5203 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [35 empty] | Low alarm breach | 6.725 | CML-10 | CML: Equal Tee | 3 | 2014-05-20 | 2014-05-31 | 2014-05-20 07:00 | 2.5 | 3.6367 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 2.5 | 3 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 |  | 8 | 2.5 | 8.3 | 8.1 | 2.8194
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-14 | 200-PG-23013-09C03-A CML-14 | Yes | FPSO 2014 | Pipe Wall Thickness | 10998 | Rope Access | 2014-01-10 | 2014-01-10 | [35 empty] | Low alarm breach | 17.875 | CML-14 | CML: type TBC | 6 | 2014-06-21 | 2014-03-31 | 2014-01-10 | 10.22 | 9.8534 | A2: Right Quadrant |  | 14.62 | 10.22 | 12.42 | 14.6 | 3 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.38 |  | 16.8 | 14.6 | 21.1 | 19 | 2.8016
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-8 | 50-PG-44022-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5851 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 11.5 | CML-8 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-06-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.6 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 15.5 | 11.2 | 9.6 | 9.7 | 2.7653
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-29 | 50-CG-38452-09C02-P CML-29 | yes | FPSO 2014 | Pipe Wall Thickness | 21767 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 18.475 | CML-29 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 15.7 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.8 |  | 16.6 | 20.8 | 20.8 | 15.7 | 2.7097
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-6 | 300-PG-20049-03C03-P CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24473 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 1.213mm/ yr | 39 | Kirstie Albone | 2017-03-23 13:10 | [32 empty] | 14.275 | CML-6 | CML: Equal Tee | 6 | 2021-02-18 | 2019-09-30 | 2016-07-09 07:00 | 4.9 | 1.2131 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 10.5 | 12 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 | 0.10282 | 10.5 | 16.2 | 15.8 | 14.6 | 2.6069
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 21624 | Protective mesh removed | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 17.55 | CML-4 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 15.8 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 21.4 | 16.2 | 15.8 | 16.8 | 2.5994
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-16 | 80-CG-38459-09C02-P CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 13016 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 22.7333 | CML-16 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 21.2 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.65 |  | 21.2 | 25.7 | 21.3 |  | 2.5697
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-6 | 150-PG-23506-25C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2780 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 23.3 | CML-6 | CML: Elbow | 3 | 2027-01-22 | 2023-08-11 | 2014-03-15 09:00 | 15.88 | 0.44454 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 21.6 | 3 O'Clock | 50 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.72 |  | 22.2 | 21.6 | 27.1 | 22.3 | 2.5521
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-10 | 50-PG-44022-01C03-P CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 22985 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 11.45 | CML-10 | CML: Reducer | 6 | 2024-12-13 | 2024-09-23 | 2015-05-04 07:00 | 2.5 | 0.54052 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.7 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 | 6.4137 | 12.8 | 12.4 | 7.7 | 12.9 | 2.5093
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-2 | 300-PG-20005-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6158 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 16.55 | CML-2 | CML: Elbow | 6 | 2022-04-20 | 2020-09-14 | 2014-07-11 07:30 | 4.9 | 1.0536 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.1 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 13.1 | 19 | 16.8 | 17.3 | 2.4853
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-42 | 50-CG-38452-09C02-P CML-42 | yes | FPSO 2014 | Pipe Wall Thickness | 21780 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 15.425 | CML-42 | CML: Elbow | 6 | 2020-06-23 | 2019-03-17 | 2014-10-01 07:00 | 4.9 | 1.3258 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.5 | 3 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 14.4 | 12.5 | 16.7 | 18.1 | 2.4757
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-19 | 50-CG-38487-09C02-P CML-19 | yes | FPSO 2015 | Pipe Wall Thickness | 23588 | Re-check of line as requested by ops supervisor (Additional CML @ corroded location) | 2015-09-10 07:00 | 2015-09-10 09:00 | Check Corrosion Rate of 2.081mm/ yr |  | John Wilson | 2017-03-24 11:13 | Need a revisit MAWT due 2016. | [30 empty] | Medium alarm breach | 6.075 | CML-19 | CML: Pipe Length | 3 | 2016-05-30 | 2015-08-20 | 2015-09-10 07:00 | 2.5 | 2.0812 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 4 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 8.7 | 4 | 7.6 | 4 | 2.4377
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-14 | 50-CG-38452-09C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21634 | Reviewed on 27/11/14. FFS. Recheck on Sep. 15 | 2014-09-27 07:00 | 2014-09-27 15:00 |  |  | Nestor | 2014-11-27 17:36 | [32 empty] | 14.55 | CML-14 | CML: Elbow | 6 | 2020-01-17 | 2018-11-08 | 2014-09-27 07:00 | 4.9 | 1.4123 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.4 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 12.4 | 15.9 | 12.6 | 17.3 | 2.4365
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-18 | 50-CG-38487-09C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 20857 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 11.45 | CML-18 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-10-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.1 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 | 26.9538 | 10.1 | 15 | 10.4 | 10.3 | 2.37
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-12 | 250-PG-23015-06C03-A CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 20080 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 19.95 | CML-12 | CML: type TBC | 6 | 2018-08-05 | 2017-08-09 | 2014-05-29 07:00 | 8.55 | 1.8739 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.4 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.85 |  | 21.1 | 21.2 | 16.4 | 21.1 | 2.3671
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-12 | 250-PG-23015-06C03-A CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 20049 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 19.95 | CML-12 | CML: type TBC | 6 | 2018-08-05 | 2017-08-09 | 2014-05-29 07:00 | 8.55 | 1.8739 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.4 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.85 | 0 | 21.1 | 21.2 | 16.4 | 21.1 | 2.3671
DC03 | Montara_Topside | No | Closed Drain (57) | Pipework | 0100-DC-57L9001-AS20-00 | CML-1 | 0100-DC-57L9001-AS20-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5057 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.55 | CML-1 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.5 | 6 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.6 | 3.5 | 3.5 | 3.6 | 0.057735
GN02 | Montara_Topside | No | Nitrogen (67) | Pipework | 0100-GN-67L9000-AS20-00 | CML-6 | 0100-GN-67L9000-AS20-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5005 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [36 empty] | 3.625 | CML-6 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-03 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.5 | 6 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.7 | 3.7 | 3.5 | 3.6 | 0.095743
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-12 | 250-PG-23015-06C03-A CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 13044 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 19.95 | CML-12 | CML: type TBC | 6 | 2016-08-16 | 2016-01-05 | 2014-01-11 13:00 | 8.55 | 3.0235 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.4 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.85 |  | 21.1 | 21.2 | 16.4 | 21.1 | 2.3671
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-5 | 100-FG-45001-09C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10420 | Deck Level | 2013-11-13 | 2013-11-13 | T Alarm. 12 Oclock | [34 empty] | Low alarm breach | 10.125 | CML-5 | CML: type TBC | 3 | 2014-02-25 | 2013-12-15 | 2013-11-13 | 4.7 | 8.6936 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 7.2 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 7.2 | 9.5 | 12.6 | 11.2 | 2.3258
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-6 | 200-PG-23505-09C02-A CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 5505 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 18.25 | CML-6 | CML: Elbow | 3 | 2017-05-14 | 2016-10-20 | 2014-05-31 07:00 | 14.06 | 1.0621 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | 0 | 17.2 | 19.3 | 19 | 17.5 | 1.0536
VA02 | Montara_Topside | No | Flare (43) | Pipework | 0100-VA-43L9002-AS20-00 | CML-11 | 0100-VA-43L9002-AS20-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5126 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.575 | CML-11 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.5 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.7 | 3.6 | 3.5 | 3.5 | 0.095743
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80001-01C02 | CML-2 | 50-VA-80001-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3135 | Rope Access | 2014-05-02 09:30 | 2014-05-02 10:30 | [36 empty] | 6.3 | CML-2 | CML: type TBC | 3 | 2017-10-11 | 2018-03-31 | 2014-05-02 09:30 | 2.5 | 0.69649 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-VA-80001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 9.7 | 4.9 | 5.4 | 5.2 | 2.276
VA02 | Montara_Topside | No | Flare (43) | Pipework | 0100-VA-43L9002-AS20-00 | CML-10 | 0100-VA-43L9002-AS20-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5125 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.65 | CML-10 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.5 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.8 | 3.6 | 3.7 | 3.5 | 0.1291
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45024-01C02 | CML-2 | 50-FG-45024-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20841 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 12.5 | CML-2 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-10-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 12.5143 | 9.2 | 14.1 | 13.9 | 12.8 | 2.273
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-9 | 300-PG-20048-03C03-P CML-9 |  | FPSO 2016 | Pipe Wall Thickness | 24480 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.73mm/ yr | 38 | Kirstie Albone | 2017-03-23 12:40 | [32 empty] | 14 | CML-9 | CML: Elbow | 6 | 2026-03-27 | 2023-12-06 | 2016-07-09 07:00 | 4.9 | 0.73046 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 12 | 6 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 | 0 | 12.1 | 15.6 | 12 | 16.3 | 2.2701
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 6509 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 16.5 | CML-3 | CML: Elbow | 6 | 2022-08-03 | 2020-12-08 | 2014-07-24 07:30 | 4.9 | 1.0209 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.1 | 12 O'Clock | 300 | 14.27 | 300-PF-20509-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 13.1 | 17.6 | 17.7 | 17.6 | 2.2672
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-6 | 200-PG-23505-09C02-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20653 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 18.25 | CML-6 | CML: Elbow | 3 | 2017-05-14 | 2016-10-20 | 2014-05-31 07:00 | 14.06 | 1.0621 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | -0.91345 | 17.2 | 19.3 | 19 | 17.5 | 1.0536
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-13 | 300-PF-20001-03C03-P CML-13 | Yes | FPSO 2014 | Pipe Wall Thickness | 21151 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.685mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:40 | [32 empty] | 14.975 | CML-13 | CML: Elbow | 6 | 2027-02-01 | 2024-08-17 | 2014-07-16 07:30 | 4.9 | 0.68497 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 3 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 18.2 | 13.5 | 14 | 14.2 | 2.1701
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-5 | 300-PG-20049-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21491 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | [36 empty] | 14.225 | CML-5 | CML: Elbow | 6 | 2020-04-06 | 2019-01-12 | 2014-06-28 10:45 | 4.9 | 1.3672 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.8 | 3 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 13 | 12.8 | 13.7 | 17.4 | 2.1515
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-12 | 80-CG-38459-09C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10962 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 19.8667 | CML-12 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A2: Right Quadrant |  | 8.27 | 5.22 | 6.745 | 17.4 | 3 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.18 |  | 21.1 | 17.4 | 21.1 |  | 2.1362
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42043-01S01 | CML-2 | 50-CI-42043-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7475 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 1.039mm/ yr | [34 empty] | Low alarm breach | 5.075 | CML-2 | CML: Elbow | 1 | 2016-05-03 | 2015-09-09 | 2015-04-13 07:00 | 2.5 | 1.0393 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.6 | 9 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 4.7 | 6.7 | 5.3 | 3.6 | 1.292
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML121 | 100-WF-71309-01K01 CML121 |  | FPSO 2015 | Pipe Wall Thickness | 7460 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 3.725 | CML121 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.9 | 3.7 | 3.6 | 3.7 | 0.12583
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71309-01K01 | CML115 | 100-WF-71309-01K01 CML115 |  | FPSO 2015 | Pipe Wall Thickness | 7454 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 3.85 | CML115 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 4.2 | 3.9 | 3.7 | 3.6 | 0.26458
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71346-01K01 | CML-1 | 150-WF-71346-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6669 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 12:32 | [32 empty] | 3.875 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 12 O'Clock | 150 | 3 | 150-WF-71346-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.7 | 4.4 | 3.8 | 0.3594
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71347-01K01 | CML-3 | 150-WF-71347-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6666 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 12:55 | [32 empty] | 4 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 3 O'Clock | 150 | 3 | 150-WF-71347-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.6 | 4.3 | 4.4 | 0.40825
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71361-01K01 | CML-17 | 40-WF-71361-01K01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6650 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:24 | [32 empty] | 3.675 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 6 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.7 | 3.6 | 3.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71361-01K01 | CML-9 | 40-WF-71361-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6642 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:13 | [32 empty] | 3.675 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 12 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.7 | 3.7 | 3.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71361-01K01 | CML-3 | 40-WF-71361-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6636 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 14:06 | [32 empty] | 3.775 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 3 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.6 | 3.7 | 4.2 | 0.28723
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71335-01K01 | CML-3 | 150-WF-71335-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6401 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.7 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 9 O'Clock | 150 | 3 | 150-WF-71335-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.8 | 3.8 | 3.6 | 0.11547
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71341-01K01 | CML-10 | 80-WF-71341-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6289 | Cast Fitting, Reading taken on adjacent piping. Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.625 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.7 | 3.6 | 3.6 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71334-01K01 | CML-18 | 40-WF-71334-01K01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6367 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.625 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 6 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.6 | 3.6 | 3.7 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71334-01K01 | CML-15 | 40-WF-71334-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6364 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.7 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.8 | 3.7 | 3.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71348-01K01 | CML-1 | 50-WF-71348-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6221 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 4.15 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 3 O'Clock | 50 | 2.5 | 50-WF-71348-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 4.5 | 3.6 | 4.2 | 4.3 | 0.3873
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71359-01K01 | CML-7 | 100-WF-71359-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6216 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.7 | CML-7 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 9 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.7 | 3.8 | 3.6 | 0.08165
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71359-01K01 | CML-1 | 100-WF-71359-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6210 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 4.2 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 12 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 4.1 | 4.9 | 4.2 | 0.53541
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-75 | 80-WF-71310-01K01 CML-75 |  | FPSO 2015 | Pipe Wall Thickness | 5560 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 3.975 | CML-75 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.6 | 12 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 4.8 | 3.7 | 3.8 | 0.55603
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-4 | 80-PG-20046-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21463 | Protective mesh removed | 2014-06-28 08:00 | 2014-06-28 09:00 | [36 empty] | 14.425 | CML-4 | CML: Equal Tee | 6 | 2099-09-17 | 2086-07-24 | 2014-06-28 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 11.6 | 3 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 14.3 | 11.6 | 16.7 | 15.1 | 2.1313
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-26 | 300-PG-20004-03C03-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 6149 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 15.1 | CML-26 | CML: Elbow | 6 | 2018-06-09 | 2017-07-14 | 2014-07-11 07:30 | 4.9 | 1.8641 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 12.2 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 16.7 | 14.8 | 16.7 | 12.2 | 2.1307
CG03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-CG-38486-09C02-P | CML-12 | 80-CG-38486-09C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22877 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 17.325 | CML-12 | CML: Equal Tee | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 15.6 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.1 | -0.18814 | 16.7 | 20.4 | 15.6 | 16.6 | 2.1093
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-2 | 300-PG-20048-03C03-P CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24477 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.344mm/ yr | 38 | Kirstie Albone | 2017-03-23 12:54 | [32 empty] | 15.1 | CML-2 | CML: Elbow | 6 | 2040-08-11 | 2035-09-20 | 2016-07-09 07:00 | 4.9 | 0.34431 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 3 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 | -0.6169 | 13.4 | 13.2 | 17.2 | 16.6 | 2.0944
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-37 | 250-PW-44006-01X01 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 23208 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.525 | CML-37 | CML: Elbow | 3 | 2016-11-22 | 2016-11-12 | 2015-05-11 07:00 | 2.5 | 1.1064 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.2 | 12 O'Clock | 50 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 | 2.3031 | 4.2 | 4.3 | 4.5 | 5.1 | 0.40311
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-1 | 50-PW-44015-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5711 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 4.65 | CML-1 | CML: Elbow | 3 | 2015-10-25 | 2016-01-27 | 2014-06-22 10:00 | 2.5 | 1.2657 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 | 6.9937 | 4.7 | 5.1 | 4.6 | 4.2 | 0.36968
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-18 | 50-CG-38487-09C02-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23587 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 14.275 | CML-18 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 12.4 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 | -2.4475 | 12.4 | 16.9 | 15 | 12.8 | 2.0903
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-11 | 250-PG-23004-06C03-A CML-11 | yes | FPSO 2014 | Pipe Wall Thickness | 20529 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 20.55 | CML-11 | CML: Elbow | 6 | 2026-02-15 | 2023-09-12 | 2014-05-30 09:30 | 8.55 | 0.76335 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.5 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.95 | -0.26302 | 17.5 | 21.2 | 22 | 21.5 | 2.0599
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-11 | 250-PG-23004-06C03-A CML-11 | yes | FPSO 2014 | Pipe Wall Thickness | 13011 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 20.4 | CML-11 | CML: Elbow | 6 | 2020-05-11 | 2019-01-12 | 2014-01-11 15:00 | 8.55 | 1.3974 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.4 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.85 |  | 17.4 | 21.1 | 22 | 21.1 | 2.0445
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-16 | 200-PG-23013-09C03-A CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 20000 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 18.85 | CML-16 | CML: type TBC | 6 | 2014-11-07 | 2014-07-19 | 2014-01-10 | 10.22 | 7.2345 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 16.2 | 6 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.98 |  | 18.3 | 20.4 | 16.2 | 20.5 | 2.0372
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20002-03C03-P | CML-6 | 300-PF-20002-03C03-P CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 6518 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:11 | [32 empty] | 19.35 | CML-6 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-24 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 17 | 3 O'Clock | 300 | 14.27 | 300-PF-20002-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.1 |  | 21 | 17 | 21.1 | 18.3 | 2.0339
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-15 | 250-PG-23003-06C02-PA CML-15 | Yes | FPSO 2014 | Pipe Wall Thickness | 24253 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 17.975 | CML-15 | CML: Reducing Tee | 3 | 2085-04-24 | 2073-10-17 | 2014-09-24 07:00 | 7.9 | 0 | A2: Right Quadrant |  | 12.09 | 7.9 | 9.0519 | 16.3 | 3 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 20.9 | 16.3 | 17.2 | 17.5 | 2.0156
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-20 | 50-PL-23042-09C03 CML-20 | yes | FPSO 2013 | Pipe Wall Thickness | 10085 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 12.925 | CML-20 | CML: type TBC | 6 | 2017-09-14 | 2017-01-22 | 2013-11-07 | 2.5 | 1.9972 | A4: Left Quadrant |  | 5.07 | 2.5 | 3.785 | 10.2 | 9 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 14.4 | 14.4 | 12.7 | 10.2 | 1.9856
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56554-01C02 | CML-3 | 50-DH-56554-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21122 | Reviewed on 20/11/14. FFS. Recheck in Oct. 18. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-20 16:37 | [32 empty] | 6.325 | CML-3 | CML: Reducer | 3 | 2030-07-23 | 2032-05-24 | 2014-10-08 07:00 | 2.5 | 0.17722 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56554-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 9.3 | 5.3 | 5.3 | 1.9839
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-4 | 300-PG-20049-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21490 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | [36 empty] | 14.475 | CML-4 | CML: Elbow | 6 | 2020-04-06 | 2019-01-12 | 2014-06-28 10:45 | 4.9 | 1.3672 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 12.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 17.3 | 14.3 | 13.5 | 12.8 | 1.9805
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-29 | 300-PF-20001-03C03-P CML-29 | Yes | FPSO 2014 | Pipe Wall Thickness | 21167 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.774mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:35 | [32 empty] | 15.7 | CML-29 | CML: Elbow | 6 | 2025-07-07 | 2023-05-04 | 2014-07-16 07:30 | 4.9 | 0.77392 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 17.8 | 16.8 | 14.8 | 13.4 | 1.9765
VA02 | Montara_Topside | No | Flare (43) | Pipework | 0100-VA-43L9002-AS20-00 | CML-13 | 0100-VA-43L9002-AS20-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5128 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.725 | CML-13 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.6 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.8 | 3.8 | 3.7 | 3.6 | 0.095743
VA02 | Montara_Topside | No | Flare (43) | Pipework | 0100-VA-43L9002-AS20-00 | CML-6 | 0100-VA-43L9002-AS20-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5121 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.725 | CML-6 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.6 | 12 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.7 | 3.7 | 3.9 | 0.12583
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9001-AS20-00 | CML-6 | 0100-AS-63L9001-AS20-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5015 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | [36 empty] | 5 | CML-6 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-04 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.6 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 5.2 | 5.8 | 5.4 | 3.6 | 0.96609
GN02 | Montara_Topside | No | Nitrogen (67) | Pipework | 0100-GN-67L9000-AS20-00 | CML-7 | 0100-GN-67L9000-AS20-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5006 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [36 empty] | 3.7 | CML-7 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-03 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.6 | 9 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.9 | 3.6 | 3.6 | 0.14142
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-6 | 300-PG-20049-03C03-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23351 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 12.475 | CML-6 | CML: Equal Tee | 6 | 2018-11-11 | 2017-11-18 | 2015-07-20 07:00 | 4.9 | 1.7189 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 10.6 | 3 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | 2.5475 | 13.7 | 10.6 | 14.6 | 11 | 1.9755
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-8 | 300-PG-20048-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21478 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 15.025 | CML-8 | CML: Elbow | 6 | 2021-05-05 | 2019-12-01 | 2014-06-28 09:30 | 4.9 | 1.1813 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13 | 9 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 13.7 | 16.7 | 16.7 | 13 | 1.9551
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-8 | 50-PL-23052-09C03 CML-8 | yes | FPSO 2013 | Pipe Wall Thickness | 10172 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 12.925 | CML-8 | CML: type TBC | 6 | 2016-10-25 | 2016-05-08 | 2013-11-09 | 2.81 | 2.4258 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 10 | 6 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.19 |  | 14 | 14 | 10 | 13.7 | 1.9551
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62004-01S01 | CML-8 | 50-DO-62004-01S01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1457 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [35 empty] | Low alarm breach | 3.925 | CML-8 | CML: type TBC | 1 | 2014-10-28 | 2014-07-06 | 2014-04-25 10:00 | 2.5 | 2.1561 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.6 | 9 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 4 | 4.4 | 3.6 | 0.3594
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-8 | 150-PL-43303-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23523 | Re-check on line as Per RBI 2014 Report | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 4.775 | CML-8 | CML: type TBC | 3 |  |  | 2015-07-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 4.6 | 12 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0.8014 | 4.6 | 4.9 | 4.7 | 4.9 | 0.15
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-15 | 150-PL-43303-01C02 CML-15 | Yes | FPSO 2016 | Pipe Wall Thickness | 24500 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.825 | CML-15 | CML: Pipe Length | 3 | 2018-07-19 | 2019-02-05 | 2016-07-09 07:00 | 2.5 | 0.59209 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | 0.19682 | 3.9 | 3.9 | 3.7 | 3.8 | 0.095743
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-9 | 150-PL-43303-01C02 CML-9 | Yes | FPSO 2016 | Pipe Wall Thickness | 24496 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.825 | CML-9 | CML: Pipe Length | 3 | 2018-07-19 | 2019-02-05 | 2016-07-09 07:00 | 2.5 | 0.59209 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | -0.19682 | 3.9 | 3.7 | 3.8 | 3.9 | 0.095743
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-6 | 150-PL-43303-01C02 CML-6 | Yes | FPSO 2016 | Pipe Wall Thickness | 24493 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.8 | CML-6 | CML: Pipe Length | 3 | 2018-07-19 | 2019-02-05 | 2016-07-09 07:00 | 2.5 | 0.59209 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | -0.09841 | 3.8 | 3.8 | 3.9 | 3.7 | 0.08165
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-5 | 150-PL-43303-01C02 CML-5 | Yes | FPSO 2016 | Pipe Wall Thickness | 24492 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.8 | CML-5 | CML: Pipe Length | 3 | 2018-07-19 | 2019-02-05 | 2016-07-09 07:00 | 2.5 | 0.59209 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | -0.29523 | 3.9 | 3.8 | 3.8 | 3.7 | 0.08165
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-PL-43303-01C02 | CML-1 | 150-PL-43303-01C02 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24432 | Re-check as requested by N.Sequera | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.596mm/ yr | [35 empty] | 4.55 | CML-1 | CML: Elbow | 3 | 2018-07-07 | 2019-01-23 | 2016-07-02 07:00 | 2.5 | 0.59576 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 3 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | 0 | 5.4 | 3.7 | 4.6 | 4.5 | 0.69522
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-5 | 150-PL-43303-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23522 | Re-check on line as Per RBI 2014 Report | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 5.125 | CML-5 | CML: type TBC | 3 |  |  | 2015-07-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5 | 6 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.36427 | 5 | 5.3 | 5 | 5.2 | 0.15
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-17 | 150-PL-43303-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23304 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.775 | CML-17 | CML: Elbow | 3 | 2016-11-13 | 2017-03-28 | 2015-07-04 09:30 | 2.5 | 0.87975 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | -0.85401 | 3.8 | 3.7 | 3.7 | 3.9 | 0.095743
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-14 | 150-PL-43303-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23301 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.85 | CML-14 | CML: Pipe Length | 3 | 2016-11-13 | 2017-03-28 | 2015-07-04 09:30 | 2.5 | 0.87975 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | -0.64051 | 4 | 3.8 | 3.7 | 3.9 | 0.1291
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-13 | 150-PL-43303-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23300 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.875 | CML-13 | CML: Elbow | 3 | 2016-11-13 | 2017-03-28 | 2015-07-04 09:30 | 2.5 | 0.87975 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | -0.2135 | 3.8 | 4.1 | 3.9 | 3.7 | 0.17078
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-3 | 150-PL-43303-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23290 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.9 | CML-3 | CML: Fitting | 3 | 2016-11-13 | 2017-03-28 | 2015-07-04 09:30 | 2.5 | 0.87975 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | -0.427 | 3.8 | 3.7 | 4 | 4.1 | 0.18257
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-PL-43303-01C02 | CML-1 | 150-PL-43303-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23119 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | Check Corrosion Rate of 0.948mm/ yr | [35 empty] | 4.425 | CML-1 | CML: Elbow | 3 | 2016-08-14 | 2016-12-17 | 2015-05-10 07:00 | 2.5 | 0.9482 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 6 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 | 0.89713 | 4.4 | 4.9 | 3.7 | 4.7 | 0.5252
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML - 2 | 150-PL-43303-01C02 CML - 2 |  | FPSO 2015 | Pipe Wall Thickness | 22571 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 4.1 | CML - 2 | CML: Equal Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 1.5 | 2.5 | 1.875 | 3.7 | 12 O'Clock | 80 | 2 | 0300-WF-71L9002-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 4.3 | 4.2 | 4.2 | 0.2708
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-9 | 150-PL-43303-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2227 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.525 | CML-9 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.3 | 6 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.7 | 5.3 | 5.4 | 0.20616
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML55 | 150-PL-43303-01C02 CML55 |  | FPSO 2015 | Pipe Wall Thickness | 7587 |  | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 17:08 | [32 empty] | 3.875 | CML55 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 3.7 | 4 | 3.9 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML44 | 150-PL-43303-01C02 CML44 |  | FPSO 2015 | Pipe Wall Thickness | 7576 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 3.9 | CML44 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4 | 3.7 | 3.9 | 4 | 0.14142
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43303-01C02 | CML-3 | 150-PL-43303-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7476 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 0.986mm/ yr | [34 empty] | Low alarm breach | 4.975 | CML-3 | CML: Elbow | 1 | 2016-06-30 | 2015-10-25 | 2015-04-13 07:00 | 2.5 | 0.98577 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.7 | 9 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.6 | 6.8 | 4.8 | 3.7 | 1.3074
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-5 | 150-PL-43303-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2223 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.65 | CML-5 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.5 | 9 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 5.7 | 5.7 | 5.5 | 0.1
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-10 | 150-PL-43303-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2228 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.8 | CML-10 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.6 | 9 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.9 | 5.9 | 5.6 | 0.14142
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML28 | 150-PL-43303-01C02 CML28 |  | FPSO 2015 | Pipe Wall Thickness | 7367 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 4.075 | CML28 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.3 | 4 | 4.3 | 3.7 | 0.28723
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML19 | 150-PL-43303-01C02 CML19 |  | FPSO 2015 | Pipe Wall Thickness | 7208 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [36 empty] | 3.95 | CML19 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4 | 3.7 | 3.9 | 4.2 | 0.20817
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-4 | 150-PL-43303-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6667 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 12:30 | [32 empty] | 4.05 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 3 O'Clock | 150 | 3 | 150-WF-71347-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.4 | 3.7 | 4.3 | 3.8 | 0.35119
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-2 | 150-PL-43303-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6665 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 12:54 | [32 empty] | 4.175 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 3 O'Clock | 150 | 3 | 150-WF-71347-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.4 | 3.7 | 4.2 | 4.4 | 0.3304
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-2 | 150-PL-43303-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6635 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 4.075 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 3 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 3.7 | 4.3 | 4.4 | 0.3304
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-4 | 150-PL-43303-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6620 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.75 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.8 | 3.8 | 3.7 | 3.7 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-1 | 150-PL-43303-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6403 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 4.15 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 3 O'Clock | 100 | 3 | 100-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.1 | 3.7 | 4.3 | 4.5 | 0.34157
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-4 | 150-PL-43303-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6283 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.8 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 3 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.8 | 3.7 | 3.9 | 3.8 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-4 | 150-PL-43303-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6388 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.75 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 9 O'Clock | 40 | 2.5 | 40-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 3.7 | 3.7 | 3.7 | 0.1
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-26 | 150-PL-43303-01C02 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 6305 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.7 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 9 O'Clock | 80 | 2.5 | 80-WF-71341-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.7 | 3.7 | 3.7 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-8 | 150-PL-43303-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6260 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 4 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 3 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.1 | 3.7 | 4.2 | 4 | 0.21602
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-2 | 150-PL-43303-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6195 | Rope Access | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 3.975 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 3 O'Clock | 50 | 2.5 | 50-WF-71363-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 3.7 | 4 | 4.3 | 0.25
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-8 | 150-PL-43303-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6118 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.95 | CML-8 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 12 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.8 | 4.1 | 4.2 | 0.23805
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-5 | 150-PL-43303-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5976 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.875 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 6 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.1 | 3.8 | 3.7 | 3.9 | 0.17078
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-18 | 150-PL-43303-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5971 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.15 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 3 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.1 | 3.7 | 4.5 | 4.3 | 0.34157
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-23 | 150-PL-43303-01C02 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 5905 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.875 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 4.1 | 3.8 | 3.7 | 0.17078
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-9 | 150-PL-43303-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5429 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.15 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 9 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.5 | 4.5 | 3.9 | 3.7 | 0.41231
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-37 | 150-PL-43303-01C02 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 5415 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.425 | CML-37 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 12 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 4.1 | 5 | 4.9 | 0.62915
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-6 | 150-PL-43303-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2224 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.925 | CML-6 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.6 | 12 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6 | 6.2 | 5.9 | 0.25
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-11 | 150-PL-43303-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2229 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.7 | CML-11 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.7 | 9 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.7 | 5.7 | 5.7 | 0
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-8 | 150-PL-43303-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2226 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.95 | CML-8 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.7 | 12 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.2 | 5.8 | 6.1 | 0.23805
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-6 | 150-PL-43303-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5324 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.925 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 3 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.1 | 3.7 | 4 | 3.9 | 0.17078
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-1 | 150-PL-43303-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5319 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.825 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 6 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4 | 3.8 | 3.7 | 3.8 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-21 | 150-PL-43303-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 5266 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.9 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.8 | 4 | 4.1 | 0.18257
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-42 | 150-PL-43303-01C02 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 5287 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.875 | CML-42 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 3.8 | 4.1 | 3.7 | 0.17078
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-38 | 150-PL-43303-01C02 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 5283 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.95 | CML-38 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.8 | 4.3 | 4 | 0.26458
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-36 | 150-PL-43303-01C02 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 5281 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.775 | CML-36 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.8 | 3.7 | 3.9 | 3.7 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-53 | 150-PL-43303-01C02 CML-53 |  | FPSO 2015 | Pipe Wall Thickness | 5298 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.825 | CML-53 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.7 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.8 | 3.9 | 3.9 | 0.095743
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-13 | 150-PL-43303-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2231 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.925 | CML-13 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.8 | 9 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 5.9 | 5.9 | 5.8 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-2 | 150-PL-43303-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5131 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.7 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 9 O'Clock | 150 | 3 | 150-WF-71315-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.7 | 3.7 | 3.7 | 0
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-7 | 150-PL-43303-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5122 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.725 | CML-7 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.7 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.8 | 3.7 | 3.7 | 0.05
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-5 | 150-PL-43303-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5120 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.825 | CML-5 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.7 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 3.9 | 3.8 | 3.7 | 0.095743
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43303-01C02 | CML-1 | 150-PL-43303-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8516 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [35 empty] | Low alarm breach | 4.325 | CML-1 | CML: type TBC | 1 | 2016-03-08 | 2015-07-28 | 2015-02-03 07:30 | 2.5 | 1.0968 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.7 | 3 O'Clock | 50 | 5.54 | 50-VA-80014-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.6 | 3.7 | 4.2 | 4.8 | 0.48563
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43303-01C02 | CML-2 | 150-PL-43303-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8514 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [35 empty] | Low alarm breach | 4.2 | CML-2 | CML: type TBC | 1 | 2016-03-08 | 2015-07-28 | 2015-02-03 07:30 | 2.5 | 1.0968 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.7 | 3 O'Clock | 50 | 5.54 | 50-VA-80012-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.1 | 3.7 | 4.2 | 4.8 | 0.45461
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-15 | 150-PL-43303-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 7887 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:44 | [32 empty] | 3.825 | CML-15 | CML: Pipe Length | 3 | 2016-02-04 | 2016-05-19 | 2015-01-14 10:30 | 2.5 | 1.1336 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.8 | 4 | 3.8 | 3.7 | 0.12583
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-6 | 150-PL-43303-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7878 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:42 | [32 empty] | 3.75 | CML-6 | CML: Pipe Length | 3 | 2016-02-04 | 2016-05-19 | 2015-01-14 10:30 | 2.5 | 1.1336 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.8 | 3.7 | 3.8 | 3.7 | 0.057735
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-2 | 150-PL-43303-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7874 | It is noted that on the isometric drawing this line has the schedule as Sch80 (5.54mm). It is believed that the majority of this line (CML2-9 & CML12-18) is actually Sch40 (3.91mm). Line has been rechecked and confirmed as Sch. 40 (wrong schedule). Upon discussions with Senior Process Engineer a decision to downgrade the line to SCH. 40 was agreed. | 2015-01-14 10:30 | 2015-01-14 14:00 |  |  | Administrator | 2015-09-06 21:40 | [32 empty] | 3.8 | CML-2 | CML: Elbow | 3 | 2016-02-04 | 2016-05-19 | 2015-01-14 10:30 | 2.5 | 1.1336 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 12 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.9 | 3.8 | 3.8 | 0.08165
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-12 | 150-PL-43303-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2230 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.125 | CML-12 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.8 | 6 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.5 | 5.8 | 6.4 | 0.37749
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43303-01C02 | CML-4 | 150-PL-43303-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3084 | Rope Access | 2014-05-04 11:30 | 2014-05-04 12:00 | Check Corrosion Rate of 1.99mm/ yr | [34 empty] | Low alarm breach | 4.15 | CML-4 | CML: Elbow | 1 | 2014-12-10 | 2014-08-09 | 2014-05-04 11:30 | 2.5 | 1.9901 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.7 | 3 O'Clock | 50 | 5.54 | 50-CI-42040-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 3.7 | 4.4 | 4.6 | 0.42032
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43303-01C02 | CML-6 | 150-PL-43303-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3099 | Rope Access | 2014-05-04 11:00 | 2014-05-04 11:30 | Check Corrosion Rate of 1.99mm/ yr | [34 empty] | Low alarm breach | 4.25 | CML-6 | CML: Elbow | 1 | 2014-12-10 | 2014-08-08 | 2014-05-04 11:00 | 2.5 | 1.9902 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.7 | 6 O'Clock | 50 | 5.54 | 50-CI-42041-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 5.2 | 4.1 | 3.7 | 4 | 0.65574
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43303-01C02 | CML-3 | 150-PL-43303-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3090 | Rope Access | 2014-05-04 10:30 | 2014-05-04 11:00 | Check Corrosion Rate of 1.99mm/ yr | [34 empty] | Low alarm breach | 4.2 | CML-3 | CML: Elbow | 1 | 2014-12-10 | 2014-08-08 | 2014-05-04 10:30 | 2.5 | 1.9903 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.7 | 3 O'Clock | 50 | 5.54 | 50-CI-42046-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.1 | 3.7 | 4.2 | 4.8 | 0.45461
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43303-01C02 | CML-3 | 150-PL-43303-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1452 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [35 empty] | Low alarm breach | 3.9 | CML-3 | CML: type TBC | 1 | 2014-11-25 | 2014-07-28 | 2014-04-25 10:00 | 2.5 | 2.045 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.7 | 9 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.1 | 4 | 3.8 | 3.7 | 0.18257
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43303-01C02 | CML-1 | 150-PL-43303-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1450 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [35 empty] | Low alarm breach | 3.825 | CML-1 | CML: type TBC | 1 | 2014-11-25 | 2014-07-28 | 2014-04-25 10:00 | 2.5 | 2.045 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.7 | 12 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.8 | 3.8 | 4 | 0.12583
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-7 | 150-PL-43303-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2225 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.275 | CML-7 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.9 | 12 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.2 | 6.4 | 6.6 | 0.29861
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-4 | 150-PL-43303-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2222 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.3 | CML-4 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.9 | 9 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.9 | 6.3 | 6.1 | 5.9 | 0.43205
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-8 | 150-PL-43303-01C02 CML-8 | Yes | FPSO 2016 | Pipe Wall Thickness | 24495 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.875 | CML-8 | CML: Pipe Length | 3 | 2018-11-03 | 2019-06-04 | 2016-07-09 07:00 | 2.5 | 0.55991 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.8 | 12 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 | -0.19682 | 3.8 | 3.9 | 3.9 | 3.9 | 0.05
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-7 | 150-PL-43303-01C02 CML-7 | Yes | FPSO 2016 | Pipe Wall Thickness | 24494 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 3.85 | CML-7 | CML: Pipe Length | 3 | 2018-11-03 | 2019-06-04 | 2016-07-09 07:00 | 2.5 | 0.55991 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.8 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 | -0.19682 | 3.9 | 3.8 | 3.8 | 3.9 | 0.057735
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-14 | 150-PL-43303-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2232 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6 | CML-14 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6 | 9 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6 | 6 | 0
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-16 | 150-PL-43303-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23303 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.95 | CML-16 | CML: Pipe Length | 3 | 2017-01-24 | 2017-06-16 | 2015-07-04 09:30 | 2.5 | 0.83194 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.8 | 12 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 | -0.64051 | 3.8 | 3.9 | 4 | 4.1 | 0.1291
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43303-01C02 | CML-4 | 150-PL-43303-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23291 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 3.95 | CML-4 | CML: Pipe Length | 3 | 2017-01-24 | 2017-06-16 | 2015-07-04 09:30 | 2.5 | 0.83194 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.8 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 | -0.85401 | 4.1 | 4 | 3.9 | 3.8 | 0.1291
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-3 | 150-PL-43303-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2221 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.125 | CML-3 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6 | 6 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6 | 6.3 | 0.15
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 150-PL-43303-01C02 | CML-7 | 150-PL-43303-01C02 CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 23775 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 4.3 | CML-7 | CML: Reducing Tee | 3 | 2016-09-27 | 2017-02-15 | 2015-04-18 07:00 | 2.5 | 0.89882 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.8 | 6 O'Clock | 40 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 | 1.8268 | 4.3 | 4.3 | 3.8 | 4.8 | 0.40825
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML3 | 150-PL-43303-01C02 CML3 |  | FPSO 2015 | Pipe Wall Thickness | 7764 |  | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 4.4 | CML3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.8 | 12 O'Clock | 150 | 3 | 150-WF-71371-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4.4 | 4.6 | 4.8 | 0.43205
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML2 | 150-PL-43303-01C02 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 7597 |  | 2015-04-15 07:00 | 2015-04-15 15:00 | [36 empty] | 4.05 | CML2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-15 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 9 O'Clock | 40 | 2.5 | 40-WF-71354-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.1 | 4.1 | 4.2 | 3.8 | 0.17321
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML39 | 150-PL-43303-01C02 CML39 |  | FPSO 2015 | Pipe Wall Thickness | 7571 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 4.075 | CML39 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.8 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.2 | 3.8 | 4.2 | 4.1 | 0.1893
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43303-01C02 | CML-3 | 150-PL-43303-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7486 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 0.932mm/ yr | [34 empty] | Low alarm breach | 5.05 | CML-3 | CML: Elbow | 1 | 2016-09-03 | 2015-12-14 | 2015-04-13 07:00 | 2.5 | 0.9322 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 6 O'Clock | 50 | 5.54 | 50-CI-42045-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 6.6 | 5 | 3.8 | 4.8 | 1.159
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43303-01C02 | CML-2 | 150-PL-43303-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7485 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 0.932mm/ yr | [34 empty] | Low alarm breach | 5.425 | CML-2 | CML: Elbow | 1 | 2016-09-03 | 2015-12-14 | 2015-04-13 07:00 | 2.5 | 0.9322 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 3 O'Clock | 50 | 5.54 | 50-CI-42045-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 5.5 | 3.8 | 5.6 | 6.8 | 1.2339
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML89 | 150-PL-43303-01C02 CML89 |  | FPSO 2015 | Pipe Wall Thickness | 7428 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 4.425 | CML89 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.8 | 6 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.7 | 4.7 | 3.8 | 4.5 | 0.4272
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML46 | 150-PL-43303-01C02 CML46 |  | FPSO 2015 | Pipe Wall Thickness | 7235 |  | 2015-04-08 07:00 | 2015-04-08 15:00 |  |  | Nestor | 2014-11-24 10:37 | [32 empty] | 3.95 | CML46 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.9 | 4.2 | 3.9 | 0.17321
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML18 | 150-PL-43303-01C02 CML18 |  | FPSO 2015 | Pipe Wall Thickness | 7207 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [36 empty] | 4 | CML18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.2 | 3.8 | 4.2 | 3.8 | 0.23094
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML12 | 150-PL-43303-01C02 CML12 |  | FPSO 2015 | Pipe Wall Thickness | 7201 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [36 empty] | 3.95 | CML12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.1 | 3.8 | 4.1 | 3.8 | 0.17321
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML2 | 150-PL-43303-01C02 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 7048 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 4.05 | CML2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4.2 | 4.4 | 3.8 | 0.3
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML128 | 150-PL-43303-01C02 CML128 |  | FPSO 2015 | Pipe Wall Thickness | 7046 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 4.175 | CML128 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.8 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.5 | 3.8 | 4.2 | 4.2 | 0.28723
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-4 | 150-PL-43303-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6672 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.95 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.8 | 9 O'Clock | 150 | 3 | 150-WF-71346-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.4 | 3.8 | 3.8 | 3.8 | 0.3
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-3 | 150-PL-43303-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6671 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 12:33 | [32 empty] | 4.075 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-31 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.8 | 6 O'Clock | 150 | 3 | 150-WF-71346-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.4 | 3.8 | 3.8 | 4.3 | 0.32016
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-5 | 150-PL-43303-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6668 | Rope access | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 12:31 | [32 empty] | 4 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.8 | 12 O'Clock | 150 | 3 | 150-WF-71347-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4 | 4.3 | 3.9 | 0.21602
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-11 | 150-PL-43303-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6627 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.85 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 9 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.9 | 3.9 | 3.8 | 3.8 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-9 | 150-PL-43303-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6625 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.875 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 3 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.8 | 4 | 3.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-8 | 150-PL-43303-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 6616 |  | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.85 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 6 O'Clock | 40 | 2.5 | 40-WF-71344-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.9 | 3.8 | 3.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-6 | 150-PL-43303-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6614 |  | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 3.925 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 3 O'Clock | 40 | 2.5 | 40-WF-71344-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4 | 3.8 | 3.9 | 4 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-5 | 150-PL-43303-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6354 | Rope Access | 2015-03-20 07:00 | 2015-03-20 15:00 | [36 empty] | 3.825 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 9 O'Clock | 40 | 2.5 | 40-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.9 | 3.8 | 3.8 | 3.8 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-7 | 150-PL-43303-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6234 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.85 | CML-7 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 6 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.9 | 3.8 | 3.8 | 3.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-39 | 150-PL-43303-01C02 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 6025 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 3.975 | CML-39 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4 | 3.9 | 4.2 | 0.17078
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-15 | 150-PL-43303-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5986 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.95 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 3 O'Clock | 50 | 2.5 | 50-WF-71325-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.8 | 4.1 | 4.1 | 0.17321
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-30 | 150-PL-43303-01C02 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 5912 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.075 | CML-30 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 3 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.7 | 3.8 | 3.9 | 3.9 | 0.41932
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-22 | 150-PL-43303-01C02 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 5904 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.85 | CML-22 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 6 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.9 | 3.8 | 3.9 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-13 | 150-PL-43303-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5895 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 12 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.9 | 4.1 | 4.2 | 0.18257
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-9 | 150-PL-43303-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5891 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 3.9 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4 | 3.8 | 4 | 3.8 | 0.11547
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-9 | 150-PL-43303-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5254 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.825 | CML-9 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.8 | 3.8 | 3.9 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-23 | 150-PL-43303-01C02 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 5268 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.875 | CML-23 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 6 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4 | 3.8 | 3.8 | 3.9 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-43 | 150-PL-43303-01C02 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 5288 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.975 | CML-43 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 12 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4.1 | 4.1 | 3.9 | 0.15
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-40 | 150-PL-43303-01C02 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 5285 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.8 | CML-40 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.8 | 3.8 | 3.8 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43303-01C02 | CML-34 | 150-PL-43303-01C02 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 5279 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 3.9 | CML-34 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.8 | 3 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.8 | 3.9 | 4.1 | 0.14142
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-14 | 150-PL-43303-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5129 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.8 | CML-14 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.8 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.8 | 3.8 | 3.8 | 0
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-12 | 150-PL-43303-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5127 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.875 | CML-12 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.8 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4 | 3.9 | 3.8 | 3.8 | 0.095743
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-4 | 150-PL-43303-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5119 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.875 | CML-4 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.8 | 3 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.8 | 3.9 | 4 | 0.095743
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-3 | 150-PL-43303-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5118 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.95 | CML-3 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.8 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.2 | 4 | 3.8 | 3.8 | 0.19149
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-2 | 150-PL-43303-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5117 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.925 | CML-2 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.8 | 3 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.8 | 4 | 4.1 | 0.15
DC01 | Montara_Topside | No | Compressed Air (63) | Pipework | 150-PL-43303-01C02 | CML-18 | 150-PL-43303-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5027 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | [36 empty] | 4.65 | CML-18 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-04 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.8 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.9 | 4.8 | 5.1 | 3.8 | 0.58023
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43303-01C02 | CML-1 | 150-PL-43303-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8519 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [35 empty] | Low alarm breach | 4.025 | CML-1 | CML: type TBC | 1 | 2016-05-05 | 2015-09-11 | 2015-02-03 07:30 | 2.5 | 1.0372 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 3 O'Clock | 50 | 5.54 | 50-VA-80013-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4 | 3.8 | 4 | 4.3 | 0.20616
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43303-01C02 | CML-6 | 150-PL-43303-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8417 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 1.042mm/ yr | [34 empty] | Low alarm breach | 4.45 | CML-6 | CML: type TBC | 1 | 2016-04-30 | 2015-09-07 | 2015-01-31 10:00 | 2.5 | 1.0421 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 12 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4.4 | 5.4 | 4.2 | 0.68069
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-2 | 150-PL-43303-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2220 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.1 | CML-2 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6 | 12 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.1 | 6.2 | 0.08165
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43303-01C02 | CML-1 | 150-PL-43303-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2219 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [37 empty] | CML-1 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 |  |  |  | 2.5 |  |  | 9 O'Clock | 100 |  | 100-PL-43303-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-9 | 150-PL-43304-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2194 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.8 | CML-9 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.6 | 3 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 6 | 6 | 0.23094
DC01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-PL-43304-01C02 | CML-7 | 150-PL-43304-01C02 CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 7830 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:01 | [32 empty] | 4.725 | CML-7 | CML: Elbow | 3 | 2016-03-30 | 2016-07-19 | 2015-01-13 13:00 | 2.5 | 1.0736 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.9 | 5.3 | 4.9 | 3.8 | 0.64485
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-7 | 150-PL-43304-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1467 | Rope access | 2014-04-25 11:00 | 2014-04-25 12:00 | [35 empty] | Low alarm breach | 4 | CML-7 | CML: type TBC | 1 | 2014-12-26 | 2014-08-21 | 2014-04-25 11:00 | 2.5 | 1.9336 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 9 O'Clock | 50 | 5.54 | 50-DO-62006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4.1 | 4.3 | 3.8 | 0.24495
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-4 | 150-PL-43304-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1464 | Rope access | 2014-04-25 11:00 | 2014-04-25 12:00 | [35 empty] | Low alarm breach | 3.9 | CML-4 | CML: type TBC | 1 | 2014-12-26 | 2014-08-21 | 2014-04-25 11:00 | 2.5 | 1.9336 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 6 O'Clock | 50 | 5.54 | 50-DO-62006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 4 | 3.8 | 4 | 0.11547
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-3 | 150-PL-43304-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1463 | Rope access | 2014-04-25 11:00 | 2014-04-25 12:00 | [35 empty] | Low alarm breach | 4.1 | CML-3 | CML: type TBC | 1 | 2014-12-26 | 2014-08-21 | 2014-04-25 11:00 | 2.5 | 1.9336 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 6 O'Clock | 50 | 5.54 | 50-DO-62006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.1 | 4.5 | 3.8 | 4 | 0.29439
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-2 | 150-PL-43304-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1462 | Rope access | 2014-04-25 11:00 | 2014-04-25 12:00 | [35 empty] | Low alarm breach | 3.95 | CML-2 | CML: type TBC | 1 | 2014-12-26 | 2014-08-21 | 2014-04-25 11:00 | 2.5 | 1.9336 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 6 O'Clock | 50 | 5.54 | 50-DO-62006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.1 | 3.9 | 3.8 | 4 | 0.1291
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-7 | 150-PL-43304-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1456 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [35 empty] | Low alarm breach | 3.95 | CML-7 | CML: type TBC | 1 | 2014-12-26 | 2014-08-21 | 2014-04-25 10:00 | 2.5 | 1.9338 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 12 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 3.8 | 3.9 | 4.1 | 4 | 0.1291
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-6 | 150-PL-43304-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1455 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [35 empty] | Low alarm breach | 4.125 | CML-6 | CML: type TBC | 1 | 2014-12-26 | 2014-08-21 | 2014-04-25 10:00 | 2.5 | 1.9338 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 9 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.1 | 4.3 | 4.3 | 3.8 | 0.23629
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1454 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [35 empty] | Low alarm breach | 4.075 | CML-5 | CML: type TBC | 1 | 2014-12-26 | 2014-08-21 | 2014-04-25 10:00 | 2.5 | 1.9338 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.8 | 3 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.1 | 3.8 | 4.1 | 4.3 | 0.20616
DC01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 150-PL-43304-01C02 | CML-1 | 150-PL-43304-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1042 |  | 2014-03-20 13:00 | 2014-03-20 14:00 | Low Reading between 9 & 6 O clock | [35 empty] | 6.1 | CML-1 | CML: type TBC | 3 | 2014-08-16 | 2014-08-13 | 2014-03-20 13:00 | 2.5 | 3.1816 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 3.8 | 9 O'Clock | 300 | 6.35 | 300-WC-40043-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 6.8 | 6.7 | 7.1 | 3.8 | 1.5427
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-10 | 150-PL-43304-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2195 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.025 | CML-10 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5.9 | 6 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 5.9 | 5.9 | 6.2 | 0.15
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-1 | 150-PL-43304-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5758 | Rope access | 2014-06-23 08:00 | 2014-06-23 09:00 | [36 empty] | 5.225 | CML-1 | CML: Elbow | 3 | 2020-01-22 | 2019-03-19 | 2014-06-23 08:00 | 0.54 | 0.74445 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 4.7 | 12 O'Clock | 80 | 5.49 | 80-FH-43307-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.16 |  | 4.7 | 5.2 | 5.6 | 5.4 | 0.38622
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-6 | 150-PL-43304-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2191 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.95 | CML-6 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5.9 | 6 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 5.9 | 5.9 | 6 | 0.057735
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43304-01C02 | CML-15 | 150-PL-43304-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23302 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 4 | CML-15 | CML: Pipe Length | 3 | 2017-04-16 | 2017-09-14 | 2015-07-04 09:30 | 2.5 | 0.78413 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.9 | 9 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 | -0.427 | 3.9 | 4.1 | 4.1 | 3.9 | 0.11547
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2190 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6 | CML-5 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.9 | 9 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6 | 6.1 | 5.9 | 0.08165
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-4 | 150-PL-43304-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2189 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.15 | CML-4 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.9 | 12 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.1 | 6.4 | 6.2 | 0.20817
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 150-PL-43304-01C02 | CML-2 | 150-PL-43304-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 9089 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.575 | CML-2 | CML: type TBC | 3 | 2016-08-29 | 2017-01-03 | 2015-03-02 07:00 | 2.5 | 0.93635 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.9 | 3.9 | 4.3 | 5.2 | 0.58523
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 22313 | Rope Access | 2014-05-06 14:00 | 2014-05-06 15:00 | [36 empty] | 4.825 | CML-5 | CML: type TBC | 3 | 2015-02-20 | 2015-04-29 | 2014-05-06 14:00 | 2.5 | 1.7628 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.9 | 6 O'Clock | 50 | 5.54 | 50-DH-56138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.5 | 5.5 | 3.9 | 5.4 | 0.76322
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-2 | 150-PL-43304-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2187 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.225 | CML-2 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.9 | 6 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 6.2 | 5.9 | 6.4 | 0.23629
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-1 | 150-PL-43304-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7484 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 0.879mm/ yr |  | Nestor | 2014-11-24 09:31 | [31 empty] | Low alarm breach | 5.125 | CML-1 | CML: Elbow | 1 | 2016-11-14 | 2016-02-08 | 2015-04-13 07:00 | 2.5 | 0.87863 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 12 O'Clock | 50 | 5.54 | 50-CI-42045-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.8 | 6.7 | 5.1 | 1.1673
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7478 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 0.879mm/ yr | [34 empty] | Low alarm breach | 5.55 | CML-5 | CML: Elbow | 1 | 2016-11-14 | 2016-02-08 | 2015-04-13 07:00 | 2.5 | 0.87863 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 6 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 7.6 | 5.3 | 3.9 | 5.4 | 1.5286
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-1 | 150-PL-43304-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7474 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 0.879mm/ yr | [34 empty] | Low alarm breach | 4.575 | CML-1 | CML: Elbow | 1 | 2016-11-14 | 2016-02-08 | 2015-04-13 07:00 | 2.5 | 0.87863 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 12 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.9 | 4.8 | 4.7 | 0.45735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML99 | 150-PL-43304-01C02 CML99 |  | FPSO 2015 | Pipe Wall Thickness | 7145 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 4.425 | CML99 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.7 | 4.2 | 4.9 | 3.9 | 0.45735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML6 | 150-PL-43304-01C02 CML6 |  | FPSO 2015 | Pipe Wall Thickness | 7052 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 4.15 | CML6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.5 | 3.9 | 3.9 | 4.3 | 0.3
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6679 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 4.2 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.9 | 3 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4 | 3.9 | 4.3 | 4.6 | 0.31623
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-6 | 150-PL-43304-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6622 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 3.95 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 3.9 | 4 | 4 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-2 | 150-PL-43304-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6618 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 4 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.9 | 6 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4 | 4 | 3.9 | 4.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-13 | 150-PL-43304-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6265 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 4.05 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 3.9 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4 | 4.2 | 4.1 | 3.9 | 0.1291
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6115 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 4.15 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.9 | 9 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.2 | 4.6 | 3.9 | 0.33166
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-7 | 150-PL-43304-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6117 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 4.7 | CML-7 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.9 | 3 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 5.5 | 3.9 | 4.6 | 4.8 | 0.65828
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-29 | 150-PL-43304-01C02 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6015 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 4.35 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.7 | 4.9 | 3.9 | 0.52599
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-26 | 150-PL-43304-01C02 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 5404 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.375 | CML-26 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.9 | 3 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.7 | 3.9 | 4.1 | 4.8 | 0.44253
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-8 | 150-PL-43304-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5326 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 3.9 | 12 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4 | 4.1 | 4 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43304-01C02 | CML-3 | 150-PL-43304-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5182 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 5.225 | CML-3 | CML: type TBC | 0.5 | 2023-06-01 | 2020-11-30 | 2015-03-12 07:00 | 3.5 | 0 | A4: Left Quadrant |  | 4 | 3.5 | 3.75 | 4.9 | 9 O'Clock | 250 | 4.5 | 250-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 5.1 | 5.5 | 5.4 | 4.9 | 0.27538
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-1 | 150-PL-43304-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5116 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 4.025 | CML-1 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.9 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.2 | 4 | 4 | 3.9 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-PL-43304-01C02 | CML-1 | 150-PL-43304-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5070 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 3.9 | CML-1 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.9 | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9003-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 3.9 | 3.9 | 3.9 | 0
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43304-01C02 | CML-3 | 150-PL-43304-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8521 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [35 empty] | Low alarm breach | 4.625 | CML-3 | CML: type TBC | 1 | 2016-07-10 | 2015-11-01 | 2015-02-03 07:30 | 2.5 | 0.97761 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 6 O'Clock | 50 | 5.54 | 50-VA-80013-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4 | 6.3 | 3.9 | 4.3 | 1.1295
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-10 | 150-PL-43304-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8421 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.982mm/ yr | [34 empty] | Low alarm breach | 4.075 | CML-10 | CML: type TBC | 1 | 2016-07-04 | 2015-10-28 | 2015-01-31 10:00 | 2.5 | 0.98225 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 9 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4 | 4.3 | 4.1 | 3.9 | 0.17078
DC01 | Montara_Topside | No | Lube Oil (69) | Pipework | 150-PL-43304-01C02 | CML-12 | 150-PL-43304-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8201 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 4.75 | CML-12 | CML: type TBC | 1 | 2016-06-21 | 2015-10-18 | 2015-01-24 07:30 | 2.5 | 0.99384 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 12 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.8 | 5.7 | 4.6 | 0.74162
DC01 | Montara_Topside | No | Lube Oil (69) | Pipework | 150-PL-43304-01C02 | CML-11 | 150-PL-43304-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8200 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 4.325 | CML-11 | CML: type TBC | 1 | 2016-06-21 | 2015-10-18 | 2015-01-24 07:30 | 2.5 | 0.99384 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 12 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.9 | 4.4 | 4.1 | 0.43493
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-12 | 150-PL-43304-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2197 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.175 | CML-12 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6 | 6 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6 | 6.5 | 0.23629
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-11 | 150-PL-43304-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2196 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.125 | CML-11 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6 | 12 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.3 | 6.1 | 0.12583
DC01 | Montara_Topside | No | Lube Oil (69) | Pipework | 150-PL-43304-01C02 | CML-1 | 150-PL-43304-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8092 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [35 empty] | Low alarm breach | 4.425 | CML-1 | CML: type TBC | 1 | 2016-07-05 | 2015-11-02 | 2015-01-23 07:30 | 2.5 | 0.96514 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 3.9 | 12 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.4 | 5 | 4.4 | 0.45
DC01 | Montara_Topside | No | Lube Oil (69) | Pipework | 150-PL-43304-01C02 | CML-13 | 150-PL-43304-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8091 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [35 empty] | Low alarm breach | 4.15 | CML-13 | CML: type TBC | 1 | 2016-07-05 | 2015-11-02 | 2015-01-23 07:30 | 2.5 | 0.96514 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 3.9 | 12 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.7 | 4 | 4 | 0.36968
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-8 | 150-PL-43304-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2193 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.2 | CML-8 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6 | 12 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.5 | 6.2 | 6.1 | 0.21602
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-3 | 150-PL-43304-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3083 | Rope Access | 2014-05-04 11:30 | 2014-05-04 12:00 | Check Corrosion Rate of 1.774mm/ yr | [34 empty] | Low alarm breach | 4.275 | CML-3 | CML: Elbow | 1 | 2015-02-16 | 2014-09-30 | 2014-05-04 11:30 | 2.5 | 1.7737 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 9 O'Clock | 50 | 5.54 | 50-CI-42040-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.3 | 4.7 | 4.2 | 3.9 | 0.3304
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-2 | 150-PL-43304-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3082 | Rope Access | 2014-05-04 11:30 | 2014-05-04 12:00 | Check Corrosion Rate of 1.774mm/ yr | [34 empty] | Low alarm breach | 4.725 | CML-2 | CML: Elbow | 1 | 2015-02-16 | 2014-09-30 | 2014-05-04 11:30 | 2.5 | 1.7737 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 3 O'Clock | 50 | 5.54 | 50-CI-42040-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.6 | 3.9 | 4.5 | 5.9 | 0.84212
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-1 | 150-PL-43304-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3081 | Rope Access | 2014-05-04 11:30 | 2014-05-04 12:00 | Check Corrosion Rate of 1.774mm/ yr | [34 empty] | Low alarm breach | 4.5 | CML-1 | CML: Elbow | 1 | 2015-02-16 | 2014-09-30 | 2014-05-04 11:30 | 2.5 | 1.7737 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 12 O'Clock | 50 | 5.54 | 50-CI-42040-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.4 | 5.5 | 4.2 | 0.69761
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3085 | Rope Access | 2014-05-04 11:30 | 2014-05-04 12:00 | Check Corrosion Rate of 1.774mm/ yr | [34 empty] | Low alarm breach | 4.25 | CML-5 | CML: Elbow | 1 | 2015-02-16 | 2014-09-30 | 2014-05-04 11:30 | 2.5 | 1.7737 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 6 O'Clock | 50 | 5.54 | 50-CI-42040-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.6 | 4.3 | 3.9 | 4.2 | 0.28868
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3098 | Rope Access | 2014-05-04 11:00 | 2014-05-04 11:30 | Check Corrosion Rate of 1.774mm/ yr | [34 empty] | Low alarm breach | 4.6 | CML-5 | CML: Elbow | 1 | 2015-02-16 | 2014-09-30 | 2014-05-04 11:00 | 2.5 | 1.7738 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 9 O'Clock | 50 | 5.54 | 50-CI-42041-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.5 | 5.7 | 4.3 | 3.9 | 0.7746
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-4 | 150-PL-43304-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3097 | Rope Access | 2014-05-04 11:00 | 2014-05-04 11:30 | Check Corrosion Rate of 1.774mm/ yr | [34 empty] | Low alarm breach | 4.2 | CML-4 | CML: Elbow | 1 | 2015-02-16 | 2014-09-30 | 2014-05-04 11:00 | 2.5 | 1.7738 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 3 O'Clock | 50 | 5.54 | 50-CI-42041-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.2 | 3.9 | 4 | 4.7 | 0.3559
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-4 | 150-PL-43304-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3091 | Rope Access | 2014-05-04 10:30 | 2014-05-04 11:00 | Check Corrosion Rate of 1.774mm/ yr | [34 empty] | Low alarm breach | 4.875 | CML-4 | CML: Elbow | 1 | 2015-02-16 | 2014-09-30 | 2014-05-04 10:30 | 2.5 | 1.774 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 3 O'Clock | 50 | 5.54 | 50-CI-42046-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 5.4 | 3.9 | 4.6 | 5.6 | 0.78049
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3092 | Rope Access | 2014-05-04 10:30 | 2014-05-04 11:00 | Check Corrosion Rate of 1.774mm/ yr | [34 empty] | Low alarm breach | 4.275 | CML-5 | CML: Elbow | 1 | 2015-02-16 | 2014-09-30 | 2014-05-04 10:30 | 2.5 | 1.774 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 6 O'Clock | 50 | 5.54 | 50-CI-42046-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.7 | 4.3 | 3.9 | 4.2 | 0.3304
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43304-01C02 | CML-4 | 150-PL-43304-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3037 | Rope Access | 2014-05-03 14:00 | 2014-05-03 15:00 | [35 empty] | Low alarm breach | 4.1 | CML-4 | CML: Pipe Length | 1 | 2015-02-14 | 2014-09-29 | 2014-05-03 14:00 | 2.5 | 1.7785 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 12 O'Clock | 50 | 5.54 | 50-VA-80009-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4.2 | 4.3 | 4 | 0.18257
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-6 | 150-PL-43304-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1466 | Rope access | 2014-04-25 11:00 | 2014-04-25 12:00 | [35 empty] | Low alarm breach | 4.3 | CML-6 | CML: type TBC | 1 | 2015-01-30 | 2014-09-17 | 2014-04-25 11:00 | 2.5 | 1.8224 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 6 O'Clock | 50 | 5.54 | 50-DO-62006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.8 | 4.5 | 3.9 | 4 | 0.42426
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-5 | 150-PL-43304-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1465 | Rope access | 2014-04-25 11:00 | 2014-04-25 12:00 | [35 empty] | Low alarm breach | 4 | CML-5 | CML: type TBC | 1 | 2015-01-30 | 2014-09-17 | 2014-04-25 11:00 | 2.5 | 1.8224 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 12 O'Clock | 50 | 5.54 | 50-DO-62006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4 | 4.1 | 4 | 0.08165
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-9 | 150-PL-43304-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1458 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [35 empty] | Low alarm breach | 4.075 | CML-9 | CML: type TBC | 1 | 2015-01-30 | 2014-09-17 | 2014-04-25 10:00 | 2.5 | 1.8227 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 9 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.3 | 4.2 | 3.9 | 3.9 | 0.20616
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-4 | 150-PL-43304-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1453 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [35 empty] | Low alarm breach | 3.95 | CML-4 | CML: type TBC | 1 | 2015-01-30 | 2014-09-17 | 2014-04-25 10:00 | 2.5 | 1.8227 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 9 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4 | 4 | 3.9 | 3.9 | 0.057735
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43304-01C02 | CML-2 | 150-PL-43304-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1451 | Rope access | 2014-04-25 10:00 | 2014-04-25 11:00 | [35 empty] | Low alarm breach | 4.025 | CML-2 | CML: type TBC | 1 | 2015-01-30 | 2014-09-17 | 2014-04-25 10:00 | 2.5 | 1.8227 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.9 | 6 O'Clock | 50 | 5.54 | 50-DO-62004-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.1 | 3.9 | 3.9 | 4.2 | 0.15
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-3 | 150-PL-43304-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2188 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.275 | CML-3 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6 | 6 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6 | 6 | 6.6 | 0.32016
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-7 | 150-PL-43304-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2192 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.3 | CML-7 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.1 | 6 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.1 | 6.1 | 6.8 | 0.33665
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43304-01C02 | CML-1 | 150-PL-43304-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2186 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [37 empty] | CML-1 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 |  |  |  | 2.5 |  |  | 9 O'Clock | 100 |  | 100-PL-43304-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-2 | 50-PW-44013-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5726 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 4.95 | CML-2 | CML: Elbow | 3 | 2016-01-04 | 2016-04-15 | 2014-06-22 13:00 | 2.5 | 1.1709 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 0.48766 | 5.2 | 4.3 | 5.2 | 5.1 | 0.43589
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-2 | 50-DC-57044-01C02 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24433 | Re-check as requested by N.Sequera | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.499mm/ yr | [35 empty] | 4.2 | CML-2 | CML: Elbow | 3 | 2019-07-05 | 2020-02-29 | 2016-07-02 07:00 | 2.5 | 0.49863 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4 | 12 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 0.26134 | 4 | 4.3 | 4.3 | 4.2 | 0.14142
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-16 | 50-CG-38487-09C02-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23585 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 7.875 | CML-16 | CML: Fitting | 3 | 2017-03-18 | 2016-03-23 | 2015-09-10 07:00 | 2.5 | 1.6421 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 5 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 3.6181 | 5 | 9.3 | 8.7 | 8.5 | 1.9466
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-13 | 250-PG-23015-06C03-A CML-13 | yes | FPSO 2014 | Pipe Wall Thickness | 20081 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 18.9 | CML-13 | CML: type TBC | 6 | 2022-07-02 | 2020-10-06 | 2014-05-29 07:00 | 8.55 | 1.0679 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.2 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.65 |  | 19.6 | 21.3 | 17.2 | 17.5 | 1.9235
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-13 | 250-PG-23015-06C03-A CML-13 | yes | FPSO 2014 | Pipe Wall Thickness | 20050 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 18.9 | CML-13 | CML: type TBC | 6 | 2022-07-02 | 2020-10-06 | 2014-05-29 07:00 | 8.55 | 1.0679 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.2 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.65 | 0.26497 | 19.6 | 21.3 | 17.2 | 17.5 | 1.9235
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-3 | 150-PL-43305-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2200 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.2 | CML-3 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.6 | 6 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.4 | 6.5 | 5.6 | 6.3 | 0.40825
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-10 | 150-PL-43305-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2207 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.075 | CML-10 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.7 | 6 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.6 | 6 | 5.7 | 6 | 0.37749
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-8 | 150-PL-43305-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2205 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.825 | CML-8 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.7 | 9 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 5.9 | 5.7 | 5.7 | 0.15
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-6 | 150-PL-43305-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2203 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.875 | CML-6 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.8 | 3 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 5.9 | 6 | 0.095743
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-11 | 150-PL-43305-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2208 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.175 | CML-11 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.9 | 6 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.4 | 5.9 | 6.2 | 0.20616
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-7 | 150-PL-43305-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2204 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.475 | CML-7 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6 | 12 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.2 | 6.8 | 6.9 | 0.44253
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-8 | 150-PL-43305-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22379 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 4.175 | CML-8 | CML: Reducing Tee | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4 | 9 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4 | 4.7 | 4 | 0.35
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 150-PL-43305-01C02 | CML-16 | 150-PL-43305-01C02 CML-16 | yes | FPSO 2015 | Pipe Wall Thickness | 23784 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 4.3 | CML-16 | CML: Pipe Length | 3 | 2017-03-09 | 2017-08-16 | 2015-04-18 07:00 | 2.5 | 0.79245 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4 | 6 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 1.5832 | 4.7 | 4.3 | 4 | 4.2 | 0.29439
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 150-PL-43305-01C02 | CML-9 | 150-PL-43305-01C02 CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 23777 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 4.225 | CML-9 | CML: Reducing Tee | 3 | 2017-03-09 | 2017-08-16 | 2015-04-18 07:00 | 2.5 | 0.79245 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4 | 9 O'Clock | 40 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 1.3396 | 4.3 | 4.2 | 4.4 | 4 | 0.17078
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-10 | 150-PL-43305-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7483 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 0.825mm/ yr | [34 empty] | Low alarm breach | 5 | CML-10 | CML: type TBC | 1 | 2017-02-04 | 2016-04-12 | 2015-04-13 07:00 | 2.5 | 0.82505 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 9 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.7 | 6.8 | 4.5 | 4 | 1.2356
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML1 | 150-PL-43305-01C02 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 7340 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 4.2 | CML1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.1 | 4.2 | 4.5 | 4 | 0.21602
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML2 | 150-PL-43305-01C02 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 7247 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 09:08 | [32 empty] | 4.5 | CML2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4 | 9 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.7 | 4.2 | 5.1 | 4 | 0.49666
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML4 | 150-PL-43305-01C02 CML4 |  | FPSO 2015 | Pipe Wall Thickness | 7193 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [36 empty] | 4.325 | CML4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4 | 9 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.5 | 4.3 | 4.5 | 4 | 0.23629
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-11 | 150-PL-43305-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6685 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 4.575 | CML-11 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.6 | 4.7 | 5 | 4 | 0.41932
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-13 | 150-PL-43305-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6629 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 4.05 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4 | 9 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.1 | 4.1 | 4 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-2 | 150-PL-43305-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6404 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 4.125 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4 | 3 O'Clock | 100 | 3 | 100-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.2 | 4 | 4.1 | 4.2 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-17 | 150-PL-43305-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6269 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 4.6 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4 | 9 O'Clock | 40 | 2.5 | 40-WF-71332-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.6 | 4.8 | 5 | 4 | 0.43205
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-4 | 150-PL-43305-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6231 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 4.125 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 4 | 6 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.1 | 4.2 | 4 | 4.2 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-13 | 150-PL-43305-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6123 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 5.025 | CML-13 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 4 | 6 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 5.7 | 4.8 | 4 | 5.6 | 0.7932
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-21 | 150-PL-43305-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6007 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 4.175 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4 | 3 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4 | 4.6 | 4.1 | 0.28723
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-35 | 150-PL-43305-01C02 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 5917 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.1 | CML-35 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.2 | 4.1 | 4.1 | 4 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-12 | 150-PL-43305-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5894 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.075 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4 | 9 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.1 | 4.1 | 4.1 | 4 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-18 | 150-PL-43305-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5396 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.075 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.1 | 4.1 | 4.1 | 4 | 0.05
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-29 | 150-PL-43305-01C02 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 5407 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.05 | CML-29 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.1 | 4.1 | 4 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-6 | 150-PL-43305-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5426 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.25 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4 | 12 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.3 | 4.4 | 4.3 | 0.17321
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-6 | 150-PL-43305-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5185 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 5.5 | CML-6 | CML: type TBC | 0.5 | 2023-06-01 | 2020-11-30 | 2015-03-12 07:00 | 3.5 | 0 | A2: Right Quadrant |  | 4 | 3.5 | 3.75 | 5 | 3 O'Clock | 250 | 4.5 | 250-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 5.8 | 5 | 5.1 | 6.1 | 0.53541
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-16 | 150-PL-43305-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 5177 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 4.4 | CML-16 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 4 | 6 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 5 | 4.5 | 4 | 4.1 | 0.45461
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-12 | 150-PL-43305-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5173 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 4.025 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 4 | 9 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.1 | 4 | 4 | 4 | 0.05
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-9 | 150-PL-43305-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5124 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 4.15 | CML-9 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 4 | 9 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.3 | 4.3 | 4 | 4 | 0.17321
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-8 | 150-PL-43305-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5123 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 4.1 | CML-8 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 4 | 12 O'Clock | 25 | 3.38 | 0100-VA-43L9002-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.1 | 4.1 | 4.2 | 0.08165
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-PL-43305-01C02 | CML-3 | 150-PL-43305-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5059 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 4.125 | CML-3 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 4 | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.2 | 4.2 | 4.1 | 4 | 0.095743
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-PL-43305-01C02 | CML-15 | 150-PL-43305-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5055 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 2.195mm/ yr | [34 empty] | Low alarm breach | 4.35 | CML-15 | CML: type TBC | 3 | 2015-11-09 | 2015-05-15 | 2015-03-05 07:00 | 2.5 | 2.1947 | A3: Inside Quadrant |  | 5.74 | 2.5 | 3.5737 | 4 | 6 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.4 | 4.3 | 4 | 4.7 | 0.28868
DC01 | Montara_Topside | No | Compressed Air (63) | Pipework | 150-PL-43305-01C02 | CML-1 | 150-PL-43305-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5010 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | [36 empty] | 4.1 | CML-1 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 4 | 12 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.1 | 4.2 | 4.1 | 0.08165
DC01 | Montara_Topside | No | Nitrogen (67) | Pipework | 150-PL-43305-01C02 | CML-1 | 150-PL-43305-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5000 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [36 empty] | 4.2 | CML-1 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-03 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.38 | 2.5 | 2.7287 | 4 | 12 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.3 | 4.3 | 4.2 | 0.14142
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-6 | 150-PL-43305-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8428 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.922mm/ yr | [34 empty] | Low alarm breach | 4.1 | CML-6 | CML: type TBC | 1 | 2016-09-16 | 2015-12-24 | 2015-01-31 10:00 | 2.5 | 0.92236 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 3 O'Clock | 50 | 5.54 | 50-CI-42314-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4 | 4.2 | 4.2 | 0.11547
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-4 | 150-PL-43305-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8426 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.922mm/ yr | [34 empty] | Low alarm breach | 4.05 | CML-4 | CML: type TBC | 1 | 2016-09-16 | 2015-12-24 | 2015-01-31 10:00 | 2.5 | 0.92236 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 9 O'Clock | 50 | 5.54 | 50-CI-42314-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.1 | 4.1 | 4 | 4 | 0.057735
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-3 | 150-PL-43305-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8425 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.922mm/ yr | [34 empty] | Low alarm breach | 4.15 | CML-3 | CML: type TBC | 1 | 2016-09-16 | 2015-12-24 | 2015-01-31 10:00 | 2.5 | 0.92236 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 6 O'Clock | 50 | 5.54 | 50-CI-42314-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.2 | 4.2 | 4 | 4.2 | 0.1
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-2 | 150-PL-43305-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8424 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.922mm/ yr | [34 empty] | Low alarm breach | 4.15 | CML-2 | CML: type TBC | 1 | 2016-09-16 | 2015-12-24 | 2015-01-31 10:00 | 2.5 | 0.92236 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 6 O'Clock | 50 | 5.54 | 50-CI-42314-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.2 | 4.1 | 4 | 4.3 | 0.1291
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-1 | 150-PL-43305-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8423 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.922mm/ yr | [34 empty] | Low alarm breach | 4.075 | CML-1 | CML: type TBC | 1 | 2016-09-16 | 2015-12-24 | 2015-01-31 10:00 | 2.5 | 0.92236 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 6 O'Clock | 50 | 5.54 | 50-CI-42314-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.1 | 4 | 4 | 4.2 | 0.095743
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-9 | 150-PL-43305-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8420 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.922mm/ yr | [34 empty] | Low alarm breach | 4.325 | CML-9 | CML: type TBC | 1 | 2016-09-16 | 2015-12-24 | 2015-01-31 10:00 | 2.5 | 0.92236 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 6 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.3 | 4 | 4 | 5 | 0.4717
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-4 | 150-PL-43305-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8415 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.922mm/ yr | [34 empty] | Low alarm breach | 4.1 | CML-4 | CML: type TBC | 1 | 2016-09-16 | 2015-12-24 | 2015-01-31 10:00 | 2.5 | 0.92236 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 12 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.1 | 4.2 | 4.1 | 0.08165
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-3 | 150-PL-43305-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8414 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.922mm/ yr | [34 empty] | Low alarm breach | 4.15 | CML-3 | CML: type TBC | 1 | 2016-09-16 | 2015-12-24 | 2015-01-31 10:00 | 2.5 | 0.92236 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 12 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.2 | 4.3 | 4.1 | 0.1291
DC01 | Montara_Topside | No | Lube Oil (69) | Pipework | 150-PL-43305-01C02 | CML-12 | 150-PL-43305-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8090 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [35 empty] | Low alarm breach | 4.525 | CML-12 | CML: type TBC | 1 | 2016-09-19 | 2015-12-31 | 2015-01-23 07:30 | 2.5 | 0.90444 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 4 | 12 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.3 | 4.8 | 5 | 0.45735
DC01 | Montara_Topside | No | Lube Oil (69) | Pipework | 150-PL-43305-01C02 | CML-1 | 150-PL-43305-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8079 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [35 empty] | Low alarm breach | 4.35 | CML-1 | CML: type TBC | 1 | 2016-09-19 | 2015-12-31 | 2015-01-23 07:30 | 2.5 | 0.90444 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 4 | 12 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.3 | 5 | 4.1 | 0.45092
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-2 | 150-PL-43305-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5759 | Rope access | 2014-06-23 08:00 | 2014-06-23 09:00 | [36 empty] | 5.475 | CML-2 | CML: Pipe Length | 3 | 2071-09-28 | 2064-04-17 | 2014-06-23 08:00 | 0.54 | 0.08481 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FH-43307-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.4 | 5.6 | 5.5 | 5.4 | 0.095743
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-6 | 150-PL-43305-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5765 | Rope access | 2014-06-23 09:30 | 2014-06-23 11:00 | [36 empty] | 5.15 | CML-6 | CML: Elbow | 3 | 2019-04-25 | 2018-07-24 | 2014-06-23 09:30 | 0.54 | 0.83855 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 4.6 | 3 O'Clock | 80 | 5.49 | 80-FH-43306-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.06 |  | 5.5 | 4.6 | 5.4 | 5.1 | 0.40415
DC01 | Montara_Topside | No | Separation (20) | Pipework | 150-PL-43305-01C02 | CML-3 | 150-PL-43305-01C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 21254 | Reviewed on 27/11/14. FFS. recheck on Sep.15 | 2014-09-30 07:00 | 2014-09-30 15:00 |  |  | Nestor | 2014-11-27 15:48 | [32 empty] | 5.825 | CML-3 | CML: Fitting | 3 | 2015-08-06 | 2015-07-31 | 2014-09-30 07:00 | 2.5 | 1.7639 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 6.7 | 6.2 | 6.4 | 1.2339
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-5 | 150-PL-43305-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2202 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.1 | CML-5 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6 | 9 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.3 | 6.1 | 6 | 0.14142
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-6 | 150-PL-43305-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3359 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.645mm/ yr | [34 empty] | Low alarm breach | 4.3 | CML-6 | CML: type TBC | 1 | 2015-04-06 | 2014-11-07 | 2014-05-08 14:30 | 2.5 | 1.6455 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 6 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 0 | 4.7 | 4.4 | 4 | 4.1 | 0.31623
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-6 | 150-PL-43305-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3322 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.645mm/ yr | [34 empty] | Low alarm breach | 4.3 | CML-6 | CML: type TBC | 1 | 2015-04-06 | 2014-11-07 | 2014-05-08 14:30 | 2.5 | 1.6455 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 6 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.7 | 4.4 | 4 | 4.1 | 0.31623
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-3 | 150-PL-43305-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3096 | Rope Access | 2014-05-04 11:00 | 2014-05-04 11:30 | Check Corrosion Rate of 1.666mm/ yr | [34 empty] | Low alarm breach | 4.65 | CML-3 | CML: Elbow | 1 | 2015-03-29 | 2014-11-01 | 2014-05-04 11:00 | 2.5 | 1.6657 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 9 O'Clock | 50 | 5.54 | 50-CI-42041-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.7 | 5.4 | 4.5 | 4 | 0.58023
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43305-01C02 | CML-1 | 150-PL-43305-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3034 | Rope Access | 2014-05-03 14:00 | 2014-05-03 15:00 | [35 empty] | Low alarm breach | 4.25 | CML-1 | CML: Elbow | 1 | 2015-03-27 | 2014-10-31 | 2014-05-03 14:00 | 2.5 | 1.67 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 9 O'Clock | 50 | 5.54 | 50-VA-80009-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.3 | 4.4 | 4.3 | 4 | 0.17321
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43305-01C02 | CML-2 | 150-PL-43305-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3035 | Rope Access | 2014-05-03 14:00 | 2014-05-03 15:00 | [35 empty] | Low alarm breach | 4.275 | CML-2 | CML: Pipe Length | 1 | 2015-03-27 | 2014-10-31 | 2014-05-03 14:00 | 2.5 | 1.67 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 9 O'Clock | 50 | 5.54 | 50-VA-80009-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4.3 | 4.2 | 4.6 | 4 | 0.25
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43305-01C02 | CML-3 | 150-PL-43305-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3032 | Rope Access | 2014-05-03 13:00 | 2014-05-03 14:00 | [35 empty] | Low alarm breach | 4.1 | CML-3 | CML: Pipe Length | 1 | 2015-03-27 | 2014-10-31 | 2014-05-03 13:00 | 2.5 | 1.6702 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 3 O'Clock | 50 | 5.54 | 50-VA-80010-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4 | 4.2 | 4.2 | 0.11547
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43305-01C02 | CML-4 | 150-PL-43305-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3033 | Rope Access | 2014-05-03 13:00 | 2014-05-03 14:00 | [35 empty] | Low alarm breach | 4.425 | CML-4 | CML: Pipe Length | 1 | 2015-03-27 | 2014-10-31 | 2014-05-03 13:00 | 2.5 | 1.6702 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 12 O'Clock | 50 | 5.54 | 50-VA-80010-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.9 | 4.3 | 4.5 | 0.37749
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43305-01C02 | CML-2 | 150-PL-43305-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3031 | Rope Access | 2014-05-03 13:00 | 2014-05-03 14:00 | [35 empty] | Low alarm breach | 4.15 | CML-2 | CML: Pipe Length | 1 | 2015-03-27 | 2014-10-31 | 2014-05-03 13:00 | 2.5 | 1.6702 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 12 O'Clock | 50 | 5.54 | 50-VA-80010-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.1 | 4.3 | 4.2 | 0.1291
DC01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-PL-43305-01C02 | CML-10 | 150-PL-43305-01C02 CML-10 | yes | FPSO 2013 | Pipe Wall Thickness | 10634 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.5 | CML-10 | CML: type TBC | 3 | 2014-08-28 | 2014-07-25 | 2013-11-18 | 2.5 | 2.8341 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 4.7 | 6 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.7 | 5.9 | 4.7 | 5.7 | 0.5416
DC01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 150-PL-43305-01C02 | CML-1 | 150-PL-43305-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1461 | Rope access | 2014-04-25 11:00 | 2014-04-25 12:00 | [35 empty] | Low alarm breach | 4.1 | CML-1 | CML: type TBC | 1 | 2015-03-11 | 2014-10-18 | 2014-04-25 11:00 | 2.5 | 1.7113 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4 | 12 O'Clock | 50 | 5.54 | 50-DO-62006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 |  | 4 | 4.2 | 4.1 | 4.1 | 0.08165
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-4 | 150-PL-43305-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2201 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.15 | CML-4 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6 | 9 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.3 | 6.1 | 6 | 0.1291
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PL-43305-01C02 | CML-3 | 150-PL-43305-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 23539 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 | [35 empty] | Medium alarm breach | 10.5 | CML-3 | CML: Pipe Length | 6 | 2016-01-01 | 2015-07-04 | 2015-08-03 09:30 | 8.55 | 3.754 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 10.1 | 3 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.55 | 0.34024 | 10.5 | 10.1 | 10.5 | 10.9 | 0.3266
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PL-43305-01C02 | CML-20 | 150-PL-43305-01C02 CML-20 | yes | FPSO 2014 | Pipe Wall Thickness | 20707 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [35 empty] | Medium alarm breach | 12.675 | CML-20 | CML: Elbow | 6 | 2014-09-09 | 2014-06-02 | 2014-06-30 13:00 | 10.22 | 8.1596 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 11.8 | 6 O'Clock | 50 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.58 |  | 13.7 | 12.6 | 11.8 | 12.6 | 0.78049
DC01 | Montara_Topside | No | Separation (20) | Pipework | 150-PL-43305-01C02 | CML-27 | 150-PL-43305-01C02 CML-27 | yes | FPSO 2014 | Pipe Wall Thickness | 13197 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.025 | CML-27 | CML: Elbow | 3 | 2014-12-11 | 2015-03-29 | 2014-01-21 13:00 | 3.61 | 1.7897 | A4: Left Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.2 | 9 O'Clock | 200 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.59 |  | 6.4 | 6.2 | 6.3 | 5.2 | 0.55603
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 150-PL-43305-01C02 | CML-5 | 150-PL-43305-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23696 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.325 | CML-5 | CML: Pipe Length | 3 | 2018-07-05 | 2019-01-21 | 2015-10-30 07:00 | 2.5 | 0.5964 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.1 | 6 O'Clock | 50 | 5.54 | 50-CG-38456-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.7 | 4.3 | 4.1 | 4.2 | 0.263
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 150-PL-43305-01C02 | CML-43 | 150-PL-43305-01C02 CML-43 | yes | FPSO 2015 | Pipe Wall Thickness | 9130 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.5 | CML-43 | CML: type TBC | 3 | 2017-02-09 | 2017-07-04 | 2015-03-02 07:00 | 2.5 | 0.82216 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.1 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.6 | 4.7 | 4.1 | 4.6 | 0.2708
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 150-PL-43305-01C02 | CML-5 | 150-PL-43305-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23773 | Reject Oil Line Re-Inspection - Point Reflectors on outside radius below 2mm | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.15 | CML-5 | CML: Elbow | 3 | 2017-06-16 | 2017-12-05 | 2015-04-18 07:00 | 2.5 | 0.73926 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.1 | 9 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 | 1.0961 | 5.3 | 5.4 | 5.8 | 4.1 | 0.73258
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML5 | 150-PL-43305-01C02 CML5 |  | FPSO 2015 | Pipe Wall Thickness | 7537 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 4.375 | CML5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.1 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.6 | 4.1 | 4.5 | 4.3 | 0.22174
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML8 | 150-PL-43305-01C02 CML8 |  | FPSO 2015 | Pipe Wall Thickness | 6926 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 4.5 | CML8 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.1 | 3 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.7 | 4.1 | 4.8 | 4.4 | 0.31623
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-3 | 150-PL-43305-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6836 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.425 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.1 | 12 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.3 | 4.4 | 4.9 | 0.34034
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-2 | 150-PL-43305-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2199 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.125 | CML-2 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6 | 6 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6 | 6.4 | 0.1893
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-11 | 150-PL-43305-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 6220 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 4.5 | CML-11 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.1 | 12 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.7 | 4.7 | 4.5 | 0.28284
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-8 | 150-PL-43305-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5994 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 4.35 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.4 | 4.5 | 4.4 | 4.1 | 0.17321
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-15 | 150-PL-43305-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5968 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.225 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.3 | 4.2 | 4.3 | 4.1 | 0.095743
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-10 | 150-PL-43305-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5927 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.575 | CML-10 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.1 | 6 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.9 | 4.7 | 4.1 | 4.6 | 0.34034
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-4 | 150-PL-43305-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5921 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.275 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.1 | 6 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.6 | 4.2 | 4.1 | 4.2 | 0.22174
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-80 | 150-PL-43305-01C02 CML-80 |  | FPSO 2015 | Pipe Wall Thickness | 5565 | Pipe Schedule Estimated. CAST Fitting. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 4.2 | CML-80 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4.1 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.3 | 4.2 | 4.2 | 4.1 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-41 | 150-PL-43305-01C02 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 5419 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.1 | CML-41 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4.1 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.1 | 4.1 | 4.1 | 0
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-21 | 150-PL-43305-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 5441 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.325 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 4.1 | 6 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.3 | 4.2 | 4.1 | 4.7 | 0.263
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-18 | 150-PL-43305-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5438 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.4 | CML-18 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4.1 | 12 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.2 | 5 | 4.3 | 0.40825
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-9 | 150-PL-43305-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2206 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.425 | CML-9 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.3 | 6 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.4 | 6.3 | 6.7 | 0.1893
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-5 | 150-PL-43305-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5184 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 5.65 | CML-5 | CML: type TBC | 0.5 | 2023-06-01 | 2020-11-30 | 2015-03-12 07:00 | 3.5 | 0 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 5.1 | 12 O'Clock | 250 | 4.5 | 250-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 5.1 | 5.6 | 5.8 | 6.1 | 0.42032
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43305-01C02 | CML-11 | 150-PL-43305-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8545 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 4.425 | CML-11 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-02-04 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4.1 | 9 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.7 | 4.4 | 4.5 | 4.1 | 0.25
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43305-01C02 | CML-2 | 150-PL-43305-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8517 |  | 2015-02-03 07:30 | 2015-02-03 15:00 | [35 empty] | Low alarm breach | 4.45 | CML-2 | CML: type TBC | 1 | 2016-12-14 | 2016-03-03 | 2015-02-03 07:30 | 2.5 | 0.85839 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 3 O'Clock | 50 | 5.54 | 50-VA-80014-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.6 | 4.1 | 4.4 | 4.7 | 0.26458
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-2 | 150-PL-43305-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8413 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.862mm/ yr | [34 empty] | Low alarm breach | 4.1 | CML-2 | CML: type TBC | 1 | 2016-12-08 | 2016-02-27 | 2015-01-31 10:00 | 2.5 | 0.86246 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 9 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.1 | 4.1 | 4.1 | 0
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43305-01C02 | CML-1 | 150-PL-43305-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8412 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | Check Corrosion Rate of 0.862mm/ yr | [34 empty] | Low alarm breach | 4.125 | CML-1 | CML: type TBC | 1 | 2016-12-08 | 2016-02-27 | 2015-01-31 10:00 | 2.5 | 0.86246 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 9 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.1 | 4.2 | 4.1 | 0.05
DC01 | Montara_Topside | No | Lube Oil (69) | Pipework | 150-PL-43305-01C02 | CML-1 | 150-PL-43305-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8190 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [35 empty] | Low alarm breach | 4.7 | CML-1 | CML: type TBC | 1 | 2016-11-23 | 2016-02-15 | 2015-01-24 07:30 | 2.5 | 0.87264 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 12 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.5 | 5.7 | 4.5 | 0.69282
DC01 | Montara_Topside | No | Lube Oil (69) | Pipework | 150-PL-43305-01C02 | CML-2 | 150-PL-43305-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8080 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [35 empty] | Low alarm breach | 4.75 | CML-2 | CML: type TBC | 1 | 2016-12-15 | 2016-03-08 | 2015-01-23 07:30 | 2.5 | 0.84374 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 4.1 | 12 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.4 | 5.1 | 5.4 | 0.60277
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43305-01C02 | CML-1 | 150-PL-43305-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2198 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [37 empty] | CML-1 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 |  |  |  | 2.5 |  |  | 9 O'Clock | 100 |  | 100-PL-43305-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-8 | 150-PL-43309-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2216 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.95 | CML-8 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.6 | 6 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.3 | 5.7 | 5.6 | 6.2 | 0.35119
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-6 | 150-PL-43309-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2214 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 5.85 | CML-6 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.6 | 6 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.9 | 5.6 | 6.1 | 0.20817
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-7 | 150-PL-43309-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2215 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.025 | CML-7 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.7 | 12 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.2 | 6.2 | 6 | 0.23629
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-7 | 150-PL-43309-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3360 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.75 | CML-7 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 12 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 | 0 | 4.1 | 4.8 | 4.5 | 5.6 | 0.63509
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-5 | 150-PL-43309-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3358 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.275 | CML-5 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 9 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 | 0 | 4.4 | 4.2 | 4.4 | 4.1 | 0.15
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-3 | 150-PL-43309-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3356 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.8 | CML-3 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 12 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 | 0 | 4.1 | 4.4 | 6 | 4.7 | 0.83666
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-2 | 150-PL-43309-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3355 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.525 | CML-2 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 12 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 | 0 | 4.1 | 4.3 | 5.1 | 4.6 | 0.43493
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-1 | 150-PL-43309-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3354 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.825 | CML-1 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 3 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.7 | 4.1 | 4.8 | 5.7 | 0.66018
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-5 | 150-PL-43309-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3321 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.275 | CML-5 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 9 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.4 | 4.2 | 4.4 | 4.1 | 0.15
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-3 | 150-PL-43309-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3319 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.8 | CML-3 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 12 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.4 | 6 | 4.7 | 0.83666
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-2 | 150-PL-43309-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3318 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.525 | CML-2 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 12 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.3 | 5.1 | 4.6 | 0.43493
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-1 | 150-PL-43309-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3317 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.825 | CML-1 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 3 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.7 | 4.1 | 4.8 | 5.7 | 0.66018
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-7 | 150-PL-43309-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3323 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.539mm/ yr | [34 empty] | Low alarm breach | 4.75 | CML-7 | CML: type TBC | 1 | 2015-05-23 | 2014-12-14 | 2014-05-08 14:30 | 2.5 | 1.5386 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 12 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.8 | 4.5 | 5.6 | 0.63509
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-2 | 150-PL-43309-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3095 | Rope Access | 2014-05-04 11:00 | 2014-05-04 11:30 | Check Corrosion Rate of 1.558mm/ yr | [34 empty] | Low alarm breach | 4.65 | CML-2 | CML: Elbow | 1 | 2015-05-14 | 2014-12-07 | 2014-05-04 11:00 | 2.5 | 1.5575 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 12 O'Clock | 50 | 5.54 | 50-CI-42041-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.1 | 4.8 | 5.3 | 4.4 | 0.51962
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43309-01C02 | CML-3 | 150-PL-43309-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3036 | Rope Access | 2014-05-03 14:00 | 2014-05-03 15:00 | [35 empty] | Low alarm breach | 4.175 | CML-3 | CML: Pipe Length | 1 | 2015-05-12 | 2014-12-06 | 2014-05-03 14:00 | 2.5 | 1.5616 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 6 O'Clock | 50 | 5.54 | 50-VA-80009-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.2 | 4.1 | 4.1 | 4.3 | 0.095743
DC01 | Montara_Topside | No | Main Power (80) | Pipework | 150-PL-43309-01C02 | CML-1 | 150-PL-43309-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3030 | Rope Access | 2014-05-03 13:00 | 2014-05-03 14:00 | [35 empty] | Low alarm breach | 4.625 | CML-1 | CML: Elbow | 1 | 2015-05-12 | 2014-12-06 | 2014-05-03 13:00 | 2.5 | 1.5618 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.1 | 9 O'Clock | 50 | 5.54 | 50-VA-80010-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.6 | 5.1 | 4.7 | 4.1 | 0.4113
DC01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 150-PL-43309-01C02 | CML-17 | 150-PL-43309-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 3079 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 1.563mm/ yr | [35 empty] | 4.85 | CML-17 | CML: Elbow | 3 | 2015-05-12 | 2015-07-27 | 2014-05-03 08:00 | 2.5 | 1.5627 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.1 | 3 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 | 1.4572 | 5.2 | 4.1 | 5.2 | 4.9 | 0.51962
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PL-43309-01C02 | CML-5 | 150-PL-43309-01C02 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 5501 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | Check Corrosion Rate of 0.872mm/ yr | [34 empty] | Medium alarm breach | 10.4 | CML-5 | CML: Pipe Length | 6 | 2014-08-13 | 2014-05-22 | 2014-05-31 07:00 | 8.55 | 8.0757 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 10.2 | 9 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.65 |  | 11 | 10.2 | 10.2 | 10.2 | 0.4
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PL-43309-01C02 | CML-9 | 150-PL-43309-01C02 CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 5504 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [35 empty] | Medium alarm breach | 10.5 | CML-9 | CML: Pipe Length | 6 | 2014-08-13 | 2014-05-22 | 2014-05-31 07:00 | 8.55 | 8.0757 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 10.2 | 9 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.65 |  | 10.8 | 10.8 | 10.2 | 10.2 | 0.34641
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PL-43309-01C02 | CML-5 | 150-PL-43309-01C02 CML-5 | yes | FPSO 2016 | Pipe Wall Thickness | 24444 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 |  |  | John Wilson | 2017-03-23 15:43 | [31 empty] | Medium alarm breach | 10.55 | CML-5 | CML: Pipe Length | 6 | 2017-02-19 | 2016-06-04 | 2016-07-03 07:00 | 8.55 | 2.6074 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 10.2 | 3 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.65 | 0.32697 | 10.7 | 10.2 | 10.6 | 10.7 | 0.23805
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PL-43309-01C02 | CML-7 | 150-PL-43309-01C02 CML-7 | yes | FPSO 2016 | Pipe Wall Thickness | 24446 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | [35 empty] | Medium alarm breach | 10.5 | CML-7 | CML: Pipe Length | 6 | 2017-02-19 | 2016-06-04 | 2016-07-03 07:00 | 8.55 | 2.6074 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 10.2 | 6 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.65 | 0.43596 | 10.5 | 10.6 | 10.2 | 10.7 | 0.21602
DC01 | Montara_Topside | No | Separation (20) | Pipework | 150-PL-43309-01C02 | CML-27 | 150-PL-43309-01C02 CML-27 | yes | FPSO 2014 | Pipe Wall Thickness | 21201 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 6.125 | CML-27 | CML: Elbow | 3 | 2016-01-05 | 2016-07-05 | 2014-05-30 09:30 | 3.61 | 1.0546 | A4: Left Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.3 | 9 O'Clock | 200 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.69 | -0.28327 | 6.4 | 6.4 | 6.4 | 5.3 | 0.55
DC01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PL-43309-01C02 | CML-2 | 150-PL-43309-01C02 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 20594 | Rope Access | 2014-05-26 14:00 | 2014-05-26 15:00 | [36 empty] | 9.05 | CML-2 | CML: type TBC | 1 | 2026-04-14 | 2023-05-14 | 2014-05-26 14:00 | 6.91 | 0.14211 | A3: Inside Quadrant |  | 7.74 | 6.91 | 7.325 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PG-23062-25S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.69 |  | 9.7 | 9.2 | 8.6 | 8.7 | 0.50662
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-PL-43309-01C02 | CML-7 | 150-PL-43309-01C02 CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24437 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | Check Corrosion Rate of 0.433mm/ yr | [35 empty] | 4.575 | CML-7 | CML: Elbow | 3 | 2020-06-03 | 2021-03-05 | 2016-07-03 07:00 | 2.5 | 0.43349 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 | 0.17056 | 4.2 | 4.7 | 4.6 | 4.8 | 0.263
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-10 | 150-PL-43309-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2218 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.05 | CML-10 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.9 | 6 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.1 | 5.9 | 6 | 0.1291
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-9 | 150-PL-43309-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2217 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.35 | CML-9 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.9 | 6 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 6.8 | 5.9 | 6 | 0.46547
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-2 | 150-PL-43309-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2210 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.2 | CML-2 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6 | 3 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6 | 6.2 | 6.3 | 0.14142
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-5 | 150-PL-43309-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2213 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.25 | CML-5 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.1 | 9 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.4 | 6.3 | 6.1 | 0.1291
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 150-PL-43309-01C02 | CML-16 | 150-PL-43309-01C02 CML-16 | yes | FPSO 2015 | Pipe Wall Thickness | 9103 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.2 | CML-16 | CML: type TBC | 3 | 2017-05-21 | 2017-10-23 | 2015-03-02 07:00 | 2.5 | 0.76507 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 3 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 6.3 | 4.2 | 6 | 4.3 | 1.1045
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 150-PL-43309-01C02 | CML-4 | 150-PL-43309-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 23772 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.175 | CML-4 | CML: Elbow | 3 | 2017-10-08 | 2018-04-11 | 2015-04-18 07:00 | 2.5 | 0.68608 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.2 | 3 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 | 1.8268 | 5.3 | 4.2 | 4.9 | 6.3 | 0.87702
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 150-PL-43309-01C02 | CML-17 | 150-PL-43309-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23785 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 4.375 | CML-17 | CML: Pipe Length | 3 | 2017-10-08 | 2018-04-11 | 2015-04-18 07:00 | 2.5 | 0.68608 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.2 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 | 0 | 4.2 | 4.6 | 4.3 | 4.4 | 0.17078
DC01 | Montara_Topside | No | Produced Water (44) | Pipework | 150-PL-43309-01C02 | CML-17 | 150-PL-43309-01C02 CML-17 | yes | FPSO 2015 | Pipe Wall Thickness | 7761 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 4.375 | CML-17 | CML: Pipe Length | 3 | 2017-10-08 | 2018-04-11 | 2015-04-18 07:00 | 2.5 | 0.68608 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.2 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.6 | 4.3 | 4.4 | 0.17078
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML40 | 150-PL-43309-01C02 CML40 |  | FPSO 2015 | Pipe Wall Thickness | 7572 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 4.325 | CML40 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.3 | 4.5 | 4.3 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML1 | 150-PL-43309-01C02 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 7533 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 4.45 | CML1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 3 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.3 | 4.2 | 4.6 | 4.7 | 0.23805
DC01 | Montara_Topside | No | Open Drain (56) | Pipework | 150-PL-43309-01C02 | CML-1 | 150-PL-43309-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 20931 | Rope Access | 2014-05-16 09:30 | 2014-05-16 11:00 | [36 empty] | 4.875 | CML-1 | CML: type TBC | 3 | 2015-08-19 | 2015-11-22 | 2014-05-16 09:30 | 2.5 | 1.3476 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.2 | 6 O'Clock | 80 | 5.49 | 80-DH-56044-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 5.5 | 4.4 | 4.2 | 5.4 | 0.6702
DC01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 150-PL-43309-01C02 | CML-4 | 150-PL-43309-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7477 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 0.718mm/ yr | [34 empty] | Low alarm breach | 4.8 | CML-4 | CML: Elbow | 1 | 2017-08-24 | 2016-09-16 | 2015-04-13 07:00 | 2.5 | 0.7179 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.2 | 3 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.7 | 4.2 | 4.7 | 5.6 | 0.5831
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML125 | 150-PL-43309-01C02 CML125 |  | FPSO 2015 | Pipe Wall Thickness | 7464 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 4.5 | CML125 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.8 | 4.8 | 4.2 | 0.34641
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML2 | 150-PL-43309-01C02 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 7191 |  | 2015-04-08 07:00 | 2015-04-08 15:00 | [36 empty] | 4.525 | CML2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-08 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 4.2 | 3 O'Clock | 80 | 2.5 | 80-WF-71320-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.5 | 4.2 | 4.6 | 4.8 | 0.25
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-45 | 150-PL-43309-01C02 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 6878 |  | 2015-04-05 07:00 | 2015-04-05 15:00 | [36 empty] | 4.775 | CML-45 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-05 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 3 O'Clock | 100 | 3 | 100-WF-71328-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 5.2 | 4.2 | 4.7 | 5 | 0.43493
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-25 | 150-PL-43309-01C02 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6699 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 4.325 | CML-25 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.5 | 4.3 | 4.3 | 4.2 | 0.12583
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-64 | 150-PL-43309-01C02 CML-64 |  | FPSO 2015 | Pipe Wall Thickness | 6738 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 4.475 | CML-64 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 12 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.6 | 4.6 | 4.5 | 0.1893
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-7 | 150-PL-43309-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6416 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 4.825 | CML-7 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 9 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.9 | 5.4 | 4.8 | 4.2 | 0.49244
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-25 | 150-PL-43309-01C02 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6434 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 4.55 | CML-25 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.2 | 4.7 | 5.1 | 0.43589
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-1 | 150-PL-43309-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6242 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 4.3 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 4.2 | 6 O'Clock | 40 | 2.5 | 40-WF-71331-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.4 | 4.3 | 4.2 | 4.3 | 0.08165
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-13 | 150-PL-43309-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6240 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 4.8 | CML-13 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4.2 | 12 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.7 | 5.6 | 4.7 | 0.5831
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-10 | 150-PL-43309-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5996 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 4.55 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 4.2 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.9 | 4.2 | 4.2 | 4.9 | 0.40415
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-8 | 150-PL-43309-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5925 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.55 | CML-8 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 3 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.6 | 4.2 | 4.6 | 4.8 | 0.25166
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-3 | 150-PL-43309-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5920 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.425 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.3 | 4.2 | 5 | 4.2 | 0.38622
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-21 | 150-PL-43309-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 5399 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.25 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 4.2 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.3 | 4.3 | 4.2 | 4.2 | 0.057735
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-12 | 150-PL-43309-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5432 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.425 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 4.2 | 6 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.7 | 4.4 | 4.2 | 4.4 | 0.20616
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-4 | 150-PL-43309-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2212 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.25 | CML-4 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.1 | 9 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.4 | 6.3 | 6.1 | 0.1291
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-3 | 150-PL-43309-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2211 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [36 empty] | 6.425 | CML-3 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.2 | 6 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 6.3 | 6.2 | 6.5 | 0.22174
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-10 | 150-PL-43309-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5328 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.9 | CML-10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4.2 | 12 O'Clock | 50 | 2.5 | 50-WF-71312-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.8 | 5.1 | 5.5 | 0.54772
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-1 | 150-PL-43309-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5180 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 5.55 | CML-1 | CML: type TBC | 0.5 | 2023-06-01 | 2020-11-30 | 2015-03-12 07:00 | 3.5 | 0 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 5.2 | 12 O'Clock | 250 | 4.5 | 250-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 5.2 | 5.8 | 5.4 | 5.8 | 0.3
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-6 | 150-PL-43309-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5167 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 4.275 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4.2 | 12 O'Clock | 50 | 2.5 | 50-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.3 | 4.3 | 4.3 | 0.05
DC01 | Montara_Topside | No | Compressed Air (63) | Pipework | 150-PL-43309-01C02 | CML-17 | 150-PL-43309-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8941 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.77mm/ yr | [35 empty] | 5.15 | CML-17 | CML: type TBC | 3 | 2017-05-12 | 2017-10-14 | 2015-02-26 09:00 | 2.5 | 0.76978 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 5 | 5.4 | 6 | 0.75498
DC01 | Montara_Topside | No | Nitrogen (67) | Pipework | 150-PL-43309-01C02 | CML-1 | 150-PL-43309-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8704 |  | 2015-02-14 07:00 | 2015-02-14 09:00 | [36 empty] | 4.525 | CML-1 | CML: type TBC | 3 | 2017-04-15 | 2017-09-13 | 2015-02-14 07:00 | 2.5 | 0.7847 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.8 | 4.5 | 4.6 | 0.25
DC01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-PL-43309-01C02 | CML-7 | 150-PL-43309-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8541 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 4.675 | CML-7 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-02-04 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 12 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.7 | 4.7 | 5.1 | 0.36856
DC01 | Montara_Topside | No | Flare (43) | Pipework | 150-PL-43309-01C02 | CML-1 | 150-PL-43309-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2209 | Rope Access | 2014-03-14 07:00 | 2014-03-14 17:00 | [37 empty] | CML-1 | CML: type TBC | 3 |  |  | 2014-03-14 07:00 | 2.5 | 0 |  |  |  | 2.5 |  |  | 9 O'Clock | 100 |  | 100-PL-43309-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-11 | 100-WF-71967-1CG CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10908 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 8.75 | CML-11 | CML: type TBC | 3 | 2073-09-12 | 2058-06-24 | 2014-01-05 | 2.5 | 0.10046 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.5 | 9 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.6 | 9.4 | 8.5 | 0.43589
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-13 | 250-PG-23015-06C03-A CML-13 | yes | FPSO 2014 | Pipe Wall Thickness | 13045 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 18.925 | CML-13 | CML: type TBC | 6 | 2019-08-20 | 2018-06-12 | 2014-01-11 13:00 | 8.55 | 1.5605 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.3 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.75 |  | 19.6 | 21.3 | 17.3 | 17.5 | 1.8945
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-2 | 100-WF-71967-1CG CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10899 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 8.75 | CML-2 | CML: type TBC | 3 | 2073-09-12 | 2058-06-24 | 2014-01-05 | 2.5 | 0.10046 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.5 | 12 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.8 | 8.8 | 8.9 | 0.17321
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-3 | 100-WF-71967-1CG CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10900 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 9.425 | CML-3 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A4: Left Quadrant |  | 5.56 | 2.5 | 4.03 | 9 | 9 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.5 | 9.7 | 9.5 | 9 | 0.29861
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42040-01S01 | CML-6 | 50-CI-42040-01S01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3086 | Rope Access | 2014-05-04 11:30 | 2014-05-04 12:00 | Check Corrosion Rate of 1.449mm/ yr | [34 empty] | Low alarm breach | 4.75 | CML-6 | CML: Elbow | 1 | 2015-07-06 | 2015-01-17 | 2014-05-04 11:30 | 2.5 | 1.4493 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-CI-42040-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.7 | 5.4 | 4.7 | 0.49329
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42041-01S01 | CML-7 | 50-CI-42041-01S01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3100 | Rope Access | 2014-05-04 11:00 | 2014-05-04 11:30 | Check Corrosion Rate of 1.449mm/ yr | [34 empty] | Low alarm breach | 4.975 | CML-7 | CML: Elbow | 1 | 2015-07-06 | 2015-01-17 | 2014-05-04 11:00 | 2.5 | 1.4494 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-CI-42041-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 5.1 | 4.5 | 6.1 | 0.83815
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-10 | 100-WF-71967-1CG CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10907 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 9.65 | CML-10 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A4: Left Quadrant |  | 5.56 | 2.5 | 4.03 | 9.1 | 9 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.9 | 10.3 | 9.3 | 9.1 | 0.55076
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-31 | 50-DC-57020-01C02 CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 2473 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 1.673mm/ yr | [35 empty] | 4.7 | CML-31 | CML: type TBC | 3 | 2015-03-26 | 2015-06-05 | 2014-03-20 09:30 | 2.5 | 1.6727 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 5.1 | 4.8 | 4.7 | 0.37417
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-PG-23404-01D03-A | CML-2 | 150-PG-23404-01D03-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2234 |  | 2014-03-14 07:00 | 2014-03-14 17:00 | [35 empty] | Medium alarm breach | 4.225 | CML-2 | CML: type TBC | 1 | 2014-08-28 | 2014-03-03 | 2014-03-14 07:00 | 2.5 | 3.71 | A1: Outside Quadrant |  | 6.11 | 2.5 | 4.305 | 4.2 | 9 O'Clock | 150 | 7.11 | 150-PG-23404-01D01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.2 | 4.3 | 4.2 | 0.05
RP01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-PG-23404-01D03-A | CML-1 | 150-PG-23404-01D03-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2233 |  | 2014-03-14 07:00 | 2014-03-14 17:00 | [35 empty] | Medium alarm breach | 4.2 | CML-1 | CML: type TBC | 1 | 2014-08-28 | 2014-03-03 | 2014-03-14 07:00 | 2.5 | 3.71 | A1: Outside Quadrant |  | 6.11 | 2.5 | 4.305 | 4.2 | 9 O'Clock | 150 | 7.11 | 150-PG-23404-01D01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.2 | 4.2 | 4.2 | 0
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-3 | 50-PL-23040-03C03 CML-3 | yes | FPSO 2013 | Pipe Wall Thickness | 10188 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 12.8333 | CML-3 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 11.7 | 6 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 11.8 |  | 11.7 | 15 | 1.8771
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-8 | 25-FG-45455-01C02-E CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2416 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 7.1 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 9.9 | 6 | 6.4 | 6.1 | 1.8744
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-11 | 200-PG-23505-09C02-A CML-11 | yes | FPSO 2014 | Pipe Wall Thickness | 5508 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 18.175 | CML-11 | CML: Elbow | 3 | 2017-05-14 | 2016-10-20 | 2014-05-31 07:00 | 14.06 | 1.0621 | A3: Inside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 6 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | 0 | 18.6 | 17.9 | 17.2 | 19 | 0.7932
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-26 | 300-PG-20005-03C03-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 6182 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 15.975 | CML-26 | CML: Elbow | 6 | 2024-02-19 | 2022-03-17 | 2014-07-11 07:30 | 4.9 | 0.87352 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 17.5 | 16.7 | 13.3 | 16.4 | 1.8428
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-2 | 100-WC-40516-1CG CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 8675 | Material Class Not Selectable.Line is FFS. Action: to recheck in two year(Feb. 2017) to confirm CR. | 2015-02-13 07:00 | 2015-02-13 14:00 | Check Corrosion Rate of 0.739mm/ yr |  | Administrator | 2015-09-08 11:53 | [32 empty] | 8.1 | CML-2 | CML: Elbow | 3 | 2021-08-10 | 2019-07-17 | 2015-02-13 07:00 | 2.5 | 0.73904 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 7.3 | 12 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 8.4 | 8.2 | 8.5 | 0.54772
VA01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-VA-23054-01C02 | CML-5 | 25-VA-23054-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5848 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 15.225 | CML-5 | CML: Reducer | 6 | 2075-10-24 | 2074-08-12 | 2014-06-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 13.1 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.6 |  | 16.6 | 16.9 | 13.1 | 14.3 | 1.8319
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-4 | 50-PL-23041-06C03 CML-4 | yes | FPSO 2013 | Pipe Wall Thickness | 10217 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 11.05 | CML-4 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 4.4941 | A4: Left Quadrant |  | 5.07 |  |  | 9.1 | 9 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 11 | 13.5 | 10.6 | 9.1 | 1.8267
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-1 | 50-PL-23040-03C03 CML-1 | yes | FPSO 2013 | Pipe Wall Thickness | 10186 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 12.8 | CML-1 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 11.7 | 9 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 14.9 | 11.8 |  | 11.7 | 1.8193
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-9 | 50-PW-44013-01X01 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10323 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.85 | CML-9 | CML: Elbow | 3 | 2014-07-03 | 2014-08-14 | 2013-11-10 | 2.5 | 2.7938 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 5 | 5 | 5.1 | 0.36968
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-8 | 100-WF-71967-1CG CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10905 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 9.65 | CML-8 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 9.1 | 6 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.8 | 9.9 | 9.1 | 9.8 | 0.36968
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-6 | 100-WF-71967-1CG CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10903 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 9.75 | CML-6 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A2: Right Quadrant |  | 5.56 | 2.5 | 4.03 | 9.1 | 3 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.8 | 9.1 | 10.3 | 9.8 | 0.49329
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-9 | 100-WF-71967-1CG CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10906 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 9.475 | CML-9 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 9.4 | 6 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.5 | 9.5 | 9.4 | 9.5 | 0.05
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-4 | 100-WF-71967-1CG CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10901 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 10.1 | CML-4 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 9.7 | 12 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 10.1 | 10.4 | 10.2 | 0.29439
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-5 | 100-WF-71967-1CG CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10902 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 10.35 | CML-5 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 9.8 | 12 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.8 | 10.4 | 10.5 | 10.7 | 0.3873
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-7 | 100-WF-71967-1CG CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10904 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 10.525 | CML-7 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 10.3 | 6 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.4 | 10.5 | 10.3 | 10.9 | 0.263
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-1 | 100-WF-71967-1CG CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10898 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 10.9 | CML-1 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A2: Right Quadrant |  | 5.56 | 2.5 | 4.03 | 10.3 | 3 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 11.2 | 10.3 | 11.3 | 10.8 | 0.45461
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-1 | 50-DC-57043-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23126 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | Check Corrosion Rate of 0.639mm/ yr | [35 empty] | 4.55 | CML-1 | CML: Elbow | 3 | 2018-03-03 | 2018-09-05 | 2015-05-10 07:00 | 2.5 | 0.639 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 9 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 0.089736 | 4.6 | 4.9 | 4.4 | 4.3 | 0.26458
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-2 | 50-DC-57044-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23120 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | Check Corrosion Rate of 0.639mm/ yr | [35 empty] | 4.75 | CML-2 | CML: Elbow | 3 | 2018-03-03 | 2018-09-05 | 2015-05-10 07:00 | 2.5 | 0.639 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 9 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 0.44856 | 4.9 | 4.6 | 5.2 | 4.3 | 0.3873
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-4 | 250-PG-23005-06C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10050 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 17.775 | CML-4 | CML: Elbow | 6 | 2015-10-16 | 2015-05-04 | 2013-11-06 | 8.6 | 4.0658 | A1: Outside Quadrant |  | 12.26 | 8.6 | 10.43 | 16.5 | 12 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 16.5 | 17.4 | 16.8 | 20.4 | 1.7896
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71340-01K01 | CML-9 | 100-WF-71340-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22380 |  | 2015-04-19 07:00 | 2015-04-19 15:00 | [36 empty] | 4.55 | CML-9 | CML: Equal Tee | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.3 | 3 O'Clock | 100 | 3 | 100-WF-71340-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 4.3 | 4.7 | 4.9 | 0.3
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-36 | 150-PG-23506-25C02 CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 2810 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.825 | CML-36 | CML: Elbow | 3 | 2015-11-12 | 2015-03-31 | 2014-03-15 09:00 | 15.88 | 2.4767 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 20 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.12 |  | 20.8 | 22.5 | 24 | 20 | 1.7858
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-5 | 150-PG-20507-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2849 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.7 | CML-5 | CML: type TBC | 6 | 2015-10-30 | 2015-06-23 | 2014-03-16 07:00 | 2.5 | 3.507 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 8.2 | 6 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 11.9 | 12 | 8.2 | 10.7 | 1.7682
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-23 | 300-PF-20500-03C03-P CML-23 | Yes | FPSO 2014 | Pipe Wall Thickness | 21643 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 16.15 | CML-23 | CML: Elbow | 6 | 2039-10-17 | 2035-01-19 | 2014-09-27 07:00 | 4.9 | 0.35496 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 3 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 17.3 | 13.8 | 15.8 | 17.7 | 1.7673
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44513-01C02 | CML-6 | 80-PL-44513-01C02 CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 7971 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:08 | [32 empty] | 5 | CML-6 | CML: Pipe Length | 3 | 2021-09-09 | 2022-08-27 | 2015-01-18 10:30 | 2.5 | 0.36106 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 5 | 5.1 | 0.08165
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-5 | 50-DH-56137-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13121 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 18.9667 | CML-5 | CML: type TBC | 6 | 2096-01-05 | 2084-09-16 | 2014-02-04 07:00 | 2.81 | 0 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 17.9 | 12 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.09 |  | 17.9 | 21 | 18 |  | 1.7616
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-4 | 50-PG-23074-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20626 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 8.6 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-07-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 9.8 | 9.4 | 9.2 | 6 | 1.7512
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-14 | 300-PF-20500-03C03-P CML-14 | Yes | FPSO 2015 | Pipe Wall Thickness | 23494 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 15 | CML-14 | CML: Elbow | 6 | 2024-10-23 | 2022-10-05 | 2015-07-27 07:00 | 4.9 | 0.82164 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.5 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 | -0.12046 | 12.5 | 16.2 | 16.2 | 15.1 | 1.7455
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-2 | 300-PG-20048-03C03-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23345 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14 | CML-2 | CML: Elbow | 6 | 2025-05-21 | 2023-03-27 | 2015-07-20 07:00 | 4.9 | 0.78218 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.6 | 3 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 | 0 | 12.7 | 12.6 | 16.3 | 14.4 | 1.7416
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-9 | 300-PG-20004-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 6132 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 15.15 | CML-9 | CML: Pipe Length | 6 | 2051-12-04 | 2044-12-31 | 2014-07-11 07:30 | 4.9 | 0.24315 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 6 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 17.7 | 14.2 | 14 | 14.7 | 1.7253
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML60 | 100-WF-71308-01K01 CML60 |  | FPSO 2015 | Pipe Wall Thickness | 6978 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 4.525 | CML60 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.3 | 12 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 4.7 | 4.4 | 4.7 | 0.20616
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 200-WF-71334-01K01 | CML-3 | 200-WF-71334-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6394 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 4.85 | CML-3 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-21 07:00 | 2.8 | 0 | A1: Outside Quadrant |  | 3.5 | 2.8 | 3.15 | 4.6 | 12 O'Clock | 200 | 4 | 200-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.6 | 4.9 | 5.2 | 4.7 | 0.26458
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71359-01K01 | CML-4 | 100-WF-71359-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6213 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 4.45 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4.3 | 9 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.6 | 4.5 | 4.4 | 4.3 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71327-01K01 | CML-12 | 100-WF-71327-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5929 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.525 | CML-12 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.3 | 12 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 4.4 | 4.8 | 4.6 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71318-01K01 | CML-4 | 50-WF-71318-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5886 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 4.575 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4.3 | 12 O'Clock | 50 | 2.5 | 50-WF-71318-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 4.8 | 4.7 | 4.5 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71313-01K01 | CML-15 | 40-WF-71313-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5435 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.775 | CML-15 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 4.3 | 3 O'Clock | 40 | 2.5 | 40-WF-71313-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 5.6 | 4.3 | 4.6 | 4.6 | 0.56789
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71310-01K01 | CML-7 | 150-WF-71310-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5318 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.65 | CML-7 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4.3 | 9 O'Clock | 150 | 3 | 150-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.5 | 4.5 | 5.3 | 4.3 | 0.44347
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71306-01K01 | CML-7 | 250-WF-71306-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5186 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 5.575 | CML-7 | CML: type TBC | 0.5 | 2023-06-01 | 2020-11-30 | 2015-03-12 07:00 | 3.5 | 0 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 5.3 | 12 O'Clock | 250 | 4.5 | 250-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 5.3 | 5.4 | 5.8 | 5.8 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-32 | 80-WF-71400-01K01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 5277 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 4.4 | CML-32 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.4 | 4.4 | 4.5 | 4.3 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-51 | 50-AI-63007-01E01 CML-51 |  | FPSO 2015 | Pipe Wall Thickness | 8975 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.712mm/ yr | [35 empty] | 4.95 | CML-51 | CML: type TBC | 3 | 2017-09-05 | 2018-02-19 | 2015-02-26 09:00 | 2.5 | 0.71234 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 5.2 | 5.2 | 4.3 | 5.1 | 0.43589
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67009-01E01 | CML-1 | 50-GN-67009-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8779 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 4.95 | CML-1 | CML: type TBC | 3 | 2017-08-09 | 2018-01-20 | 2015-02-15 07:00 | 2.5 | 0.72498 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 4.9 | 5.1 | 5.5 | 0.5
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-13 | 50-WD-53007-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8152 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 4.4 | CML-13 | CML: type TBC | 3 | 2017-06-16 | 2017-11-22 | 2015-01-24 07:30 | 2.5 | 0.75144 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.4 | 4.4 | 4.3 | 4.5 | 0.08165
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69004-01S01 | CML-11 | 80-OL-69004-01S01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8102 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [35 empty] | Low alarm breach | 4.9 | CML-11 | CML: type TBC | 1 | 2017-07-20 | 2016-08-25 | 2015-01-23 07:30 | 2.5 | 0.72234 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 4.3 | 12 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 4.6 | 6 | 4.7 | 0.75277
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69003-01S01 | CML-5 | 80-OL-69003-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8083 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [35 empty] | Low alarm breach | 5.15 | CML-5 | CML: type TBC | 1 | 2017-07-20 | 2016-08-25 | 2015-01-23 07:30 | 2.5 | 0.72234 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 4.3 | 12 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 5.5 | 5.2 | 5.6 | 0.59161
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-13 | 250-PG-23005-06C03 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10059 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 18.5 | CML-13 | CML: Elbow | 6 | 2015-04-07 | 2014-11-30 | 2013-11-06 | 8.6 | 5.2209 | A3: Inside Quadrant |  | 12.26 | 8.6 | 10.43 | 16 | 6 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 19 | 19.9 | 16 | 19.1 | 1.7146
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-12 | 100-WF-71967-1CG CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10909 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 11.725 | CML-12 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 10.5 | 6 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 12.2 | 12 | 10.5 | 12.2 | 0.82209
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71967-1CG | CML-13 | 100-WF-71967-1CG CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10910 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 19.025 | CML-13 | CML: type TBC | 3 | 2074-01-04 | 2058-09-17 | 2014-01-05 | 2.5 | 0 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 18.7 | 3 O'Clock | 100 | 8.56 | 100-WF-71967-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.2 |  | 18.7 | 18.7 | 19.4 | 19.3 | 0.37749
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-10 | 300-PL-13L9004-BC11X-P-50 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 6495 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.5 | CML-10 | CML: Reducer | 6 |  |  | 2014-07-23 07:30 |  | 0 | A4: Left Quadrant |  | 11.48 |  |  | 17.8 | 9 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19.1 | 20.1 | 21 | 17.8 | 1.3736
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9004-BC11X-P-50 |  | 300-PL-13L9004-BC11X-P-50 | yes | FPSO 2014 | Pipe Wall Thickness | 22101 | Rope access | 2014-06-02 09:30 | 2014-06-02 11:00 | [36 empty] | 4.7 | 50-CG-38302-01C02-P | Piping | 3 | 2015-11-16 |  | 2014-06-02 09:30 |  | 1.2353 | A1: Outside Quadrant |  |  | 2.5 |  | 4.3 | 12 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 4.3 | 4.3 | 4.8 | 5 | 4.7 | 0.29439
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9004-BC11X-P-50 |  | 300-PL-13L9004-BC11X-P-50 | yes | FPSO 2014 | Pipe Wall Thickness | 22091 | Rope access | 2014-06-02 07:00 | 2014-06-02 08:00 | [36 empty] | 4.75 | 50-CG-38301-01C02-P | Piping | 3 | 2015-11-16 |  | 2014-06-02 07:00 |  | 1.2356 | A2: Right Quadrant |  |  | 2.5 |  | 4.3 | 3 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 4.3 | 5 | 4.3 | 5.2 | 4.5 | 0.42032
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-11 | 300-PL-13L9004-BC11X-P-50 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 6496 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 17.5 | CML-11 | CML: Pipe Length | 6 |  |  | 2014-07-23 07:30 |  | 0.18143 | A1: Outside Quadrant |  | 11.48 |  |  | 17.2 | 12 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 17.2 | 17.7 | 17.7 | 17.4 | 0.24495
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-3 | 300-PL-13L9004-BC11X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3065 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 1.346mm/ yr | [35 empty] | 5.65 | CML-3 | CML: Equal Tee | 3 | 2015-09-03 | 2015-12-01 | 2014-05-03 08:00 | 2.5 | 1.3457 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 2.7063 | 4.3 | 5.6 | 6.8 | 5.9 | 1.0344
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-9 | 300-PL-13L9004-BC11X-P-50 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 6494 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 18.875 | CML-9 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A1: Outside Quadrant |  | 11.48 |  |  | 18.3 | 12 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 18.3 | 19.4 | 19.2 | 18.6 | 0.51235
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-18 | 300-PL-13L9004-BC11X-P-50 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10615 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 2.678mm/ yr | [35 empty] | 4.85 | CML-18 | CML: type TBC | 3 | 2014-07-20 | 2014-09-02 | 2013-11-17 | 2.5 | 2.6781 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 5.2 | 4.6 | 5.3 | 0.47958
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-14 | 300-PL-13L9004-BC11X-P-50 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10638 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 7.2333 | CML-14 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2013-11-18 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.76 | 6.9 | 9 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  |  | 7.2 | 7.6 | 6.9 | 0.35119
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-8 | 300-PL-13L9004-BC11X-P-50 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 6493 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.825 | CML-8 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A4: Left Quadrant |  | 11.48 |  |  | 19.3 | 9 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19.4 | 20.3 | 20.3 | 19.3 | 0.55
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-7 | 300-PL-13L9004-BC11X-P-50 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 6492 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 17.425 | CML-7 | CML: Pipe Length | 6 |  |  | 2014-07-23 07:30 |  | 0.11663 | A1: Outside Quadrant |  | 11.48 |  |  | 17.3 | 12 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 17.3 | 17.4 | 17.5 | 17.5 | 0.095743
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-10 | 300-PL-13L9004-BC11X-P-50 CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 23546 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 | Check Corrosion Rate of 0.308mm/ yr |  | John Wilson | 2017-03-23 15:35 | Loss within CA no further action required. | [30 empty] | Medium alarm breach | 12.475 | CML-10 | CML: Elbow | 6 | 2016-02-06 | 2015-08-02 | 2015-08-03 09:30 | 8.55 | 3.616 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 10.4 | 3 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.85 | 0.38482 | 13.6 | 10.4 | 12.1 | 13.8 | 1.5777
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-6 | 300-PL-13L9004-BC11X-P-50 CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 23542 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 | Check Corrosion Rate of 0.308mm/ yr | [34 empty] | Medium alarm breach | 12.05 | CML-6 | CML: Elbow | 6 | 2016-02-06 | 2015-08-02 | 2015-08-03 09:30 | 8.55 | 3.616 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 10.4 | 9 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.85 | 0.085061 | 12.5 | 12.3 | 13 | 10.4 | 1.1387
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-4 | 300-PL-13L9004-BC11X-P-50 CML-4 | yes | FPSO 2016 | Pipe Wall Thickness | 24443 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 |  |  | John Wilson | 2017-03-23 15:47 | [31 empty] | Medium alarm breach | 11.375 | CML-4 | CML: Elbow | 6 | 2017-03-25 | 2016-07-02 | 2016-07-03 07:00 | 8.55 | 2.5427 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 10.4 | 12 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.85 | 0 | 10.4 | 11 | 12.7 | 11.4 | 0.97425
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-4 | 300-PL-13L9004-BC11X-P-50 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 23540 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 | [35 empty] | Medium alarm breach | 11.775 | CML-4 | CML: Elbow | 6 | 2016-02-06 | 2015-08-02 | 2015-08-03 09:30 | 8.55 | 3.616 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 10.4 | 12 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.85 | 0.17012 | 10.4 | 12 | 12.2 | 12.5 | 0.93941
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-9 | 300-PL-13L9004-BC11X-P-50 CML-9 | yes | FPSO 2016 | Pipe Wall Thickness | 24447 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 |  |  | John Wilson | 2017-03-23 15:48 | [31 empty] | Medium alarm breach | 10.75 | CML-9 | CML: Pipe Length | 6 | 2017-03-25 | 2016-07-02 | 2016-07-03 07:00 | 8.55 | 2.5427 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 10.4 | 9 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.85 | 0.10899 | 10.9 | 10.9 | 10.8 | 10.4 | 0.23805
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-3 | 300-PL-13L9004-BC11X-P-50 CML-3 | yes | FPSO 2016 | Pipe Wall Thickness | 24442 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 |  |  | John Wilson | 2017-03-23 15:46 | [31 empty] | Medium alarm breach | 10.625 | CML-3 | CML: Pipe Length | 6 | 2017-03-25 | 2016-07-02 | 2016-07-03 07:00 | 8.55 | 2.5427 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 10.4 | 3 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.85 | -0.32697 | 10.8 | 10.4 | 10.8 | 10.5 | 0.20616
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24393 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 3.95 | CML-1 | CML: Elbow | 1 | 2034-10-31 | 2028-12-28 | 2016-06-07 07:00 | 1.71 | 0.10265 | A1: Outside Quadrant |  | 2.91 | 1.71 | 2.31 | 3.6 | 12 O'Clock | 50 | 3.91 | 50-FG-45056-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.89 |  | 3.6 | 4.1 | 4.2 | 3.9 | 0.26458
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-2 | 300-PL-13L9004-BC11X-P-50 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24386 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 3.75 | CML-2 | CML: Elbow | 1 | 2034-10-31 | 2028-12-28 | 2016-06-07 07:00 | 1.71 | 0.10265 | A1: Outside Quadrant |  | 2.91 | 1.71 | 2.31 | 3.6 | 6 O'Clock | 50 | 3.91 | 50-FG-45055-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.89 |  | 3.6 | 3.6 | 3.6 | 4.2 | 0.3
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-13 | 300-PL-13L9004-BC11X-P-50 CML-13 | yes | FPSO 2014 | Pipe Wall Thickness | 21199 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 6.375 | CML-13 | CML: Elbow | 3 | 2016-08-15 | 2017-03-28 | 2014-05-30 09:30 | 3.61 | 0.85375 | A3: Inside Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.5 | 6 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.89 | 0.28327 | 6.4 | 6.6 | 5.5 | 7 | 0.63443
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-3 | 300-PL-13L9004-BC11X-P-50 CML-3 | yes | FPSO 2016 | Pipe Wall Thickness | 24438 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | Check Corrosion Rate of 0.353mm/ yr | [35 empty] | 4.875 | CML-3 | CML: Elbow | 3 | 2021-11-21 | 2022-11-16 | 2016-07-03 07:00 | 2.5 | 0.35261 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.4 | 12 O'Clock | 80 | 5.49 | 80-FL-43171-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 0.086288 | 4.4 | 5 | 5 | 5.1 | 0.32016
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-12 | 300-PL-13L9004-BC11X-P-50 CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 23601 | Re-check of line as requested by ops supervisor, additional CML added due to corroded area | 2015-09-15 15:30 | 2015-09-15 16:30 | [35 empty] | Low alarm breach | 5.325 | CML-12 |  | 3 | 2016-09-15 | 2015-11-08 | 2015-09-15 15:30 | 2.5 | 1.8934 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 4.4 | 3 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 7.1 | 4.4 | 5 | 4.8 | 1.2093
PF03 | Montara_Topside | No | Produced Water (44) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-3 | 300-PL-13L9004-BC11X-P-50 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 23238 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.725 | CML-3 | CML: Elbow | 3 | 2018-08-05 | 2019-02-24 | 2015-05-11 07:00 | 2.5 | 0.58664 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 0.53415 | 5 | 4.8 | 4.4 | 4.7 | 0.25
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-6 | 300-PL-13L9004-BC11X-P-50 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 6491 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.95 | CML-6 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A3: Inside Quadrant |  | 11.48 |  |  | 18.9 | 6 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 20.3 | 19.6 | 18.9 | 21 | 0.9037
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-5 | 300-PL-13L9004-BC11X-P-50 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6490 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.05 | CML-5 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A1: Outside Quadrant |  | 11.48 |  |  | 18.5 | 12 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 18.5 | 19.5 | 19.6 | 18.6 | 0.58023
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-6 | 300-PL-13L9004-BC11X-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23131 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | Check Corrosion Rate of 0.587mm/ yr | [35 empty] | 4.95 | CML-6 | CML: Pipe Length | 3 | 2018-08-02 | 2019-02-21 | 2015-05-10 07:00 | 2.5 | 0.58747 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 0.80762 | 5.8 | 4.7 | 4.4 | 4.9 | 0.60277
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-7 | 300-PL-13L9004-BC11X-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22941 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | Check Corrosion Rate of 0.594mm/ yr | [35 empty] | 4.925 | CML-7 | CML: Elbow | 3 | 2018-07-12 | 2019-01-28 | 2015-05-02 07:00 | 2.5 | 0.59418 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 0.45739 | 4.7 | 5.4 | 4.4 | 5.2 | 0.45735
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-4 | 300-PL-13L9004-BC11X-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6489 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.125 | CML-4 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A2: Right Quadrant |  | 11.48 |  |  | 18.7 | 9 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19.8 | 18.7 | 19.3 | 18.7 | 0.53151
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-3 | 300-PL-13L9004-BC11X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6488 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.075 | CML-3 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A1: Outside Quadrant |  | 11.48 |  |  | 18.3 | 12 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 18.3 | 19.7 | 19.7 | 18.6 | 0.73201
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-2 | 300-PL-13L9004-BC11X-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22547 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 4.675 | CML-2 | CML: Reducing Tee | 0.5 | 2021-01-05 | 2021-09-13 | 2015-04-23 07:00 | 2.7 | 0 | A1: Outside Quadrant |  | 3 | 2.7 | 2.6313 | 4.6 | 3 O'Clock | 150 | 3.5 | 0600-WF-71L9000-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.6 | 4.6 | 4.7 | 4.8 | 0.095743
PF03 | Montara_Topside | No | Produced Water (44) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-10 | 300-PL-13L9004-BC11X-P-50 CML-10 | no | FPSO 2015 | Pipe Wall Thickness | 23778 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.2 | CML-10 | CML: Elbow | 3 | 2018-07-27 | 2019-03-03 | 2015-04-18 07:00 | 2.5 | 0.57971 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.4 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 1.3396 | 4.4 | 5.2 | 5.8 | 5.4 | 0.58878
PF03 | Montara_Topside | No | Produced Water (44) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-3 | 300-PL-13L9004-BC11X-P-50 CML-3 | no | FPSO 2015 | Pipe Wall Thickness | 23771 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.35 | CML-3 | CML: Elbow | 3 | 2018-07-27 | 2019-03-03 | 2015-04-18 07:00 | 2.5 | 0.57971 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.4 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 1.4614 | 4.4 | 5.4 | 5.3 | 6.3 | 0.77675
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-44 | 300-PL-13L9004-BC11X-P-50 CML-44 | yes | FPSO 2015 | Pipe Wall Thickness | 9131 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.775 | CML-44 | CML: type TBC | 3 | 2018-01-30 | 2018-08-01 | 2015-03-02 07:00 | 2.5 | 0.65088 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.5 | 5.2 | 4.4 | 5 | 0.38622
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-42 | 300-PL-13L9004-BC11X-P-50 CML-42 | yes | FPSO 2015 | Pipe Wall Thickness | 9129 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.55 | CML-42 | CML: type TBC | 3 | 2018-01-30 | 2018-08-01 | 2015-03-02 07:00 | 2.5 | 0.65088 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.8 | 4.5 | 4.4 | 4.5 | 0.17321
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML1 | 300-PL-13L9004-BC11X-P-50 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 6919 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 4.55 | CML1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4.4 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.6 | 4.5 | 4.7 | 4.4 | 0.1291
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-6 | 300-PL-13L9004-BC11X-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6397 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 4.875 | CML-6 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-21 07:00 | 2.8 | 0 | A3: Inside Quadrant |  | 3.5 | 2.8 | 3.15 | 4.7 | 6 O'Clock | 200 | 4 | 200-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5 | 5 | 4.7 | 4.8 | 0.15
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-2 | 300-PL-13L9004-BC11X-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6393 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 4.9 | CML-2 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-21 07:00 | 2.8 | 0 | A1: Outside Quadrant |  | 3.5 | 2.8 | 3.15 | 4.7 | 12 O'Clock | 200 | 4 | 200-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.7 | 4.8 | 5 | 5.1 | 0.18257
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6392 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 4.825 | CML-1 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-21 07:00 | 2.8 | 0 | A1: Outside Quadrant |  | 3.5 | 2.8 | 3.15 | 4.7 | 6 O'Clock | 200 | 4 | 200-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.7 | 4.8 | 4.7 | 5.1 | 0.1893
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-5 | 300-PL-13L9004-BC11X-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6214 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 4.65 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.4 | 12 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 4.7 | 4.8 | 4.7 | 0.17321
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-21 | 300-PL-13L9004-BC11X-P-50 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6096 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 4.525 | CML-21 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 4.4 | 3 O'Clock | 50 | 2.5 | 50-WF-71351-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.6 | 4.4 | 4.6 | 4.5 | 0.095743
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-5 | 300-PL-13L9004-BC11X-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5383 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.725 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4.4 | 12 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 4.9 | 4.9 | 4.7 | 0.23629
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-4 | 300-PL-13L9004-BC11X-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5382 | Pipe Schedule Estimated. Rope Access | 2015-03-14 07:00 | 2015-03-14 15:00 | [36 empty] | 4.65 | CML-4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4.4 | 9 O'Clock | 50 | 2.5 | 50-WF-71316-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.6 | 5 | 4.6 | 4.4 | 0.25166
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-3 | 300-PL-13L9004-BC11X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5189 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 5.225 | CML-3 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-12 07:00 | 2.8 | 0 | A1: Outside Quadrant |  | 3.5 | 2.8 | 3.15 | 4.7 | 12 O'Clock | 200 | 4 | 200-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.7 | 5.1 | 5.7 | 5.4 | 0.4272
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-5 | 300-PL-13L9004-BC11X-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5191 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 4.875 | CML-5 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-12 07:00 | 2.8 | 0 | A2: Right Quadrant |  | 3.5 | 2.8 | 3.15 | 4.7 | 3 O'Clock | 200 | 4 | 200-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.9 | 4.7 | 4.8 | 5.1 | 0.17078
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-2 | 300-PL-13L9004-BC11X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6487 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.2 | CML-2 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A4: Left Quadrant |  | 11.48 |  |  | 18.5 | 9 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19.3 | 19.4 | 19.6 | 18.5 | 0.48305
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-37 | 300-PL-13L9004-BC11X-P-50 CML-37 | yes | FPSO 2015 | Pipe Wall Thickness | 9124 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.725 | CML-37 | CML: type TBC | 3 | 2018-01-30 | 2018-08-01 | 2015-03-02 07:00 | 2.5 | 0.65088 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 4.8 | 5 | 4.7 | 0.25
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-30 | 300-PL-13L9004-BC11X-P-50 CML-30 | yes | FPSO 2015 | Pipe Wall Thickness | 9117 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.7 | CML-30 | CML: type TBC | 3 | 2018-01-30 | 2018-08-01 | 2015-03-02 07:00 | 2.5 | 0.65088 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 3 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5.2 | 4.4 | 4.6 | 4.6 | 0.34641
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-14 | 300-PL-13L9004-BC11X-P-50 CML-14 | yes | FPSO 2014 | Pipe Wall Thickness | 21003 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.575 | CML-14 | CML: Elbow | 3 | 2016-01-10 | 2016-04-21 | 2014-05-24 10:30 | 2.5 | 1.1641 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 5.6 | 6 | 6.3 | 0.83417
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 20990 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.175 | CML-1 | CML: Elbow | 3 | 2016-01-10 | 2016-04-21 | 2014-05-24 10:30 | 2.5 | 1.1641 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 5.4 | 5.6 | 5.3 | 0.53151
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 21051 | Rope Access | 2014-05-22 13:00 | 2014-05-22 14:00 | [36 empty] | 5.1 | CML-1 | CML: Elbow | 3 | 2016-02-01 | 2016-05-24 | 2014-05-22 13:00 | 2.5 | 1.119 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.4 | 12 O'Clock | 80 | 5.49 | 80-DH-56128-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 4.9 | 5.3 | 5.8 | 0.59442
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-3 | 300-PL-13L9004-BC11X-P-50 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 20986 | Rope Access | 2014-05-17 13:00 | 2014-05-17 15:00 | [36 empty] | 5.125 | CML-3 | CML: type TBC | 3 | 2016-01-18 | 2016-05-09 | 2014-05-17 13:00 | 2.5 | 1.135 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.4 | 9 O'Clock | 80 | 5.49 | 80-DH-56092-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.8 | 5.4 | 5.9 | 4.4 | 0.66018
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-2 | 300-PL-13L9004-BC11X-P-50 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 21065 | Rope Access | 2014-05-15 11:00 | 2014-05-15 12:00 | [36 empty] | 4.875 | CML-2 | CML: type TBC | 3 | 2015-12-17 | 2016-03-25 | 2014-05-15 11:00 | 2.5 | 1.1941 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 3 O'Clock | 50 | 5.54 | 50-DH-56139-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5 | 4.4 | 4.6 | 5.5 | 0.48563
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 3369 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 4.75 | CML-1 | CML: type TBC | 3 | 2015-06-17 | 2015-07-11 | 2014-05-10 09:30 | 2.5 | 1.7219 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.4 | 9 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5.1 | 4.9 | 4.6 | 4.4 | 0.31091
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-4 | 300-PL-13L9004-BC11X-P-50 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 3364 | Rope Access | 2014-05-10 07:00 | 2014-05-10 08:00 | [36 empty] | 5.3 | CML-4 | CML: type TBC | 3 | 2015-12-03 | 2016-03-10 | 2014-05-10 07:00 | 2.5 | 1.2121 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5.8 | 5.4 | 4.4 | 5.6 | 0.62183
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-5 | 300-PL-13L9004-BC11X-P-50 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 3282 | Rope Access | 2014-05-09 14:00 | 2014-05-09 15:00 | [36 empty] | 5.175 | CML-5 | CML: type TBC | 3 | 2015-12-01 | 2016-03-08 | 2014-05-09 14:00 | 2.5 | 1.2146 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56066-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5 | 5.9 | 4.4 | 5.4 | 0.63443
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-4 | 300-PL-13L9004-BC11X-P-50 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 1837 | Rope Access | 2014-05-06 09:30 | 2014-05-06 10:30 | [36 empty] | 5.05 | CML-4 | CML: type TBC | 3 | 2015-11-23 | 2016-02-28 | 2014-05-06 09:30 | 2.5 | 1.226 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.7 | 5.7 | 4.4 | 5.4 | 0.60277
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-4 | 300-PL-13L9004-BC11X-P-50 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 22317 | Rope Access | 2014-05-06 09:30 | 2014-05-06 10:30 | [36 empty] | 5.05 | CML-4 | CML: type TBC | 3 | 2015-11-23 | 2016-02-28 | 2014-05-06 09:30 | 2.5 | 1.226 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.7 | 5.7 | 4.4 | 5.4 | 0.60277
PF03 | Montara_Topside | No | Compressed Air (63) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 9032 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | Check Corrosion Rate of 0.652mm/ yr | [35 empty] | 4.575 | CML-1 | CML: type TBC | 3 | 2018-01-28 | 2018-07-29 | 2015-03-01 07:00 | 2.5 | 0.6519 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 3 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 4.4 | 5 | 4.5 | 0.28723
PF03 | Montara_Topside | No | Steam (55) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8859 |  | 2015-02-24 13:00 | 2015-02-24 14:00 | [36 empty] | 5.425 | CML-1 | CML: type TBC | 3 | 2018-01-15 | 2018-07-15 | 2015-02-24 13:00 | 2.5 | 0.65678 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-SL-55006-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 6.2 | 5.8 | 4.4 | 5.3 | 0.77621
PF03 | Montara_Topside | No | Steam (55) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-5 | 300-PL-13L9004-BC11X-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8857 |  | 2015-02-24 11:00 | 2015-02-24 12:00 | [36 empty] | 4.725 | CML-5 | CML: type TBC | 3 | 2018-01-15 | 2018-07-15 | 2015-02-24 11:00 | 2.5 | 0.65687 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 3 O'Clock | 50 | 5.54 | 50-SL-55003-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.9 | 4.4 | 5 | 4.6 | 0.27538
PF03 | Montara_Topside | No | Steam (55) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-3 | 300-PL-13L9004-BC11X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8855 |  | 2015-02-24 11:00 | 2015-02-24 12:00 | [36 empty] | 4.825 | CML-3 | CML: type TBC | 3 | 2018-01-15 | 2018-07-15 | 2015-02-24 11:00 | 2.5 | 0.65687 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-SL-55003-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5 | 4.9 | 5 | 4.4 | 0.28723
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 | High Priority | FPSO 2013 | Pipe Wall Thickness | 10701 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 5.7 | CML-1 | CML: type TBC | 1 | 2015-02-14 | 2014-08-09 | 2013-11-07 | 3.8 | 1.4921 | A1: Outside Quadrant |  | 5.35 | 3.8 | 4.575 | 5.7 | 9 O'Clock | 300 | 6.35 | 300-PG-23038-03D01 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5.7 | 5.7 | 5.7 | 5.7 | 0
PF03 | Montara_Topside | No | Diesel Oil (62) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8054 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 4.975 | CML-1 | CML: type TBC | 3 | 2017-10-16 | 2018-04-05 | 2015-01-21 07:30 | 2.5 | 0.6943 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-DO-62005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5 | 5 | 5.5 | 4.4 | 0.45
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-4 | 300-PL-13L9004-BC11X-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7862 |  | 2015-01-14 08:00 | 2015-01-14 09:00 | [36 empty] | 4.75 | CML-4 | CML: Elbow | 3 | 2017-09-27 | 2018-03-16 | 2015-01-14 08:00 | 2.5 | 0.70248 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 15 | 5.54 | 50-CG-38009-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.7 | 5.2 | 4.4 | 4.7 | 0.33166
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-11 | 300-PL-13L9004-BC11X-P-50 CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 7834 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:38 | [32 empty] | 4.75 | CML-11 | CML: Elbow | 3 | 2017-09-25 | 2018-03-13 | 2015-01-13 13:00 | 2.5 | 0.70342 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.6 | 5 | 5 | 4.4 | 0.3
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-8 | 300-PL-13L9004-BC11X-P-50 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7721 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in a year (Jan. 2016) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.708mm/ yr |  | Administrator | 2015-09-08 09:29 | [32 empty] | 4.925 | CML-8 | CML: Elbow | 3 | 2017-09-14 | 2018-03-01 | 2015-01-09 13:00 | 2.5 | 0.70821 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 1.8935 | 5 | 5.2 | 5.1 | 4.4 | 0.3594
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9004-BC11X-P-50 |  | 300-PL-13L9004-BC11X-P-50 | yes | FPSO 2014 | Pipe Wall Thickness | 22104 | Rope access | 2014-06-02 09:30 | 2014-06-02 11:00 | [36 empty] | 4.825 | 50-CG-38302-01C02-P | Piping | 3 | 2016-02-03 |  | 2014-06-02 09:30 |  | 1.1357 | A3: Inside Quadrant |  |  | 2.5 |  | 4.4 | 6 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 4.4 | 5.1 | 4.9 | 4.4 | 4.9 | 0.29861
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9004-BC11X-P-50 |  | 300-PL-13L9004-BC11X-P-50 | yes | FPSO 2014 | Pipe Wall Thickness | 22090 | Rope access | 2014-06-02 07:00 | 2014-06-02 08:00 | [36 empty] | 4.9 | 50-CG-38301-01C02-P | Piping | 3 | 2016-02-02 |  | 2014-06-02 07:00 |  | 1.136 | A3: Inside Quadrant |  |  | 2.5 |  | 4.4 | 6 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 4.4 | 5 | 4.9 | 4.4 | 5.3 | 0.37417
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9004-BC11X-P-50 |  | 300-PL-13L9004-BC11X-P-50 | yes | FPSO 2014 | Pipe Wall Thickness | 22089 | Rope access | 2014-06-02 07:00 | 2014-06-02 08:00 | [36 empty] | 4.875 | 50-CG-38301-01C02-P | Piping | 3 | 2016-02-02 |  | 2014-06-02 07:00 |  | 1.136 | A2: Right Quadrant |  |  | 2.5 |  | 4.4 | 3 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 4.4 | 5.4 | 4.4 | 4.9 | 4.8 | 0.4113
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9004-BC11X-P-50 | CML-1 | 300-PL-13L9004-BC11X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6486 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 21.275 | CML-1 | CML: Reducer | 6 |  |  | 2014-07-23 07:30 |  | 0 | A1: Outside Quadrant |  | 11.48 |  |  | 21 | 9 O'Clock | 300 | 17.48 | 1200-PL-13L9004-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 21 | 21.1 | 22 | 21 | 0.48563
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-13 | 300-PL-13L9005-BC11X-P-50 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 6485 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 17.075 | CML-13 | CML: Pipe Length | 6 |  |  | 2014-07-23 07:30 |  | 0.37581 | A2: Right Quadrant |  | 11.48 |  |  | 16.9 | 9 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 17.6 | 16.9 | 16.9 | 16.9 | 0.35
PF03 | Montara_Topside | No | Chemical Injection (42) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-6 | 300-PL-13L9005-BC11X-P-50 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3093 | Rope Access | 2014-05-04 10:30 | 2014-05-04 11:00 | Check Corrosion Rate of 1.233mm/ yr | [34 empty] | Low alarm breach | 5.25 | CML-6 | CML: Elbow | 1 | 2015-11-17 | 2015-05-02 | 2014-05-04 10:30 | 2.5 | 1.2331 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.4 | 12 O'Clock | 50 | 5.54 | 50-CI-42046-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 5.4 | 6.5 | 4.7 | 0.93274
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5766 | Rope access | 2014-06-23 09:30 | 2014-06-23 11:00 | [36 empty] | 5.2 | CML-7 | CML: Elbow | 3 | 2024-02-17 | 2022-10-05 | 2014-06-23 09:30 | 0.54 | 0.46167 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5 | 12 O'Clock | 80 | 5.49 | 80-FH-43306-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.46 |  | 5 | 5.4 | 5.2 | 5.2 | 0.1633
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-5 | 300-PL-13L9005-BC11X-P-50 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 3048 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 4.725 | CML-5 | CML: type TBC | 3 | 2015-11-14 | 2016-02-19 | 2014-05-03 07:00 | 2.5 | 1.2373 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 3 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.8 | 4.4 | 4.8 | 4.9 | 0.22174
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1406 | Rope access | 2014-04-05 15:00 | 2014-04-05 16:00 | Check Corrosion Rate of 1.348mm/ yr | [35 empty] | 5.075 | CML-7 | CML: type TBC | 3 | 2015-09-02 | 2015-11-29 | 2014-04-05 15:00 | 2.5 | 1.3482 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5.9 | 5.4 | 4.6 | 4.4 | 0.6994
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2146 | Rope Access | 2014-03-29 13:00 | 2014-03-29 15:00 | Check Corrosion Rate of 1.38mm/ yr | [35 empty] | 4.875 | CML-1 | CML: Elbow | 3 | 2015-08-14 | 2015-11-08 | 2014-03-29 13:00 | 2.5 | 1.3799 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5.1 | 5.1 | 4.4 | 4.9 | 0.3304
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-4 | 300-PL-13L9005-BC11X-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5763 | Rope access | 2014-06-23 09:30 | 2014-06-23 11:00 | [36 empty] | 5.5 | CML-4 | CML: Pipe Length | 3 | 2071-10-01 | 2064-04-20 | 2014-06-23 09:30 | 0.54 | 0.0848 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43306-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 5.5 | 5.4 | 5.4 | 5.7 | 0.14142
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-10 | 300-PL-13L9005-BC11X-P-50 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10607 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 2.462mm/ yr | [35 empty] | 4.75 | CML-10 | CML: type TBC | 3 | 2014-08-25 | 2014-10-13 | 2013-11-17 | 2.5 | 2.4621 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 12 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 4.8 | 5 | 4.8 | 0.25166
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-15 | 300-PL-13L9005-BC11X-P-50 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10639 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.35 | CML-15 | CML: type TBC | 3 | 2014-11-17 | 2014-10-08 | 2013-11-18 | 2.5 | 2.4047 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 4.9 | 12 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.5 | 5.6 | 5.4 | 0.31091
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5762 | Rope access | 2014-06-23 09:30 | 2014-06-23 11:00 | [36 empty] | 7.025 | CML-3 | CML: Equal Tee | 3 | 2062-11-29 | 2056-08-05 | 2014-06-23 09:30 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 6.6 | 12 O'Clock | 80 | 5.49 | 80-FH-43306-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.06 |  | 6.6 | 7.7 | 6.8 | 7 | 0.47871
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-16 | 300-PL-13L9005-BC11X-P-50 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10640 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.35 | CML-16 | CML: type TBC | 3 | 2015-05-31 | 2015-04-07 | 2013-11-18 | 2.5 | 1.7606 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.76 | 5.2 | 9 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.4 | 5.3 | 5.2 | 0.1291
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-17 | 300-PL-13L9005-BC11X-P-50 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10641 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 8.1 | CML-17 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2013-11-18 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.76 | 7.7 | 3 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.4 | 7.7 | 8.4 | 7.9 | 0.3559
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-12 | 300-PL-13L9005-BC11X-P-50 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 6484 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.125 | CML-12 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A2: Right Quadrant |  | 11.48 |  |  | 18.7 | 3 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19 | 18.7 | 19.4 | 19.4 | 0.34034
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-11 | 300-PL-13L9005-BC11X-P-50 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 6483 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 18.725 | CML-11 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A3: Inside Quadrant |  | 11.48 |  |  | 18.4 | 6 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19.3 | 18.5 | 18.4 | 18.7 | 0.40311
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-10 | 300-PL-13L9005-BC11X-P-50 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 6482 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.15 | CML-10 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A3: Inside Quadrant |  | 11.48 |  |  | 18.4 | 6 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19.6 | 18.9 | 18.4 | 19.7 | 0.61373
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-21 | 300-PL-13L9005-BC11X-P-50 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10161 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 2.584mm/ yr | [35 empty] | 4.85 | CML-21 | CML: type TBC | 3 | 2014-08-04 | 2014-09-19 | 2013-11-09 | 2.5 | 2.5845 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 4.7 | 5.3 | 5 | 0.3873
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-8 | 300-PL-13L9005-BC11X-P-50 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 23544 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 |  |  | John Wilson | 2017-03-23 15:38 | [31 empty] | Low alarm breach | 12.375 | CML-8 | CML: Elbow | 6 | 2016-02-18 | 2015-08-13 | 2015-08-03 09:30 | 8.55 | 3.57 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 10.5 | 9 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.95 | 0.4253 | 13.4 | 13.4 | 12.2 | 10.5 | 1.372
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-6 | 300-PL-13L9005-BC11X-P-50 CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 5502 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [35 empty] | Low alarm breach | 12.15 | CML-6 | CML: Elbow | 6 | 2014-08-30 | 2014-06-04 | 2014-05-31 07:00 | 8.55 | 7.7751 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 10.5 | 3 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.95 |  | 13 | 10.5 | 11.9 | 13.2 | 1.2396
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-9 | 300-PL-13L9005-BC11X-P-50 CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 23545 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 | [35 empty] | Low alarm breach | 10.775 | CML-9 | CML: Pipe Length | 6 | 2016-02-18 | 2015-08-13 | 2015-08-03 09:30 | 8.55 | 3.57 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 10.5 | 3 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.95 | -0.25518 | 10.7 | 10.5 | 10.6 | 11.3 | 0.3594
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 5499 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [35 empty] | Low alarm breach | 10.75 | CML-3 | CML: Pipe Length | 6 | 2014-08-30 | 2014-06-04 | 2014-05-31 07:00 | 8.55 | 7.7751 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 10.5 | 3 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.95 |  | 10.7 | 10.5 | 11.1 | 10.7 | 0.25166
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 13058 |  | 2014-01-11 07:00 | 2014-01-11 09:00 | Measured thickness below alarm thickness | [34 empty] | Low alarm breach | 10.8 | CML-7 | CML: Pipe Length | 6 | 2014-03-08 | 2014-01-14 | 2014-01-11 07:00 | 8.55 | 12.6282 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 10.5 | 9 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.95 |  | 10.9 | 10.9 | 10.9 | 10.5 | 0.2
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-5 | 300-PL-13L9005-BC11X-P-50 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23541 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 | [35 empty] | Low alarm breach | 10.725 | CML-5 | CML: Pipe Length | 6 | 2016-02-18 | 2015-08-13 | 2015-08-03 09:30 | 8.55 | 3.57 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 10.5 | 9 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.95 | -0.25518 | 10.7 | 10.9 | 10.8 | 10.5 | 0.17078
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24394 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.075 | CML-2 | CML: Elbow | 1 | 2045-01-11 | 2036-05-29 | 2016-06-07 07:00 | 1.71 | 0.06954 | A1: Outside Quadrant |  | 2.91 | 1.71 | 2.31 | 3.7 | 12 O'Clock | 50 | 3.91 | 50-FG-45056-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.99 |  | 3.7 | 4.3 | 4.2 | 4.1 | 0.263
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24391 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.325 | CML-3 | CML: Equal Tee | 1 | 2045-01-11 | 2036-05-29 | 2016-06-07 07:00 | 1.71 | 0.06954 | A2: Right Quadrant |  | 2.91 | 1.71 | 2.31 | 3.7 | 3 O'Clock | 50 | 3.91 | 50-FG-45049-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.99 |  | 4.2 | 3.7 | 4.4 | 5 | 0.53774
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-13 | 300-PL-13L9005-BC11X-P-50 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 13183 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.4 | CML-13 | CML: Elbow | 3 | 2015-10-05 | 2016-03-18 | 2014-01-21 13:00 | 3.61 | 1.1672 | A3: Inside Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.6 | 6 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.99 |  | 6.2 | 6.6 | 5.6 | 7.2 | 0.6733
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-9 | 300-PL-13L9005-BC11X-P-50 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 6481 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 17.5 | CML-9 | CML: Pipe Length | 6 |  |  | 2014-07-23 07:30 |  | 0.05184 | A2: Right Quadrant |  | 11.48 |  |  | 17.4 | 3 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 17.5 | 17.4 | 17.6 | 17.5 | 0.08165
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-8 | 300-PL-13L9005-BC11X-P-50 CML-8 |  | FPSO 2016 | Pipe Wall Thickness | 24441 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | Check Corrosion Rate of 0.336mm/ yr | 37 | John Wilson | 2017-03-22 10:25 | Included at next inspection | [31 empty] | 4.875 | CML-8 | CML: Elbow | 3 | 2022-06-12 | 2023-06-01 | 2016-07-03 07:00 | 2.5 | 0.33644 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 0.4264 | 4.5 | 5.1 | 4.9 | 5 | 0.263
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 | yes | FPSO 2016 | Pipe Wall Thickness | 24408 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.8 | CML-2 | CML: Elbow | 3 | 2022-07-16 | 2022-07-21 | 2016-06-08 07:00 | 2.5 | 0.32752 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.495 | 4.5 | 12 O'Clock | 80 | 5.49 | 80-FG-45046-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.9 | 4.8 | 5 | 0.21602
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-8 | 300-PL-13L9005-BC11X-P-50 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 6480 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.725 | CML-8 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A3: Inside Quadrant |  | 11.48 |  |  | 18 | 6 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19.7 | 21.1 | 18 | 20.1 | 1.292
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 6479 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 18.925 | CML-7 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A1: Outside Quadrant |  | 11.48 |  |  | 18.3 | 12 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 18.3 | 19.1 | 19.7 | 18.6 | 0.61305
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-6 | 300-PL-13L9005-BC11X-P-50 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 6478 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.3 | CML-6 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A4: Left Quadrant |  | 11.48 |  |  | 18.4 | 9 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19.8 | 20 | 19 | 18.4 | 0.73937
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 | Yes | FPSO 2015 | Pipe Wall Thickness | 23639 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 4.675 | CML-7 | CML: Elbow | 3 | 2020-06-14 | 2021-03-17 | 2015-10-28 07:00 | 2.5 | 0.43171 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.9 | 4.5 | 4.6 | 4.7 | 0.17078
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-6 | 300-PL-13L9005-BC11X-P-50 CML-6 | Yes | FPSO 2015 | Pipe Wall Thickness | 23638 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 4.675 | CML-6 | CML: Elbow | 3 | 2020-06-14 | 2021-03-17 | 2015-10-28 07:00 | 2.5 | 0.43171 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.9 | 4.6 | 4.7 | 4.5 | 0.17078
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-16 | 300-PL-13L9005-BC11X-P-50 CML-16 | yes | FPSO 2016 | Pipe Wall Thickness | 24474 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Minimum WT reading has exceeded Low Alarm | 3 | John Wilson | 2017-03-24 11:17 | Recheck at next inspection. | [30 empty] | Low alarm breach | 6.5 | CML-16 | CML: Fitting | 3 | 2017-12-26 | 2016-10-18 | 2016-07-09 07:00 | 2.5 | 1.3644 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 4.5 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 0.60231 | 4.5 | 4.5 | 8.6 | 8.4 | 2.3108
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-11 | 300-PL-13L9005-BC11X-P-50 CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 23600 | Re-check of line as requested by ops supervisor, additional CML added due to corroded area | 2015-09-15 15:30 | 2015-09-15 16:30 | [35 empty] | Low alarm breach | 4.85 | CML-11 |  | 3 | 2016-10-14 | 2015-11-29 | 2015-09-15 15:30 | 2.5 | 1.8498 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 4.5 | 12 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.2 | 5.1 | 4.6 | 0.35119
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-5 | 300-PL-13L9005-BC11X-P-50 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6477 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.35 | CML-5 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A1: Outside Quadrant |  | 11.48 |  |  | 18.9 | 12 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 18.9 | 19.7 | 19.2 | 19.6 | 0.36968
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23132 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | Check Corrosion Rate of 0.536mm/ yr | [35 empty] | 5.3 | CML-7 | CML: Elbow | 3 | 2019-01-31 | 2019-09-10 | 2015-05-10 07:00 | 2.5 | 0.53594 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 0.35894 | 4.7 | 6.2 | 4.5 | 5.8 | 0.82865
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-5 | 300-PL-13L9005-BC11X-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23130 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | Check Corrosion Rate of 0.536mm/ yr | [35 empty] | 5.325 | CML-5 | CML: Equal Tee | 3 | 2019-01-31 | 2019-09-10 | 2015-05-10 07:00 | 2.5 | 0.53594 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 0.53841 | 4.5 | 4.8 | 6.5 | 5.5 | 0.88835
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23127 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | Check Corrosion Rate of 0.536mm/ yr | [35 empty] | 4.65 | CML-2 | CML: Elbow | 3 | 2019-01-31 | 2019-09-10 | 2015-05-10 07:00 | 2.5 | 0.53594 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 0.35894 | 4.8 | 4.6 | 4.7 | 4.5 | 0.1291
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23097 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.125 | CML-3 | CML: Elbow | 3 | 2019-04-01 | 2019-12-05 | 2015-05-07 07:00 | 2.5 | 0.51234 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 12 O'Clock | 80 | 5.49 | 80-FL-43171-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 1.1995 | 4.5 | 5.2 | 5.6 | 5.2 | 0.45735
PF03 | Montara_Topside | No | Produced Water (44) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22905 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.175 | CML-3 | CML: Elbow | 3 | 2019-03-17 | 2019-11-18 | 2015-05-02 07:00 | 2.5 | 0.516 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 1.4314 | 4.5 | 5.3 | 5.6 | 5.3 | 0.4717
PF03 | Montara_Topside | No | Produced Water (44) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-15 | 300-PL-13L9005-BC11X-P-50 CML-15 | no | FPSO 2015 | Pipe Wall Thickness | 23783 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.375 | CML-15 | CML: Elbow | 3 | 2019-02-02 | 2019-10-02 | 2015-04-18 07:00 | 2.5 | 0.52653 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 1.4614 | 4.5 | 5.6 | 6.4 | 5 | 0.81803
PF03 | Montara_Topside | No | Produced Water (44) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-6 | 300-PL-13L9005-BC11X-P-50 CML-6 | no | FPSO 2015 | Pipe Wall Thickness | 23774 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 5.525 | CML-6 | CML: Elbow | 3 | 2019-02-02 | 2019-10-02 | 2015-04-18 07:00 | 2.5 | 0.52653 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 1.705 | 4.5 | 5.6 | 6.3 | 5.7 | 0.75
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML6 | 300-PL-13L9005-BC11X-P-50 CML6 |  | FPSO 2015 | Pipe Wall Thickness | 7538 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 4.675 | CML6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.5 | 9 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5 | 4.7 | 4.5 | 0.23629
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-6 | 300-PL-13L9005-BC11X-P-50 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5992 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 4.775 | CML-6 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 4.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5 | 4.9 | 4.5 | 4.7 | 0.22174
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-4 | 300-PL-13L9005-BC11X-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5190 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 5.05 | CML-4 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-12 07:00 | 2.8 | 0 | A4: Left Quadrant |  | 3.5 | 2.8 | 3.15 | 4.8 | 9 O'Clock | 200 | 4 | 200-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5 | 5.1 | 5.3 | 4.8 | 0.20817
PF03 | Montara_Topside | No | Fire Water (71) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5193 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 5.325 | CML-7 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-12 07:00 | 2.8 | 0 | A1: Outside Quadrant |  | 3.5 | 2.8 | 3.15 | 4.8 | 12 O'Clock | 200 | 4 | 200-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.8 | 5.2 | 5.1 | 6.2 | 0.60759
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-38 | 300-PL-13L9005-BC11X-P-50 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 9125 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.05 | CML-38 | CML: type TBC | 3 | 2018-07-13 | 2019-01-30 | 2015-03-02 07:00 | 2.5 | 0.59378 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.1 | 4.5 | 5.6 | 5 | 0.45092
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-31 | 300-PL-13L9005-BC11X-P-50 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 9118 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.925 | CML-31 | CML: type TBC | 3 | 2018-07-13 | 2019-01-30 | 2015-03-02 07:00 | 2.5 | 0.59378 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.6 | 4.9 | 4.7 | 4.5 | 0.47871
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-4 | 300-PL-13L9005-BC11X-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 9091 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.675 | CML-4 | CML: type TBC | 3 | 2018-07-13 | 2019-01-30 | 2015-03-02 07:00 | 2.5 | 0.59378 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.6 | 4.9 | 4.5 | 4.7 | 0.17078
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5233 | Rope Access | 2014-05-20 13:00 | 2014-05-20 14:00 | [36 empty] | 5.025 | CML-2 | CML: Elbow | 3 | 2016-03-30 | 2016-07-19 | 2014-05-20 13:00 | 2.5 | 1.0737 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-DH-56115-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.2 | 5.1 | 5.3 | 4.5 | 0.3594
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5227 | Rope Access | 2014-05-20 11:00 | 2014-05-20 12:00 | [36 empty] | 4.9 | CML-2 | CML: Elbow | 3 | 2016-03-30 | 2016-07-19 | 2014-05-20 11:00 | 2.5 | 1.074 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-DH-56114-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.1 | 5.5 | 4.5 | 0.4899
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-4 | 300-PL-13L9005-BC11X-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5214 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 4.95 | CML-4 | CML: Elbow | 3 | 2016-03-30 | 2016-07-18 | 2014-05-20 09:30 | 2.5 | 1.0741 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.5 | 5.4 | 5.4 | 0.51962
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5213 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 4.925 | CML-3 | CML: Elbow | 3 | 2016-03-30 | 2016-07-18 | 2014-05-20 09:30 | 2.5 | 1.0741 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.5 | 4.5 | 5 | 4.7 | 0.43493
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21016 | Rope Access | 2014-05-19 13:00 | 2014-05-19 14:00 | [36 empty] | 4.9 | CML-3 | CML: type TBC | 3 | 2016-03-27 | 2016-07-16 | 2014-05-19 13:00 | 2.5 | 1.0768 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.6 | 5 | 4.5 | 5.5 | 0.45461
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20926 | Rope Access | 2014-05-18 08:00 | 2014-05-18 09:00 | [36 empty] | 5.075 | CML-1 | CML: type TBC | 3 | 2016-04-27 | 2016-08-28 | 2014-05-18 08:00 | 2.5 | 1.0285 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 12 O'Clock | 80 | 5.49 | 80-DH-56042-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.9 | 5.7 | 5.2 | 0.5058
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20935 | Rope Access | 2014-05-17 09:30 | 2014-05-17 11:00 | [36 empty] | 5.1 | CML-1 | CML: type TBC | 3 | 2016-04-24 | 2016-08-25 | 2014-05-17 09:30 | 2.5 | 1.0313 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 12 O'Clock | 80 | 5.49 | 80-DH-56046-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.7 | 5.3 | 4.9 | 0.5164
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-15 | 300-PL-13L9005-BC11X-P-50 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20974 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 5.075 | CML-15 | CML: type TBC | 3 | 2015-08-19 | 2015-09-15 | 2014-05-16 13:00 | 2.5 | 1.5872 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.5 | 12 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.6 | 5.4 | 5.8 | 0.62915
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20934 | Rope Access | 2014-05-16 11:00 | 2014-05-16 12:00 | [36 empty] | 4.75 | CML-2 | CML: type TBC | 3 | 2016-04-21 | 2016-08-22 | 2014-05-16 11:00 | 2.5 | 1.034 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 9 O'Clock | 80 | 5.49 | 80-DH-56045-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.8 | 4.8 | 4.9 | 4.5 | 0.17321
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3461 | Rope Access | 2014-05-13 09:30 | 2014-05-13 10:30 | [36 empty] | 4.975 | CML-1 | CML: type TBC | 3 | 2016-04-12 | 2016-08-11 | 2014-05-13 09:30 | 2.5 | 1.0432 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 3 O'Clock | 80 | 5.49 | 80-DH-56019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.4 | 4.5 | 5.3 | 4.7 | 0.44253
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-6 | 300-PL-13L9005-BC11X-P-50 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3414 | Rope Access | 2014-05-11 09:30 | 2014-05-11 11:00 | [36 empty] | 5.125 | CML-6 | CML: type TBC | 3 | 2016-03-03 | 2016-06-19 | 2014-05-11 09:30 | 2.5 | 1.1022 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56065-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.6 | 5.2 | 4.5 | 5.2 | 0.45735
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3402 | Rope Access | 2014-05-10 14:00 | 2014-05-10 15:00 | [36 empty] | 4.95 | CML-3 | CML: type TBC | 3 | 2016-03-01 | 2016-06-17 | 2014-05-10 14:00 | 2.5 | 1.1048 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.8 | 5.1 | 4.5 | 5.4 | 0.3873
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-14 | 300-PL-13L9005-BC11X-P-50 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 3382 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 4.65 | CML-14 | CML: type TBC | 3 | 2015-08-05 | 2015-08-31 | 2014-05-10 09:30 | 2.5 | 1.6156 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.5 | 9 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.9 | 4.5 | 4.7 | 4.5 | 0.19149
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-13 | 300-PL-13L9005-BC11X-P-50 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 3381 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 4.725 | CML-13 | CML: type TBC | 3 | 2015-08-05 | 2015-08-31 | 2014-05-10 09:30 | 2.5 | 1.6156 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.5 | 6 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.7 | 4.9 | 4.5 | 4.8 | 0.17078
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-27 | 300-PL-13L9005-BC11X-P-50 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 3243 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 4.925 | CML-27 | CML: type TBC | 3 | 2016-02-26 | 2016-06-12 | 2014-05-09 07:00 | 2.5 | 1.109 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5 | 5.2 | 4.5 | 5 | 0.29861
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1834 | Rope Access | 2014-05-06 09:30 | 2014-05-06 10:30 | [36 empty] | 4.825 | CML-1 | CML: type TBC | 3 | 2016-02-18 | 2016-06-03 | 2014-05-06 09:30 | 2.5 | 1.1185 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-DH-56011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.1 | 4.5 | 4.6 | 5.1 | 0.32016
PF03 | Montara_Topside | No | Open Drain (56) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22314 | Rope Access | 2014-05-06 09:30 | 2014-05-06 10:30 | [36 empty] | 4.825 | CML-1 | CML: type TBC | 3 | 2016-02-18 | 2016-06-03 | 2014-05-06 09:30 | 2.5 | 1.1185 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-DH-56011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.1 | 4.5 | 4.6 | 5.1 | 0.32016
PF03 | Montara_Topside | No | Steam (55) | Pipework | 300-PL-13L9005-BC11X-P-50 |  | 300-PL-13L9005-BC11X-P-50 |  | FPSO 2015 | Pipe Wall Thickness | 8990 | LAGGING REMOVAL REQUIRED | 2015-02-27 07:00 | 2015-02-27 09:00 | [36 empty] | 4.975 | 80-SC-55002-01C02-P | Piping | 3 | 2018-09-04 |  | 2015-02-27 07:00 |  | 0.5679 | A4: Left Quadrant |  |  | 2.5 |  | 4.5 | 9 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.1 | 5.2 | 5.1 | 4.5 | 0.32016
PF03 | Montara_Topside | No | Compressed Air (63) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-27 | 300-PL-13L9005-BC11X-P-50 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 8951 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.597mm/ yr | [35 empty] | 5.55 | CML-27 | CML: type TBC | 3 | 2018-07-02 | 2019-01-17 | 2015-02-26 09:00 | 2.5 | 0.59744 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 6.1 | 6.4 | 4.5 | 5.2 | 0.86603
PF03 | Montara_Topside | No | Compressed Air (63) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-15 | 300-PL-13L9005-BC11X-P-50 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8939 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.597mm/ yr | [35 empty] | 5.05 | CML-15 | CML: type TBC | 3 | 2018-07-02 | 2019-01-17 | 2015-02-26 09:00 | 2.5 | 0.59744 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.4 | 5.6 | 4.7 | 0.53229
PF03 | Montara_Topside | No | Steam (55) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-10 | 300-PL-13L9005-BC11X-P-50 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8840 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 4.775 | CML-10 | CML: type TBC | 3 | 2018-08-26 | 2019-04-06 | 2015-02-24 07:00 | 2.5 | 0.57059 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 9 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.8 | 5.3 | 4.5 | 4.5 | 0.37749
PF03 | Montara_Topside | No | Diesel Oil (62) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-4 | 300-PL-13L9005-BC11X-P-50 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8057 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.05 | CML-4 | CML: type TBC | 3 | 2018-03-18 | 2018-09-22 | 2015-01-21 07:30 | 2.5 | 0.63339 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-DO-62005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.4 | 5.3 | 5 | 4.5 | 0.40415
PF03 | Montara_Topside | No | Diesel Oil (62) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-5 | 300-PL-13L9005-BC11X-P-50 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8053 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.075 | CML-5 | CML: type TBC | 3 | 2018-03-18 | 2018-09-22 | 2015-01-21 07:30 | 2.5 | 0.63339 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-DO-62003-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5 | 5 | 5.8 | 0.53774
PF03 | Montara_Topside | No | Diesel Oil (62) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8051 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 4.9 | CML-3 | CML: type TBC | 3 | 2018-03-18 | 2018-09-22 | 2015-01-21 07:30 | 2.5 | 0.63339 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-DO-62003-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.7 | 5.1 | 5.3 | 4.5 | 0.36515
PF03 | Montara_Topside | No | Produced Water (44) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-11 | 300-PL-13L9005-BC11X-P-50 CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 7976 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:09 | [32 empty] | 5.075 | CML-11 | CML: Elbow | 3 | 2018-05-07 | 2018-12-03 | 2015-01-18 10:30 | 2.5 | 0.60585 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 12 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.1 | 5.4 | 5.3 | 0.40311
PF03 | Montara_Topside | No | Produced Water (44) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-9 | 300-PL-13L9005-BC11X-P-50 CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 7974 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:09 | [32 empty] | 4.675 | CML-9 | CML: Pipe Length | 3 | 2018-05-07 | 2018-12-03 | 2015-01-18 10:30 | 2.5 | 0.60585 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 12 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.7 | 4.8 | 4.7 | 0.12583
PF03 | Montara_Topside | No | Produced Water (44) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-5 | 300-PL-13L9005-BC11X-P-50 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 7970 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:08 | [32 empty] | 4.775 | CML-5 | CML: Fitting | 3 | 2018-05-07 | 2018-12-03 | 2015-01-18 10:30 | 2.5 | 0.60585 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.5 | 6 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.9 | 4.6 | 4.5 | 5.1 | 0.27538
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-25 | 300-PL-13L9005-BC11X-P-50 CML-25 | yes | FPSO 2015 | Pipe Wall Thickness | 7848 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:42 | [32 empty] | 5.05 | CML-25 | CML: Elbow | 3 | 2018-02-24 | 2018-08-28 | 2015-01-13 13:00 | 2.5 | 0.64171 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.4 | 5.1 | 5.2 | 4.5 | 0.3873
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-21 | 300-PL-13L9005-BC11X-P-50 CML-21 | yes | FPSO 2015 | Pipe Wall Thickness | 7844 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:41 | [32 empty] | 4.85 | CML-21 | CML: Elbow | 3 | 2018-02-24 | 2018-08-28 | 2015-01-13 13:00 | 2.5 | 0.64171 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5 | 4.8 | 5.1 | 4.5 | 0.26458
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-20 | 300-PL-13L9005-BC11X-P-50 CML-20 | yes | FPSO 2015 | Pipe Wall Thickness | 7843 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:41 | [32 empty] | 4.825 | CML-20 | CML: Elbow | 3 | 2018-02-24 | 2018-08-28 | 2015-01-13 13:00 | 2.5 | 0.64171 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5 | 5.2 | 4.5 | 4.6 | 0.3304
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-16 | 300-PL-13L9005-BC11X-P-50 CML-16 | yes | FPSO 2015 | Pipe Wall Thickness | 7839 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:39 | [32 empty] | 4.65 | CML-16 | CML: Elbow | 3 | 2018-02-24 | 2018-08-28 | 2015-01-13 13:00 | 2.5 | 0.64171 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.6 | 4.7 | 4.8 | 4.5 | 0.1291
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-8 | 300-PL-13L9005-BC11X-P-50 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 7831 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:02 | [32 empty] | 5.1 | CML-8 | CML: Elbow | 3 | 2018-02-24 | 2018-08-28 | 2015-01-13 13:00 | 2.5 | 0.64171 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.2 | 5.3 | 5.4 | 4.5 | 0.40825
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 7737 | Line is FFS despite the High CR on CML-1 to 6. Current RBI frequency is 48m. Action: Inspect in 24m. RBI to be updated. Action: RBI frequency to stay at 48m. | 2015-01-10 08:00 | 2015-01-10 10:00 |  |  | Administrator | 2015-09-21 14:29 | [32 empty] | 4.925 | CML-2 | CML: Elbow | 3 | 2018-02-14 | 2018-08-18 | 2015-01-10 08:00 | 2.5 | 0.64521 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45503-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.2 | 5 | 5 | 0.29861
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7714 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.646mm/ yr |  | Administrator | 2015-09-08 09:31 | [32 empty] | 4.9 | CML-1 | CML: Elbow | 3 | 2018-02-12 | 2018-08-15 | 2015-01-09 13:00 | 2.5 | 0.64608 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 1.5148 | 5 | 5.3 | 4.8 | 4.5 | 0.33665
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-9 | 300-PL-13L9005-BC11X-P-50 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7678 | New Isometric drawing. Line is FFS. Action: to recheck in two year(Jan. 2017) to confirm CR. Only CML’s 6 to 10 which are showing high CR | 2015-01-08 09:30 | 2015-01-08 12:00 | Check Corrosion Rate of 0.647mm/ yr |  | Administrator | 2015-09-08 12:37 | [32 empty] | 4.8 | CML-9 | CML: Elbow | 3 | 2018-02-09 | 2018-08-12 | 2015-01-08 09:30 | 2.5 | 0.64734 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.1 | 4.8 | 4.8 | 0.24495
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-10 | 300-PL-13L9005-BC11X-P-50 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7679 | New Isometric drawing. Line is FFS. Action: to recheck in two year(Jan. 2017) to confirm CR. Only CML’s 6 to 10 which are showing high CR | 2015-01-08 09:30 | 2015-01-08 12:00 | Check Corrosion Rate of 0.647mm/ yr |  | Administrator | 2015-09-08 12:37 | [32 empty] | 4.775 | CML-10 | CML: Elbow | 3 | 2018-02-09 | 2018-08-12 | 2015-01-08 09:30 | 2.5 | 0.64734 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5 | 4.6 | 5 | 0.263
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-4 | 300-PL-13L9005-BC11X-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6476 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 17.6 | CML-4 | CML: Pipe Length | 6 |  |  | 2014-07-23 07:30 |  | 0 | A3: Inside Quadrant |  | 11.48 |  |  | 17.5 | 6 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 17.6 | 17.7 | 17.5 | 17.6 | 0.08165
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6475 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 18.975 | CML-3 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A4: Left Quadrant |  | 11.48 |  |  | 18.2 | 9 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 18.8 | 19.1 | 19.8 | 18.2 | 0.66521
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9005-BC11X-P-50 |  | 300-PL-13L9005-BC11X-P-50 | yes | FPSO 2014 | Pipe Wall Thickness | 22103 | Rope access | 2014-06-02 09:30 | 2014-06-02 11:00 | [36 empty] | 4.875 | 50-CG-38302-01C02-P | Piping | 3 | 2016-05-07 |  | 2014-06-02 09:30 |  | 1.036 | A2: Right Quadrant |  |  | 2.5 |  | 4.5 | 3 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 4.5 | 5 | 4.5 | 4.8 | 5.2 | 0.29861
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9005-BC11X-P-50 |  | 300-PL-13L9005-BC11X-P-50 | yes | FPSO 2014 | Pipe Wall Thickness | 22102 | Rope access | 2014-06-02 09:30 | 2014-06-02 11:00 | [36 empty] | 4.875 | 50-CG-38302-01C02-P | Piping | 3 | 2016-05-07 |  | 2014-06-02 09:30 |  | 1.036 | A4: Left Quadrant |  |  | 2.5 |  | 4.5 | 9 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 4.5 | 5.2 | 4.8 | 5 | 4.5 | 0.29861
PF03 | Montara_Topside | No | Chemical Injection (42) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3089 | Rope Access | 2014-05-04 10:30 | 2014-05-04 11:00 | Check Corrosion Rate of 1.125mm/ yr | [34 empty] | Low alarm breach | 4.75 | CML-2 | CML: Elbow | 1 | 2016-02-12 | 2015-07-08 | 2014-05-04 10:30 | 2.5 | 1.1249 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-CI-42046-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.1 | 4.8 | 4.6 | 0.26458
PF03 | Montara_Topside | No | Main Power (80) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-5 | 300-PL-13L9005-BC11X-P-50 CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 3131 | Rope Access | 2014-05-02 10:30 | 2014-05-02 11:30 | [36 empty] | 5.025 | CML-5 | CML: type TBC | 3 | 2016-02-06 | 2016-05-21 | 2014-05-02 10:30 | 2.5 | 1.1317 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-VA-80005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.1 | 4.5 | 5.4 | 5.1 | 0.37749
PF03 | Montara_Topside | No | Main Power (80) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 3129 | Rope Access | 2014-05-02 10:30 | 2014-05-02 11:30 | [36 empty] | 4.8 | CML-3 | CML: type TBC | 3 | 2016-02-06 | 2016-05-21 | 2014-05-02 10:30 | 2.5 | 1.1317 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-VA-80005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.9 | 5.2 | 4.6 | 4.5 | 0.31623
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-29 | 300-PL-13L9005-BC11X-P-50 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 2471 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 1.298mm/ yr | [35 empty] | 5.075 | CML-29 | CML: type TBC | 3 | 2015-10-03 | 2016-01-03 | 2014-03-20 09:30 | 2.5 | 1.2982 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.2 | 5.3 | 4.5 | 5.3 | 0.38622
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-11 | 300-PL-13L9005-BC11X-P-50 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2430 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 1.898mm/ yr | [35 empty] | 5.05 | CML-11 | CML: type TBC | 3 | 2015-04-08 | 2015-05-01 | 2014-03-20 07:00 | 2.5 | 1.8981 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.5 | 12 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.2 | 5.1 | 5.4 | 0.3873
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2346 | Rope Access | 2014-03-17 11:30 | 2014-03-17 12:00 | [36 empty] | 5.8 | CML-2 | CML: type TBC | 3 | 2039-09-30 | 2042-10-23 | 2014-03-17 11:30 | 2.5 | 0.11348 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FH-43179-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 6 | 5.8 | 5.4 | 0.28284
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10626 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.5 | CML-2 | CML: type TBC | 3 | 2015-05-31 | 2015-04-07 | 2013-11-18 | 2.5 | 1.7606 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.76 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.2 | 5.7 | 5.4 | 0.24495
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-3 | 300-PL-13L9005-BC11X-P-50 CML-3 | yes | FPSO 2013 | Pipe Wall Thickness | 10627 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 4.8 | CML-3 | CML: type TBC | 3 | 2014-07-27 | 2014-06-26 | 2013-11-18 | 2.5 | 3.0488 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 4.6 | 6 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.8 | 5.1 | 4.6 | 4.7 | 0.21602
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-4 | 300-PL-13L9005-BC11X-P-50 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2348 | Rope Access | 2014-03-17 11:30 | 2014-03-17 12:00 | [36 empty] | 6.15 | CML-4 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-17 11:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 3 O'Clock | 80 | 5.49 | 80-FH-43179-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 5.9 | 6.5 | 6.2 | 0.26458
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-20 | 300-PL-13L9005-BC11X-P-50 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10617 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 2.246mm/ yr | [35 empty] | 5.05 | CML-20 | CML: type TBC | 3 | 2014-10-08 | 2014-11-30 | 2013-11-17 | 2.5 | 2.2462 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.5 | 5.2 | 4.5 | 5 | 0.42032
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-11 | 300-PL-13L9005-BC11X-P-50 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10608 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 2.246mm/ yr | [35 empty] | 4.75 | CML-11 | CML: type TBC | 3 | 2014-10-08 | 2014-11-30 | 2013-11-17 | 2.5 | 2.2462 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5 | 5 | 4.5 | 0.28868
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-4 | 300-PL-13L9005-BC11X-P-50 CML-4 | yes | FPSO 2013 | Pipe Wall Thickness | 10628 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.4 | CML-4 | CML: type TBC | 3 | 2014-10-04 | 2014-08-29 | 2013-11-18 | 2.5 | 2.6194 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 4.8 | 6 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.6 | 5.5 | 4.8 | 5.7 | 0.40825
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-5 | 300-PL-13L9005-BC11X-P-50 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10629 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.85 | CML-5 | CML: type TBC | 3 | 2020-11-11 | 2020-04-24 | 2013-11-18 | 2.5 | 0.47235 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6 | 5.8 | 0.1
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-6 | 300-PL-13L9005-BC11X-P-50 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10630 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.575 | CML-6 | CML: type TBC | 3 | 2016-01-22 | 2015-11-11 | 2013-11-18 | 2.5 | 1.3312 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.4 | 6 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.7 | 5.4 | 5.7 | 0.15
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2351 | Rope Access | 2014-03-17 11:30 | 2014-03-17 12:00 | [36 empty] | 6.1 | CML-7 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-17 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 3 O'Clock | 80 | 5.49 | 80-FH-43179-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.3 | 6.1 | 0.14142
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-6 | 300-PL-13L9005-BC11X-P-50 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2350 | Rope Access | 2014-03-17 11:30 | 2014-03-17 12:00 | [36 empty] | 6.25 | CML-6 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-17 11:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 9 O'Clock | 80 | 5.49 | 80-FH-43179-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6.5 | 6.2 | 6 | 0.20817
PF03 | Montara_Topside | No | Flare (43) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-5 | 300-PL-13L9005-BC11X-P-50 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2349 | Rope Access | 2014-03-17 11:30 | 2014-03-17 12:00 | [36 empty] | 6.125 | CML-5 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-17 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 12 O'Clock | 80 | 5.49 | 80-FH-43179-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.3 | 6.1 | 6.1 | 0.12583
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10631 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.575 | CML-7 | CML: type TBC | 3 | 2016-01-22 | 2015-11-11 | 2013-11-18 | 2.5 | 1.3312 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.4 | 6 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.7 | 5.4 | 5.7 | 0.15
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-8 | 300-PL-13L9005-BC11X-P-50 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10632 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.625 | CML-8 | CML: type TBC | 3 | 2016-01-22 | 2015-11-11 | 2013-11-18 | 2.5 | 1.3312 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.4 | 9 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 5.9 | 5.4 | 0.263
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-9 | 300-PL-13L9005-BC11X-P-50 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10633 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.225 | CML-9 | CML: type TBC | 3 | 2015-01-08 | 2014-11-26 | 2013-11-18 | 2.5 | 2.19 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.76 | 5 | 3 O'Clock | 100 | 6.02 | 100-FG-45017-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 5.3 | 5.3 | 0.15
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 | yes | FPSO 2013 | Pipe Wall Thickness | 10642 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 5.45 | CML-1 | CML: type TBC | 3 |  |  | 2013-11-18 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.2 | 6 O'Clock | 100 |  | 100-FG-45032-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.5 | 5.2 | 5.5 | 0.17321
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-20 | 300-PL-13L9005-BC11X-P-50 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10160 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 2.358mm/ yr | [35 empty] | 4.775 | CML-20 | CML: type TBC | 3 | 2014-09-14 | 2014-11-04 | 2013-11-09 | 2.5 | 2.3578 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.7 | 4.9 | 5 | 0.22174
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-11 | 300-PL-13L9005-BC11X-P-50 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10151 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 2.358mm/ yr | [35 empty] | 4.95 | CML-11 | CML: Reducer | 3 | 2014-09-14 | 2014-11-04 | 2013-11-09 | 2.5 | 2.3578 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.6 | 5.1 | 5.6 | 0.50662
PF03 | Montara_Topside | No | Cooling Medium (40) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10141 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 2.358mm/ yr | [35 empty] | 5.05 | CML-1 | CML: Reducer | 3 | 2014-09-14 | 2014-11-04 | 2013-11-09 | 2.5 | 2.3578 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.8 | 4.9 | 6 | 0.65574
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-4 | 300-PL-13L9005-BC11X-P-50 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 5500 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [35 empty] | Low alarm breach | 14.025 | CML-4 | CML: Elbow | 6 | 2014-09-05 | 2014-06-09 | 2014-05-31 07:00 | 8.55 | 7.6749 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 10.6 | 12 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.05 |  | 10.6 | 13.7 | 13.9 | 17.9 | 2.9926
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 23543 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 | [35 empty] | Low alarm breach | 11.075 | CML-7 | CML: Pipe Length | 6 | 2016-03-02 | 2015-08-23 | 2015-08-03 09:30 | 8.55 | 3.524 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 10.6 | 6 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.05 | -0.064136 | 11.6 | 11.2 | 10.6 | 10.9 | 0.4272
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-25 | 300-PL-13L9005-BC11X-P-50 CML-25 | yes | FPSO 2014 | Pipe Wall Thickness | 21200 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 6.375 | CML-25 | CML: Elbow | 3 | 2017-08-10 | 2018-06-01 | 2014-05-30 09:30 | 3.61 | 0.65287 | A1: Outside Quadrant |  | 3.35 | 3.61 | 3.0831 | 5.7 | 12 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.09 | 0.28327 | 5.7 | 6.3 | 6.8 | 6.7 | 0.49917
PF03 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 20593 | Rope Access | 2014-05-26 14:00 | 2014-05-26 15:00 | [36 empty] | 9.05 | CML-1 | CML: type TBC | 1 | 2031-09-18 | 2027-07-26 | 2014-05-26 14:00 | 6.91 | 0 | A1: Outside Quadrant |  | 7.74 | 6.91 | 7.325 | 9 | 6 O'Clock | 50 | 8.74 | 50-PG-23062-25S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.09 |  | 9 | 9 | 9 | 9.2 | 0.1
PF03 | Montara_Topside | No | Closed Drain (57) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-7 | 300-PL-13L9005-BC11X-P-50 CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24440 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | Check Corrosion Rate of 0.304mm/ yr | 37 | [34 empty] | 4.825 | CML-7 | CML: Elbow | 3 | 2023-05-28 | 2024-06-23 | 2016-07-03 07:00 | 2.5 | 0.30409 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0 | 4.8 | 4.9 | 4.6 | 5 | 0.17078
PF03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 | yes | FPSO 2016 | Pipe Wall Thickness | 24316 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.775 | CML-2 | CML: Elbow | 3 | 2023-02-14 | 2023-01-22 | 2016-06-01 07:00 | 2.5 | 0.31296 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FG-45042-03C02-E | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.7 | 5 | 4.8 | 4.6 | 0.17078
PF03 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 23665 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.1 | CML-1 | CML: Elbow | 3 | 2021-03-21 | 2022-01-21 | 2015-10-30 07:00 | 2.5 | 0.38931 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.4 | 4.6 | 5.1 | 5.3 | 0.3559
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-2 | 300-PL-13L9005-BC11X-P-50 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6474 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 19.4 | CML-2 | CML: Elbow | 6 |  |  | 2014-07-23 07:30 |  | 0 | A2: Right Quadrant |  | 11.48 |  |  | 18.4 | 3 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 19.7 | 18.4 | 19.9 | 19.6 | 0.67823
PF03 | Montara_Topside | No | Separation (20) | Pipework | 300-PL-13L9005-BC11X-P-50 | CML-1 | 300-PL-13L9005-BC11X-P-50 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6473 | Protective mesh removed/Rope Access | 2014-07-23 07:30 | 2014-07-23 15:00 | [36 empty] | 21.1 | CML-1 | CML: Reducer | 6 |  |  | 2014-07-23 07:30 |  | 0 | A1: Outside Quadrant |  | 11.48 |  |  | 21.1 | 9 O'Clock | 300 | 17.48 | 1200-PL-13L9005-BC11X-P-50 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 21.1 | 21.1 | 21.1 | 21.1 | 0
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-15 | 150-PG-23506-25C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2789 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 24.85 | CML-15 | CML: Elbow | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 23.1 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.22 |  | 24.7 | 23.1 | 24.4 | 27.2 | 1.7137
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-6 | 50-PW-44013-01X01 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10320 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.7 | CML-6 | CML: Elbow | 3 | 2014-07-03 | 2014-08-14 | 2013-11-10 | 2.5 | 2.7938 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 4.6 | 5.1 | 4.8 | 0.33665
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23018-09C03-A | CML-1 | 200-PG-23018-09C03-A CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 13062 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 19.675 | CML-1 | CML: type TBC | 6 | 2016-01-21 | 2015-06-29 | 2014-01-10 07:00 | 10.17 | 3.9558 | A2: Right Quadrant |  | 14.62 | 10.17 | 12.395 | 18.2 | 3 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.03 |  | 18.3 | 18.2 | 21.6 | 20.6 | 1.6958
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-37 | 300-PF-20003-03C03-P CML-37 | Yes | FPSO 2014 | Pipe Wall Thickness | 21775 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 15.525 | CML-37 | CML: Elbow | 6 | 2032-01-27 | 2028-09-19 | 2014-10-01 07:00 | 4.9 | 0.50186 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14.6 | 16.9 | 17 | 13.6 | 1.6958
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-13 | 150-PG-23506-25C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2787 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 24.1 | CML-13 | CML: Elbow | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 22.2 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.32 |  | 23.7 | 26.3 | 24.2 | 22.2 | 1.6951
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-19 | 250-PG-23015-06C03-A CML-19 | yes | FPSO 2014 | Pipe Wall Thickness | 13051 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 20.125 | CML-19 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 13:00 | 8.55 | 0 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 18.5 | 9 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.95 |  | 18.9 | 21.1 | 22 | 18.5 | 1.6939
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-11 | 200-PG-23505-09C02-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20656 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 18.175 | CML-11 | CML: Elbow | 3 | 2017-05-14 | 2016-10-20 | 2014-05-31 07:00 | 14.06 | 1.0621 | A3: Inside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 6 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | 0 | 18.6 | 17.9 | 17.2 | 19 | 0.7932
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23016-06C03-A | CML-10 | 250-PG-23016-06C03-A CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 13061 |  | 2014-01-11 07:00 | 2014-01-11 09:00 | Measured thickness below alarm thickness | [34 empty] | Low alarm breach | 13.35 | CML-10 | CML: Elbow | 6 | 2014-03-27 | 2014-01-29 | 2014-01-11 07:00 | 8.55 | 11.8145 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 11 | 6 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.45 |  | 15 | 13.5 | 11 | 13.9 | 1.6902
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-41 | 300-PF-20500-03C03-P CML-41 | yes | FPSO 2014 | Pipe Wall Thickness | 21661 | Reviewed on 27/11/14. FFS. Recheck on Sep. 15 | 2014-09-27 07:00 | 2014-09-27 15:00 |  |  | Nestor | 2014-11-27 17:40 | [32 empty] | 15.4 | CML-41 | CML: Elbow | 6 | 2025-01-01 | 2022-12-02 | 2014-09-27 07:00 | 4.9 | 0.8081 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 15 | 17 | 16.4 | 13.2 | 1.6892
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43127-01C02 | CML-2 | 150-FH-43127-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1795 | Rope access | 2014-04-28 10:30 | 2014-04-28 12:00 | [36 empty] | 8.55 | CML-2 | CML: Reducer | 3 | 2059-07-07 | 2055-11-27 | 2014-04-28 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43127-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 11 | 8.3 | 7.4 | 7.5 | 1.6823
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23029-25C02-P | CML-3 | 80-PG-23029-25C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20561 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [36 empty] | 18.95 | CML-3 | CML: Elbow | 3 | 2090-10-23 | 2076-08-20 | 2014-07-02 07:00 | 7.5 | 0 | A1: Outside Quadrant |  | 12.24 | 7.5 | 8.9175 | 17.4 | 12 O'Clock | 80 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 17.4 | 17.7 | 20.9 | 19.8 | 1.6823
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-4 | 50-PL-23042-09C03 CML-4 | yes | FPSO 2013 | Pipe Wall Thickness | 10069 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 12.075 | CML-4 | CML: type TBC | 6 | 2018-12-25 | 2018-02-23 | 2013-11-07 | 2.5 | 1.538 | A4: Left Quadrant |  | 5.07 | 2.5 | 3.785 | 10.4 | 9 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 14.4 | 11.6 | 11.9 | 10.4 | 1.68
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0600-WF-71L9000-AK11-00 | CML-7 | 0600-WF-71L9000-AK11-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22552 | Rope Access | 2015-04-23 07:00 | 2015-04-23 15:00 | [36 empty] | 4.875 | CML-7 | CML: Reducing Tee | 0.5 | 2021-01-05 | 2021-09-13 | 2015-04-23 07:00 | 2.7 | 0 | A2: Right Quadrant |  | 3 | 2.7 | 2.6313 | 4.8 | 3 O'Clock | 150 | 3.5 | 0600-WF-71L9000-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 4.8 | 4.9 | 4.9 | 0.05
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-6 | 200-PG-23006-09C02-PA CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 23839 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 19.125 | CML-6 | CML: Fitting | 3 | 2031-04-21 | 2025-05-09 | 2014-09-25 07:00 | 9.3 | 0.50053 | A4: Left Quadrant |  | 15.26 | 9.3 | 12.28 | 17.6 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 20.9 | 20.2 | 17.8 | 17.6 | 1.6721
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71308-01K01 | CML109 | 100-WF-71308-01K01 CML109 |  | FPSO 2015 | Pipe Wall Thickness | 7027 |  | 2015-04-06 07:00 | 2015-04-06 15:00 | [36 empty] | 4.85 | CML109 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4.6 | 9 O'Clock | 100 | 3 | 100-WF-71308-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.3 | 4.7 | 4.8 | 4.6 | 0.31091
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71345-01K01 | CML-99 | 150-WF-71345-01K01 CML-99 |  | FPSO 2015 | Pipe Wall Thickness | 6773 |  | 2015-04-04 07:00 | 2015-04-04 15:00 | [36 empty] | 4.675 | CML-99 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.6 | 9 O'Clock | 150 | 3 | 150-WF-71345-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 4.6 | 4.6 | 4.6 | 0.15
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-1 | 300-PF-20001-03C03-P CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 21139 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.418mm/ yr | 40 | Kirstie Albone | 2017-03-23 16:04 | [32 empty] | 15.7 | CML-1 | CML: Elbow | 6 | 2035-10-24 | 2031-10-14 | 2014-07-16 07:30 | 4.9 | 0.4181 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 17.1 | 17.1 | 14.8 | 13.8 | 1.6673
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 200-WF-71334-01K01 | CML-7 | 200-WF-71334-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6398 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 5.125 | CML-7 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-21 07:00 | 2.8 | 0 | A2: Right Quadrant |  | 3.5 | 2.8 | 3.15 | 4.9 | 3 O'Clock | 200 | 4 | 200-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.1 | 4.9 | 5.3 | 5.2 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 200-WF-71334-01K01 | CML-5 | 200-WF-71334-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6396 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 4.975 | CML-5 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-21 07:00 | 2.8 | 0 | A3: Inside Quadrant |  | 3.5 | 2.8 | 3.15 | 4.9 | 6 O'Clock | 200 | 4 | 200-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5 | 5 | 4.9 | 5 | 0.05
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-32 | 300-PF-20001-03C03-P CML-32 | yes | FPSO 2014 | Pipe Wall Thickness | 21170 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.418mm/ yr | 40 | Kirstie Albone | 2017-03-23 16:06 | [32 empty] | 15.525 | CML-32 | CML: Elbow | 6 | 2035-10-24 | 2031-10-14 | 2014-07-16 07:30 | 4.9 | 0.4181 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 3 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14.4 | 13.8 | 16.9 | 17 | 1.6641
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 200-WF-71306-01K01 | CML-2 | 200-WF-71306-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5188 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 5.3 | CML-2 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-12 07:00 | 2.8 | 0 | A1: Outside Quadrant |  | 3.5 | 2.8 | 3.15 | 4.9 | 12 O'Clock | 200 | 4 | 200-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 5.3 | 5.8 | 5.2 | 0.37417
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-7 | 250-PG-23004-06C03-A CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 13007 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.525 | CML-7 | CML: Elbow | 6 | 2019-08-20 | 2018-06-12 | 2014-01-11 15:00 | 8.55 | 1.5599 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.3 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.75 |  | 17.3 | 20.2 | 19.4 | 21.2 | 1.656
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-48 | 300-PF-20003-03C03-P CML-48 | Yes | FPSO 2014 | Pipe Wall Thickness | 21786 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 13.525 | CML-48 | CML: Elbow | 6 | 2021-07-16 | 2019-11-16 | 2014-10-01 07:00 | 4.1 | 1.2509 | A4: Left Quadrant |  | 8.27 | 4.1 | 6.185 | 12.6 | 9 O'Clock | 250 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 12.7 | 16 | 12.8 | 12.6 | 1.652
FL01 | Montara_Topside | Yes | Steam (55) | Pipework | 150-FL-43174-01C02 | CML-9 | 150-FL-43174-01C02 CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 8839 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 4.325 | CML-9 | CML: type TBC | 3 | 2015-11-24 | 2016-03-08 | 2015-02-24 07:00 | 2.5 | 1.2046 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 3.4 | 9 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 6.8 | 3.5 | 3.6 | 3.4 | 1.652
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20002-03C03-P | CML-5 | 300-PF-20002-03C03-P CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 6517 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:11 | [32 empty] | 18.55 | CML-5 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-24 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.6 | 3 O'Clock | 300 | 14.27 | 300-PF-20002-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.7 |  | 17.6 | 17.6 | 21 | 18 | 1.6442
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-12 | 300-PG-20004-03C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 6135 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 15.45 | CML-12 | CML: Elbow | 6 | 2051-12-04 | 2044-12-31 | 2014-07-11 07:30 | 4.9 | 0.24315 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 6 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 16.5 | 17.2 | 14 | 14.1 | 1.6422
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-2 | 250-PG-23005-06C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10048 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 18.25 | CML-2 | CML: Elbow | 6 | 2015-07-19 | 2015-02-22 | 2013-11-06 | 8.6 | 4.5278 | A1: Outside Quadrant |  | 12.26 | 8.6 | 10.43 | 16.3 | 12 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 16.3 | 18.2 | 18.2 | 20.3 | 1.634
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-4 | 50-DH-56137-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2739 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 19.025 | CML-4 | CML: Elbow | 3 | 2096-09-16 | 2070-01-23 | 2014-03-13 09:00 | 2.8 | 0 | A3: Inside Quadrant |  | 8.13 | 2.8 | 5.465 | 17.5 | 6 O'Clock | 80 | 11.13 | 80-PG-23050-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.7 |  | 21 | 19.7 | 17.5 | 17.9 | 1.6276
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-10 | 250-PG-23015-06C03-A CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 20079 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 18.925 | CML-10 | CML: type TBC | 6 | 2019-03-21 | 2018-02-09 | 2014-05-29 07:00 | 8.55 | 1.6724 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.6 | 6 O'Clock | 100 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.05 |  | 19.3 | 20.4 | 16.6 | 19.4 | 1.6276
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-10 | 250-PG-23015-06C03-A CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 20048 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 18.925 | CML-10 | CML: type TBC | 6 | 2019-03-21 | 2018-02-09 | 2014-05-29 07:00 | 8.55 | 1.6724 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.6 | 6 O'Clock | 100 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.05 | 0.26497 | 19.3 | 20.4 | 16.6 | 19.4 | 1.6276
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38486-09C02-P | CML-6 | 80-CG-38486-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5447 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 6.001mm/ yr | [34 empty] | Low alarm breach | 17.8 | CML-6 | CML: Straight | 3 | 2016-07-26 | 2015-03-30 | 2014-05-28 07:00 | 2.5 | 6.001 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 15.5 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13 |  | 19.3 | 18 | 18.4 | 15.5 | 1.6269
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-12 | 80-DH-56140-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21083 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 7.125 | CML-12 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.9 | 6 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 9.5 | 6.3 | 5.9 | 6.8 | 1.6256
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56142-01C02 | CML-7 | 25-DH-56142-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7528 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 6.625 | CML-7 | CML: Elbow | 3 | 2021-11-11 | 2021-10-20 | 2015-04-13 07:00 | 2.5 | 0.45538 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 25 | 6.35 | 25-DH-56142-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 9 | 6.3 | 5.5 | 5.7 | 1.6194
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-7 | 200-PG-23505-09C02-A CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 2688 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 17.825 | CML-7 | CML: Pipe Length | 3 | 2016-07-01 | 2016-01-22 | 2014-03-12 09:00 | 14.06 | 1.3605 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | 0 | 17.2 | 17.2 | 18.2 | 18.7 | 0.75
FH02 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43313-01S01-P | CML-1 | 150-FH-43313-01S01-P CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 20475 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [35 empty] | Low alarm breach | 7.75 | CML-1 | CML: Elbow | 1 | 2017-07-03 | 2016-04-18 | 2014-10-03 07:00 | 2.5 | 1.1264 | A1: Outside Quadrant |  | 6.11 | 2.5 | 3.8606 | 5.6 | 12 O'Clock | 150 | 7.11 | 150-FH-43313-01S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 8 | 7.9 | 9.5 | 1.6093
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-7 | 200-PG-23505-09C02-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 377 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 17.825 | CML-7 | CML: Pipe Length | 3 | 2016-06-30 | 2016-01-21 | 2014-03-12 | 14.06 | 1.3623 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 |  | 17.2 | 17.2 | 18.2 | 18.7 | 0.75
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-7 | 80-DH-56140-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21078 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 9 | CML-7 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 8.1 | 9 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.4 | 11.4 | 8.1 | 1.6062
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-23 | 50-GN-67002-01E01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 9082 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.375 | CML-23 | CML: type TBC | 3 | 2019-01-25 | 2019-09-04 | 2015-03-01 09:30 | 2.5 | 0.53744 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.5 | 5.4 | 6 | 0.57951
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P |  | 80-SC-55002-01C02-P |  | FPSO 2015 | Pipe Wall Thickness | 8991 | LAGGING REMOVAL REQUIRED | 2015-02-27 07:00 | 2015-02-27 09:00 | [36 empty] | 4.85 | 80-SC-55002-01C02-P | Piping | 3 | 2019-04-08 |  | 2015-02-27 07:00 |  | 0.51054 | A4: Left Quadrant |  |  | 2.5 |  | 4.6 | 9 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.1 | 4.9 | 4.8 | 4.6 | 0.20817
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-35 | 50-AI-63007-01E01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 8959 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.54mm/ yr | [35 empty] | 5.075 | CML-35 | CML: type TBC | 3 | 2019-01-15 | 2019-08-24 | 2015-02-26 09:00 | 2.5 | 0.54 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.3 | 5.3 | 5.1 | 4.6 | 0.3304
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-4 | 50-DH-56137-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13075 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 18.55 | CML-4 | CML: Elbow | 6 | 2096-09-16 | 2085-01-22 | 2014-02-07 11:00 | 2.8 | 0 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 17 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.2 |  | 17 | 19.2 | 20.5 | 17.5 | 1.6052
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-22 | 250-PG-23004-06C03-A CML-22 | yes | FPSO 2014 | Pipe Wall Thickness | 13022 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.6 | CML-22 | CML: Elbow | 6 | 2021-04-09 | 2019-10-09 | 2014-01-11 15:00 | 8.55 | 1.2349 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.5 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.95 |  | 17.5 | 19.3 | 20.4 | 21.2 | 1.6021
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-22 | 250-PG-23004-06C03-A CML-22 | yes | FPSO 2014 | Pipe Wall Thickness | 20533 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 19.575 | CML-22 | CML: Elbow | 6 | 2026-02-15 | 2023-09-12 | 2014-05-30 09:30 | 8.55 | 0.76335 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.5 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.95 | 0 | 17.5 | 19.2 | 20.5 | 21.1 | 1.5945
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-1 | 50-DH-56137-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13072 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.575 | CML-1 | CML: Elbow | 6 | 2096-09-16 | 2085-01-22 | 2014-02-07 11:00 | 2.8 | 0 | A3: Inside Quadrant |  | 5.13 | 2.8 | 3.965 | 17.4 | 6 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.6 |  | 21.2 | 19.9 | 17.4 | 19.8 | 1.584
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-3 | 80-DH-56004-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 6607 |  | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 4.125 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.3 | 9 O'Clock | 80 | 2.5 | 80-WF-71342-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 6.5 | 3.4 | 3.3 | 3.3 | 1.584
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-10 | 250-PG-23015-06C03-A CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 13042 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 18.95 | CML-10 | CML: type TBC | 6 | 2017-03-29 | 2016-07-05 | 2014-01-11 13:00 | 8.55 | 2.5358 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.7 | 6 O'Clock | 100 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.15 |  | 19.3 | 20.4 | 16.7 | 19.4 | 1.5801
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-12 | 80-PW-20024-01C03-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23056 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 7.375 | CML-12 | CML: Elbow | 6 | 2017-01-03 | 2016-06-17 | 2015-05-06 07:00 | 2.5 | 2.3995 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 6.5 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7.4 | 8.1 | 7.5 | 0.66018
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-8 | 50-PL-23042-09C03 CML-8 | yes | FPSO 2013 | Pipe Wall Thickness | 10073 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 11.85 | CML-8 | CML: type TBC | 6 | 2016-11-25 | 2016-05-18 | 2013-11-07 | 2.5 | 2.4563 | A3: Inside Quadrant |  | 5.07 | 2.5 | 3.785 | 10 | 6 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 13.7 | 12.4 | 10 | 11.3 | 1.5759
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-18 | 80-PW-44016-01C02-P CML-18 | yes | FPSO 2015 | Pipe Wall Thickness | 22920 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 4.45 | CML-18 | CML: Elbow | 3 | 2015-05-02 | 2015-07-22 | 2015-05-02 07:00 | 2.5 | 1.5584 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 2.5 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0 | 4.8309 | 2.5 | 5.4 | 4.8 | 5.1 | 1.3229
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-39 | 150-PG-23506-25C02 CML-39 |  | FPSO 2014 | Pipe Wall Thickness | 2813 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.55 | CML-39 | CML: Elbow | 3 |  |  | 2014-03-15 09:00 |  | 3.4928 | A2: Right Quadrant |  | 18.95 |  |  | 19.2 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 22.5 | 19.2 | 22.2 | 22.3 | 1.5716
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-1 | 300-PF-20003-03C03-P CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 21739 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 15.25 | CML-1 | CML: Elbow | 6 | 2032-01-27 | 2028-09-19 | 2014-10-01 07:00 | 4.9 | 0.50186 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 16.1 | 17 | 14.3 | 13.6 | 1.5716
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-11 | 200-PG-23505-09C02-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2692 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.075 | CML-11 | CML: Elbow | 3 | 2016-07-01 | 2016-01-22 | 2014-03-12 09:00 | 14.06 | 1.3605 | A3: Inside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 6 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | 0 | 18.6 | 17.8 | 17.2 | 18.7 | 0.70887
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-23 | 250-PG-23004-06C03-A CML-23 | yes | FPSO 2014 | Pipe Wall Thickness | 13023 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 18.425 | CML-23 | CML: Pipe Length | 6 | 2017-03-30 | 2016-07-06 | 2014-01-11 15:00 | 8.55 | 2.5349 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.7 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.15 |  | 16.7 | 18.1 | 18.4 | 20.5 | 1.5692
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-18 | 300-PG-20005-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 6174 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 16.725 | CML-18 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.4 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 14.4 | 17.5 | 17.8 | 17.2 | 1.5692
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-8 | 80-PL-44008-01C02 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 23776 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 6.025 | CML-8 | CML: Elbow | 3 | 2024-11-17 | 2026-03-20 | 2015-04-18 07:00 | 2.5 | 0.2606 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 6 O'Clock | 40 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 1.705 | 7.2 | 6.3 | 5 | 5.6 | 0.94648
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-20 | 50-WC-40071-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 7733 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.584mm/ yr |  | Administrator | 2015-09-08 09:36 | [32 empty] | 4.75 | CML-20 | CML: Elbow | 3 | 2018-08-14 | 2019-03-06 | 2015-01-09 13:00 | 2.5 | 0.58396 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 1.7673 | 4.6 | 5.1 | 4.7 | 4.6 | 0.23805
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-5 | 50-WC-40071-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7718 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.584mm/ yr |  | Administrator | 2015-09-08 09:33 | [32 empty] | 4.975 | CML-5 | CML: Elbow | 3 | 2018-08-14 | 2019-03-06 | 2015-01-09 13:00 | 2.5 | 0.58396 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 1.5148 | 4.9 | 5.4 | 4.6 | 5 | 0.3304
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-7 | 250-PG-23004-06C03-A CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 20528 | Rope access (Re-checking line) | 2014-05-30 11:30 | 2014-05-30 09:30 | [36 empty] | 19.475 | CML-7 | CML: Elbow | 6 | 2023-06-25 | 2021-07-23 | 2014-05-30 11:30 | 8.55 | 0.96402 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.3 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.75 | 0 | 17.3 | 20 | 19.6 | 21 | 1.565
FG02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-FG-45455-01C02-E | CML-12 | 25-FG-45455-01C02-E CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5205 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 7.55 | CML-12 | CML: Reducing Tee | 3 | 2183-08-28 | 2189-04-11 | 2014-05-20 07:00 | 2.5 | 0.02066 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7 | 6 | 9.7 | 7.5 | 1.5631
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38459-09C02-P | CML-18 | 80-CG-38459-09C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 5459 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 7.516mm/ yr | [34 empty] | Low alarm breach | 51.325 | CML-18 | CML: Elbow | 3 | 2015-12-07 | 2014-11-15 | 2014-05-28 07:00 | 2.5 | 7.5164 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 14 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 17.8 | 15.8 | 15.5 | 14 | 1.5628
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-39 | 150-PG-23506-25C02 CML-39 |  | FPSO 2014 | Pipe Wall Thickness | 20092 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 20.6 | CML-39 | CML: Elbow | 3 |  |  | 2014-05-29 07:00 |  | 2.7706 | A2: Right Quadrant |  | 18.95 |  |  | 19.2 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 0 | 19.3 | 19.2 | 21.9 | 22 | 1.5599
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-7 | 50-DC-57013-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7676 | New Isometric drawing. Line is FFS. Action: to recheck in two year(Jan. 2017) to confirm CR. Only CML’s 6 to 10 which are showing high CR | 2015-01-08 09:30 | 2015-01-08 12:00 | Check Corrosion Rate of 0.585mm/ yr |  | Administrator | 2015-09-08 12:37 | [32 empty] | 4.75 | CML-7 | CML: Elbow | 3 | 2018-08-10 | 2019-03-01 | 2015-01-08 09:30 | 2.5 | 0.5851 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5 | 4.6 | 4.8 | 0.19149
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57300-01C02 | CML-7 | 50-DC-57300-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20297 | Reviewed on 24/11/14. FFS. Recheck on Oct. 17 | 2014-10-17 07:00 | 2014-10-17 15:00 | Check Corrosion Rate of 0.682mm/ yr |  | Nestor | 2014-11-24 09:40 | [32 empty] | 5.025 | CML-7 | CML: Elbow | 3 | 2017-11-14 | 2018-05-08 | 2014-10-17 07:00 | 2.5 | 0.68171 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DC-57300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5 | 4.6 | 5.5 | 5 | 0.36856
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-33 | 150-PG-23506-25C02 CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 2807 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.825 | CML-33 | CML: Elbow | 3 | 2015-05-13 | 2014-11-14 | 2014-03-15 09:00 | 15.88 | 3.1118 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 19.5 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.62 |  | 22.8 | 22.6 | 19.5 | 22.4 | 1.5586
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38462-01C02 | CML-4 | 50-CG-38462-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20832 | Reviewed on 20/11/14. FFS. CML to be rechecked Oct.16. This line has not been RBI assessed. | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 15:54 | [32 empty] | 4.975 | CML-4 | CML: Elbow | 3 | 2017-10-03 | 2018-03-22 | 2014-10-04 07:00 | 2.5 | 0.69979 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-CG-38462-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.4 | 4.6 | 5.1 | 4.8 | 0.35
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20302-03C03-P | CML-8 | 200-PG-20302-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5862 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 13.7667 | CML-8 | CML: Equal Tee | 6 | 2027-09-25 | 2025-02-21 | 2014-06-25 10:30 | 3.3 | 0.65607 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 12 | 9 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14.4 | 14.9 |  | 12 | 1.5503
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-23 | 250-PG-23004-06C03-A CML-23 | yes | FPSO 2014 | Pipe Wall Thickness | 20534 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 18.4 | CML-23 | CML: Pipe Length | 6 | 2020-01-12 | 2018-10-08 | 2014-05-30 09:30 | 8.55 | 1.4664 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.8 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.25 | -0.26302 | 16.8 | 18.3 | 18 | 20.5 | 1.5427
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-16 | 80-DC-57005-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20262 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | Check Corrosion Rate of 0.886mm/ yr | [35 empty] | 5.4 | CML-16 | CML: type TBC | 3 | 2016-10-14 | 2017-03-06 | 2014-06-02 13:00 | 2.5 | 0.88626 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 6 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.3 | 5.5 | 4.6 | 6.2 | 0.65828
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42044-01S01 | CML-6 | 50-CI-42044-01S01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3460 | Rope Access | 2014-05-13 08:00 | 2014-05-13 09:00 | Check Corrosion Rate of 0.991mm/ yr | [35 empty] | 5.25 | CML-6 | CML: type TBC | 1 | 2016-06-25 | 2015-10-20 | 2014-05-13 08:00 | 2.5 | 0.99066 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-CI-42044-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5 | 5.7 | 5.7 | 0.54467
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42044-01S01 | CML-5 | 50-CI-42044-01S01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3459 | Rope Access | 2014-05-13 08:00 | 2014-05-13 09:00 | Check Corrosion Rate of 0.991mm/ yr | [35 empty] | 5 | CML-5 | CML: type TBC | 1 | 2016-06-25 | 2015-10-20 | 2014-05-13 08:00 | 2.5 | 0.99066 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-CI-42044-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.8 | 5.8 | 4.8 | 4.6 | 0.5416
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42044-01S01 | CML-3 | 50-CI-42044-01S01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3457 | Rope Access | 2014-05-13 08:00 | 2014-05-13 09:00 | Check Corrosion Rate of 0.991mm/ yr | [35 empty] | 5.025 | CML-3 | CML: type TBC | 1 | 2016-06-25 | 2015-10-20 | 2014-05-13 08:00 | 2.5 | 0.99066 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-CI-42044-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.8 | 4.8 | 5.9 | 0.5909
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42042-01S01 | CML-3 | 50-CI-42042-01S01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3450 | Rope Access | 2014-05-13 07:00 | 2014-05-13 08:00 | Check Corrosion Rate of 0.991mm/ yr | [35 empty] | 5.525 | CML-3 | CML: type TBC | 1 | 2016-06-24 | 2015-10-20 | 2014-05-13 07:00 | 2.5 | 0.99078 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-CI-42042-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.5 | 5.8 | 6.2 | 0.68007
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42047-01S01 | CML-4 | 50-CI-42047-01S01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3357 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.004mm/ yr | [35 empty] | 5.05 | CML-4 | CML: type TBC | 1 | 2016-06-09 | 2015-10-08 | 2014-05-08 14:30 | 2.5 | 1.0044 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0 | 4.6 | 4.8 | 5.3 | 5.5 | 0.42032
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42047-01S01 | CML-4 | 50-CI-42047-01S01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3320 | Rope Access | 2014-05-08 14:30 | 2014-05-08 15:00 | Check Corrosion Rate of 1.004mm/ yr | [35 empty] | 5.05 | CML-4 | CML: type TBC | 1 | 2016-06-09 | 2015-10-08 | 2014-05-08 14:30 | 2.5 | 1.0044 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-CI-42047-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.8 | 5.3 | 5.5 | 0.42032
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-10 | 80-DH-56140-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21081 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 10.65 | CML-10 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 8.4 | 3 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 11.7 | 8.4 | 11.6 | 10.9 | 1.5416
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23018-09C03-A | CML-3 | 200-PG-23018-09C03-A CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 13064 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 23.2 | CML-3 | CML: type TBC | 6 | 2117-11-29 | 2095-08-30 | 2014-01-10 07:00 | 10.17 | 0 | A2: Right Quadrant |  | 14.62 | 10.17 | 12.395 | 21.2 | 3 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.03 |  | 22.8 | 21.2 | 24.2 | 24.6 | 1.5406
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-FH-43507-01C02 | CML-22 | 100-FH-43507-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 2796 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 23.8 | CML-22 | CML: Elbow | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 22 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.12 |  | 24.1 | 25.7 | 23.4 | 22 | 1.5384
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-2 | 80-CG-38459-09C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22764 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 17.775 | CML-2 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 16.7 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.8 | -4.5003 | 16.8 | 17.6 | 16.7 | 20 | 1.537
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-9 | 50-PG-44022-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5852 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 10.025 | CML-9 | CML: Elbow | 6 | 2032-12-22 | 2032-08-07 | 2014-06-25 07:00 | 2.5 | 0.31878 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.9 | 12.1 | 9.7 | 1.5349
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-2 | 250-PG-23004-06C03-A CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 23370 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | Check Corrosion Rate of 0.683mm/ yr |  | John Wilson | 2017-03-23 14:31 | Loss within CA no further action required. | [31 empty] | 18.975 | CML-2 | CML: Elbow | 6 | 2027-08-16 | 2024-11-28 | 2015-07-21 07:00 | 8.55 | 0.68295 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 16.8 | 3 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.25 |  | 20 | 16.8 | 19 | 20.1 | 1.5327
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-3 | 50-PW-44012-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23162 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.6 | CML-3 | CML: Elbow | 3 | 2018-03-05 | 2018-09-08 | 2015-05-11 07:00 | 2.5 | 0.6381 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 3 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 0.35619 | 5 | 4.3 | 4.4 | 4.7 | 0.31623
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-5 | 100-PG-23028-25C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 444 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.1 | CML-5 | CML: Elbow | 3 | 2040-09-25 | 2032-05-20 | 2014-03-12 09:00 | 9.4 | 0.28237 | A1: Outside Quadrant |  | 14.12 | 9.4 | 11.76 | 16.9 | 12 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 16.9 | 19.3 | 20 | 20.2 | 1.5166
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57027-01C02 | CML-4 | 50-DC-57027-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1403 | Rope access | 2014-04-05 15:00 | 2014-04-05 16:00 | Check Corrosion Rate of 1.112mm/ yr | [35 empty] | 5.05 | CML-4 | CML: type TBC | 3 | 2016-02-24 | 2016-06-10 | 2014-04-05 15:00 | 2.5 | 1.1117 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-DC-57027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.1 | 4.6 | 5.9 | 4.6 | 0.61373
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57051-01C02 | CML-2 | 50-DC-57051-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1395 | Rope access | 2014-04-05 14:00 | 2014-04-05 15:00 | Check Corrosion Rate of 1.112mm/ yr | [35 empty] | 5.175 | CML-2 | CML: type TBC | 3 | 2016-02-23 | 2016-06-10 | 2014-04-05 14:00 | 2.5 | 1.1119 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-DC-57051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5 | 5.5 | 5.6 | 4.6 | 0.46458
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-12 | 50-DC-57451-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1383 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | Check Corrosion Rate of 1.112mm/ yr | [35 empty] | 5.225 | CML-12 | CML: type TBC | 3 | 2016-02-23 | 2016-06-09 | 2014-04-05 10:30 | 2.5 | 1.1124 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.3 | 4.6 | 5.5 | 5.5 | 0.4272
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-12 | 80-CG-38459-09C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21396 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 17.825 | CML-12 | CML: Equal Tee | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 16.4 | 3 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.3 |  | 19.5 | 16.4 | 16.7 | 18.7 | 1.513
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-6 | 80-CG-38459-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10956 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 18.925 | CML-6 | CML: Pipe Length | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 17.5 | 6 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.28 |  | 18.2 | 19 | 17.5 | 21 | 1.513
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-5 | 300-PG-20004-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6128 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 17.125 | CML-5 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 16 | 3 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 16 | 16 | 19.2 | 17.3 | 1.513
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-40 | 300-PF-20501-03C03-P CML-40 | Yes | FPSO 2014 | Pipe Wall Thickness | 21716 | Protective mesh removed. Reviewed on 1/12/14. FFS. Recheck on Sep.15 | 2014-09-28 07:00 | 2014-09-28 15:00 |  |  | Nestor | 2014-12-01 08:53 | [32 empty] | 14.725 | CML-40 | CML: type TBC | 6 | 2025-01-09 | 2022-12-09 | 2014-09-28 07:00 | 4.9 | 0.80644 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 13.8 | 15.4 | 16.5 | 13.2 | 1.5042
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-5 | 80-PL-44008-01C02 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 5742 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 6.025 | CML-5 | CML: Elbow | 3 | 2019-11-15 | 2020-08-16 | 2014-06-22 14:00 | 2.5 | 0.46264 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 6 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 7 | 6.2 | 5 | 5.9 | 0.82614
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-19 | 50-DH-56137-01C02 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 23063 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 18.75 | CML-19 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2015-05-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 16.8 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.3 |  | 19.2 | 20.4 | 18.6 | 16.8 | 1.5
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-1 | 300-PG-20048-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21471 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 14.875 | CML-1 | CML: Elbow | 6 | 2023-10-17 | 2021-12-04 | 2014-06-28 09:30 | 4.9 | 0.90228 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 13.3 | 14.2 | 15.2 | 16.8 | 1.4997
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23029-25C02-P | CML-4 | 80-PG-23029-25C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20562 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [36 empty] | 19.525 | CML-4 | CML: Elbow | 3 | 2090-10-23 | 2076-08-20 | 2014-07-02 07:00 | 7.5 | 0 | A3: Inside Quadrant |  | 12.24 | 7.5 | 8.9175 | 17.8 | 6 O'Clock | 80 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.3 |  | 21.4 | 19.1 | 17.8 | 19.8 | 1.4997
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-1 | 300-PG-20048-03C03-P CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24476 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.441mm/ yr | 38 | Kirstie Albone | 2017-03-23 12:48 | [32 empty] | 14.725 | CML-1 | CML: Elbow | 6 | 2034-08-27 | 2030-11-01 | 2016-07-09 07:00 | 4.9 | 0.44085 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.9 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | 0.51408 | 12.9 | 14.4 | 16.5 | 15.1 | 1.4975
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-17 | 100-DH-56088-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 5210 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 9.925 | CML-17 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.7 | 3 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 10.4 | 7.7 | 10.8 | 10.8 | 1.4953
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-2 | 50-DH-56137-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5443 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 3.98mm/ yr | [34 empty] | Low alarm breach | 19.625 | CML-2 | CML: Reducing Tee | 3 | 2018-03-03 | 2016-03-02 | 2014-05-28 07:00 | 2.5 | 3.9804 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 17.5 | 3 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15 |  | 20 | 17.5 | 21 | 20 | 1.493
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23029-25C02-P | CML-6 | 80-PG-23029-25C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20564 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [36 empty] | 19.775 | CML-6 | CML: Reducer | 3 | 2090-10-23 | 2076-08-20 | 2014-07-02 07:00 | 7.5 | 0 | A3: Inside Quadrant |  | 12.24 | 7.5 | 8.9175 | 17.6 | 6 O'Clock | 80 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.1 |  | 20.3 | 20.2 | 17.6 | 21 | 1.493
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-16 | 250-PG-23015-06C03-A CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 20082 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 18.85 | CML-16 | CML: type TBC | 6 | 2028-01-04 | 2025-03-21 | 2014-05-29 07:00 | 8.55 | 0.66493 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.6 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.05 |  | 18.6 | 18.2 | 17.6 | 21 | 1.4911
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-16 | 250-PG-23015-06C03-A CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 20051 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 18.85 | CML-16 | CML: type TBC | 6 | 2028-01-04 | 2025-03-21 | 2014-05-29 07:00 | 8.55 | 0.66493 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.6 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.05 | 0 | 18.6 | 18.2 | 17.6 | 21 | 1.4911
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-16 | 250-PG-23015-06C03-A CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 13048 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 18.85 | CML-16 | CML: type TBC | 6 | 2022-06-17 | 2020-09-24 | 2014-01-11 13:00 | 8.55 | 1.0729 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.6 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.05 |  | 18.6 | 18.2 | 17.6 | 21 | 1.4911
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56141-01C02 | CML-7 | 50-DH-56141-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13078 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.925 | CML-7 | CML: Elbow | 6 | 2096-09-16 | 2085-01-22 | 2014-02-07 11:00 | 2.8 | 0 | A3: Inside Quadrant |  | 5.13 | 2.8 | 3.965 | 18.4 | 6 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.6 |  | 21.9 | 20.1 | 18.4 | 19.3 | 1.4886
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-19 | 80-PW-44016-01C02-P CML-19 | yes | FPSO 2015 | Pipe Wall Thickness | 22921 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 4.825 | CML-19 | CML: Equal Tee | 3 | 2015-05-26 | 2015-08-18 | 2015-05-02 07:00 | 2.5 | 1.5063 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 2.6 | 9 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 | 4.2941 | 5.5 | 5.7 | 5.5 | 2.6 | 1.4863
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-4 | 300-PG-20049-03C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23349 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.375 | CML-4 | CML: Elbow | 6 | 2029-02-26 | 2026-04-29 | 2015-07-20 07:00 | 4.9 | 0.59484 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13 | 3 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | -0.18871 | 16.1 | 13 | 13.3 | 15.1 | 1.4773
PG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45306-03C03-P | CML-2 | 80-FG-45306-03C03-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 22086 | Protective mesh removed | 2014-07-02 11:00 | 2014-07-02 12:00 | [36 empty] | 12.575 | CML-2 | CML: Elbow | 6 | 2031-02-02 | 2028-05-24 | 2014-07-02 11:00 | 2.5 | 0.48795 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 10.6 | 9 O'Clock | 80 | 11.13 | 80-FG-45306-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 13.6 | 13.8 | 12.3 | 10.6 | 1.4751
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-11 | 50-CG-38487-09C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23580 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 11.825 | CML-11 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-10 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 10.6 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | -2.2347 | 10.7 | 13.7 | 12.3 | 10.6 | 1.4728
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-7 | 200-FH-43025-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2480 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 9.825 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 10 | 10.7 | 10.9 | 1.4683
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-4 | 300-PG-20005-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6160 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 15.95 | CML-4 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.6 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 18 | 15.9 | 15.3 | 14.6 | 1.4663
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-5 | 300-PG-20048-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21475 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | Check Corrosion Rate of 0.437mm/ yr | 38 | Kirstie Albone | 2017-03-23 12:50 | [32 empty] | 14.925 | CML-5 | CML: Elbow | 6 | 2034-10-31 | 2030-12-25 | 2014-06-28 09:30 | 4.9 | 0.43719 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 13.8 | 14 | 14.9 | 17 | 1.4637
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45024-01C02 | CML-11 | 50-FG-45024-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 450 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.025 | CML-11 | CML: Elbow | 3 | 2019-04-23 | 2017-07-04 | 2014-03-12 09:00 | 9.4 | 1.3092 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 16.1 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 18.7 | 16.1 | 17.8 | 19.5 | 1.4592
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56114-01C02 | CML-3 | 50-DH-56114-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5228 | Rope Access | 2014-05-20 11:00 | 2014-05-20 12:00 | [36 empty] | 5.85 | CML-3 | CML: Elbow | 3 | 2017-05-23 | 2017-10-25 | 2014-05-20 11:00 | 2.5 | 0.76416 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56114-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 8 | 5.2 | 5.4 | 4.8 | 1.4549
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57058-06C02 | CML-2 | 50-DC-57058-06C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10343 | Deck Level | 2013-11-11 | 2013-11-11 | Check Corrosion Rate of 2.15mm/ yr | [35 empty] | 4.825 | CML-2 | CML: Elbow | 3 | 2014-11-02 | 2014-12-26 | 2013-11-11 | 2.5 | 2.1497 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.1825 | 4.6 | 9 O'Clock | 20 | 5.56 | 50-DC-57058-06C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5 | 5.1 | 4.6 | 0.263
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 | yes | FPSO 2013 | Pipe Wall Thickness | 20024 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.625 | CML-5 | CML: type TBC | 3 | 2014-08-25 | 2014-10-13 | 2013-11-17 | 2.5 | 2.4621 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.8 | 4.5 | 4.4 | 4.8 | 0.20616
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-32 | 80-CG-38459-09C02-P CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 22794 | New location | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 18.2 | CML-32 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 16.8 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 |  | 16.8 | 18.2 | 17.6 | 20.2 | 1.4514
FG03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-FG-45055-06S01-E | CML-4 | 50-FG-45055-06S01-E CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24388 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.25 | CML-4 | CML: Elbow | 1 | 283930 | 217792 | 2016-06-07 07:00 | 1.71 | 0.00331 | A1: Outside Quadrant |  | 2.91 | 1.71 | 2.31 | 3.9 | 12 O'Clock | 50 | 3.91 | 50-FG-45055-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.19 |  | 3.9 | 4.1 | 4.2 | 4.8 | 0.3873
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-33 | 300-PF-20003-03C03-P CML-33 | Yes | FPSO 2014 | Pipe Wall Thickness | 21771 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.5 | CML-33 | CML: Reducing Tee | 6 | 2021-12-02 | 2020-05-22 | 2014-10-01 07:00 | 4.9 | 1.1011 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.8 | 3 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 16.1 | 12.8 | 13.9 | 15.2 | 1.4491
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-15 | 150-WC-40006-01C02 CML-15 | yes | FPSO 2013 | Pipe Wall Thickness | 20034 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.875 | CML-15 | CML: type TBC | 3 | 2014-10-08 | 2014-11-30 | 2013-11-17 | 2.5 | 2.2462 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.2 | 4.9 | 4.9 | 0.28723
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-15 | 250-PG-23004-06C03-A CML-15 | yes | FPSO 2014 | Pipe Wall Thickness | 13015 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 18.925 | CML-15 | CML: Elbow | 6 | 2026-05-25 | 2023-12-01 | 2014-01-11 15:00 | 8.55 | 0.74747 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 17.8 | 3 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.25 |  | 21 | 17.8 | 18.1 | 18.8 | 1.4454
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57058-06C02 | CML-1 | 50-DC-57058-06C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10342 | Deck Level | 2017-05-29 07:15 | 2013-11-11 | Check Corrosion Rate of 1.926mm/ yr | [35 empty] | 4.775 | CML-1 | CML: Pipe Length | 3 | 2027-08-15 | 2029-02-04 | 2017-05-29 07:15 | 2.5 | 0.21525 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.1825 | 4.7 | 6 O'Clock | 20 | 5.56 | 50-DC-57058-06C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.8 | 4.8 | 4.7 | 4.8 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-3 | 50-DC-57013-01C02 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24439 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | [36 empty] | 5.05 | CML-3 | CML: Elbow | 3 | 2024-08-05 | 2025-10-17 | 2016-07-03 07:00 | 2.5 | 0.27174 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0 | 4.7 | 5.2 | 4.9 | 5.4 | 0.31091
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-9 | 300-PG-20048-03C03-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23348 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 13.2 | CML-9 | CML: Elbow | 6 | 2022-03-22 | 2020-08-21 | 2015-07-20 07:00 | 4.9 | 1.0632 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 12 | 9 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 | 0.18868 | 12.7 | 15.3 | 12.8 | 12 | 1.4445
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9004-AS20-00 | CML-7 | 0100-AI-63L9004-AS20-00 CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24283 | No pipe material class specified | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 5.175 | CML-7 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 4.7 | 6 O'Clock | 25 | 3.38 | 0100-AI-63L9004-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.5 | 5.2 | 4.7 | 5.3 | 0.34034
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-6 | 300-PG-20049-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21492 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | [36 empty] | 15.45 | CML-6 | CML: Equal Tee | 6 | 2023-10-17 | 2021-12-05 | 2014-06-28 10:45 | 4.9 | 0.90216 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 12 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 13.3 | 16.1 | 16 | 16.4 | 1.4434
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-9 | 50-PW-44014-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23154 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 4.7 | CML-9 | CML: Pipe Length | 3 | 2018-03-03 | 2018-09-05 | 2015-05-10 07:00 | 2.5 | 0.639 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 6 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 0.62489 | 4.8 | 4.9 | 4.3 | 4.8 | 0.2708
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-9 | 300-PG-20048-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21479 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 13.875 | CML-9 | CML: Elbow | 6 | 2018-04-12 | 2017-05-27 | 2014-06-28 09:30 | 4.9 | 1.9255 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.2 | 3 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 14 | 12.2 | 13.6 | 15.7 | 1.4408
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-25 | 300-PF-20003-03C03-P CML-25 | Yes | FPSO 2014 | Pipe Wall Thickness | 21763 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 16.825 | CML-25 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.7 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 17.4 | 17.9 | 17.3 | 14.7 | 1.4408
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-2 | 50-DH-56137-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2737 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 18.825 | CML-2 | CML: Elbow | 3 | 2096-09-16 | 2070-01-23 | 2014-03-13 09:00 | 2.8 | 0 | A2: Right Quadrant |  | 8.13 | 2.8 | 5.465 | 17.8 | 3 O'Clock | 80 | 11.13 | 80-PG-23050-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15 |  | 17.9 | 17.8 | 18.7 | 20.9 | 1.4408
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-11 | 200-PG-23505-09C02-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 381 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 18.075 | CML-11 | CML: Elbow | 3 | 2016-06-30 | 2016-01-21 | 2014-03-12 | 14.06 | 1.3623 | A3: Inside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 6 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 |  | 18.6 | 17.8 | 17.2 | 18.7 | 0.70887
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-26 | 300-PF-20501-03C03-P CML-26 | Yes | FPSO 2014 | Pipe Wall Thickness | 21702 | Protective mesh removed. Reviewed on 1/12/14. FFS. Recheck on Sep.15 | 2014-09-28 07:00 | 2014-09-28 15:00 |  |  | Nestor | 2014-12-01 08:53 | [32 empty] | 14.675 | CML-26 | CML: Elbow | 6 | 2025-01-09 | 2022-12-09 | 2014-09-28 07:00 | 4.9 | 0.80644 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 15.7 | 16.1 | 13.2 | 13.7 | 1.4385
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-4 | 300-PG-20048-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21474 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 15.525 | CML-4 | CML: Elbow | 6 | 2026-06-27 | 2024-02-20 | 2014-06-28 09:30 | 4.9 | 0.71624 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 9 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 15.9 | 16.9 | 15.8 | 13.5 | 1.4385
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-8 | 300-PG-20005-03C03-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22770 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 15.225 | CML-8 | CML: Elbow | 6 | 2051-06-23 | 2044-08-18 | 2015-04-29 07:00 | 4.9 | 0.24602 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 | 0.62504 | 13.8 | 14.2 | 16.2 | 16.7 | 1.4385
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-9 | 50-PW-44040-01C02 CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 1984 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.225 | CML-9 | CML: Elbow | 3 | 2016-01-24 | 2016-05-07 | 2014-03-27 07:00 | 2.5 | 1.1464 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.5 | 5.3 | 4.6 | 5.5 | 0.4272
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-17 | 300-PF-20501-03C03-P CML-17 | Yes | FPSO 2014 | Pipe Wall Thickness | 21693 | Protective mesh removed. Reviewed on 1/12/14. FFS. Recheck on Sep.15 | 2014-09-28 07:00 | 2014-09-28 15:00 |  |  | Nestor | 2014-12-01 08:52 | [32 empty] | 14.575 | CML-17 | CML: Elbow | 6 | 2026-03-23 | 2023-12-02 | 2014-09-28 07:00 | 4.9 | 0.73107 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 14.8 | 13.3 | 13.7 | 16.5 | 1.4315
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-27 | 300-PF-20500-03C03-P CML-27 | Yes | FPSO 2014 | Pipe Wall Thickness | 21647 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 15.625 | CML-27 | CML: Elbow | 6 | 2035-03-02 | 2031-04-03 | 2014-09-27 07:00 | 4.9 | 0.43049 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 3 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 15.4 | 13.7 | 16.9 | 16.5 | 1.4315
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-33 | 300-PG-20005-03C03-P CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 22795 | New location | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.475 | CML-33 | CML: Elbow | 6 | 2030-02-18 | 2027-02-16 | 2015-04-29 07:00 | 4.9 | 0.5601 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 13.2 | 13.6 | 14.7 | 16.4 | 1.4315
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-8 | 300-PG-20005-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 6164 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 15.275 | CML-8 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.3 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 17.4 | 14.8 | 14.3 | 14.6 | 1.4315
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-9 | 50-DC-57013-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22933 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | Check Corrosion Rate of 0.438mm/ yr |  | John Wilson | 2017-03-22 09:33 | Included this CML at the next inspection | [31 empty] | 4.95 | CML-9 | CML: Elbow | 3 | 2020-05-09 | 2021-02-05 | 2015-05-02 07:00 | 2.5 | 0.43782 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | -0.64094 | 4.7 | 5.3 | 4.9 | 4.9 | 0.25166
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-3 | 50-DC-57013-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22927 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | Check Corrosion Rate of 0.438mm/ yr | 37 | [34 empty] | 5.075 | CML-3 | CML: Elbow | 3 | 2020-05-09 | 2021-02-05 | 2015-05-02 07:00 | 2.5 | 0.43782 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.64094 | 4.7 | 5.1 | 5 | 5.5 | 0.3304
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-10 | 50-DH-56137-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23054 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 18.725 | CML-10 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2015-05-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 17.3 | 3 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 |  | 17.8 | 17.3 | 19.4 | 20.4 | 1.4315
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44513-01C02 | CML-12 | 80-PL-44513-01C02 CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 7977 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:10 | [32 empty] | 5.3 | CML-12 | CML: Elbow | 3 | 2023-05-19 | 2024-07-16 | 2015-01-18 10:30 | 2.5 | 0.29986 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.5 | 5.3 | 5.4 | 0.21602
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-47 | 150-PG-23506-25C02 CML-47 |  | FPSO 2014 | Pipe Wall Thickness | 2821 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.575 | CML-47 | CML: Elbow | 3 | 2015-05-13 | 2014-11-14 | 2014-03-15 09:00 | 15.88 | 3.1118 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 19.5 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.62 |  | 22.4 | 22.6 | 19.5 | 21.8 | 1.4245
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-6 | 400-FH-43500-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5642 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 13.075 | CML-6 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 12 | 9 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 15 | 13.3 | 12 | 12 | 1.4221
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-13 | 50-PL-23042-09C03 CML-13 | yes | FPSO 2013 | Pipe Wall Thickness | 10078 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 11.875 | CML-13 | CML: type TBC | 6 | 2016-05-08 | 2015-11-30 | 2013-11-07 | 2.5 | 2.9154 | A2: Right Quadrant |  | 5.07 | 2.5 | 3.785 | 9.8 | 3 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 12.2 | 9.8 | 13 | 12.5 | 1.4221
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-2 | 80-CG-38459-09C02-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 10986 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 22.775 | CML-2 | CML: Elbow | 6 | 2117-05-30 | 2095-05-30 | 2014-01-10 | 10.22 | 0 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 22 | 6 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.78 |  | 22.1 | 22.1 | 22 | 24.9 | 1.4175
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-20 | 50-DH-56137-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 5688 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 1.022mm/ yr | [34 empty] | Low alarm breach | 17.675 | CML-20 | CML: Pipe Length | 3 | 2017-05-19 | 2015-09-18 | 2014-06-21 14:00 | 2.5 | 4.771 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 16.4 | 3 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.9 |  | 16.9 | 16.4 | 19.6 | 17.8 | 1.408
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-11 | 150-WC-40006-01C02 CML-11 | yes | FPSO 2013 | Pipe Wall Thickness | 20030 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.8 | CML-11 | CML: type TBC | 3 | 2014-10-08 | 2014-11-30 | 2013-11-17 | 2.5 | 2.2462 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 4.8 | 5.1 | 4.8 | 0.24495
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71326-01K01 | CML52 | 100-WF-71326-01K01 CML52 |  | FPSO 2015 | Pipe Wall Thickness | 7584 |  | 2015-04-14 07:00 | 2015-04-14 15:00 |  |  | Nestor | 2014-11-21 16:58 | [32 empty] | 4.825 | CML52 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.7 | 12 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 4.9 | 4.8 | 4.9 | 0.095743
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML4 | 80-WF-71311-01K01 CML4 |  | FPSO 2015 | Pipe Wall Thickness | 7249 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-21 08:56 | [32 empty] | 4.925 | CML4 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 4.7 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.8 | 4.7 | 4.8 | 5.4 | 0.32016
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML85 | 80-WF-71338-01K01 CML85 |  | FPSO 2015 | Pipe Wall Thickness | 7131 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 4.875 | CML85 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4.7 | 9 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 4.8 | 4.9 | 4.7 | 0.17078
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71338-01K01 | CML11 | 80-WF-71338-01K01 CML11 |  | FPSO 2015 | Pipe Wall Thickness | 7057 |  | 2015-04-07 07:00 | 2015-04-07 15:00 | [36 empty] | 4.85 | CML11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 4.7 | 6 O'Clock | 80 | 2.5 | 80-WF-71338-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 4.8 | 4.7 | 5 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 200-WF-71334-01K01 | CML-4 | 200-WF-71334-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6395 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 5.325 | CML-4 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-21 07:00 | 2.8 | 0 | A3: Inside Quadrant |  | 3.5 | 2.8 | 3.15 | 5 | 6 O'Clock | 200 | 4 | 200-WF-71334-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.4 | 5.5 | 5 | 5.4 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71329-01K01 | CML-3 | 50-WF-71329-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6252 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 5.175 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4.7 | 9 O'Clock | 50 | 2.5 | 50-WF-71329-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 5.2 | 5.7 | 4.7 | 0.4113
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71310-01K01 | CML-6 | 150-WF-71310-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5317 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 5.025 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.7 | 12 O'Clock | 150 | 3 | 150-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.2 | 5.1 | 5.1 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-8 | 80-WF-71400-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5253 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 4.95 | CML-8 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 4.7 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 4.9 | 5 | 4.7 | 0.20817
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-4 | 50-WC-40452-01C02 CML-4 | yes | FPSO 2013 | Pipe Wall Thickness | 10601 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 2.03mm/ yr | [35 empty] | 4.95 | CML-4 | CML: type TBC | 3 | 2014-11-29 | 2015-01-27 | 2013-11-17 | 2.5 | 2.0302 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.2 | 5.3 | 4.6 | 4.7 | 0.35119
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-12 | 50-AU-63015-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 9043 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | Check Corrosion Rate of 0.48mm/ yr | [35 empty] | 5.35 | CML-12 | CML: type TBC | 3 | 2019-09-28 | 2020-06-01 | 2015-03-01 07:00 | 2.5 | 0.48034 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.3 | 5.7 | 5.7 | 0.47258
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-16 | 50-AI-63007-01E01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8940 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.483mm/ yr | [35 empty] | 4.9 | CML-16 | CML: type TBC | 3 | 2019-09-17 | 2020-05-21 | 2015-02-26 09:00 | 2.5 | 0.48255 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.8 | 4.7 | 4.7 | 5.4 | 0.33665
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-21 | 50-AU-63018-01E01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 8917 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | Check Corrosion Rate of 0.483mm/ yr | [35 empty] | 5 | CML-21 | CML: type TBC | 3 | 2019-09-14 | 2020-05-17 | 2015-02-25 13:00 | 2.5 | 0.48318 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 4.9 | 5.4 | 5 | 0.29439
SD02 | Montara_Topside | No | Steam (55) | Pipework | 50-SL-55003-01C02-P | CML-1 | 50-SL-55003-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8853 |  | 2015-02-24 11:00 | 2015-02-24 12:00 | [36 empty] | 4.85 | CML-1 | CML: type TBC | 3 | 2019-09-10 | 2020-05-13 | 2015-02-24 11:00 | 2.5 | 0.48401 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-SL-55003-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.1 | 4.8 | 4.8 | 0.17321
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-2 | 50-FL-43454-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2752 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 17.85 | CML-2 | CML: Elbow | 3 | 2018-10-20 | 2017-02-25 | 2014-03-13 09:00 | 9.4 | 1.4325 | A3: Inside Quadrant |  | 14.12 | 9.4 | 11.76 | 16 | 6 O'Clock | 100 | 17.12 | 100-PG-23049-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 17.9 | 19.4 | 16 | 18.1 | 1.4012
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62003-01C02 | CML-4 | 50-DO-62003-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8052 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 4.875 | CML-4 | CML: type TBC | 3 | 2019-05-09 | 2019-12-28 | 2015-01-21 07:30 | 2.5 | 0.51159 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DO-62003-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 4.8 | 5.2 | 4.8 | 0.22174
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62001-01C02 | CML-2 | 50-DO-62001-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8042 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 4.875 | CML-2 | CML: type TBC | 3 | 2019-05-09 | 2019-12-28 | 2015-01-21 07:30 | 2.5 | 0.51159 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-DO-62001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 4.7 | 5 | 4.8 | 0.15
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-20 | 50-PW-44040-01C02 CML-20 | yes | FPSO 2014 | Pipe Wall Thickness | 1995 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.1 | CML-20 | CML: Elbow | 3 | 2016-01-24 | 2016-05-07 | 2014-03-27 07:00 | 2.5 | 1.1464 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.2 | 5 | 4.6 | 5.6 | 0.41633
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-16 | 50-WC-40452-01C02 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10613 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 2.03mm/ yr | [35 empty] | 4.925 | CML-16 | CML: type TBC | 3 | 2014-11-29 | 2015-01-27 | 2013-11-17 | 2.5 | 2.0302 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.8 | 4.9 | 5.4 | 0.34034
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-14 | 200-PG-23007-09C03-PA CML-14 | yes | FPSO 2015 | Pipe Wall Thickness | 23404 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [35 empty] | High alarm breach | 11.925 | CML-14 | CML: Elbow | 6 | 2015-02-16 | 2020-02-08 | 2015-07-22 07:00 | 10.22 | 0.51389 | A2: Right Quadrant |  | 5.1 | 10.22 | 7.66 | 10 | 3 O'Clock | 50 | 11.1 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.22 | 0 | 12.9 | 10 | 11.8 | 13 | 1.3937
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-3 | 80-CG-38459-09C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22765 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 18.175 | CML-3 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 16.7 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.8 | -0.50004 | 17.3 | 19.2 | 19.5 | 16.7 | 1.3841
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-17 | 250-PG-23005-06C03 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10063 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 18.7 | CML-17 | CML: Elbow | 6 | 2017-10-07 | 2016-12-10 | 2013-11-06 | 8.6 | 2.2177 | A1: Outside Quadrant |  | 12.26 | 8.6 | 10.43 | 17.3 | 12 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 17.3 | 19.2 | 17.9 | 20.4 | 1.3832
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-6 | 300-PG-20048-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21476 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 15.275 | CML-6 | CML: Elbow | 6 | 2050-09-12 | 2043-12-29 | 2014-06-28 09:30 | 4.9 | 0.25115 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 6 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 15.2 | 14.7 | 14 | 17.2 | 1.3745
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-17 | 50-PL-23042-09C03 CML-17 | Yes | FPSO 2013 | Pipe Wall Thickness | 10082 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 11.25 | CML-17 | CML: type TBC | 6 | 2015-08-25 | 2015-04-25 | 2013-11-07 | 2.5 | 3.8337 | A3: Inside Quadrant |  | 5.07 | 2.5 | 3.785 | 9.4 | 6 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 11.3 | 12.7 | 9.4 | 11.6 | 1.3723
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-12 | 50-CG-38487-09C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23581 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 12.125 | CML-12 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-10 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 10.1 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 | 1.0641 | 12.5 | 13.1 | 12.8 | 10.1 | 1.372
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56019-01C02 | CML-5 | 80-DH-56019-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3465 | Rope Access | 2014-05-13 09:30 | 2014-05-13 10:30 | [36 empty] | 8.75 | CML-5 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-13 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 8 | 9 O'Clock | 80 | 5.49 | 80-DH-56019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 10.8 | 8 | 8.2 | 8 | 1.3699
DH01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-DH-56137-01C02 | CML-3 | 50-DH-56137-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20794 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 |  |  | Administrator | 2015-09-07 10:59 | [32 empty] | 20.45 | CML-3 | CML: Reducer | 3 | 2054-10-24 | 2049-02-10 | 2014-07-18 11:00 | 4.6 | 0 | A3: Inside Quadrant |  | 5.74 | 4.6 | 5.17 | 18.4 | 6 O'Clock | 100 | 8.74 | 50-CG-38002-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.8 |  | 21.2 | 21.1 | 18.4 | 21.1 | 1.3675
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-4 | 50-DH-56137-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20543 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 18.45 | CML-4 | CML: Elbow | 6 | 2096-09-16 | 2085-01-22 | 2014-05-27 08:00 | 2.8 | 0 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 17.1 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.3 | -0.33525 | 17.1 | 17.9 | 18.5 | 20.3 | 1.3601
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-9 | 300-PF-20003-03C03-P CML-9 | Yes | FPSO 2014 | Pipe Wall Thickness | 21747 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [35 empty] | Low alarm breach | 9.275 | CML-9 | CML: Elbow | 6 | 2015-12-02 | 2015-04-22 | 2014-10-01 07:00 | 2.5 | 4.6965 | A2: Right Quadrant |  | 8.27 | 2.5 | 5.385 | 8 | 3 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 9.7 | 8 | 8.4 | 11 | 1.3598
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-8 | 50-WC-40452-01C02 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10605 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 2.03mm/ yr | [35 empty] | 4.925 | CML-8 | CML: type TBC | 3 | 2014-11-29 | 2015-01-27 | 2013-11-17 | 2.5 | 2.0302 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5 | 4.6 | 4.8 | 5.3 | 0.29861
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-10 | 250-PG-23004-06C03-A CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 13010 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.575 | CML-10 | CML: Elbow | 6 | 2026-05-25 | 2023-12-01 | 2014-01-11 15:00 | 8.55 | 0.74747 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 17.8 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.25 |  | 21.1 | 19.7 | 19.7 | 17.8 | 1.3549
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-9 | 250-PG-23004-06C03-A CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 13009 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.575 | CML-9 | CML: Elbow | 6 | 2026-05-25 | 2023-12-01 | 2014-01-11 15:00 | 8.55 | 0.74747 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 17.8 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.25 |  | 21.1 | 19.7 | 19.7 | 17.8 | 1.3549
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-18 | 300-PG-20005-03C03-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 22780 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.85 | CML-18 | CML: Elbow | 6 | 2044-10-18 | 2039-02-26 | 2015-04-29 07:00 | 4.9 | 0.29837 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | 0.87506 | 13.7 | 14 | 16.7 | 15 | 1.3528
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-6 | 50-PL-23023-03C03 CML-6 | Yes | FPSO 2013 | Pipe Wall Thickness | 10206 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 13.5333 | CML-6 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 12.2 | 6 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 13.5 | 14.9 | 12.2 |  | 1.3503
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-5 | 300-PG-20049-03C03-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23350 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.525 | CML-5 | CML: Elbow | 6 | 2032-02-06 | 2028-09-27 | 2015-07-20 07:00 | 4.9 | 0.50116 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 9 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 | -0.37741 | 13.7 | 16.2 | 15 | 13.2 | 1.35
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45044-03C02 | CML-28 | 50-FG-45044-03C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 6184 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 9.9 | CML-28 | CML: Elbow | 6 | 2015-09-20 | 2015-02-26 | 2014-07-11 07:30 | 2.5 | 5.1061 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.6 | 9 O'Clock | 50 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 11.7 | 10.1 | 9.2 | 8.6 | 1.3491
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-10 | 50-PG-44022-01C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5853 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 15.05 | CML-10 | CML: Reducer | 6 | 2075-10-24 | 2074-08-12 | 2014-06-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 13.2 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 16 | 14.9 | 13.2 | 16.1 | 1.3478
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-3 | 50-DH-56137-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5444 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 4.688mm/ yr | [34 empty] | Low alarm breach | 18.275 | CML-3 | CML: Reducing Tee | 3 | 2017-06-14 | 2015-10-03 | 2014-05-28 07:00 | 2.5 | 4.6876 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 16.8 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.3 |  | 20 | 17.8 | 18.5 | 16.8 | 1.3451
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-11 | 250-PG-23004-06C03-A CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 23378 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.3 | CML-11 | CML: Elbow | 6 | 2037-07-15 | 2032-12-04 | 2015-07-21 07:00 | 8.55 | 0.40229 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 17.4 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.85 | 0.087552 | 20.2 | 20.3 | 19.3 | 17.4 | 1.3441
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-47 | 150-PG-23506-25C02 CML-47 |  | FPSO 2014 | Pipe Wall Thickness | 20096 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 20.9 | CML-47 | CML: Elbow | 3 | 2015-11-15 | 2015-04-02 | 2014-05-29 07:00 | 15.88 | 2.4683 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 19.5 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.62 | 0 | 22 | 22.1 | 19.5 | 20 | 1.3441
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-10 | 150-WC-40006-01C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 20029 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.825 | CML-10 | CML: type TBC | 3 | 2014-11-29 | 2015-01-27 | 2013-11-17 | 2.5 | 2.0302 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.7 | 4.8 | 5.2 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56111-01C02 | CML-2 | 50-DH-56111-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21011 | Rope Access | 2014-05-24 14:00 | 2014-05-24 15:00 | [36 empty] | 8.275 | CML-2 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-24 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 12 O'Clock | 50 | 5.54 | 50-DH-56111-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 8.6 | 9.2 | 9 | 1.3401
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-12 | 50-PW-44014-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23157 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 4.575 | CML-12 | CML: Elbow | 3 | 2018-03-03 | 2018-09-05 | 2015-05-10 07:00 | 2.5 | 0.639 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 1.339 | 4.3 | 4.8 | 4.8 | 4.4 | 0.263
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-18 | 50-WC-40071-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 7731 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.522mm/ yr |  | Administrator | 2015-09-08 09:36 | [32 empty] | 4.925 | CML-18 | CML: Elbow | 3 | 2019-03-28 | 2019-11-11 | 2015-01-09 13:00 | 2.5 | 0.52184 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 1.1361 | 5.2 | 5 | 4.7 | 4.8 | 0.22174
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-12 | 50-WC-40071-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 7725 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.522mm/ yr |  | Administrator | 2015-09-08 09:34 | [32 empty] | 4.925 | CML-12 | CML: Elbow | 3 | 2019-03-28 | 2019-11-11 | 2015-01-09 13:00 | 2.5 | 0.52184 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 1.7673 | 5 | 5 | 5 | 4.7 | 0.15
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-10 | 50-WC-40071-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7723 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.522mm/ yr |  | Administrator | 2015-09-08 09:34 | [32 empty] | 4.975 | CML-10 | CML: Elbow | 3 | 2019-03-28 | 2019-11-11 | 2015-01-09 13:00 | 2.5 | 0.52184 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 1.0099 | 4.9 | 5.4 | 4.9 | 4.7 | 0.29861
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-9 | 50-WC-40071-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7722 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in a year (Jan. 2016) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.522mm/ yr |  | Administrator | 2015-09-08 09:34 | [32 empty] | 5.075 | CML-9 | CML: Pipe Length | 3 | 2019-03-28 | 2019-11-11 | 2015-01-09 13:00 | 2.5 | 0.52184 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.63117 | 4.7 | 5 | 5.8 | 4.8 | 0.49917
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-8 | 50-DC-57013-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7677 | New Isometric drawing. Line is FFS. Action: to recheck in two year(Jan. 2017) to confirm CR. Only CML’s 6 to 10 which are showing high CR | 2015-01-08 09:30 | 2015-01-08 12:00 | Check Corrosion Rate of 0.523mm/ yr |  | Administrator | 2015-09-08 12:37 | [32 empty] | 5.05 | CML-8 | CML: Elbow | 3 | 2019-03-24 | 2019-11-06 | 2015-01-08 09:30 | 2.5 | 0.52286 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.1 | 5.2 | 5.2 | 0.23805
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-6 | 50-DC-57013-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7675 | New Isometric drawing.Line is FFS. Action: to recheck in two year(Jan. 2017) to confirm CR. Only CML’s 6 to 10 which are showing high CR | 2015-01-08 09:30 | 2015-01-08 12:00 | Check Corrosion Rate of 0.523mm/ yr |  | Administrator | 2015-09-08 12:36 | [32 empty] | 5.05 | CML-6 | CML: Elbow | 3 | 2019-03-24 | 2019-11-06 | 2015-01-08 09:30 | 2.5 | 0.52286 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 4.7 | 5.2 | 5.1 | 0.23805
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-4 | 50-DC-57013-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7673 | New Isometric drawing. Line is FFS. Action: to recheck in two year(Jan. 2017) to confirm CR. Only CML’s 4 & 6 to 10 which are showing high CR | 2015-01-08 09:30 | 2015-01-08 12:00 | Check Corrosion Rate of 0.523mm/ yr |  | Administrator | 2015-09-08 12:40 | [32 empty] | 4.8 | CML-4 | CML: Elbow | 3 | 2019-03-24 | 2019-11-06 | 2015-01-08 09:30 | 2.5 | 0.52286 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.1 | 4.7 | 4.7 | 0.2
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57300-01C02 | CML-6 | 50-DC-57300-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20296 | Reviewed on 24/11/14. FFS. Recheck on Oct. 17 | 2014-10-17 07:00 | 2014-10-17 15:00 | Check Corrosion Rate of 0.609mm/ yr |  | Nestor | 2014-11-24 09:40 | [32 empty] | 5.35 | CML-6 | CML: Pipe Length | 3 | 2018-05-27 | 2018-12-08 | 2014-10-17 07:00 | 2.5 | 0.60919 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DC-57300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.5 | 5.4 | 5.8 | 4.7 | 0.46547
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44025-01X01 | CML-1 | 50-PW-44025-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21901 |  | 2014-06-19 08:00 | 2014-06-19 08:30 | [36 empty] | 4.425 | CML-1 | CML: Pipe Length | 3 | 2015-12-27 | 2016-04-06 | 2014-06-19 08:00 | 2.5 | 1.1807 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-PW-44025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 0.66263 | 4.3 | 4.6 | 4.4 | 4.4 | 0.12583
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-39 | 300-PF-20003-03C03-P CML-39 | yes | FPSO 2014 | Pipe Wall Thickness | 21777 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 16.925 | CML-39 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 15.5 | 12 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.6 |  | 15.5 | 16.5 | 17 | 18.7 | 1.3376
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45024-01C02 | CML-11 | 50-FG-45024-01C02 CML-11 | Yes | FPSO 2014 | Pipe Wall Thickness | 20555 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 17.9 | CML-11 | CML: Elbow | 3 | 2020-12-11 | 2018-08-23 | 2014-05-30 09:30 | 9.4 | 1.0245 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 16.1 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 0 | 18.7 | 16.1 | 17.7 | 19.1 | 1.3367
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-4 | 50-PW-44013-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22723 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 4.75 | CML-4 | CML: Elbow | 3 | 2018-07-01 | 2019-01-17 | 2015-04-28 07:00 | 2.5 | 0.59759 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 0.47135 | 4.8 | 5.2 | 4.4 | 4.6 | 0.34157
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-35 | 300-PF-20003-03C03-P CML-35 | yes | FPSO 2014 | Pipe Wall Thickness | 21773 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.825 | CML-35 | CML: Fitting | 6 | 2040-01-05 | 2035-03-25 | 2014-10-01 07:00 | 4.9 | 0.35205 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 16.6 | 15.1 | 13.8 | 13.8 | 1.3326
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-15 | 200-PG-23007-09C03-PA CML-15 | yes | FPSO 2014 | Pipe Wall Thickness | 20702 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [35 empty] | Medium alarm breach | 12.375 | CML-15 | CML: Elbow | 6 | 2014-07-15 | 2014-04-19 | 2014-06-30 13:00 | 10.22 | 9.2697 | A2: Right Quadrant |  | 14.62 | 10.22 | 12.42 | 10.6 | 3 O'Clock | 50 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.38 |  | 13 | 10.6 | 12.2 | 13.7 | 1.3326
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-17 | 200-PG-23007-09C03-PA CML-17 | yes | FPSO 2015 | Pipe Wall Thickness | 23406 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 19.1 | CML-17 | CML: Fitting | 6 | 2021-08-05 | 2019-11-12 | 2015-07-22 07:00 | 10.22 | 1.2707 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 17.9 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.68 | 0.56626 | 20.2 | 20.3 | 18 | 17.9 | 1.3292
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-20 | 300-PG-20506-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 13234 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.925 | CML-20 | CML: type TBC | 6 | 2018-11-13 | 2017-11-20 | 2014-02-04 15:00 | 4.9 | 1.7176 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.1 | 12 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 13.1 | 14.8 | 15.8 | 16 | 1.3251
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20302-03C03-P | CML-2 | 200-PG-20302-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5855 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 12.325 | CML-2 | CML: Elbow | 6 | 2019-04-24 | 2018-03-30 | 2014-06-25 10:30 | 3.3 | 1.5933 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 11 | 12 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 11 | 11.4 | 13.7 | 13.2 | 1.3251
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-2 | 80-PW-44035-01C02-P CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 23266 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.725 | CML-2 | CML: Elbow | 3 | 2020-10-10 | 2021-08-19 | 2015-05-12 07:00 | 2.5 | 0.40596 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 3 O'Clock | 20 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.5093 | 5.8 | 4.7 | 6.1 | 6.3 | 0.71356
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-13 | 80-PW-20024-01C03-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23057 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 10.35 | CML-13 | CML: Reducing Tee | 6 | 2033-06-18 | 2030-05-30 | 2015-05-06 07:00 | 2.5 | 0.43015 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.3 | 3 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 10.3 | 10.4 | 10.4 | 0.057735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-14 | 50-PW-44015-01X01 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10297 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.8 | CML-14 | CML: Reducer | 3 | 2014-08-02 | 2014-09-15 | 2013-11-10 | 2.5 | 2.6136 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.1825 | 4.4 | 6 O'Clock | 50 | 5.56 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5.2 | 4.8 | 4.4 | 4.8 | 0.3266
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-42 | 150-PG-23506-25C02 CML-42 |  | FPSO 2014 | Pipe Wall Thickness | 2816 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.75 | CML-42 | CML: Elbow | 3 | 2019-10-13 | 2018-03-04 | 2014-03-15 09:00 | 15.88 | 0.95259 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.2 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.32 |  | 24.2 | 22.2 | 21.2 | 23.4 | 1.3204
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-6 | 250-PW-44010-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21923 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 19.325 | CML-6 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 18 | 9 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.5 |  | 19.7 | 21 | 18.6 | 18 | 1.32
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-6 | 250-PW-44010-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5825 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 19.325 | CML-6 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 18 | 9 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.5 |  | 19.7 | 21 | 18.6 | 18 | 1.32
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-40 | 300-PF-20500-03C03-P CML-40 | yes | FPSO 2014 | Pipe Wall Thickness | 21660 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 16.975 | CML-40 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 15.6 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 15.6 | 16.2 | 17.6 | 18.5 | 1.3175
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-14 | 200-PG-23007-09C03-PA CML-14 | yes | FPSO 2014 | Pipe Wall Thickness | 20701 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [35 empty] | High alarm breach | 11.475 | CML-14 | CML: Elbow | 6 | 2014-04-12 | 2016-10-16 | 2014-06-30 13:00 | 10.22 | 1.0176 | A2: Right Quadrant |  | 5.1 | 10.22 | 7.66 | 10 | 3 O'Clock | 50 | 11.1 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.22 |  | 12.2 | 10 | 10.8 | 12.9 | 1.315
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-18 | 50-CG-38465-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 20881 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.35 | CML-18 | CML: Elbow | 3 | 2018-04-10 | 2018-10-17 | 2014-10-04 07:00 | 2.5 | 0.62534 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.4 | 4.7 | 5.6 | 5.7 | 0.45092
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-9 | 50-CG-38465-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20872 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 4.975 | CML-9 | CML: Elbow | 3 | 2018-04-10 | 2018-10-17 | 2014-10-04 07:00 | 2.5 | 0.62534 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 5 | 5.2 | 4.7 | 0.20616
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-7 | 50-CG-38465-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20870 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.25 | CML-7 | CML: Elbow | 3 | 2018-04-10 | 2018-10-17 | 2014-10-04 07:00 | 2.5 | 0.62534 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 80 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.7 | 5.3 | 4.7 | 5.3 | 0.41231
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38462-01C02 | CML-6 | 50-CG-38462-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20834 | Reviewed on 20/11/14. FFS. CML to be rechecked Oct.16. This line has not been RBI assessed. | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 15:56 | [32 empty] | 5 | CML-6 | CML: Elbow | 3 | 2018-04-10 | 2018-10-17 | 2014-10-04 07:00 | 2.5 | 0.62534 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38462-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 4.7 | 5.2 | 4.9 | 0.24495
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-5 | 50-DH-56137-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21438 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 17.475 | CML-5 | CML: Equal Tee | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 5.35 | 2.5 | 3.925 | 16.5 | 6 O'Clock | 250 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14 |  | 17.2 | 16.8 | 16.5 | 19.4 | 1.315
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-12 | 200-PG-23505-09C02-A CML-12 | Yes | FPSO 2014 | Pipe Wall Thickness | 2693 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.15 | CML-12 | CML: Pipe Length | 3 | 2016-07-01 | 2016-01-22 | 2014-03-12 09:00 | 14.06 | 1.3605 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | 0 | 18.3 | 17.2 | 18.4 | 18.7 | 0.65574
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42044-01S01 | CML-2 | 50-CI-42044-01S01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3456 | Rope Access | 2014-05-13 08:00 | 2014-05-13 09:00 | Check Corrosion Rate of 0.885mm/ yr | [35 empty] | 5.025 | CML-2 | CML: type TBC | 1 | 2016-11-05 | 2016-02-01 | 2014-05-13 08:00 | 2.5 | 0.88527 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-CI-42044-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 5.6 | 4.8 | 4.7 | 0.40311
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38459-09C02-P | CML-1 | 80-CG-38459-09C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8624 | Rope Access / Material Class Not Selectable. Line is FFS. Action: to recheck in a year(Feb. 2016) to confirm CR. | 2015-02-10 07:00 | 2015-02-10 08:00 | Check Corrosion Rate of 0.583mm/ yr |  | Administrator | 2015-09-08 10:07 | [32 empty] | 15.775 | CML-1 | CML: Pipe Length | 3 | 2034-12-23 | 2026-10-07 | 2015-02-10 07:00 | 2.5 | 0.58349 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 14.1 | 6 O'Clock | 250 | 15.09 | 250-WC-40506-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.6 |  | 15.8 | 15.9 | 14.1 | 17.3 | 1.3099
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-5 | 300-PG-20506-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13219 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.175 | CML-5 | CML: type TBC | 6 | 2018-06-09 | 2017-07-14 | 2014-02-04 15:00 | 4.9 | 1.8644 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13 | 3 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 15.5 | 13 | 13.1 | 15.1 | 1.3099
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-17 | 50-CG-38487-09C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20856 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 9.175 | CML-17 | CML: Elbow | 3 | 2020-02-22 | 2018-05-25 | 2014-10-02 07:00 | 2.5 | 0.9269 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 7.5 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 | 9.6264 | 9.2 | 10.7 | 9.3 | 7.5 | 1.3099
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-7 | 200-PG-20300-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5872 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | [36 empty] | 14.3 | CML-7 | CML: Equal Tee | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 09:30 | 3.3 | 0 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 12.8 | 9 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 14.9 | 15.2 |  | 12.8 | 1.3077
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-7 | 300-PG-20049-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21493 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | Check Corrosion Rate of 0.623mm/ yr | 39 | Kirstie Albone | 2017-03-23 13:21 | [32 empty] | 14.625 | CML-7 | CML: Elbow | 6 | 2028-06-10 | 2025-09-27 | 2014-06-28 10:45 | 4.9 | 0.62314 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 6 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14.5 | 16.5 | 13.6 | 13.9 | 1.3048
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45044-03C02 | CML-6 | 50-FG-45044-03C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20806 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.9 | CML-6 | CML: Elbow | 3 | 2063-09-30 | 2050-09-06 | 2014-07-18 11:00 | 2.5 | 0.12389 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 11.7 | 9.8 | 9.5 | 8.6 | 1.3038
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-12 | 200-PG-23505-09C02-A CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 382 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 18.15 | CML-12 | CML: Pipe Length | 3 | 2016-06-30 | 2016-01-21 | 2014-03-12 | 14.06 | 1.3623 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 |  | 18.3 | 17.2 | 18.4 | 18.7 | 0.65574
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-1 | 250-PG-23004-06C03-A CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 23369 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 |  |  | John Wilson | 2017-03-23 13:50 | Loss within CA no further action required. | [31 empty] | 18.675 | CML-1 | CML: Elbow | 6 | 2027-08-16 | 2024-11-28 | 2015-07-21 07:00 | 8.55 | 0.68295 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.8 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.25 |  | 19.6 | 19.5 | 16.8 | 18.8 | 1.2997
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-12 | 50-PL-23041-06C03 CML-12 | Yes | FPSO 2013 | Pipe Wall Thickness | 10225 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.525 | CML-12 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 7.9159 | A1: Outside Quadrant |  | 5.07 |  |  | 7.6 | 12 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 7.6 | 10.4 | 10.2 | 9.9 | 1.2997
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-37 | 300-PF-20001-03C03-P CML-37 | yes | FPSO 2014 | Pipe Wall Thickness | 21175 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 14.45 | CML-37 | CML: Fitting | 6 | 2019-09-20 | 2018-08-02 | 2014-07-16 07:30 | 4.9 | 1.4856 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 12.6 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 14.5 | 15.4 | 15.3 | 12.6 | 1.2974
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-15 | 50-PL-23042-09C03 CML-15 | yes | FPSO 2013 | Pipe Wall Thickness | 10080 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 11.625 | CML-15 | CML: type TBC | 6 | 2016-05-08 | 2015-11-30 | 2013-11-07 | 2.5 | 2.9154 | A3: Inside Quadrant |  | 5.07 | 2.5 | 3.785 | 9.8 | 6 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 12.5 | 12.6 | 9.8 | 11.6 | 1.2971
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23042-09C03 | CML-7 | 50-PL-23042-09C03 CML-7 | yes | FPSO 2013 | Pipe Wall Thickness | 10072 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 11.8 | CML-7 | CML: type TBC | 6 | 2016-08-08 | 2016-02-16 | 2013-11-07 | 2.5 | 2.6858 | A1: Outside Quadrant |  | 5.07 | 2.5 | 3.785 | 9.9 | 12 O'Clock | 50 | 11.07 | 50-PL-23042-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 12.1 | 12.6 | 12.6 | 1.2884
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-1 | 50-DH-56137-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20540 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 18.75 | CML-1 | CML: Elbow | 6 | 2096-09-16 | 2085-01-22 | 2014-05-27 08:00 | 2.8 | 0 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 17.6 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 | -0.67049 | 17.6 | 17.7 | 19.6 | 20.1 | 1.2871
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-16 | 300-PG-20004-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 6139 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 16.425 | CML-16 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 15 | 6 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.1 |  | 17.3 | 15.7 | 15 | 17.7 | 1.2842
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-17 | 100-WC-40516-1CG CML-17 | yes | FPSO 2015 | Pipe Wall Thickness | 8690 | Material Class Not Selectable.Line is FFS. Action: to recheck in two year(Feb. 2017) to confirm CR. | 2015-02-13 07:00 | 2015-02-13 14:00 | Check Corrosion Rate of 0.68mm/ yr |  | Administrator | 2015-09-08 11:57 | [32 empty] | 8.075 | CML-17 | CML: Pipe Length | 3 | 2022-04-25 | 2020-01-26 | 2015-02-13 07:00 | 2.5 | 0.68039 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 7.4 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.3 | 8.1 | 7.4 | 8.5 | 0.47871
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-30 | 300-PF-20001-03C03-P CML-30 | yes | FPSO 2014 | Pipe Wall Thickness | 21168 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 16.275 | CML-30 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.4 | 3 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 16.5 | 14.4 | 17.1 | 17.1 | 1.2816
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-12 | 200-PG-23013-09C03-A CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 10996 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 16.65 | CML-12 | CML: Elbow | 6 | 2014-09-25 | 2014-06-15 | 2014-01-10 | 10.22 | 7.8892 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 15.8 | 9 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.58 |  | 18.5 | 16.5 | 15.8 | 15.8 | 1.2767
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-33 | 350-FL-43512-01C02 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 6547 | Rope Access. No access to CML''s 34 - 60 due to Flare | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.825 | CML-33 | CML: Pipe Length | 3 | 2020-11-30 | 2019-12-05 | 2015-03-30 07:00 | 2.5 | 0.72202 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 6.6 | 6 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 8.3 | 7 | 6.6 | 9.4 | 1.2764
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-12 | 300-PG-20506-03C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 13226 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.275 | CML-12 | CML: type TBC | 6 | 2019-05-18 | 2018-04-21 | 2014-02-04 15:00 | 4.9 | 1.5708 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 6 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 13.7 | 14.1 | 13.2 | 16.1 | 1.2712
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-33 | 150-PG-23506-25C02 CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 20087 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.475 | CML-33 | CML: Elbow | 3 | 2015-12-23 | 2015-05-01 | 2014-05-29 07:00 | 15.88 | 2.3676 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 19.6 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.72 | 255.501 | 21.9 | 22 | 19.6 | 22.4 | 1.2685
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-17 | 50-DN-56101-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 857 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.025 | CML-17 | CML: Elbow | 3 | 2016-06-10 | 2016-10-07 | 2014-04-02 14:00 | 2.5 | 1.0033 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.2 | 5.1 | 5.1 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-1 | 50-DC-57044-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2139 | Rope Access | 2014-03-29 10:30 | 2014-03-29 12:00 | Check Corrosion Rate of 1.017mm/ yr | [35 empty] | 4.95 | CML-1 | CML: Elbow | 3 | 2016-05-26 | 2016-09-20 | 2014-03-29 10:30 | 2.5 | 1.0171 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 5.1 | 4.7 | 5.1 | 0.19149
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-40 | 300-PF-20001-03C03-P CML-40 | yes | FPSO 2014 | Pipe Wall Thickness | 21178 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 15.225 | CML-40 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.4 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 14.4 | 14.8 | 14.6 | 17.1 | 1.2606
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-13 | 200-PG-23505-09C02-A CML-13 | yes | FPSO 2014 | Pipe Wall Thickness | 2694 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 17.9 | CML-13 | CML: Pipe Length | 3 | 2016-07-01 | 2016-01-22 | 2014-03-12 09:00 | 14.06 | 1.3605 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | 0 | 18 | 17.2 | 18.1 | 18.3 | 0.48305
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-30 | 50-DC-57020-01C02 CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 2472 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 1.049mm/ yr | [35 empty] | 5.6 | CML-30 | CML: type TBC | 3 | 2016-04-24 | 2016-08-15 | 2014-03-20 09:30 | 2.5 | 1.0486 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 6.2 | 6.3 | 4.7 | 0.77889
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-20 | 50-DC-57020-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 2462 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 1.049mm/ yr | [35 empty] | 5.3 | CML-20 | CML: type TBC | 3 | 2016-04-24 | 2016-08-15 | 2014-03-20 09:30 | 2.5 | 1.0486 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.7 | 5.7 | 4.7 | 5.1 | 0.4899
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-4 | 300-PG-20048-03C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23346 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 15.375 | CML-4 | CML: Elbow | 6 | 2048-06-27 | 2042-03-07 | 2015-07-20 07:00 | 4.9 | 0.26697 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 9 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | -0.18868 | 15.7 | 16.7 | 15.4 | 13.7 | 1.2473
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-3 | 250-PG-23004-06C03-A CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 24504 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 |  |  | John Wilson | 2017-03-23 13:49 | Loss within CA no further action required. | [31 empty] | 18.575 | CML-3 | CML: Pipe Length | 6 | 2040-09-16 | 2035-06-30 | 2015-07-21 07:00 | 8.55 | 0.35551 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.5 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.95 | -130764301.6631 | 20.2 | 18.9 | 17.5 | 17.7 | 1.2473
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23017-03C03-A | CML-7 | 250-PG-23017-03C03-A CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 10981 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 16.625 | CML-7 | CML: Pipe Length | 6 | 2096-05-30 | 2084-11-28 | 2014-01-09 | 4.4 | 0 | A1: Outside Quadrant |  | 6.7 | 4.4 | 5.55 | 15.5 | 12 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 15.5 | 17.7 | 15.6 | 17.7 | 1.242
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-17 | 250-PG-23015-06C03-A CML-17 | yes | FPSO 2014 | Pipe Wall Thickness | 13049 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 19.725 | CML-17 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 13:00 | 8.55 | 0 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 18.6 | 3 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.05 |  | 19.9 | 18.6 | 21.4 | 19 | 1.242
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-2 | 80-FL-43015-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20407 | Reviewed on 20/11/14. Line is FFS. Repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-20 11:12 | [32 empty] | 6.85 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 12 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 8.5 | 6 | 7.1 | 1.2396
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-7 | 50-DH-56137-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20546 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 19.25 | CML-7 | CML: Elbow | 6 | 2096-09-16 | 2085-01-22 | 2014-05-27 08:00 | 2.8 | 0 | A2: Right Quadrant |  | 5.13 | 2.8 | 3.965 | 17.5 | 3 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.7 | 3.0172 | 19.9 | 17.5 | 19.3 | 20.3 | 1.2369
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-18 | 300-PG-20004-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 6141 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 15.475 | CML-18 | CML: Elbow | 6 | 2161-12-15 | 2135-03-31 | 2014-07-11 07:30 | 4.9 | 0.06304 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 17 | 14.8 | 15.9 | 14.2 | 1.2366
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-18 | 250-PG-23004-06C03-A CML-18 | yes | FPSO 2014 | Pipe Wall Thickness | 13018 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 17.8 | CML-18 | CML: Pipe Length | 6 | 2017-10-21 | 2016-12-19 | 2014-01-11 15:00 | 8.55 | 2.2099 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 16.9 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.35 |  | 17.1 | 19.6 | 17.6 | 16.9 | 1.2356
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-26 | 50-DH-56137-01C02 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 23454 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 18 | CML-26 | CML: Elbow | 3 | 2021-02-26 | 2017-11-24 | 2015-07-23 07:00 | 2.5 | 2.4449 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 16.2 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.7 |  | 18.5 | 19 | 18.3 | 16.2 | 1.2356
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-14 | 80-PW-20024-01C03-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23058 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 10.825 | CML-14 | CML: Reducer | 6 | 2039-10-30 | 2035-10-21 | 2015-05-06 07:00 | 2.5 | 0.3265 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 10.5 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 10.9 | 11.1 | 10.8 | 10.5 | 0.25
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-26 | 300-PF-20003-03C03-P CML-26 | yes | FPSO 2014 | Pipe Wall Thickness | 21764 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 18.475 | CML-26 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.6 | 12 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.7 |  | 17.6 | 20.3 | 18.1 | 17.9 | 1.2339
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-2 | 50-PW-44015-01X01 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10285 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.65 | CML-2 | CML: Elbow | 3 | 2014-08-07 | 2014-09-22 | 2013-11-10 | 2.5 | 2.5685 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.4 | 5 | 4.8 | 4.4 | 0.3
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23016-06C03-A | CML-8 | 250-PG-23016-06C03-A CML-8 | yes | FPSO 2014 | Pipe Wall Thickness | 5503 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [35 empty] | Low alarm breach | 12.725 | CML-8 | CML: Elbow | 6 | 2014-10-01 | 2014-06-30 | 2014-05-31 07:00 | 8.55 | 7.2741 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 11 | 6 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.45 |  | 13.9 | 13 | 11 | 13 | 1.2258
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-4 | 300-PG-20049-03C03-P CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24471 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.409mm/ yr | 39 | Kirstie Albone | 2017-03-23 13:25 | [32 empty] | 14.025 | CML-4 | CML: Elbow | 6 | 2036-04-29 | 2032-03-16 | 2016-07-09 07:00 | 4.9 | 0.40867 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13 | 12 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | 0 | 13 | 13.6 | 15.8 | 13.7 | 1.223
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-29 | 250-PL-20006-01C02-P CML-29 | yes | FPSO 2014 | Pipe Wall Thickness | 13199 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.525 | CML-29 | CML: Reducer | 3 | 2025-02-22 | 2027-05-27 | 2014-01-21 13:00 | 3.61 | 0.23343 | A1: Outside Quadrant |  | 3.35 | 3.61 | 3.0831 | 6.2 | 12 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.59 |  | 6.2 | 6.5 | 7 | 6.4 | 0.34034
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-17 | 50-PL-23020-01C03 CML-17 | yes | FPSO 2013 | Pipe Wall Thickness | 10131 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.7 | CML-17 | CML: type TBC | 6 | 2015-04-25 | 2015-04-12 | 2013-11-08 | 2.5 | 3.285 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.3 | 6 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.3 | 10.2 | 7.3 | 9 | 1.2193
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-15 | 80-PW-20024-01C03-P CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23059 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 10.75 | CML-15 | CML: Reducer | 6 | 2044-10-23 | 2040-01-11 | 2015-05-06 07:00 | 2.5 | 0.27467 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.6 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.6 | 10.7 | 10.8 | 10.9 | 0.1291
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20031-01C03-P | CML-9 | 150-PG-20031-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 23871 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 19.8 | CML-9 | CML: Reducer | 6 | 2098-02-09 | 2085-10-05 | 2014-09-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 18.6 | 3 O'Clock | 150 | 10.97 | 150-PG-20031-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.1 |  | 18.9 | 18.6 | 20.9 | 20.8 | 1.2193
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-14 | 250-PG-23004-06C03-A CML-14 | yes | FPSO 2014 | Pipe Wall Thickness | 13014 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.05 | CML-14 | CML: Elbow | 6 | 2024-01-29 | 2022-01-15 | 2014-01-11 15:00 | 8.55 | 0.90996 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.7 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.15 |  | 20.5 | 19.5 | 17.7 | 18.5 | 1.2152
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-2 | 25-PW-44026-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5755 | Rope access | 2014-06-23 07:00 | 2014-06-23 08:00 | [36 empty] | 8.9667 | CML-2 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.6 | 3 O'Clock | 50 | 5.54 | 50-PW-44026-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  |  | 7.6 | 9.9 | 9.4 | 1.2097
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56142-01C02 | CML-6 | 25-DH-56142-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7527 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 |  |  | Nestor | 2014-11-24 09:40 | [32 empty] | 6.575 | CML-6 | CML: Elbow | 3 | 2021-11-11 | 2021-10-20 | 2015-04-13 07:00 | 2.5 | 0.45538 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 9 O'Clock | 25 | 6.35 | 25-DH-56142-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.4 | 8.3 | 6.1 | 5.5 | 1.2093
WC01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-WC-40006-01C02 | CML-14 | 150-WC-40006-01C02 CML-14 | yes | FPSO 2013 | Pipe Wall Thickness | 10542 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 4.9 | CML-14 | CML: type TBC | 3 | 2014-11-26 | 2014-11-22 | 2013-11-16 | 2.5 | 2.0423 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5 | 4.6 | 4.8 | 5.2 | 0.2582
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23029-25C02-P | CML-1 | 80-PG-23029-25C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20559 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [36 empty] | 18.35 | CML-1 | CML: Elbow | 3 | 2090-10-23 | 2076-08-20 | 2014-07-02 07:00 | 7.5 | 0 | A2: Right Quadrant |  | 12.24 | 7.5 | 8.9175 | 17.1 | 3 O'Clock | 80 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 17.8 | 17.1 | 19.9 | 18.6 | 1.2014
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-41 | 150-PG-23506-25C02 CML-41 |  | FPSO 2014 | Pipe Wall Thickness | 2815 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.075 | CML-41 | CML: Pipe Length | 3 | 2017-12-18 | 2016-10-24 | 2014-03-15 09:00 | 15.88 | 1.3336 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 20.9 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.02 |  | 21.2 | 22.9 | 23.3 | 20.9 | 1.201
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-12 | 250-PG-23004-06C03-A CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 13012 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.325 | CML-12 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 18.5 | 3 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.95 |  | 18.8 | 18.5 | 18.9 | 21.1 | 1.1955
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-FH-43507-01C02 | CML-1 | 100-FH-43507-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23400 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 17.875 | CML-1 | CML: Pipe Length | 3 | 2022-03-30 | 2019-06-20 | 2015-07-22 07:00 | 10.17 | 0.91566 | A4: Left Quadrant |  | 15.26 | 10.17 | 12.715 | 16.3 | 9 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.13 | -0.26134 | 17.9 | 18.1 | 19.2 | 16.3 | 1.1955
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-13 | 50-PW-44015-01X01 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10296 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.625 | CML-13 | CML: Reducing Tee | 3 | 2014-08-07 | 2014-09-22 | 2013-11-10 | 2.5 | 2.5685 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.6 | 4.5 | 5 | 4.4 | 0.263
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-FH-43507-01C02 | CML-3 | 100-FH-43507-01C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 20722 | Protective mesh removed | 2014-06-30 10:30 | 2014-06-30 12:00 | [36 empty] | 17.75 | CML-3 | CML: Elbow | 6 | 2016-01-29 | 2015-07-07 | 2014-06-30 10:30 | 10.22 | 3.9051 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 16.4 | 12 O'Clock | 100 | 20.62 | 200-PG-23014-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.18 |  | 16.4 | 17.2 | 18.3 | 19.1 | 1.1902
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-8 | 300-PG-20048-03C03-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23347 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.125 | CML-8 | CML: Elbow | 6 | 2036-05-24 | 2032-04-05 | 2015-07-20 07:00 | 4.9 | 0.40749 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 | -0.37736 | 13.4 | 15.9 | 13.7 | 13.5 | 1.1899
VA01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-VA-23054-01C02 | CML-24 | 25-VA-23054-01C02 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 22889 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 13.875 | CML-24 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 12.9 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 | -6.3969 | 13.4 | 13.6 | 12.9 | 15.6 | 1.1871
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-12 | 50-CG-38487-09C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20851 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 12.1 | CML-12 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-10-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 11.1 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 | 2.4066 | 11.1 | 13.6 | 12.5 | 11.2 | 1.186
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-1 | 50-PG-44022-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5844 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 10.3 | CML-1 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-06-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.8 | 12 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 10.4 | 11.7 | 10.3 | 1.186
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-13 | 250-PG-23004-06C03-A CML-13 | yes | FPSO 2015 | Pipe Wall Thickness | 23380 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.575 | CML-13 | CML: Elbow | 6 | 2058-07-05 | 2049-11-23 | 2015-07-21 07:00 | 8.55 | 0.21518 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 17.8 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.25 | 0.9853 | 20.2 | 20.2 | 20.1 | 17.8 | 1.1843
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-9 | 300-PG-20049-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21495 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | [36 empty] | 15.15 | CML-9 | CML: Elbow | 6 | 2157-03-29 | 2131-05-19 | 2014-06-28 10:45 | 4.9 | 0.0651 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 6 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 15.2 | 16.8 | 14.2 | 14.4 | 1.1818
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45044-03C02 | CML-1 | 50-FG-45044-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20801 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.75 | CML-1 | CML: Elbow | 3 | 2063-09-30 | 2050-09-06 | 2014-07-18 11:00 | 2.5 | 0.12389 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 11.4 | 9.4 | 9.6 | 8.6 | 1.1818
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-1 | 80-PL-44008-01C02 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 23769 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 5.975 | CML-1 | CML: Equal Tee | 3 | 2027-10-27 | 2029-07-01 | 2015-04-18 07:00 | 2.5 | 0.20742 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 9 O'Clock | 50 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.24357 | 5.9 | 5.8 | 7.1 | 5.1 | 0.83016
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-15 | 80-CG-38459-09C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 6171 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 18.4 | CML-15 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 17.4 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.5 |  | 20.1 | 17.4 | 18.2 | 17.9 | 1.1804
PG02 | Montara_Topside | No | Separation (20) | Pipework | 300-PG-20025-03D01-P | CML-2 | 300-PG-20025-03D01-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22797 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 6.175 | CML-2 | CML: Equal Tee | 1 | 2032-06-06 | 2026-09-28 | 2015-04-29 07:00 | 3.86 | 0.13086 | A1: Outside Quadrant |  | 5.35 | 3.86 | 4.605 | 6.1 | 12 O'Clock | 300 | 6.35 | 300-PG-20025-03D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.24 | 0 | 6.1 | 6.2 | 6.2 | 6.2 | 0.05
PG02 | Montara_Topside | No | Separation (20) | Pipework | 300-PG-20028-03D01-P | CML-2 | 300-PG-20028-03D01-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21329 | Protective mesh removed | 2014-06-27 08:00 | 2014-06-27 09:00 | [36 empty] | 6.125 | CML-2 | CML: Reducing Tee | 1 | 2024-02-01 | 2020-11-22 | 2014-06-27 08:00 | 3.86 | 0.23318 | A1: Outside Quadrant |  | 5.35 | 3.86 | 4.605 | 6.1 | 6 O'Clock | 300 | 6.35 | 300-PG-20028-03D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.24 |  | 6.1 | 6.1 | 6.1 | 6.2 | 0.05
PG02 | Montara_Topside | No | Separation (20) | Pipework | 300-PG-20025-03D01-P | CML-2 | 300-PG-20025-03D01-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21322 | Protective mesh removed | 2014-06-27 07:00 | 2014-06-27 08:00 | [36 empty] | 6.425 | CML-2 | CML: Equal Tee | 1 | 2024-02-01 | 2020-11-22 | 2014-06-27 07:00 | 3.86 | 0.2332 | A2: Right Quadrant |  | 5.35 | 3.86 | 4.605 | 6.1 | 9 O'Clock | 300 | 6.35 | 300-PG-20025-03D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.24 |  | 6.8 | 6.1 | 6.7 | 6.1 | 0.37749
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-2 | 250-PW-44010-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21919 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 9.5 | CML-2 | CML: Equal Tee | 6 | 2022-10-06 | 2022-03-26 | 2014-06-24 09:30 | 2.5 | 0.72362 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.5 | 6 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9 | 11.2 | 8.5 | 9.3 | 1.1804
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-2 | 250-PW-44010-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5821 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 9.5 | CML-2 | CML: Equal Tee | 6 | 2022-10-06 | 2022-03-26 | 2014-06-24 09:30 | 2.5 | 0.72362 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.5 | 6 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9 | 11.2 | 8.5 | 9.3 | 1.1804
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-4 | 300-PG-20048-03C03-P CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24478 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 15.35 | CML-4 | CML: Elbow | 6 | 2064-06-19 | 2055-04-15 | 2016-07-09 07:00 | 4.9 | 0.18342 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | 0 | 13.7 | 15.6 | 15.6 | 16.5 | 1.179
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38477-01C02-P | CML-4 | 50-CG-38477-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1783 | Rope access | 2014-04-28 08:00 | 2014-04-28 09:00 | [36 empty] | 5.95 | CML-4 | CML: Elbow | 3 | 2021-07-11 | 2022-05-25 | 2014-04-28 08:00 | 2.5 | 0.37455 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FH-43129-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 7.7 | 5.6 | 5.2 | 5.3 | 1.179
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-5 | 80-CG-38459-09C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23702 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 14.475 | CML-5 | CML: Reducing Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 12.9 | 12 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 12.9 | 15.7 | 14.9 | 14.4 | 1.1786
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-19 | 250-PG-23004-06C03-A CML-19 | yes | FPSO 2014 | Pipe Wall Thickness | 13019 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.25 | CML-19 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 18.5 | 3 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.95 |  | 18.8 | 18.5 | 18.7 | 21 | 1.1733
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-40 | 300-PF-20501-03C03-P CML-40 | yes | FPSO 2015 | Pipe Wall Thickness | 23536 | Re-check | 2015-07-29 07:00 | 2015-07-29 12:00 | [36 empty] | 13.525 | CML-40 | CML: type TBC | 6 | 2023-09-06 | 2021-11-01 | 2015-07-29 07:00 | 4.9 | 0.91216 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.3 | 12 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 | 1.0806 | 12.3 | 12.8 | 14.8 | 14.2 | 1.1701
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-11 | 80-CG-38459-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10043 | Rope Access | 2014-01-06 | 2014-01-06 | [36 empty] | 13.5333 | CML-11 | CML: Tee | 6 | 2091-02-10 | 2082-04-06 | 2014-01-06 | 0.97 | 0 | A2: Right Quadrant |  | 2.74 | 0.97 | 1.855 | 12.5 | 3 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.53 |  |  | 12.5 | 14.8 | 13.3 | 1.1676
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44513-01C02 | CML-3 | 80-PL-44513-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 7968 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:06 | [32 empty] | 5.425 | CML-3 | CML: Elbow | 3 | 2025-12-07 | 2027-05-24 | 2015-01-18 10:30 | 2.5 | 0.23867 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 12 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.5 | 5.4 | 5.7 | 0.25
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-31 | 300-PF-20001-03C03-P CML-31 | yes | FPSO 2014 | Pipe Wall Thickness | 21169 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 15.95 | CML-31 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.7 | 3 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 15.7 | 14.7 | 17.5 | 15.9 | 1.159
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-10 | 50-PW-44012-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23169 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.675 | CML-10 | CML: Elbow | 3 | 2018-08-05 | 2019-02-24 | 2015-05-11 07:00 | 2.5 | 0.58664 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 0.53428 | 5 | 4.6 | 4.7 | 4.4 | 0.25
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-13 | 50-DH-56137-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 13084 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 18.875 | CML-13 | CML: Fitting | 6 | 2096-09-16 | 2085-01-22 | 2014-02-07 11:00 | 2.8 | 0 | A2: Right Quadrant |  | 5.13 | 2.8 | 3.965 | 18.2 | 9 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 |  | 20.6 | 18.2 | 18.5 | 18.2 | 1.1587
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-2 | 300-PG-20049-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21488 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | Check Corrosion Rate of 0.623mm/ yr | 39 | Kirstie Albone | 2017-03-23 13:13 | [32 empty] | 14.825 | CML-2 | CML: Elbow | 6 | 2028-06-10 | 2025-09-27 | 2014-06-28 10:45 | 4.9 | 0.62314 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 6 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 16.3 | 15.1 | 13.6 | 14.3 | 1.1587
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-23 | 100-FG-45001-09C02 CML-23 |  | FPSO 2013 | Pipe Wall Thickness | 10438 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 11.075 | CML-23 | CML: type TBC | 3 | 2015-12-26 | 2015-04-20 | 2013-11-13 | 4.7 | 2.4997 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 10 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 10 | 10.6 | 11 | 12.7 | 1.1587
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40500-1CG | CML-14 | 400-WC-40500-1CG CML-14 | yes | FPSO 2015 | Pipe Wall Thickness | 23442 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Medium alarm breach | 9.95 | CML-14 | CML: Elbow | 3 | 2016-05-06 | 2015-02-11 | 2015-07-23 07:00 | 2.5 | 6.4574 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 7.6 | 3 O'Clock | 150 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | 9.2007 | 9.4 | 7.6 | 11.6 | 11.2 | 1.8358
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-14 | 250-PG-23004-06C03-A CML-14 | yes | FPSO 2014 | Pipe Wall Thickness | 20530 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 19.125 | CML-14 | CML: Elbow | 6 | 2040-04-01 | 2035-02-15 | 2014-05-30 09:30 | 8.55 | 0.36159 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.9 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.35 | -0.52605 | 20.5 | 19.6 | 17.9 | 18.5 | 1.1558
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-8 | 100-PG-23028-25C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 447 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.425 | CML-8 | CML: Elbow | 3 | 2027-09-23 | 2023-05-09 | 2014-03-12 09:00 | 9.4 | 0.53908 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 16.7 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 19.1 | 16.7 | 18.9 | 19 | 1.1529
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-9 | 250-PW-20040-03C03-P CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 21393 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 7.4 | CML-9 | CML: Reducer | 6 | 2015-05-04 | 2014-12-10 | 2014-07-12 07:30 | 2.5 | 5.3001 | A1: Outside Quadrant |  | 6.7 | 2.5 | 4.6 | 6.8 | 6 O'Clock | 20 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 9.1 | 6.8 | 6.9 | 1.1343
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-3 | 300-PG-20005-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6159 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 17.3 | CML-3 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 16.3 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.4 |  | 17.6 | 18.8 | 16.3 | 16.5 | 1.1518
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-17 | 150-FL-43456-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 7907 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 5.275 | CML-17 | CML: type TBC | 3 | 2016-05-25 | 2016-03-01 | 2015-01-15 07:00 | 2.5 | 1.5442 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 4.6 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 6 | 5.1 | 5.4 | 4.6 | 0.58523
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-18 | 150-FL-43456-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 7908 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 5.375 | CML-18 | CML: type TBC | 3 | 2017-05-02 | 2017-01-10 | 2015-01-15 07:00 | 2.5 | 1.175 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.2 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.6 | 5.5 | 5.2 | 0.20616
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-57066-01C03 | CML-4 | 50-PL-57066-01C03 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 20723 | Protective mesh removed | 2014-06-30 10:30 | 2014-06-30 12:00 | [36 empty] | 18.425 | CML-4 | CML: Elbow | 6 | 2016-07-08 | 2015-11-11 | 2014-06-30 10:30 | 10.22 | 3.3498 | A2: Right Quadrant |  | 14.62 | 10.22 | 12.42 | 17 | 3 O'Clock | 100 | 20.62 | 200-PG-23014-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.78 |  | 18.3 | 17 | 19.8 | 18.6 | 1.15
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-14 | 100-WC-40516-1CG CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8687 | Material Class Not Selectable.Line is FFS. Action: to recheck in two year(Feb. 2017) to confirm CR. | 2015-02-13 07:00 | 2015-02-13 14:00 | Check Corrosion Rate of 0.563mm/ yr |  | Administrator | 2015-09-08 11:56 | [32 empty] | 8.275 | CML-14 | CML: Pipe Length | 3 | 2024-03-03 | 2021-06-15 | 2015-02-13 07:00 | 2.5 | 0.56308 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 7.6 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.4 | 8.2 | 7.6 | 8.9 | 0.53774
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-5 | 50-CG-38488-09C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20823 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.85 | CML-5 | CML: Elbow | 3 | 2034-02-20 | 2028-10-04 | 2014-07-18 11:00 | 2.5 | 0.30088 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 11.2 | 10 | 9.8 | 8.4 | 1.1475
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-57066-01C03 | CML-5 | 50-PL-57066-01C03 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 20724 | Protective mesh removed | 2014-06-30 10:30 | 2014-06-30 12:00 | [36 empty] | 18.475 | CML-5 | CML: Reducer | 6 | 2016-07-08 | 2015-11-11 | 2014-06-30 10:30 | 10.22 | 3.3498 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 17 | 12 O'Clock | 80 | 20.62 | 200-PG-23014-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.78 |  | 17 | 18.6 | 19.8 | 18.5 | 1.1471
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23030-09C02-P | CML-4 | 50-PG-23030-09C02-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 20747 | Protective mesh removed/Rope access | 2014-07-02 09:30 | 2014-07-02 11:00 | [36 empty] | 13.65 | CML-4 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-07-02 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 12.3 | 6 O'Clock | 50 | 8.74 | 50-PG-23030-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 13.1 | 14.6 | 12.3 | 14.6 | 1.1446
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-4 | 200-FH-43038-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12685 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 9.225 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 12 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.8 | 10.8 | 9.2 | 1.1442
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23016-06C03-A | CML-6 | 250-PG-23016-06C03-A CML-6 | yes | FPSO 2016 | Pipe Wall Thickness | 24445 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 |  |  | John Wilson | 2017-03-23 15:44 | [31 empty] | Medium alarm breach | 12 | CML-6 | CML: Elbow | 6 | 2017-03-08 | 2016-06-18 | 2016-07-03 07:00 | 8.55 | 2.575 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 10.3 | 9 O'Clock | 50 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.75 | 0.10899 | 12.6 | 12.7 | 12.4 | 10.3 | 1.1402
CG03 | Montara_Topside | Yes | Steam (55) | Pipework | 80-CG-38459-09C02-P | CML-7 | 80-CG-38459-09C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8837 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 15.75 | CML-7 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 14.4 | 12 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 |  | 14.4 | 15.3 | 16.3 | 17 | 1.1387
FH02 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43313-01S01-P | CML-9 | 150-FH-43313-01S01-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20483 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 8.05 | CML-9 | CML: Elbow | 1 | 2028-06-23 | 2024-01-12 | 2014-10-03 07:00 | 2.5 | 0.30585 | A2: Right Quadrant |  | 6.11 | 2.5 | 3.8606 | 6.7 | 3 O'Clock | 150 | 7.11 | 150-FH-43313-01S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.7 | 6.7 | 8.4 | 9.4 | 1.1387
CG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-CG-38452-09C02-P | CML-34 | 50-CG-38452-09C02-P CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 1440 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 8.4 | CML-34 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 8.9 | 9.2 |  | 1.1358
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-19 | 150-FL-43456-01C02 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 7909 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 5.6 | CML-19 | CML: type TBC | 3 | 2017-10-17 | 2017-06-14 | 2015-01-15 07:00 | 2.5 | 1.052 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.4 | 12 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 5.7 | 5.8 | 0.18257
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-25 | 250-PG-23004-06C03-A CML-25 | yes | FPSO 2014 | Pipe Wall Thickness | 13025 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.925 | CML-25 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.6 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.05 |  | 21.1 | 20.6 | 18.6 | 19.4 | 1.1354
FH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-FH-43507-01C02 | CML-14 | 100-FH-43507-01C02 CML-14 |  | FPSO 2016 | Pipe Wall Thickness | 24429 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.735mm/ yr | [34 empty] | Medium alarm breach | 10.375 | CML-14 | CML: Elbow | 3 | 2018-01-01 | 2016-01-27 | 2016-07-02 07:00 | 2.5 | 4.125 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 8.7 | 12 O'Clock | 150 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 | -1.1638 | 8.7 | 11.2 | 10.7 | 10.9 | 1.1354
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67301-01E01 | CML-7 | 25-GN-67301-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22501 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.5 | CML-7 | CML: Elbow | 3 | 2018-02-04 | 2018-01-23 | 2015-04-20 07:00 | 2.5 | 0.82196 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.8 | 6 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.6 | 5.6 | 4.8 | 6 | 0.50332
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44513-01C02 | CML-2 | 80-PL-44513-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 7967 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:05 | [32 empty] | 5.425 | CML-2 | CML: Elbow | 3 | 2025-12-07 | 2027-05-24 | 2015-01-18 10:30 | 2.5 | 0.23867 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 3 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.1 | 5.4 | 5.5 | 0.25
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71311-01K01 | CML10 | 80-WF-71311-01K01 CML10 |  | FPSO 2015 | Pipe Wall Thickness | 7255 |  | 2015-04-09 07:00 | 2015-04-09 15:00 |  |  | Nestor | 2014-11-20 17:42 | [32 empty] | 5.175 | CML10 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-04-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 4.8 | 3 O'Clock | 80 | 2.5 | 80-WF-71311-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 4.8 | 5.7 | 5.1 | 0.37749
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-16 | 80-CG-38459-09C02-P CML-16 | yes | FPSO 2015 | Pipe Wall Thickness | 23383 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 20.8 | CML-16 | CML: Pipe Length | 6 | 2110-07-06 | 2091-12-17 | 2015-07-21 07:00 | 8.55 | 0 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 20.2 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.65 | 0.65687 | 20.2 | 20.3 | 22.5 | 20.2 | 1.1343
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71337-01K01 | CML-4 | 100-WF-71337-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6406 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 5.05 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 4.8 | 9 O'Clock | 100 | 3 | 100-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 5.1 | 5 | 4.8 | 0.20817
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-11 | 150-FL-43456-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 7901 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.075 | CML-11 | CML: type TBC | 3 | 2019-02-17 | 2018-09-07 | 2015-01-15 07:00 | 2.5 | 0.80593 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.8 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 5.9 | 6.2 | 5.8 | 0.27538
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71400-01K01 | CML-44 | 80-WF-71400-01K01 CML-44 |  | FPSO 2015 | Pipe Wall Thickness | 5289 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 4.95 | CML-44 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 4.8 | 9 O'Clock | 80 | 2.5 | 80-WF-71400-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 4.9 | 4.8 | 4.8 | 0.23805
WD03 | Montara_Topside | No | Potable Water (53) | Pipework | 0100-WZ-53L9001-AS20-00 | CML-1 | 0100-WZ-53L9001-AS20-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5105 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | [36 empty] | 5.5 | CML-1 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 4.8 | 9 O'Clock | 25 | 3.38 | 0100-WZ-53L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6.2 | 5.8 | 5.2 | 4.8 | 0.62183
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-6 | 0200-DC-57L9006-AC21-00 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5046 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.824mm/ yr | [34 empty] | Low alarm breach | 4.925 | CML-6 | CML: type TBC | 3 | 2016-06-07 | 2015-11-05 | 2015-03-05 07:00 | 2.5 | 1.8243 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 4.8 | 12 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.1 | 4.9 | 4.9 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-7 | 0200-DC-57L9006-AC21-00 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5047 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.824mm/ yr | [34 empty] | Low alarm breach | 5.175 | CML-7 | CML: type TBC | 3 | 2016-06-07 | 2015-11-05 | 2015-03-05 07:00 | 2.5 | 1.8243 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 4.8 | 12 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.9 | 5.1 | 5.9 | 0.49917
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-14 | 0200-DC-57L9006-AC21-00 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5054 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.824mm/ yr | [34 empty] | Low alarm breach | 5.45 | CML-14 | CML: type TBC | 3 | 2016-06-07 | 2015-11-05 | 2015-03-05 07:00 | 2.5 | 1.8243 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 4.8 | 12 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.7 | 6 | 5.3 | 0.51962
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9001-AS20-00 | CML-3 | 0100-AS-63L9001-AS20-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5012 |  | 2015-03-04 07:00 | 2015-03-04 14:00 | [36 empty] | 4.9 | CML-3 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.38 | 2.5 | 2.7287 | 4.8 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 4.8 | 5.1 | 4.8 | 0.14142
GN02 | Montara_Topside | No | Nitrogen (67) | Pipework | 0100-GN-67L9000-AS20-00 | CML-9 | 0100-GN-67L9000-AS20-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5008 |  | 2015-03-03 07:00 | 2015-03-03 14:00 | [36 empty] | 5.375 | CML-9 | CML: type TBC | 0 | 2021-10-25 | 2019-07-12 | 2015-03-03 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.38 | 2.5 | 2.7287 | 4.8 | 9 O'Clock | 25 | 3.38 | 0100-GN-67L9000-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.9 | 6 | 4.8 | 4.8 | 0.66521
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-13 | 50-GN-67002-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 9072 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.6 | CML-13 | CML: type TBC | 3 | 2020-08-05 | 2021-05-14 | 2015-03-01 09:30 | 2.5 | 0.42309 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.7 | 6.2 | 5.7 | 4.8 | 0.5831
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-10 | 50-AU-63015-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 9041 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | Check Corrosion Rate of 0.423mm/ yr | [35 empty] | 5.25 | CML-10 | CML: type TBC | 3 | 2020-08-05 | 2021-05-13 | 2015-03-01 07:00 | 2.5 | 0.42316 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 5.4 | 4.8 | 5.4 | 0.3
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P |  | 80-SC-55002-01C02-P |  | FPSO 2015 | Pipe Wall Thickness | 8989 | LAGGING REMOVAL REQUIRED | 2015-02-27 07:00 | 2015-02-27 09:00 | [36 empty] | 5.125 | 80-SC-55002-01C02-P | Piping | 3 | 2020-12-18 |  | 2015-02-27 07:00 |  | 0.39581 | A2: Right Quadrant |  |  | 2.5 |  | 4.8 | 3 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 4.8 | 5.2 | 5.1 | 0.25
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-46 | 50-AI-63007-01E01 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 8970 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 5.125 | CML-46 | CML: type TBC | 3 | 2020-07-24 | 2021-04-30 | 2015-02-26 09:00 | 2.5 | 0.4251 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.5 | 4.8 | 5.4 | 4.8 | 0.37749
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-44 | 50-AI-63007-01E01 CML-44 |  | FPSO 2015 | Pipe Wall Thickness | 8968 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 5.075 | CML-44 | CML: type TBC | 3 | 2020-07-24 | 2021-04-30 | 2015-02-26 09:00 | 2.5 | 0.4251 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 5.4 | 4.8 | 5 | 0.25
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-29 | 50-AI-63007-01E01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 8953 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 5.15 | CML-29 | CML: type TBC | 3 | 2020-07-24 | 2021-04-30 | 2015-02-26 09:00 | 2.5 | 0.4251 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 4.8 | 5.3 | 5.5 | 0.31091
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-18 | 50-AI-63007-01E01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8942 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 5.4 | CML-18 | CML: type TBC | 3 | 2020-07-24 | 2021-04-30 | 2015-02-26 09:00 | 2.5 | 0.4251 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.9 | 4.8 | 5.4 | 5.5 | 0.45461
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-13 | 50-AI-63007-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8937 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 5.225 | CML-13 | CML: type TBC | 3 | 2020-07-24 | 2021-04-30 | 2015-02-26 09:00 | 2.5 | 0.4251 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 4.8 | 5.6 | 5.3 | 0.3304
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-5 | 50-AI-63007-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8929 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 5.2 | CML-5 | CML: type TBC | 3 | 2020-07-24 | 2021-04-30 | 2015-02-26 09:00 | 2.5 | 0.4251 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5.4 | 5.4 | 4.8 | 0.28284
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-4 | 50-AI-63007-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8928 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 4.875 | CML-4 | CML: type TBC | 3 | 2020-07-24 | 2021-04-30 | 2015-02-26 09:00 | 2.5 | 0.4251 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5 | 4.9 | 4.8 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-3 | 50-AI-63007-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8927 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 5 | CML-3 | CML: type TBC | 3 | 2020-07-24 | 2021-04-30 | 2015-02-26 09:00 | 2.5 | 0.4251 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5 | 4.8 | 5.4 | 0.28284
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-1 | 50-AI-63007-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8925 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.425mm/ yr | [35 empty] | 5.35 | CML-1 | CML: type TBC | 3 | 2020-07-24 | 2021-04-30 | 2015-02-26 09:00 | 2.5 | 0.4251 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.7 | 4.8 | 5.4 | 5.5 | 0.3873
SD02 | Montara_Topside | No | Steam (55) | Pipework | 50-SL-55003-01C02-P | CML-2 | 50-SL-55003-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8854 |  | 2015-02-24 11:00 | 2015-02-24 12:00 | [36 empty] | 4.975 | CML-2 | CML: type TBC | 3 | 2020-07-16 | 2021-04-21 | 2015-02-24 11:00 | 2.5 | 0.42639 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-SL-55003-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 4.8 | 4.8 | 5.2 | 0.20616
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-12 | 150-FL-43456-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 7902 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.2 | CML-12 | CML: type TBC | 3 | 2019-08-09 | 2019-02-13 | 2015-01-15 07:00 | 2.5 | 0.74441 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.9 | 3 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.3 | 5.9 | 6.2 | 6.4 | 0.21602
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-8 | 250-PW-20040-03C03-P CML-8 | yes | FPSO 2014 | Pipe Wall Thickness | 21392 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 8.025 | CML-8 | CML: Elbow | 6 | 2015-08-06 | 2015-02-23 | 2014-07-12 07:30 | 2.5 | 4.6713 | A2: Right Quadrant |  | 6.7 | 2.5 | 4.6 | 7.5 | 9 O'Clock | 40 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 9.6 | 7.5 | 7.5 | 7.5 | 1.05
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62005-01C02 | CML-2 | 50-DO-62005-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8055 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5 | CML-2 | CML: type TBC | 3 | 2020-02-27 | 2020-11-17 | 2015-01-21 07:30 | 2.5 | 0.45068 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DO-62005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 5.2 | 4.9 | 4.8 | 0.18257
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62001-01C02 | CML-7 | 50-DO-62001-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8047 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 4.975 | CML-7 | CML: type TBC | 3 | 2020-02-27 | 2020-11-17 | 2015-01-21 07:30 | 2.5 | 0.45068 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DO-62001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.3 | 4.8 | 5 | 0.23629
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62001-01C02 | CML-4 | 50-DO-62001-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8044 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.05 | CML-4 | CML: type TBC | 3 | 2020-02-27 | 2020-11-17 | 2015-01-21 07:30 | 2.5 | 0.45068 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DO-62001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.2 | 5.3 | 4.9 | 0.23805
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-11 | 200-PG-24001-09C02 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10267 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 17.725 | CML-11 | CML: Elbow | 3 | 2015-10-27 | 2015-01-06 | 2013-11-09 | 9.2 | 3.7633 | A2: Right Quadrant |  | 15.26 | 9.2 | 12.23 | 16.6 | 3 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 18.7 | 16.6 | 16.9 | 18.7 | 1.1325
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-38 | 300-PF-20501-03C03-P CML-38 | yes | FPSO 2014 | Pipe Wall Thickness | 21714 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 17.325 | CML-38 | CML: type TBC | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 16.2 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 17.1 | 18.9 | 17.1 | 16.2 | 1.1325
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22324 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 6.125 | CML-2 | CML: type TBC | 3 | 2033-08-02 | 2035-10-02 | 2014-05-06 07:00 | 2.5 | 0.15061 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 7.8 | 5.8 | 5.4 | 5.5 | 1.1295
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1844 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 6.125 | CML-2 | CML: type TBC | 3 | 2033-08-02 | 2035-10-02 | 2014-05-06 07:00 | 2.5 | 0.15061 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 7.8 | 5.8 | 5.4 | 5.5 | 1.1295
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-8 | 80-FH-43151-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2242 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 7 | CML-8 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 7.6 |  | 7.7 | 1.1269
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-3 | 150-FL-43456-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7893 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.275 | CML-3 | CML: type TBC | 3 | 2020-02-29 | 2019-08-20 | 2015-01-15 07:00 | 2.5 | 0.68289 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.4 | 6.7 | 6 | 0.34034
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-20 | 150-FL-43456-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 7910 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.475 | CML-20 | CML: type TBC | 3 | 2020-10-29 | 2020-04-01 | 2015-01-15 07:00 | 2.5 | 0.62136 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.1 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.9 | 6.6 | 6.3 | 6.1 | 0.35
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-13 | 50-WC-40071-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7726 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.46mm/ yr |  | Administrator | 2015-09-08 09:35 | [32 empty] | 4.9 | CML-13 | CML: Pipe Length | 3 | 2020-01-09 | 2020-09-24 | 2015-01-09 13:00 | 2.5 | 0.45971 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 1.1361 | 5.1 | 4.8 | 4.9 | 4.8 | 0.14142
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-2 | 25-VA-23054-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 6125 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 16.85 | CML-2 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 15.3 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 15.3 | 17 | 18 | 17.1 | 1.1269
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-12 | 200-FH-43037-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12681 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 9.475 | CML-12 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.1 | 12 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 9.1 | 10.7 | 10 | 1.1266
CG03 | Montara_Topside | Yes | Steam (55) | Pipework | 80-CG-38459-09C02-P | CML-4 | 80-CG-38459-09C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8834 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 15.65 | CML-4 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 14.4 | 12 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 |  | 14.4 | 16.6 | 16.6 | 15 | 1.124
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-6 | 80-CG-38459-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20545 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 15.55 | CML-6 | CML: Pipe Length | 6 | 2096-09-16 | 2085-01-22 | 2014-05-27 08:00 | 2.8 | 0 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 14.3 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 | -11.3984 | 14.3 | 16.5 | 16.5 | 14.9 | 1.124
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20062-01C03-P | CML-1 | 250-PG-20062-01C03-P CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 21538 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 9.525 | CML-1 | CML: Fitting | 6 | 2019-05-12 | 2019-01-08 | 2014-07-13 07:30 | 2.5 | 1.1381 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 8 | 3 O'Clock | 250 | 9.27 | 250-PG-20062-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 9.8 | 8 | 9.6 | 10.7 | 1.1236
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-5 | 50-DH-56137-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20544 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 18.675 | CML-5 | CML: Pipe Length | 6 | 2096-09-16 | 2085-01-22 | 2014-05-27 08:00 | 2.8 | 0 | A2: Right Quadrant |  | 5.13 | 2.8 | 3.965 | 17.4 | 3 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.6 | -21.4558 | 18.2 | 17.4 | 19.1 | 20 | 1.1236
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-1 | 50-PW-44012-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23160 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.7 | CML-1 | CML: Elbow | 3 | 2018-08-05 | 2019-02-24 | 2015-05-11 07:00 | 2.5 | 0.58664 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 6 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 0.80142 | 4.7 | 4.9 | 4.4 | 4.8 | 0.21602
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-9 | 250-PG-23003-06C02-PA CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 24247 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 13.6 | CML-9 | CML: Elbow | 3 | 2016-07-29 | 2016-01-26 | 2014-09-24 07:00 | 7.9 | 2.2723 | A2: Right Quadrant |  | 12.09 | 7.9 | 9.0519 | 12.1 | 3 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 14.3 | 12.1 | 13.4 | 14.6 | 1.1225
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-9 | 250-PG-23003-06C02-PA CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20527 | Reviewed 20/11/14. FFS. CML rechecked in Sep.15. Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 |  |  | Nestor | 2014-11-20 13:59 | [32 empty] | 13.6 | CML-9 | CML: Elbow | 3 | 2016-07-29 | 2016-01-26 | 2014-09-24 07:00 | 7.9 | 2.2723 | A2: Right Quadrant |  | 12.09 | 7.9 | 9.0519 | 12.1 | 3 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 14.3 | 12.1 | 13.4 | 14.6 | 1.1225
FG02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-FG-45455-01C02-E | CML-15 | 25-FG-45455-01C02-E CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 3438 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 7.15 | CML-15 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6 | 12 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.5 | 8.5 | 7.6 | 1.121
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-12 | 50-DC-57450-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20328 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | Check Corrosion Rate of 0.565mm/ yr | [35 empty] | 5.225 | CML-12 | CML: Elbow | 3 | 2018-12-10 | 2019-07-14 | 2014-10-05 07:00 | 2.5 | 0.54978 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 20 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5 | 5.9 | 4.8 | 0.47871
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-2 | 150-FL-43456-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7892 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.625 | CML-2 | CML: type TBC | 3 | 2020-10-29 | 2020-04-01 | 2015-01-15 07:00 | 2.5 | 0.62136 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.1 | 3 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7.4 | 6.1 | 6.6 | 6.4 | 0.55603
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-10 | 50-CG-38465-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20873 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.125 | CML-10 | CML: Elbow | 3 | 2018-12-06 | 2019-07-10 | 2014-10-04 07:00 | 2.5 | 0.5509 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 4.8 | 5.7 | 4.8 | 0.4272
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-6 | 50-CG-38465-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20869 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.075 | CML-6 | CML: Elbow | 3 | 2018-12-06 | 2019-07-10 | 2014-10-04 07:00 | 2.5 | 0.5509 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 4.9 | 5.2 | 4.8 | 0.27538
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-5 | 50-CG-38465-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20868 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 4.9 | CML-5 | CML: Elbow | 3 | 2018-12-06 | 2019-07-10 | 2014-10-04 07:00 | 2.5 | 0.5509 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.9 | 4.9 | 5 | 0.08165
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38464-01C02 | CML-4 | 50-CG-38464-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20838 | Reviewed on 20/11/14. FFS. CML to be rechecked Oct.16. This line has not been RBI assessed. | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 16:17 | [32 empty] | 5.2 | CML-4 | CML: Elbow | 3 | 2018-12-06 | 2019-07-10 | 2014-10-04 07:00 | 2.5 | 0.5509 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-CG-38464-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 4.8 | 5.6 | 5 | 0.36515
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38464-01C02 | CML-1 | 50-CG-38464-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20835 | Reviewed on 20/11/14. FFS. CML to be rechecked Oct.16. This line has not been RBI assessed. | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 16:14 | [32 empty] | 4.925 | CML-1 | CML: Elbow | 3 | 2018-12-06 | 2019-07-10 | 2014-10-04 07:00 | 2.5 | 0.5509 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-CG-38464-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 4.8 | 5 | 5 | 0.095743
FL02 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FL-43454-01C02-P | CML-25 | 50-FL-43454-01C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 21276 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 10.1 | CML-25 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.1 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.7 | 9.9 | 11.7 | 1.1195
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-5 | 100-DH-56088-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5198 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 7.675 | CML-5 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 12 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 8.2 | 8.8 | 7.5 | 1.1177
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-7 | 50-CG-38487-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20846 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 9.1 | CML-7 | CML: Pipe Length | 3 | 2023-05-07 | 2020-10-07 | 2014-10-02 07:00 | 2.5 | 0.6279 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 7.9 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 2.4066 | 8.9 | 9 | 10.6 | 7.9 | 1.1165
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-8 | 150-FL-43456-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7898 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.325 | CML-8 | CML: type TBC | 3 | 2021-08-23 | 2020-12-31 | 2015-01-15 07:00 | 2.5 | 0.55984 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.2 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.3 | 6.3 | 6.2 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-9 | 80-DC-57005-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20255 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | Check Corrosion Rate of 0.687mm/ yr | [35 empty] | 5.2 | CML-9 | CML: type TBC | 3 | 2017-10-06 | 2018-04-09 | 2014-06-02 13:00 | 2.5 | 0.6871 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 12 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.4 | 5.2 | 5.4 | 0.28284
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-6 | 50-FL-43454-01C02-P CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 24265 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 14.9 | CML-6 | CML: Pipe Length | 3 | 2027-09-07 | 2023-06-30 | 2014-09-24 07:00 | 7 | 0.50917 | A4: Left Quadrant |  | 11.27 | 7 | 9.135 | 13.6 | 9 O'Clock | 150 | 14.27 | 150-PG-23026-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 15.5 | 16.1 | 14.4 | 13.6 | 1.1165
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-57 | 300-PF-20001-03C03-P CML-57 | yes | FPSO 2014 | Pipe Wall Thickness | 21195 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 12.85 | CML-57 | CML: Elbow | 6 | 2017-09-10 | 2016-10-25 | 2014-07-16 07:30 | 4.1 | 2.3751 | A4: Left Quadrant |  | 8.27 | 4.1 | 6.185 | 11.6 | 9 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 14.3 | 12.9 | 12.6 | 11.6 | 1.115
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-16 | 50-PL-23021-03C03 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10248 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 12.8333 | CML-16 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 12 | 3 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 14.1 | 12 |  | 12.4 | 1.115
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44513-01C02 | CML-4 | 80-PL-44513-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 7969 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:07 | [32 empty] | 5.425 | CML-4 | CML: Elbow | 3 | 2025-12-07 | 2027-05-24 | 2015-01-18 10:30 | 2.5 | 0.23867 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.5 | 5.6 | 5.1 | 5.5 | 0.22174
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-3 | 50-CG-38474-01C02-P CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24465 | Re-check as requested by N.Sequera | 2016-07-07 07:00 | 2016-07-07 15:00 | Check Corrosion Rate of 0.464mm/ yr |  | John Wilson | 2017-03-24 10:27 | Include this CML in the next inspection. | [31 empty] | 6.95 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2016-07-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 40 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | -0.28854 | 7.3 | 8.3 | 6.5 | 5.7 | 1.1121
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-14 | 80-PW-44016-01C02-P CML-14 | yes | FPSO 2015 | Pipe Wall Thickness | 22916 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.025 | CML-14 | CML: Elbow | 3 | 2020-09-02 | 2021-07-08 | 2015-05-02 07:00 | 2.5 | 0.41176 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 9 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 1.0735 | 5.4 | 4.7 | 5.3 | 4.7 | 0.37749
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-22 | 100-WC-40516-1CG CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 8695 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 | Check Corrosion Rate of 0.387mm/ yr |  | Administrator | 2015-09-08 11:58 | [32 empty] | 8.375 | CML-22 | CML: Fitting | 3 | 2029-01-21 | 2025-02-09 | 2015-02-13 07:00 | 2.5 | 0.38712 | A2: Right Quadrant |  | 5.56 | 2.5 | 4.03 | 7.9 | 3 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.4 | 7.9 | 8.7 | 8.5 | 0.34034
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-9 | 250-PG-23003-06C02-PA CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 10983 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 8.925 | CML-9 | CML: type TBC | 6 | 2014-05-08 | 2014-03-21 | 2014-01-09 | 4.4 | 8.8784 | A4: Left Quadrant |  | 6.7 | 4.4 | 5.55 | 7.3 | 9 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 9.2 | 9.4 | 9.8 | 7.3 | 1.1117
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-26 | 300-PG-20005-03C03-P CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 23363 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.65 | CML-26 | CML: Elbow | 6 | 2048-06-27 | 2042-03-07 | 2015-07-20 07:00 | 4.9 | 0.26697 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | 0.44512 | 15.4 | 15.8 | 13.7 | 13.7 | 1.1091
FL01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-FL-43174-01C02 | CML-3 | 150-FL-43174-01C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 20595 | Rope Access | 2014-05-26 14:00 | 2014-05-26 15:00 | [36 empty] | 9.175 | CML-3 | CML: type TBC | 1 | 2015-07-24 | 2015-01-27 | 2014-05-26 14:00 | 6.91 | 0.85265 | A4: Left Quadrant |  | 7.74 | 6.91 | 7.325 | 7.9 | 9 O'Clock | 50 | 8.74 | 50-PG-23062-25S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.99 |  | 10.6 | 9 | 9.2 | 7.9 | 1.1087
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-22 | 300-PF-20003-03C03-P CML-22 | yes | FPSO 2014 | Pipe Wall Thickness | 21760 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 13.675 | CML-22 | CML: Fitting | 6 | 2019-10-05 | 2018-08-14 | 2014-10-01 07:00 | 4.9 | 1.4756 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.3 | 3 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 14.3 | 12.3 | 13.3 | 14.8 | 1.1087
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-20 | 300-PG-20004-03C03-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23367 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 13.625 | CML-20 | CML: Pipe Length | 6 | 2025-05-21 | 2023-03-27 | 2015-07-20 07:00 | 4.9 | 0.78218 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.6 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 | 0.68319 | 12.6 | 14.9 | 14.2 | 12.8 | 1.1087
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-4 | 400-FH-43500-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5640 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 12.675 | CML-4 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 11.8 | 9 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.3 | 14.3 | 12.3 | 11.8 | 1.1087
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-14 | 25-FG-45455-01C02-E CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1385 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 7.05 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 8.6 | 6.7 | 6.9 | 6 | 1.103
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-1 | 50-PL-23041-06C03 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10214 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 14.5667 | CML-1 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 0 | A1: Outside Quadrant |  | 5.07 |  |  | 13.5 | 12 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 13.5 |  | 14.5 | 15.7 | 1.1015
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-4 | 25-VA-23054-01C02 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 21379 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | [36 empty] | 17.25 | CML-4 | CML: Elbow | 6 | 2102-10-24 | 2088-02-10 | 2014-06-29 13:00 | 5.33 | 0 | A1: Outside Quadrant |  | 8.27 | 5.33 | 6.8 | 15.8 | 12 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.47 |  | 15.8 | 17 | 18 | 18.2 | 1.1
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-16 | 100-DH-56088-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 5209 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 9.275 | CML-16 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.7 | 3 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 10.2 | 7.7 | 9.4 | 9.8 | 1.0996
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-5 | 50-WC-40451-01C02 CML-5 | yes | FPSO 2013 | Pipe Wall Thickness | 10145 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 3.219mm/ yr | [35 empty] | 4.775 | CML-5 | CML: Fitting | 3 | 2014-11-03 | 2014-12-29 | 2013-11-09 | 2.5 | 2.1311 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 100 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.9 | 5 | 4.6 | 0.20616
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 24244 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.775 | CML-6 | CML: Elbow | 3 | 2029-06-10 | 2026-11-15 | 2014-09-24 07:00 | 7.9 | 0.44837 | A1: Outside Quadrant |  | 12.09 | 7.9 | 9.0519 | 14.5 | 12 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 14.5 | 15.4 | 17.1 | 16.1 | 1.0996
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-19 | 50-CG-38001-09C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 10933 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 9 | CML-19 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.8828 | A2: Right Quadrant |  | 5.74 |  |  | 7.6 | 3 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.6 | 8.7 | 7.6 | 10.1 | 9.6 | 1.0985
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20053-01C03-P | CML-4 | 80-PG-20053-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21511 | Protective mesh removed | 2014-06-29 08:00 | 2014-06-29 09:00 | [36 empty] | 14.825 | CML-4 | CML: Equal Tee | 6 | 2099-09-17 | 2086-07-24 | 2014-06-29 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 13.8 | 12 O'Clock | 80 | 11.13 | 80-PG-20053-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 13.8 | 14.1 | 16.2 | 15.2 | 1.0966
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-9 | 50-DH-56109-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20998 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 7.4 | CML-9 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-05-24 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.8 | 8.6 | 8 | 1.0954
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-6 | 50-PL-23041-06C03 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10219 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 11.425 | CML-6 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 2.6691 | A1: Outside Quadrant |  | 5.07 |  |  | 9.9 | 12 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 9.9 | 11.7 | 12.5 | 11.6 | 1.0935
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-5 | 50-DH-56137-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 6161 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 19.2 | CML-5 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 18.5 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.6 |  | 20.8 | 19 | 18.5 | 18.5 | 1.0924
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-4 | 50-PW-44015-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22709 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 4.65 | CML-4 | CML: Elbow | 3 | 2018-07-01 | 2019-01-17 | 2015-04-28 07:00 | 2.5 | 0.59759 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 | 0.23558 | 4.6 | 4.9 | 4.7 | 4.4 | 0.20817
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-15 | 300-PF-20501-03C03-P CML-15 | yes | FPSO 2014 | Pipe Wall Thickness | 21691 | Protective mesh removed. Reviewed on 1/12/14. FFS. Recheck on Sep.15 | 2014-09-28 07:00 | 2014-09-28 15:00 |  |  | Nestor | 2014-12-01 08:52 | [32 empty] | 14.225 | CML-15 | CML: Pipe Length | 6 | 2021-11-12 | 2020-05-06 | 2014-09-28 07:00 | 4.9 | 1.1079 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.8 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 14 | 12.8 | 15.3 | 14.8 | 1.0905
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-9 | 50-CG-38452-09C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23749 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.925 | CML-9 | CML: Elbow | 3 | 2023-11-14 | 2021-02-26 | 2015-10-30 07:00 | 2.5 | 0.5964 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 7.3 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 9.3 | 7.3 | 9.5 | 9.6 | 1.0905
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-8 | 50-PG-44022-01C03-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22983 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.3 | CML-8 | CML: Elbow | 6 | 2063-05-29 | 2062-06-12 | 2015-05-04 07:00 | 2.5 | 0.12473 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 1.2827 | 10.8 | 8.5 | 8.5 | 9.4 | 1.0863
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-4 | 150-PG-20054-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21515 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 12.85 | CML-4 | CML: Elbow | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 11.3 | 9 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 13.8 | 13.3 | 13 | 11.3 | 1.0847
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-4 | 300-PF-20501-03C03-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 21680 | Protective mesh removed | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 15.575 | CML-4 | CML: Equal Tee | 6 | 2190-11-25 | 2158-12-26 | 2014-09-28 07:00 | 4.9 | 0.05276 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 15.4 | 15.9 | 14.2 | 16.8 | 1.0844
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-18 | 50-PL-23041-06C03 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10231 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.925 | CML-18 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 7.4597 | A4: Left Quadrant |  | 5.07 |  |  | 7.8 | 9 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.4 | 8.8 | 8.7 | 7.8 | 1.0813
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-53 | 300-PF-20003-03C03-P CML-53 | yes | FPSO 2014 | Pipe Wall Thickness | 21791 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 19.5 | CML-53 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 18.1 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.2 |  | 19.2 | 20.3 | 20.4 | 18.1 | 1.0801
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-9 | 250-PG-23003-06C02-PA CML-9 | High Priority | FPSO 2015 | Pipe Wall Thickness | 23527 | Re-check on line as Per RBI 2014 Report | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 13.125 | CML-9 | CML: Elbow | 3 | 2018-08-07 | 2017-10-07 | 2015-07-28 07:00 | 7.9 | 1.3862 | A2: Right Quadrant |  | 12.09 | 7.9 | 9.0519 | 12.1 | 3 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 | 0 | 14.2 | 12.1 | 12.3 | 13.9 | 1.0782
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-27 | 300-PF-20501-03C03-P CML-27 | yes | FPSO 2014 | Pipe Wall Thickness | 21703 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 15.65 | CML-27 | CML: type TBC | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.3 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 16.9 | 15.9 | 14.3 | 15.5 | 1.0755
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-44 | 150-PG-23506-25C02 CML-44 |  | FPSO 2014 | Pipe Wall Thickness | 2818 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.925 | CML-44 | CML: Elbow | 3 | 2032-07-08 | 2027-09-08 | 2014-03-15 09:00 | 15.88 | 0.31753 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 21.7 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.82 |  | 24.3 | 22.7 | 23 | 21.7 | 1.072
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-17 | 300-PG-23001-03C03 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 10967 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 16.625 | CML-17 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 15.2 | 6 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.98 |  | 17.4 | 17.5 | 15.2 | 16.4 | 1.072
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-9 | 50-PW-44013-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5733 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 5.125 | CML-9 | CML: Elbow | 3 | 2016-07-04 | 2016-11-03 | 2014-06-22 13:00 | 2.5 | 0.98204 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | -0.32511 | 4.5 | 5.6 | 5.3 | 5.1 | 0.46458
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-5 | 80-CG-38459-09C02-P CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10169 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 15.0667 | CML-5 | CML: type TBC | 6 | 2096-01-05 | 2084-09-16 | 2013-11-09 | 2.81 | 0 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 14.4 | 6 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.59 |  | 14.5 | 16.3 | 14.4 |  | 1.0693
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 2687 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.275 | CML-6 | CML: Elbow | 3 | 2016-01-04 | 2015-08-22 | 2014-03-12 09:00 | 14.06 | 1.6172 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.94 | 0 | 17 | 19.3 | 19 | 17.8 | 1.0689
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 376 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 18.275 | CML-6 | CML: Elbow | 3 | 2016-01-03 | 2015-08-21 | 2014-03-12 | 14.06 | 1.6194 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.94 |  | 17 | 19.3 | 19 | 17.8 | 1.0689
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-2 | 50-PL-23052-09C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10166 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 11.75 | CML-2 | CML: type TBC | 6 | 2018-11-06 | 2018-02-08 | 2013-11-09 | 2.81 | 1.5189 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 10.4 | 3 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.59 |  | 11.8 | 10.4 | 13 | 11.8 | 1.063
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-13 | 200-PG-23505-09C02-A CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 383 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 17.9 | CML-13 | CML: Pipe Length | 3 | 2016-06-30 | 2016-01-21 | 2014-03-12 | 14.06 | 1.3623 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 |  | 18 | 17.2 | 18.1 | 18.3 | 0.48305
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-5 | 300-PF-20501-03C03-P CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 21681 | Protective mesh removed | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.925 | CML-5 | CML: Elbow | 6 | 2035-03-19 | 2031-04-17 | 2014-09-28 07:00 | 4.9 | 0.4296 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 16 | 13.7 | 14.4 | 15.6 | 1.0626
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-11 | 50-PW-44012-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23170 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.925 | CML-11 | CML: Pipe Length | 3 | 2019-02-03 | 2019-09-13 | 2015-05-11 07:00 | 2.5 | 0.53518 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 0.71238 | 5.1 | 5.1 | 4.5 | 5 | 0.28723
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-11 | 80-CG-38459-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 6134 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 18.2 | CML-11 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.2 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.3 |  | 17.2 | 17.9 | 19.7 | 18 | 1.0614
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-5 | 150-FL-43456-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7895 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.425 | CML-5 | CML: type TBC | 3 | 2021-08-23 | 2020-12-31 | 2015-01-15 07:00 | 2.5 | 0.55984 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.2 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.9 | 6.2 | 0.3304
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-14 | 150-FL-43456-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7904 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.55 | CML-14 | CML: type TBC | 3 | 2023-12-18 | 2023-02-19 | 2015-01-15 07:00 | 2.5 | 0.4368 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.6 | 6.6 | 6.4 | 0.1
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42044-01S01 | CML-4 | 50-CI-42044-01S01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3458 | Rope Access | 2014-05-13 08:00 | 2014-05-13 09:00 | Check Corrosion Rate of 0.78mm/ yr | [35 empty] | 5.275 | CML-4 | CML: type TBC | 1 | 2017-04-23 | 2016-06-12 | 2014-05-13 08:00 | 2.5 | 0.77988 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-CI-42044-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 5.8 | 4.8 | 5.5 | 0.45735
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42042-01S01 | CML-7 | 50-CI-42042-01S01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3454 | Rope Access | 2014-05-13 07:00 | 2014-05-13 08:00 | Check Corrosion Rate of 0.78mm/ yr | [35 empty] | 5.15 | CML-7 | CML: type TBC | 1 | 2017-04-23 | 2016-06-12 | 2014-05-13 07:00 | 2.5 | 0.77998 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-CI-42042-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5 | 4.9 | 5.9 | 0.50662
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42042-01S01 | CML-6 | 50-CI-42042-01S01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3453 | Rope Access | 2014-05-13 07:00 | 2014-05-13 08:00 | Check Corrosion Rate of 0.78mm/ yr | [35 empty] | 5.375 | CML-6 | CML: type TBC | 1 | 2017-04-23 | 2016-06-12 | 2014-05-13 07:00 | 2.5 | 0.77998 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-CI-42042-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 4.8 | 5.5 | 6.2 | 0.62383
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42042-01S01 | CML-5 | 50-CI-42042-01S01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3452 | Rope Access | 2014-05-13 07:00 | 2014-05-13 08:00 | Check Corrosion Rate of 0.78mm/ yr | [35 empty] | 5.075 | CML-5 | CML: type TBC | 1 | 2017-04-23 | 2016-06-12 | 2014-05-13 07:00 | 2.5 | 0.77998 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-CI-42042-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 4.8 | 4.8 | 5.8 | 0.48563
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42042-01S01 | CML-2 | 50-CI-42042-01S01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3449 | Rope Access | 2014-05-13 07:00 | 2014-05-13 08:00 | Check Corrosion Rate of 0.78mm/ yr | [35 empty] | 5.225 | CML-2 | CML: type TBC | 1 | 2017-04-23 | 2016-06-12 | 2014-05-13 07:00 | 2.5 | 0.77998 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-CI-42042-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 4.8 | 5 | 6 | 0.53151
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-2 | 150-FL-43453-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2246 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 7.4 | CML-2 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.4 | 9 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 8.9 | 7.2 | 7.1 | 6.4 | 1.0614
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2571 | Rope Access | 2014-04-08 07:30 | 2014-04-08 08:30 | [36 empty] | 8.5 | CML-6 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-04-08 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 6 O'Clock | 150 | 7.11 | 150-FL-43084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 9.8 | 8.5 | 7.2 | 8.5 | 1.0614
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-20 | 200-PL-20008-01C02-H CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 8817 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.025 | CML-20 | CML: Elbow | 3 | 2022-04-10 | 2022-03-17 | 2015-02-21 07:00 | 2.5 | 0.43432 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 3 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.3 | 5.6 | 6.2 | 6 | 0.30957
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-6 | 50-PW-44015-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5716 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 4.75 | CML-6 | CML: Elbow | 3 | 2016-07-04 | 2016-11-02 | 2014-06-22 10:00 | 2.5 | 0.98236 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 | 0.48793 | 4.6 | 5 | 4.5 | 4.9 | 0.23805
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-19 | 80-CG-38459-09C02-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21403 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 16.85 | CML-19 | CML: Equal Tee | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 15.9 | 3 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.8 |  | 17.5 | 15.9 | 16 | 18 | 1.0599
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-31 | 300-PG-20004-03C03-P CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 6154 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 9.825 | CML-31 | CML: Elbow | 6 | 2015-10-21 | 2015-03-21 | 2014-07-11 07:30 | 2.5 | 4.926 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.8 | 9 O'Clock | 50 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.5 | 11.3 | 9.7 | 8.8 | 1.0563
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 | yes | FPSO 2013 | Pipe Wall Thickness | 20022 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.85 | CML-3 | CML: type TBC | 3 | 2014-11-29 | 2015-01-27 | 2013-11-17 | 2.5 | 2.0302 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 4.9 | 5 | 4.6 | 0.17321
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-16 | 50-CG-38452-09C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2297 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 8.25 | CML-16 | CML: type TBC | 3 | 2019-05-19 | 2018-08-04 | 2014-03-17 08:00 | 2.5 | 0.90829 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.2 | 3 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 9.3 | 7.2 | 7.5 | 9 | 1.0536
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-7 | 200-PG-23505-09C02-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5506 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 17.6 | CML-7 | CML: Pipe Length | 3 | 2017-05-14 | 2016-10-20 | 2014-05-31 07:00 | 14.06 | 1.0621 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | 0 | 17.2 | 17.2 | 18 | 18 | 0.46188
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-7 | 200-PG-23505-09C02-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20654 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 17.6 | CML-7 | CML: Pipe Length | 3 | 2017-05-14 | 2016-10-20 | 2014-05-31 07:00 | 14.06 | 1.0621 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.2 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | 0 | 17.2 | 17.2 | 18 | 18 | 0.46188
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-9 | 50-CG-38487-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20848 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.85 | CML-9 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-10-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.8 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 | -0.48132 | 9.8 | 8.8 | 9.5 | 11.3 | 1.0536
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43110-01C02 | CML-5 | 200-FH-43110-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12796 |  | 2014-01-18 13:30 | 2014-01-18 14:30 | [36 empty] | 8.55 | CML-5 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 13:30 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.5 | 12 O'Clock | 200 | 6.35 | 200-FH-43110-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.16 |  | 7.5 | 8.5 | 10 | 8.2 | 1.0536
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-8 | 50-WC-40451-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3070 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 0.912mm/ yr | [35 empty] | 5.675 | CML-8 | CML: Equal Tee | 3 | 2016-09-30 | 2017-02-07 | 2014-05-03 08:00 | 2.5 | 0.9116 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 5.4125 | 4.7 | 5.5 | 6.7 | 5.8 | 0.82614
FH01 | Montara_Topside | Yes | Chemical Injection (42) | Pipework | 150-FH-43141-01C02 | CML-7 | 150-FH-43141-01C02 CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 7480 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 1.147mm/ yr | [34 empty] | Low alarm breach | 4.425 | CML-7 | CML: Reducer | 1 | 2016-01-24 | 2015-06-24 | 2015-04-13 07:00 | 2.5 | 1.1465 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.4 | 9 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 4.2 | 5.9 | 4.2 | 3.4 | 1.0532
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20302-03C03-P | CML-6 | 200-PG-20302-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5859 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 12.325 | CML-6 | CML: Elbow | 6 | 2019-04-24 | 2018-03-30 | 2014-06-25 10:30 | 3.3 | 1.5933 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 11 | 12 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 11 | 12.1 | 13.5 | 12.7 | 1.0532
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-14 | 50-CG-38487-09C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20814 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.725 | CML-14 | CML: Elbow | 3 | 2189-07-31 | 2143-11-05 | 2014-07-18 11:00 | 2.5 | 0.0354 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 11.2 | 9.5 | 9.5 | 8.7 | 1.0532
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-4 | 50-PL-20033-01C02 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 2268 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 5.575 | CML-4 | CML: Elbow | 3 | 2020-06-23 | 2021-03-27 | 2014-03-16 11:30 | 2.5 | 0.43019 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.2 | 5.6 | 5.2 | 5.3 | 0.45
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-13 | 250-PW-20022-01C03-P CML-13 | yes | FPSO 2015 | Pipe Wall Thickness | 23111 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 7.9 | CML-13 | CML: Elbow | 6 | 2021-04-11 | 2020-10-30 | 2015-05-10 07:00 | 2.5 | 0.86059 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 7.6 | 6 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | 2.0576 | 8.1 | 7.6 | 7.6 | 8.3 | 0.3559
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-2 | 150-PG-23043-06C02-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 24271 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 9.5 | CML-2 | CML: Elbow | 3 | 2016-04-15 | 2015-11-08 | 2014-09-24 07:00 | 4.7 | 2.1811 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.1 | 3 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 10.2 | 8.1 | 10.4 | 9.3 | 1.0488
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-16 | 25-VA-23054-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 10966 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 17.25 | CML-16 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A4: Left Quadrant |  | 8.27 | 5.22 | 6.745 | 15.7 | 9 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.48 |  | 18 | 17.7 | 17.6 | 15.7 | 1.0472
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38477-01C02-P | CML-6 | 50-CG-38477-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1785 | Rope access | 2014-04-28 08:00 | 2014-04-28 09:00 | [36 empty] | 5.95 | CML-6 | CML: Elbow | 3 | 2021-07-11 | 2022-05-25 | 2014-04-28 08:00 | 2.5 | 0.37455 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-FH-43129-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.2 | 7.5 | 5.5 | 1.0472
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-26 | 300-PG-20005-03C03-P CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 22788 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.825 | CML-26 | CML: Elbow | 6 | 2051-06-23 | 2044-08-18 | 2015-04-29 07:00 | 4.9 | 0.24602 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 | -0.62504 | 16 | 15.4 | 14.1 | 13.8 | 1.0468
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-13 | 50-CG-38487-09C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20852 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 13.525 | CML-13 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-10-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 12 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 | -2.4066 | 14.3 | 13.7 | 14.1 | 12 | 1.0468
FG02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-FG-45455-01C02-E | CML-1 | 25-FG-45455-01C02-E CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5232 | Rope Access | 2014-05-20 13:00 | 2014-05-20 14:00 | [36 empty] | 7.425 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-20 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-DH-56115-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 7.7 | 8.5 | 7.5 | 1.0436
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-21 | 300-PF-20003-03C03-P CML-21 | yes | FPSO 2014 | Pipe Wall Thickness | 21759 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 15.2 | CML-21 | CML: Elbow | 6 | 2059-09-18 | 2051-05-22 | 2014-10-01 07:00 | 4.9 | 0.20224 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 15.8 | 16.3 | 14.7 | 14 | 1.0424
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-9 | 50-PL-23023-03C03 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10209 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.9 | CML-9 | CML: type TBC | 6 | 2017-09-08 | 2017-08-09 | 2013-11-08 | 2.5 | 1.46 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.8 | 8.1 | 8.3 | 10.4 | 1.0424
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57027-01C02 | CML-5 | 50-DC-57027-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1404 | Rope access | 2014-04-05 15:00 | 2014-04-05 16:00 | Check Corrosion Rate of 0.875mm/ yr | [35 empty] | 5.45 | CML-5 | CML: type TBC | 3 | 2016-11-19 | 2017-04-04 | 2014-04-05 15:00 | 2.5 | 0.87517 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DC-57027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5.7 | 6.1 | 4.8 | 0.56862
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-1 | 150-FL-43456-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7891 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 7.575 | CML-1 | CML: type TBC | 3 | 2025-09-09 | 2024-09-23 | 2015-01-15 07:00 | 2.5 | 0.37528 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.5 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 8.1 | 8.5 | 7.2 | 6.5 | 0.89954
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-15 | 150-FL-43456-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 7905 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 7.35 | CML-15 | CML: type TBC | 3 | 2028-02-05 | 2026-12-13 | 2015-01-15 07:00 | 2.5 | 0.31376 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 12 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.7 | 7.6 | 8.5 | 0.88882
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57067-01C02 | CML-6 | 50-DC-57067-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1343 | Rope access | 2014-04-04 08:00 | 2014-04-04 09:00 | Check Corrosion Rate of 0.879mm/ yr | [35 empty] | 5.025 | CML-6 | CML: type TBC | 3 | 2016-11-14 | 2017-03-30 | 2014-04-04 08:00 | 2.5 | 0.87885 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-DC-57067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 4.8 | 5 | 4.9 | 0.263
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57067-01C02 | CML-5 | 50-DC-57067-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1342 | Rope access | 2014-04-04 08:00 | 2014-04-04 09:00 | Check Corrosion Rate of 0.879mm/ yr | [35 empty] | 5.125 | CML-5 | CML: type TBC | 3 | 2016-11-14 | 2017-03-30 | 2014-04-04 08:00 | 2.5 | 0.87885 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-DC-57067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 4.8 | 5.3 | 5.1 | 0.23629
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-15 | 50-DN-56101-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 855 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.2 | CML-15 | CML: Elbow | 3 | 2016-11-07 | 2017-03-22 | 2014-04-02 14:00 | 2.5 | 0.88388 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 5.3 | 4.8 | 5.3 | 0.2708
CG03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-CG-38486-09C02-P | CML-12 | 80-CG-38486-09C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21854 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 16.65 | CML-12 | CML: Equal Tee | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 15.5 | 12 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13 |  | 15.5 | 17.8 | 17.2 | 16.1 | 1.0408
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-3 | 50-CG-38474-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23627 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 6.925 | CML-3 | CML: Elbow | 3 | 2196-05-18 | 2216-01-06 | 2015-10-28 07:00 | 2.5 | 0.0166 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 40 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 7.1 | 5.5 | 7.1 | 8 | 1.0404
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56097-01C02 | CML-1 | 50-DN-56097-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1323 |  | 2014-04-01 07:00 | 2014-04-01 08:00 | [36 empty] | 5.075 | CML-1 | CML: type TBC | 3 | 2016-11-02 | 2017-03-16 | 2014-04-01 07:00 | 2.5 | 0.88764 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DN-56097-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.4 | 4.9 | 5.2 | 0.27538
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56133-01C02 | CML-4 | 50-DN-56133-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1321 |  | 2014-03-31 10:15 | 2014-03-31 10:30 | [36 empty] | 5.125 | CML-4 | CML: type TBC | 3 | 2016-10-29 | 2017-03-12 | 2014-03-31 10:15 | 2.5 | 0.89016 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DN-56133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 5.1 | 5.5 | 4.8 | 0.28723
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-2 | 50-DC-57044-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2140 | Rope Access | 2014-03-29 10:30 | 2014-03-29 12:00 | Check Corrosion Rate of 0.896mm/ yr | [35 empty] | 5.125 | CML-2 | CML: Elbow | 3 | 2016-10-21 | 2017-03-03 | 2014-03-29 10:30 | 2.5 | 0.89604 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5 | 5.5 | 4.8 | 0.29861
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-13 | 150-FL-43456-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7903 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.85 | CML-13 | CML: type TBC | 3 | 2031-09-05 | 2030-04-02 | 2015-01-15 07:00 | 2.5 | 0.25224 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.9 | 6.9 | 6.9 | 6.7 | 0.1
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-10 | 150-FL-43456-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7900 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 7.075 | CML-10 | CML: type TBC | 3 | 2037-07-27 | 2035-09-06 | 2015-01-15 07:00 | 2.5 | 0.19072 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 12 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.9 | 7.6 | 7 | 0.3594
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-8 | 50-DH-56109-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20997 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.425 | CML-8 | CML: Equal Tee | 3 | 2016-07-30 | 2016-12-02 | 2014-05-24 10:30 | 2.5 | 0.95989 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.4 | 4.6 | 4.8 | 6.9 | 1.0404
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-9 | 150-FL-43456-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 7899 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 6.95 | CML-9 | CML: type TBC | 3 | 2037-07-27 | 2035-09-06 | 2015-01-15 07:00 | 2.5 | 0.19072 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 12 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7 | 7 | 7 | 0.1
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-25 | 50-DC-57020-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 2467 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.924mm/ yr | [35 empty] | 5 | CML-25 | CML: type TBC | 3 | 2016-09-14 | 2017-01-21 | 2014-03-20 09:30 | 2.5 | 0.92375 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 5.1 | 5.1 | 4.8 | 0.14142
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-4 | 50-DC-57020-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2446 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.924mm/ yr | [35 empty] | 5.15 | CML-4 | CML: type TBC | 3 | 2016-09-14 | 2017-01-21 | 2014-03-20 09:30 | 2.5 | 0.92375 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5.4 | 4.8 | 5.2 | 0.25166
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-10 | 100-DC-57075-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2429 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 1.523mm/ yr | [35 empty] | 5.25 | CML-10 | CML: type TBC | 3 | 2015-09-22 | 2015-10-20 | 2014-03-20 07:00 | 2.5 | 1.5235 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 6 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 6 | 4.8 | 5.2 | 0.52599
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-24 | 300-PF-20003-03C03-P CML-24 | yes | FPSO 2014 | Pipe Wall Thickness | 21762 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 18 | CML-24 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.3 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.4 |  | 19.5 | 17.9 | 17.3 | 17.3 | 1.0392
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-2 | 50-CG-38487-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20802 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 12.7 | CML-2 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 11.8 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.4 | 12.4 | 11.8 | 14.2 | 1.0392
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-7 | 250-PW-20022-01C03-P CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 23105 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 8.825 | CML-7 | CML: Elbow | 6 | 2021-10-11 | 2021-04-20 | 2015-05-10 07:00 | 2.5 | 0.80906 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 7.7 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 | 1.163 | 8.4 | 7.7 | 9.4 | 9.8 | 0.9535
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-4 | 50-CG-24002-09C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2550 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 9.5 | CML-4 | CML: type TBC | 3 | 2028-10-25 | 2024-10-26 | 2014-04-03 13:00 | 2.5 | 0.40484 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 10.9 | 9.4 | 9.3 | 8.4 | 1.036
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-12 | 250-PG-23003-06C02-PA CML-12 | Yes | FPSO 2014 | Pipe Wall Thickness | 24250 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 16.2 | CML-12 | CML: Elbow | 3 | 2046-01-06 | 2040-10-17 | 2014-09-24 07:00 | 7.9 | 0.22039 | A3: Inside Quadrant |  | 12.09 | 7.9 | 9.0519 | 14.8 | 6 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 17.3 | 16.3 | 14.8 | 16.4 | 1.036
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20060-01C02 | CML-2 | 50-PL-20060-01C02 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 21536 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 5.5 | CML-2 | CML: Fitting | 3 | 2023-06-26 | 2024-07-25 | 2014-07-17 07:30 | 2.5 | 0.30172 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PL-20060-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.8 | 5.2 | 5.6 | 0.2582
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-2 | 200-PL-20008-01C02-H CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8799 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.55 | CML-2 | CML: Elbow | 3 | 2023-08-21 | 2023-07-24 | 2015-02-21 07:00 | 2.5 | 0.37641 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.3 | 6.8 | 5.7 | 7.4 | 0.72342
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-1 | 50-PL-23515-01C03 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 8650 | Line is FFS despite the High CR on CML-3 &1. They are all in the same spool. Current RBI frequency is 48m. | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:49 | [32 empty] | 8.575 | CML-1 | CML: Elbow | 6 | 2022-09-22 | 2022-07-19 | 2015-02-12 07:00 | 2.5 | 0.66973 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.6 | 6 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 10 | 8.6 | 7.6 | 8.1 | 1.034
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-7 | 80-PW-44035-01C02-P CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 23271 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.25 | CML-7 | CML: Elbow | 3 | 2020-10-10 | 2021-08-19 | 2015-05-12 07:00 | 2.5 | 0.40596 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 3 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.5093 | 5.5 | 4.7 | 5.4 | 5.4 | 0.36968
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-2 | 50-WC-40451-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3064 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 0.912mm/ yr | [35 empty] | 5 | CML-2 | CML: Elbow | 3 | 2016-09-30 | 2017-02-07 | 2014-05-03 08:00 | 2.5 | 0.9116 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.8327 | 4.9 | 5.6 | 4.7 | 4.8 | 0.40825
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-11 | 50-PL-23515-01C03 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8660 | Line is FFS despite the High CR on CML-1 to 6. They are all in the same spool. Current RBI frequency is 48m. Action: to recheck CML-1 to 6 in a year to confirm CR. RBI frequency to stay at 48m | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:52 | [32 empty] | 9.05 | CML-11 | CML: Elbow | 6 | 2026-01-19 | 2025-10-22 | 2015-02-12 07:00 | 2.5 | 0.49349 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 12 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 9 | 10.4 | 8.9 | 1.0279
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-17 | 80-PW-20024-01C03-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23061 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 11 | CML-17 | CML: Equal Tee | 6 | 2052-02-11 | 2046-03-21 | 2015-05-06 07:00 | 2.5 | 0.22285 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.7 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.7 | 11.4 | 10.8 | 11.1 | 0.31623
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-5 | 300-PG-20037-03C03-PA CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 21380 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | [36 empty] | 17.75 | CML-5 | CML: Elbow | 6 | 2102-10-24 | 2088-02-10 | 2014-06-29 13:00 | 5.33 | 0 | A2: Right Quadrant |  | 8.27 | 5.33 | 6.8 | 16.6 | 3 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.27 |  | 18.8 | 16.6 | 18.4 | 17.2 | 1.0247
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-21 | 50-PL-23021-03C03 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10253 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.75 | CML-21 | CML: type TBC | 6 | 2016-04-28 | 2016-04-07 | 2013-11-08 | 2.5 | 2.1444 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.8 | 12 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.6 | 8.4 | 10.2 | 1.0247
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-11 | 250-PG-23003-06C02-PA CML-11 | Yes | FPSO 2014 | Pipe Wall Thickness | 24249 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 16.025 | CML-11 | CML: Elbow | 3 | 2029-06-10 | 2026-11-15 | 2014-09-24 07:00 | 7.9 | 0.44837 | A2: Right Quadrant |  | 12.09 | 7.9 | 9.0519 | 14.5 | 3 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 16.4 | 14.5 | 16.5 | 16.7 | 1.0243
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-11 | 50-DH-56137-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5679 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [35 empty] | Low alarm breach | 18.5 | CML-11 | CML: Pipe Length | 3 | 2018-10-05 | 2016-07-05 | 2014-06-21 14:00 | 2.5 | 3.5404 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.7 | 6 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.2 |  | 18.1 | 18.2 | 17.7 | 20 | 1.0231
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-45 | 300-PF-20001-03C03-P CML-45 | yes | FPSO 2015 | Pipe Wall Thickness | 23486 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 15.175 | CML-45 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2015-07-27 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.3 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 | -1.4562 | 14.3 | 14.6 | 15.2 | 16.6 | 1.021
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-4 | 80-CG-38459-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21452 | Protective mesh removed | 2014-06-29 09:30 | 2014-06-29 11:00 | [36 empty] | 15.475 | CML-4 | CML: Equal Tee | 6 | 2099-09-17 | 2086-07-24 | 2014-06-29 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 14.2 | 9 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.7 |  | 15.5 | 15.5 | 16.7 | 14.2 | 1.021
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-18 | 250-PG-23004-06C03-A CML-18 | yes | FPSO 2014 | Pipe Wall Thickness | 20532 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 17.825 | CML-18 | CML: Pipe Length | 6 | 2021-01-30 | 2019-08-14 | 2014-05-30 09:30 | 8.55 | 1.2656 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 17 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.45 | -0.26302 | 17.1 | 19.2 | 18 | 17 | 1.021
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-9 | 250-PG-23004-06C03-A CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 23376 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.375 | CML-9 | CML: Elbow | 6 | 2143-01-24 | 2118-04-19 | 2015-07-21 07:00 | 8.55 | 0.07484 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.1 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.55 | -0.19706 | 20.2 | 20.2 | 18.1 | 19 | 1.021
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-17 | 200-PG-23007-09C03-PA CML-17 | yes | FPSO 2016 | Pipe Wall Thickness | 24451 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | Check Corrosion Rate of 0.912mm/ yr |  | John Wilson | 2017-03-23 08:57 | [32 empty] | 19.2 | CML-17 | CML: Fitting | 6 | 2024-10-22 | 2022-05-25 | 2016-07-03 07:00 | 10.22 | 0.91226 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 17.8 | 6 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.58 | 0.10519 | 20.2 | 19.6 | 17.8 | 19.2 | 1.0198
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56065-01C02 | CML-4 | 50-DH-56065-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3412 | Rope Access | 2014-05-11 09:30 | 2014-05-11 11:00 | [36 empty] | 7.45 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-11 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-DH-56065-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 7.1 | 8.5 | 8 | 1.0149
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-7 | 200-PG-23013-09C03-A CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 10991 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 21.825 | CML-7 | CML: Pipe Length | 6 | 2042-04-11 | 2036-03-03 | 2014-01-10 | 10.22 | 0.36009 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 20.4 | 9 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.18 |  | 22.8 | 22 | 22.1 | 20.4 | 1.0145
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-26 | 300-PF-20501-03C03-P CML-26 | yes | FPSO 2015 | Pipe Wall Thickness | 23532 | Re-check | 2015-07-29 07:00 | 2015-07-29 12:00 | [36 empty] | 13.725 | CML-26 | CML: Elbow | 6 | 2024-03-24 | 2022-04-14 | 2015-07-29 07:00 | 4.9 | 0.86586 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 12.4 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 | 0.96053 | 14.3 | 14.7 | 13.5 | 12.4 | 1.0145
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-17 | 200-PG-23007-09C03-PA CML-17 | yes | FPSO 2014 | Pipe Wall Thickness | 20704 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 19.825 | CML-17 | CML: Fitting | 6 | 2018-09-18 | 2017-08-05 | 2014-06-30 13:00 | 10.22 | 1.9613 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 18.5 | 6 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.28 |  | 20.8 | 20.4 | 18.5 | 19.6 | 1.0145
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-14 | 50-WC-40451-01C02 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10154 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 1.904mm/ yr | [35 empty] | 5.15 | CML-14 | CML: Elbow | 3 | 2015-01-04 | 2015-03-08 | 2013-11-09 | 2.5 | 1.9043 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.4 | 5.3 | 4.7 | 5.2 | 0.31091
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-13 | 50-PL-23020-01C03 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10127 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.85 | CML-13 | CML: type TBC | 6 | 2016-01-17 | 2015-12-29 | 2013-11-08 | 2.5 | 2.3725 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.7 | 3 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.4 | 7.7 | 9.3 | 10 | 1.0083
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20060-01C02 | CML-1 | 50-PL-20060-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 21535 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 5.475 | CML-1 | CML: Elbow | 3 | 2023-06-26 | 2024-07-25 | 2014-07-17 07:30 | 2.5 | 0.30172 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PL-20060-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.5 | 5.5 | 5.2 | 0.20616
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-7 | 100-WC-40516-1CG CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8680 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 | Check Corrosion Rate of 0.387mm/ yr |  | Administrator | 2015-09-08 11:55 | [32 empty] | 7.975 | CML-7 | CML: Pipe Length | 3 | 2029-01-21 | 2025-02-09 | 2015-02-13 07:00 | 2.5 | 0.38712 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 7.9 | 3 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 7.9 | 8.1 | 8 | 0.095743
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-11 | 50-PL-23021-03C03 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10243 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.025 | CML-11 | CML: type TBC | 6 | 2016-09-01 | 2016-08-09 | 2013-11-08 | 2.5 | 1.9163 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 6 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 10.3 | 9.2 | 7.9 | 8.7 | 1.0046
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-7 | 150-FL-43456-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7897 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 7.025 | CML-7 | CML: type TBC | 3 | 2037-07-27 | 2035-09-06 | 2015-01-15 07:00 | 2.5 | 0.19072 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 9 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.9 | 7.5 | 6.9 | 6.8 | 0.32016
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-6 | 150-FL-43456-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7896 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 7.375 | CML-6 | CML: type TBC | 3 | 2049-01-27 | 2046-04-14 | 2015-01-15 07:00 | 2.5 | 0.12919 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.9 | 6 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.4 | 7.7 | 6.9 | 7.5 | 0.34034
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-4 | 150-FL-43456-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7894 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 7.6 | CML-4 | CML: type TBC | 3 | 2049-01-27 | 2046-04-14 | 2015-01-15 07:00 | 2.5 | 0.12919 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.9 | 12 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.9 | 7.7 | 7.9 | 0.4761
RP01 | Montara_Topside | No | Flare (43) | Pipework | 150-FL-43456-01C02 | CML-16 | 150-FL-43456-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 7906 |  | 2015-01-15 07:00 | 2015-01-15 09:00 | [36 empty] | 8.25 | CML-16 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2015-01-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8 | 12 O'Clock | 150 | 7.11 | 150-FL-43456-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.6 | 8.3 | 8.1 | 0.26458
PF02 | Montara_Topside | No | Separation (20) | Pipework | 50-PF-20064-03S01-P | CML-1 | 50-PF-20064-03S01-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21546 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 8.225 | CML-1 | CML: Reducer | 1 | 2027-07-07 | 2025-06-19 | 2014-07-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.91 | 2.5 | 2.705 | 8 | 3 O'Clock | 100 | 3.91 | 150-PF-20064-03S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8 | 8.4 | 8.5 | 0.263
PF02 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PF-20064-03S01-P | CML-17 | 50-PF-20064-03S01-P CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10157 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 1.678mm/ yr | [35 empty] | 5.15 | CML-17 | CML: Elbow | 3 | 2015-03-24 | 2015-06-03 | 2013-11-09 | 2.5 | 1.6776 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 4.8 | 5.2 | 5.2 | 0.25166
PF02 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PF-20064-03S01-P | CML-4 | 50-PF-20064-03S01-P CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10144 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 2.766mm/ yr | [35 empty] | 5.1 | CML-4 | CML: Reducer | 3 | 2015-03-24 | 2015-06-03 | 2013-11-09 | 2.5 | 1.6776 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 100 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 4.8 | 5.2 | 5.2 | 0.2
PF02 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-PF-20064-03S01-P | CML-4 | 50-PF-20064-03S01-P CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10003 | Deck Level | 2013-11-01 | 2013-11-01 | Check Corrosion Rate of 1.646mm/ yr | [35 empty] | 4.8 | CML-4 | CML: type TBC | 3 | 2015-03-26 | 2015-06-11 | 2013-11-01 | 2.5 | 1.6461 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 9 O'Clock | 80 | 5.49 | 80-DC-57004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.8 | 4.8 | 4.8 | 0
PF02 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PF-20064-03S01-P | CML-11 | 50-PF-20064-03S01-P CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 23412 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 18.325 | CML-11 | CML: Elbow | 3 | 2018-03-31 | 2017-07-22 | 2015-07-22 07:00 | 14.06 | 0.86895 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 16.4 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.34 | 0.70024 | 16.4 | 19.2 | 18.3 | 19.4 | 1.3696
PF02 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-PF-20064-03S01-P | CML-4 | 50-PF-20064-03S01-P CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24392 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.325 | CML-4 | CML: Elbow | 1 | 2035-06-01 | 2029-05-31 | 2016-06-07 07:00 | 1.71 | 0 | A1: Outside Quadrant |  | 2.91 | 1.71 | 2.31 | 4.1 | 12 O'Clock | 50 | 3.91 | 50-FG-45049-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.39 |  | 4.1 | 4.2 | 4.6 | 4.4 | 0.22174
PF02 | Montara_Topside | No | Separation (20) | Pipework | 50-PF-20064-03S01-P | CML-21 | 50-PF-20064-03S01-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 13191 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.475 | CML-21 | CML: Pipe Length | 3 | 2018-06-11 | 2019-05-30 | 2014-01-21 13:00 | 3.61 | 0.54468 | A4: Left Quadrant |  | 3.35 | 3.61 | 3.0831 | 6 | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.39 |  | 6.8 | 6.1 | 7 | 6 | 0.49917
PF02 | Montara_Topside | No | Separation (20) | Pipework | 50-PF-20064-03S01-P | CML-2 | 50-PF-20064-03S01-P CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24460 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | [36 empty] | 5.175 | CML-2 | CML: Elbow | 3 | 2023-02-21 | 2023-06-18 | 2016-07-05 07:00 | 2.5 | 0.36168 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 9 O'Clock | 100 | 6.02 | 100-PL-20068-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0 | 5 | 5.6 | 5.2 | 4.9 | 0.30957
PF02 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PF-20064-03S01-P | CML-2 | 50-PF-20064-03S01-P CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24418 | Re-check as requested by N.Sequera | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.363mm/ yr |  | John Wilson | 2017-03-23 10:27 | Loss within CA CML on 12 month schedule | [31 empty] | 5.2 | CML-2 | CML: Elbow | 3 | 2023-02-11 | 2023-06-08 | 2016-07-02 07:00 | 2.5 | 0.36264 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 3 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.1058 | 5.3 | 4.9 | 5.3 | 5.3 | 0.2
PF02 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-PF-20064-03S01-P | CML-1 | 50-PF-20064-03S01-P CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24417 | Re-check as requested by N.Sequera | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.363mm/ yr |  | John Wilson | 2017-03-23 10:06 | Loss within CA no further action required include in next inspection | [31 empty] | 5.15 | CML-1 | CML: Elbow | 3 | 2023-02-11 | 2023-06-08 | 2016-07-02 07:00 | 2.5 | 0.36264 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 3 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.1058 | 5.1 | 4.9 | 5.3 | 5.3 | 0.19149
PF02 | Montara_Topside | No | Separation (20) | Pipework | 50-PF-20064-03S01-P | CML-2 | 50-PF-20064-03S01-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21547 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 8.375 | CML-2 | CML: Reducer | 1 | 2027-07-07 | 2025-06-19 | 2014-07-13 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.91 | 2.5 | 2.705 | 8.2 | 6 O'Clock | 150 | 3.91 | 150-PF-20064-03S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.3 | 8.6 | 8.2 | 8.4 | 0.17078
PF02 | Montara_Topside | No | Separation (20) | Pipework | 50-PF-20064-03S01-P | CML-3 | 50-PF-20064-03S01-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21548 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 8.525 | CML-3 | CML: Pipe Length | 1 | 2027-07-07 | 2025-06-19 | 2014-07-13 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.91 | 2.5 | 2.705 | 8.3 | 9 O'Clock | 150 | 3.91 | 150-PF-20064-03S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.7 | 8.5 | 8.6 | 8.3 | 0.17078
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-23 | 150-WF-71372-01K01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 5353 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.775 | CML-23 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3.5 | 4.3 | 4.3 | 0.63966
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-27 | 300-PF-20001-03C03-P CML-27 | Yes | FPSO 2014 | Pipe Wall Thickness | 21165 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 16.275 | CML-27 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.9 | 3 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 17.2 | 14.9 | 16.8 | 16.2 | 1.0046
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23026-09C02-P | CML-5 | 150-PG-23026-09C02-P CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 24264 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 19.775 | CML-5 | CML: Elbow | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A4: Left Quadrant |  | 11.27 | 7 | 9.135 | 18.5 | 9 O'Clock | 150 | 14.27 | 150-PG-23026-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 20.9 | 20.1 | 19.6 | 18.5 | 1.0046
SD01 | Montara_Topside | No | Steam (55) | Pipework | 150-SL-55001-01C02-H | CML-1 | 150-SL-55001-01C02-H CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23602 |  | 2015-09-28 07:00 | 2015-09-28 15:00 | [36 empty] | 5.375 | CML-1 | CML: Elbow | 3 | 2018-04-07 | 2017-11-20 | 2015-09-28 07:00 | 2.5 | 0.94979 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 4.9 | 12 O'Clock | 50 | 7.11 | 150-SL-55001-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.6 | 5.5 | 5.5 | 0.32016
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-6 | 50-CG-38488-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20824 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 12 | CML-6 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 11.4 | 6 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 13.5 | 11.5 | 11.4 | 11.6 | 1.0033
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-2 | 150-WF-71372-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5332 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 3 | 3 | 3 | 3 | 0
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-48 | 150-WF-71372-01K01 CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 5378 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.95 | CML-48 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 4.4 | 4.6 | 3.7 | 0.68557
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-17 | 300-PG-20506-03C03-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 13231 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 16.975 | CML-17 | CML: type TBC | 6 | 2107-02-11 | 2090-04-05 | 2014-02-04 15:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 16.2 | 9 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 16.2 | 17.2 | 18.3 | 16.2 | 1.0012
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-35 | 150-WF-71372-01K01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 5365 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.45 | CML-35 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 6 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.3 | 3.9 | 3.1 | 3.5 | 0.34157
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-19 | 50-PL-23021-03C03 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10251 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.675 | CML-19 | CML: type TBC | 6 | 2015-04-25 | 2015-04-12 | 2013-11-08 | 2.5 | 3.285 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.3 | 6 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 9.7 | 8.9 | 7.3 | 8.8 | 1.0012
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-2 | 50-PL-23040-03C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10187 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.725 | CML-2 | CML: type TBC | 6 | 2016-01-17 | 2015-12-29 | 2013-11-08 | 2.5 | 2.3725 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.7 | 12 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 10.1 | 8.6 | 8.5 | 1.0012
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-28 | 150-WF-71372-01K01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 5358 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.725 | CML-28 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.6 | 4.4 | 3.8 | 0.53774
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-7 | 50-DC-57044-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23125 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | Check Corrosion Rate of 0.33mm/ yr | [35 empty] | 5.5 | CML-7 | CML: Pipe Length | 3 | 2022-08-17 | 2023-08-13 | 2015-05-10 07:00 | 2.5 | 0.32981 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0 | 5.5 | 5.6 | 4.9 | 6 | 0.45461
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-4 | 50-DC-57013-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22928 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | Check Corrosion Rate of 0.334mm/ yr | 37 | [34 empty] | 5.125 | CML-4 | CML: Elbow | 3 | 2022-07-10 | 2023-07-02 | 2015-05-02 07:00 | 2.5 | 0.33358 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.64094 | 5.3 | 4.9 | 5.3 | 5 | 0.20616
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-3 | 50-PW-44015-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22708 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.2 | CML-3 | CML: Elbow | 3 | 2019-07-31 | 2020-03-29 | 2015-04-28 07:00 | 2.5 | 0.49275 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0.47116 | 5.5 | 5.7 | 5 | 4.6 | 0.49666
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-8 | 300-PF-20003-03C03-P CML-8 | Yes | FPSO 2014 | Pipe Wall Thickness | 21746 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 9.825 | CML-8 | CML: Elbow | 6 | 2016-04-14 | 2015-08-01 | 2014-10-01 07:00 | 2.5 | 4.0972 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.8 | 9 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.6 | 11.2 | 9.7 | 8.8 | 1.0012
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-11 | 50-PW-44014-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23156 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.075 | CML-11 | CML: Pipe Length | 3 | 2019-09-08 | 2020-05-11 | 2015-05-10 07:00 | 2.5 | 0.4844 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0.53562 | 5.6 | 5.1 | 5 | 4.6 | 0.4113
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-27 | 150-WF-71372-01K01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 5357 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.7 | CML-27 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.6 | 4.3 | 3.8 | 0.49666
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-17 | 250-PW-20022-01C03-P CML-17 | Yes | FPSO 2015 | Pipe Wall Thickness | 23115 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 8.425 | CML-17 | CML: Elbow | 6 | 2022-05-06 | 2021-11-02 | 2015-05-10 07:00 | 2.5 | 0.75753 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 7.8 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 | 1.6998 | 8.7 | 7.8 | 8.5 | 8.7 | 0.4272
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-2 | 50-DH-56137-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5480 | Rope Access | 2014-05-28 11:30 | 2014-05-28 14:00 | [36 empty] | 18.95 | CML-2 | CML: Elbow | 3 | 2163-03-18 |  | 2014-05-28 11:30 |  | 0 | A4: Left Quadrant |  |  | 2.5 |  | 17.6 | 9 O'Clock | 300 | 17.48 | 300-WC-40513-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.1 |  | 18.8 | 19.6 | 19.8 | 17.6 | 0.99833
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-5 | 200-PG-24001-09C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10261 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 18.45 | CML-5 | CML: Elbow | 3 | 2020-07-18 | 2018-02-28 | 2013-11-09 | 9.2 | 1.2696 | A2: Right Quadrant |  | 15.26 | 9.2 | 12.23 | 17.7 | 6 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 19.8 | 17.7 | 17.7 | 18.6 | 0.99499
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-26 | 150-WF-71372-01K01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 5356 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.525 | CML-26 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 3 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.7 | 3.1 | 3.7 | 3.6 | 0.28723
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67301-01E01 | CML-3 | 25-GN-67301-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22497 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.5 | CML-3 | CML: Elbow | 3 | 2018-06-02 | 2018-05-20 | 2015-04-20 07:00 | 2.5 | 0.76893 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.9 | 12 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 6 | 5.8 | 0.49666
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-1 | 50-PW-44013-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22720 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.025 | CML-1 | CML: Elbow | 3 | 2019-07-31 | 2020-03-29 | 2015-04-28 07:00 | 2.5 | 0.49275 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | -0.70702 | 4.6 | 5.1 | 5.3 | 5.1 | 0.29861
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71342-01K01 | CML-2 | 80-WF-71342-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6606 |  | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.475 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 4.9 | 12 O'Clock | 80 | 2.5 | 80-WF-71342-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.8 | 5.7 | 5.5 | 0.40311
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-3 | 50-DH-56137-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20542 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 17.85 | CML-3 | CML: Pipe Length | 6 | 2096-09-16 | 2085-01-22 | 2014-05-27 08:00 | 2.8 | 0 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 17.1 | 6 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.3 | -21.1206 | 17.1 | 19.2 | 17.1 | 18 | 0.99499
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-19 | 150-WF-71372-01K01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 5349 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.875 | CML-19 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 6 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.5 | 3.6 | 3.1 | 4.3 | 0.64485
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71359-01K01 | CML-9 | 100-WF-71359-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 6218 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 5.5 | CML-9 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.9 | 6 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 5.9 | 4.9 | 5.9 | 0.4899
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71359-01K01 | CML-3 | 100-WF-71359-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6212 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 5.525 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.9 | 6 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 6.1 | 5.2 | 4.9 | 5.9 | 0.56789
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-42 | 150-WF-71372-01K01 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 5372 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.7 | CML-42 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.6 | 4.3 | 3.7 | 0.45461
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71310-01K01 | CML-5 | 150-WF-71310-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5316 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 5.35 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.9 | 12 O'Clock | 150 | 3 | 150-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5.5 | 5.6 | 0.31091
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71306-01K01 | CML-2 | 250-WF-71306-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5181 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 6.25 | CML-2 | CML: type TBC | 0.5 | 2023-06-01 | 2020-11-30 | 2015-03-12 07:00 | 3.5 | 0 | A3: Inside Quadrant |  | 4 | 3.5 | 3.75 | 5.9 | 6 O'Clock | 250 | 4.5 | 250-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 6.6 | 6.2 | 5.9 | 6.3 | 0.28868
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-13 | 0200-DC-57L9006-AC21-00 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5053 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.778mm/ yr | [34 empty] | Low alarm breach | 5.175 | CML-13 | CML: type TBC | 3 | 2016-07-09 | 2015-12-02 | 2015-03-05 07:00 | 2.5 | 1.778 | A2: Right Quadrant |  | 5.74 | 2.5 | 3.5737 | 4.9 | 3 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.7 | 4.9 | 5.1 | 5 | 0.3594
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-10 | 0200-DC-57L9006-AC21-00 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5050 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.778mm/ yr | [34 empty] | Low alarm breach | 5.05 | CML-10 | CML: type TBC | 3 | 2016-07-09 | 2015-12-02 | 2015-03-05 07:00 | 2.5 | 1.778 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 4.9 | 9 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 | 5.4 | 4.9 | 0.23805
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-9 | 0200-DC-57L9006-AC21-00 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5049 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.778mm/ yr | [34 empty] | Low alarm breach | 5.2 | CML-9 | CML: type TBC | 3 | 2016-07-09 | 2015-12-02 | 2015-03-05 07:00 | 2.5 | 1.778 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 4.9 | 12 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 5.6 | 5 | 0.31623
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-3 | 0200-DC-57L9006-AC21-00 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5043 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.778mm/ yr | [34 empty] | Low alarm breach | 5.075 | CML-3 | CML: type TBC | 3 | 2016-07-09 | 2015-12-02 | 2015-03-05 07:00 | 2.5 | 1.778 | A4: Left Quadrant |  | 5.74 | 2.5 | 3.5737 | 4.9 | 9 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5.1 | 5.1 | 4.9 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-1 | 0200-DC-57L9006-AC21-00 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5041 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.778mm/ yr | [34 empty] | Low alarm breach | 5.075 | CML-1 | CML: type TBC | 3 | 2016-07-09 | 2015-12-02 | 2015-03-05 07:00 | 2.5 | 1.778 | A4: Left Quadrant |  | 5.74 | 2.5 | 3.5737 | 4.9 | 9 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5.1 | 5.1 | 4.9 | 0.12583
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-14 | 50-AI-63004-01E01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 9005 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | Check Corrosion Rate of 0.367mm/ yr | [35 empty] | 5.425 | CML-14 | CML: type TBC | 3 | 2021-09-14 | 2022-08-05 | 2015-02-28 07:00 | 2.5 | 0.36655 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5.4 | 6 | 0.45
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-63 | 50-AI-63007-01E01 CML-63 |  | FPSO 2015 | Pipe Wall Thickness | 8987 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.368mm/ yr | [35 empty] | 5.575 | CML-63 | CML: type TBC | 3 | 2021-09-05 | 2022-07-25 | 2015-02-26 09:00 | 2.5 | 0.36766 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 6 | 6 | 5.4 | 4.9 | 0.53151
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-60 | 50-AI-63007-01E01 CML-60 |  | FPSO 2015 | Pipe Wall Thickness | 8984 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.368mm/ yr | [35 empty] | 5.175 | CML-60 | CML: type TBC | 3 | 2021-09-05 | 2022-07-25 | 2015-02-26 09:00 | 2.5 | 0.36766 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 5.1 | 5.4 | 0.22174
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-56 | 50-AI-63007-01E01 CML-56 |  | FPSO 2015 | Pipe Wall Thickness | 8980 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.368mm/ yr | [35 empty] | 5.325 | CML-56 | CML: type TBC | 3 | 2021-09-05 | 2022-07-25 | 2015-02-26 09:00 | 2.5 | 0.36766 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 5.3 | 4.9 | 5.8 | 0.36856
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-30 | 50-AI-63007-01E01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 8954 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.368mm/ yr | [35 empty] | 5.275 | CML-30 | CML: type TBC | 3 | 2021-09-05 | 2022-07-25 | 2015-02-26 09:00 | 2.5 | 0.36766 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.3 | 4.9 | 5.9 | 0.45
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67009-01E01 | CML-3 | 50-GN-67009-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8781 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.05 | CML-3 | CML: type TBC | 3 | 2021-07-14 | 2022-05-28 | 2015-02-15 07:00 | 2.5 | 0.37418 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 5 | 5.3 | 0.17321
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67009-01E01 | CML-2 | 50-GN-67009-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8780 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.075 | CML-2 | CML: type TBC | 3 | 2021-07-14 | 2022-05-28 | 2015-02-15 07:00 | 2.5 | 0.37418 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 4.9 | 5 | 5.3 | 0.17078
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67010-01E01 | CML-3 | 50-GN-67010-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8706 |  | 2015-02-14 07:00 | 2015-02-14 09:00 | [36 empty] | 5.5 | CML-3 | CML: type TBC | 3 | 2021-07-09 | 2022-05-23 | 2015-02-14 07:00 | 2.5 | 0.37478 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.8 | 4.9 | 5.8 | 5.5 | 0.42426
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67010-01E01 | CML-2 | 50-GN-67010-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8705 |  | 2015-02-14 07:00 | 2015-02-14 09:00 | [36 empty] | 5.15 | CML-2 | CML: type TBC | 3 | 2021-07-09 | 2022-05-23 | 2015-02-14 07:00 | 2.5 | 0.37478 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 5.2 | 4.9 | 5.4 | 0.20817
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62001-01C02 | CML-3 | 50-DO-62001-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8043 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.275 | CML-3 | CML: type TBC | 3 | 2021-03-17 | 2022-01-17 | 2015-01-21 07:30 | 2.5 | 0.38978 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DO-62001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5.4 | 5.4 | 0.25
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-40 | 150-WF-71372-01K01 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 5370 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.85 | CML-40 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.5 | 4.2 | 4.5 | 0.60277
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-12 | 25-VA-23054-01C02 CML-12 | Yes | FPSO 2014 | Pipe Wall Thickness | 23845 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 20.45 | CML-12 | CML: Elbow | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A2: Right Quadrant |  | 15.26 | 9.3 | 12.28 | 19.8 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.5 |  | 20.3 | 19.8 | 21.9 | 19.8 | 0.99499
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40047-01C02 | CML-3 | 50-WC-40047-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1703 | Rope Access | 2014-04-13 10:15 | 2014-04-13 11:15 | Check Corrosion Rate of 0.969mm/ yr | [35 empty] | 5.075 | CML-3 | CML: Elbow | 3 | 2016-07-20 | 2016-11-20 | 2014-04-13 10:15 | 2.5 | 0.96894 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-WC-40047-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 4.7 | 5 | 5.4 | 0.29861
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 20021 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.075 | CML-2 | CML: type TBC | 3 | 2015-02-02 | 2015-04-09 | 2013-11-17 | 2.5 | 1.8142 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5 | 5.2 | 5.4 | 0.29861
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-2 | 250-PW-20022-01C03-P CML-2 | Yes | FPSO 2015 | Pipe Wall Thickness | 23100 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 8.425 | CML-2 | CML: Elbow | 6 | 2022-12-31 | 2022-06-15 | 2015-05-10 07:00 | 2.5 | 0.70599 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.9 | 12 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | 0.53676 | 7.9 | 8.8 | 8.6 | 8.4 | 0.38622
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-16 | 50-PL-23041-06C03 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10229 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.325 | CML-16 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 4.9503 | A3: Inside Quadrant |  | 5.07 |  |  | 8.9 | 6 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.9 | 10.4 | 8.9 | 11.1 | 0.99457
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-34 | 150-WF-71372-01K01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 5364 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.775 | CML-34 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.7 | 4.5 | 3.7 | 0.53774
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-13 | 50-DH-56070-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 3229 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.2 | CML-13 | CML: type TBC | 3 | 2021-10-17 | 2022-09-10 | 2014-05-09 07:00 | 2.5 | 0.36256 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 7.4 | 6.6 | 5.2 | 0.99331
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-1 | 80-CG-38486-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21410 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 18.675 | CML-1 | CML: Reducer | 6 | 2091-05-30 | 2082-05-30 | 2014-07-12 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 6.7 | 4.9 | 5.8 | 17.8 | 12 O'Clock | 300 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.9 |  | 17.8 | 18.4 | 18.4 | 20.1 | 0.99121
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-23 | 300-PF-20003-03C03-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21761 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 9.825 | CML-23 | CML: Elbow | 6 | 2016-07-06 | 2015-10-02 | 2014-10-01 07:00 | 2.5 | 3.7976 | A2: Right Quadrant |  | 8.27 | 2.5 | 5.385 | 9.2 | 3 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.5 | 9.2 | 9.3 | 11.3 | 0.99121
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-14 | 50-WC-40071-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7727 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.398mm/ yr |  | Administrator | 2015-09-08 09:35 | [32 empty] | 5.075 | CML-14 | CML: Elbow | 3 | 2021-01-20 | 2021-11-16 | 2015-01-09 13:00 | 2.5 | 0.39759 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 1.1361 | 5.1 | 5.2 | 5.1 | 4.9 | 0.12583
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-11 | 50-WC-40071-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 7724 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.398mm/ yr |  | Administrator | 2015-09-08 09:34 | [32 empty] | 5.075 | CML-11 | CML: Pipe Length | 3 | 2021-01-20 | 2021-11-16 | 2015-01-09 13:00 | 2.5 | 0.39759 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.88364 | 4.9 | 5 | 5.2 | 5.2 | 0.15
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-6 | 50-WC-40071-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7719 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.398mm/ yr |  | Administrator | 2015-09-08 09:33 | [32 empty] | 5.075 | CML-6 | CML: Pipe Length | 3 | 2021-01-20 | 2021-11-16 | 2015-01-09 13:00 | 2.5 | 0.39759 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.50494 | 4.9 | 5.1 | 5.1 | 5.2 | 0.12583
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-3 | 50-WC-40071-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7716 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.398mm/ yr |  | Administrator | 2015-09-08 09:32 | [32 empty] | 5.1 | CML-3 | CML: Elbow | 3 | 2021-01-20 | 2021-11-16 | 2015-01-09 13:00 | 2.5 | 0.39759 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.63117 | 5 | 5.5 | 5 | 4.9 | 0.2708
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40052-01C02 | CML-4 | 50-WC-40052-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1527 |  | 2014-04-03 11:00 | 2014-04-03 12:00 | Check Corrosion Rate of 1mm/ yr | [35 empty] | 5 | CML-4 | CML: Elbow | 3 | 2016-06-14 | 2016-10-11 | 2014-04-03 11:00 | 2.5 | 1.0005 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-WC-40052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 5.1 | 4.7 | 5.3 | 0.2582
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-52 | 300-PF-20003-03C03-P CML-52 |  | FPSO 2014 | Pipe Wall Thickness | 21790 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 13.275 | CML-52 | CML: Elbow | 6 | 2019-05-24 | 2018-03-02 | 2014-10-01 07:00 | 4.1 | 1.7003 | A4: Left Quadrant |  | 8.27 | 4.1 | 6.185 | 12 | 9 O'Clock | 250 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 13.2 | 14.4 | 13.5 | 12 | 0.99121
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23030-09C02-P | CML-2 | 50-PG-23030-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20745 | Protective mesh removed/Rope access | 2014-07-02 09:30 | 2014-07-02 11:00 | [36 empty] | 9.875 | CML-2 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-07-02 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.8 | 3 O'Clock | 50 | 8.74 | 50-PG-23030-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.8 | 8.8 | 9.7 | 11.2 | 0.99121
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-3 | 50-DC-57013-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7672 | New Isometric drawing | 2015-01-08 09:30 | 2015-01-08 12:00 | Check Corrosion Rate of 0.398mm/ yr |  | Administrator | 2015-09-08 12:38 | [32 empty] | 5.1 | CML-3 | CML: Elbow | 3 | 2021-01-15 | 2021-11-10 | 2015-01-08 09:30 | 2.5 | 0.39837 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 5.3 | 4.9 | 0.23094
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57300-01C02 | CML-3 | 50-DC-57300-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20293 | Reviewed on 24/11/14. FFS. Recheck on Oct. 17 | 2014-10-17 07:00 | 2014-10-17 15:00 | Check Corrosion Rate of 0.464mm/ yr |  | Nestor | 2014-11-24 09:39 | [32 empty] | 5.075 | CML-3 | CML: Elbow | 3 | 2019-12-17 | 2020-08-30 | 2014-10-17 07:00 | 2.5 | 0.46414 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-DC-57300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 5.3 | 5 | 4.9 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-19 | 150-FH-43026-01C02 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 23518 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 29.5 | CML-19 | CML: Reducing Tee | 3 | 520099 | 433841 | 2015-07-28 07:00 | 1.03 | 0.00464 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.1 | 12 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.07 | 1.4704 | 7.1 | 9.4 | 8.1 | 8.8 | 0.98826
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-24 | 300-PG-20004-03C03-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 6147 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 15.625 | CML-24 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.4 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 14.4 | 16.8 | 15.5 | 15.8 | 0.98784
FG01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-FG-45024-01C02 | CML-7 | 50-FG-45024-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8037 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:32 | [32 empty] | 10.425 | CML-7 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2015-01-20 14:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.2 | 9 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.3 | 11.6 | 10.6 | 9.2 | 0.98784
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-25 | 300-PG-20004-03C03-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 6148 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.45 | CML-25 | CML: Fitting | 6 | 2026-12-02 | 2024-06-28 | 2014-07-11 07:30 | 4.9 | 0.69342 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 6 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 15.3 | 15.3 | 13.5 | 13.7 | 0.98489
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38483-01C02 | CML-2 | 25-CG-38483-01C02 CML-2 | Yes | FPSO 2013 | Pipe Wall Thickness | 10391 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.175 | CML-2 | CML: type TBC | 3 | 2014-06-18 | 2014-06-15 | 2013-11-12 | 2.5 | 3.6723 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.7 | 12 O'Clock | 25 | 6.35 | 25-CG-38483-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 4.7 | 4.7 | 6.6 | 6.7 | 6.7 | 0.98446
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-2 | 50-PG-44022-01C03-P CML-2 | no | FPSO 2015 | Pipe Wall Thickness | 22977 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 8.075 | CML-2 | CML: Reducing Tee | 6 | 2019-01-08 | 2018-11-30 | 2015-05-04 07:00 | 2.5 | 1.1122 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 6.6 | 12 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 | 2.9153 | 6.6 | 8.6 | 8.6 | 8.5 | 0.98446
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-30 | 80-CG-38486-09C02-P CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 22792 | New location | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 19.675 | CML-30 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 18.2 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.3 |  | 20.2 | 20.1 | 20.2 | 18.2 | 0.98446
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-14 | 200-PG-23007-09C03-PA CML-14 | yes | FPSO 2016 | Pipe Wall Thickness | 24449 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | [35 empty] | High alarm breach | 11.275 | CML-14 | CML: Elbow | 6 | 2015-11-20 | 2023-01-28 | 2016-07-03 07:00 | 10.22 | 0.35585 | A2: Right Quadrant |  | 5.1 | 10.22 | 7.66 | 10 | 3 O'Clock | 50 | 11.1 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | -0.22 | 0 | 12.4 | 10 | 11.3 | 11.4 | 0.98446
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-52 | 300-PF-20001-03C03-P CML-52 |  | FPSO 2014 | Pipe Wall Thickness | 21190 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.623mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:46 | [32 empty] | 12.525 | CML-52 | CML: Fitting | 6 | 2018-06-13 | 2017-06-01 | 2014-07-16 07:30 | 4.1 | 2.0193 | A1: Outside Quadrant |  | 8.27 | 4.1 | 6.185 | 12 | 6 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 12 | 14 | 12 | 12.1 | 0.98446
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-11 | 50-CG-38465-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20874 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.175 | CML-11 | CML: Elbow | 3 | 2019-10-16 | 2020-06-22 | 2014-10-04 07:00 | 2.5 | 0.47645 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 4.9 | 5.2 | 5.2 | 0.20616
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-4 | 50-CG-38465-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20867 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.375 | CML-4 | CML: Elbow | 3 | 2019-10-16 | 2020-06-22 | 2014-10-04 07:00 | 2.5 | 0.47645 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.7 | 5.4 | 5.5 | 4.9 | 0.34034
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-1 | 50-CG-38465-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20864 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.125 | CML-1 | CML: Elbow | 3 | 2019-10-16 | 2020-06-22 | 2014-10-04 07:00 | 2.5 | 0.47645 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 5 | 5.5 | 4.9 | 0.263
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-33 | 150-WF-71372-01K01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 5363 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.725 | CML-33 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.7 | 4.2 | 3.8 | 0.4113
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-24 | 150-WF-71372-01K01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 5354 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.8 | CML-24 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.8 | 4.5 | 3.7 | 0.53541
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57301-01C02 | CML-3 | 50-DC-57301-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5663 | Rope access | 2014-06-21 13:00 | 2014-06-21 14:00 | Check Corrosion Rate of 0.606mm/ yr | [35 empty] | 5.35 | CML-3 | CML: Elbow | 3 | 2018-06-06 | 2018-12-19 | 2014-06-21 13:00 | 2.5 | 0.6059 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-DC-57301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 6.1 | 5.2 | 4.9 | 0.51962
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-15 | 150-WF-71372-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5345 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.875 | CML-15 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 4.3 | 4.1 | 3.9 | 3.2 | 0.47871
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-46 | 150-WF-71372-01K01 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 5376 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.8 | CML-46 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.9 | 4.3 | 3.7 | 0.41633
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-10 | 80-DC-57005-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20256 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | Check Corrosion Rate of 0.588mm/ yr | [35 empty] | 5.425 | CML-10 | CML: type TBC | 3 | 2018-07-02 | 2019-02-03 | 2014-06-02 13:00 | 2.5 | 0.58752 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 9 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 5.5 | 6.2 | 4.9 | 0.57373
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-8 | 80-DC-57005-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20254 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | Check Corrosion Rate of 0.588mm/ yr | [35 empty] | 5.3 | CML-8 | CML: type TBC | 3 | 2018-07-02 | 2019-02-03 | 2014-06-02 13:00 | 2.5 | 0.58752 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 6 | 5.1 | 4.9 | 5.2 | 0.48305
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-7 | 80-DC-57005-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20253 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | Check Corrosion Rate of 0.588mm/ yr | [35 empty] | 5.325 | CML-7 | CML: type TBC | 3 | 2018-07-02 | 2019-02-03 | 2014-06-02 13:00 | 2.5 | 0.58752 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 5.4 | 4.9 | 5.4 | 0.29861
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 23409 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 18.275 | CML-6 | CML: Elbow | 3 | 2020-07-18 | 2019-07-12 | 2015-07-22 07:00 | 14.06 | 0.58864 | A4: Left Quadrant |  | 15.26 | 14.06 | 14.66 | 17 | 9 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.94 | 0.17506 | 18.4 | 18.3 | 19.4 | 17 | 0.98446
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-13 | 50-PL-23021-03C03 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10245 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.2 | CML-13 | CML: type TBC | 6 | 2019-08-18 | 2019-07-05 | 2013-11-08 | 2.5 | 1.0037 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 12 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.9 | 10.6 | 9 | 0.98319
FH02 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43313-01S01-P | CML-3 | 150-FH-43313-01S01-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20477 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.85 | CML-3 | CML: Elbow | 1 | 2028-06-23 | 2024-01-12 | 2014-10-03 07:00 | 2.5 | 0.30585 | A2: Right Quadrant |  | 6.11 | 2.5 | 3.8606 | 6.7 | 3 O'Clock | 150 | 7.11 | 150-FH-43313-01S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.8 | 6.7 | 7.8 | 9.1 | 0.9815
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-1 | 50-PW-44009-01C03-P CML-1 | Yes | FPSO 2015 | Pipe Wall Thickness | 22808 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 9.075 | CML-1 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.5 | 12 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 0.23548 | 8.5 | 9.7 | 8.7 | 9.4 | 0.56789
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-24 | 100-FG-45001-09C02 CML-24 |  | FPSO 2013 | Pipe Wall Thickness | 10439 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 11.55 | CML-24 | CML: type TBC | 3 | 2026-01-16 | 2022-09-04 | 2013-11-13 | 4.7 | 0.50879 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.9 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 13 | 10.9 | 11.3 | 11 | 0.9815
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-23 | 300-PF-20001-03C03-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21161 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.391mm/ yr | 40 | Kirstie Albone | 2017-03-23 16:11 | [32 empty] | 9.525 | CML-23 | CML: Elbow | 6 | 2015-08-18 | 2015-02-01 | 2014-07-16 07:30 | 2.5 | 5.3107 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.3 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 10.7 | 9.6 | 9.5 | 8.3 | 0.98107
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-32 | 200-PG-23007-09C03-PA CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 20719 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 20.675 | CML-32 | CML: Fitting | 6 | 2025-08-17 | 2023-01-16 | 2014-06-30 13:00 | 10.22 | 0.85111 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 19.7 | 12 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.48 |  | 19.7 | 21 | 21.9 | 20.1 | 0.98107
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-10 | 200-PG-23006-09C02-PA CML-10 | Yes | FPSO 2014 | Pipe Wall Thickness | 23843 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 19.625 | CML-10 | CML: Elbow | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A4: Left Quadrant |  | 15.26 | 9.3 | 12.28 | 18.6 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 19.8 | 19.2 | 20.9 | 18.6 | 0.98107
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38460-01C02-P | CML-3 | 80-CG-38460-01C02-P CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 20884 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 7.675 | CML-3 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-04 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.5 | 9 O'Clock | 80 | 5.49 | 80-CG-38460-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 8.9 | 7.7 | 7.6 | 6.5 | 0.98107
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-1 | 400-FH-43500-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5637 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 10.025 | CML-1 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 8.7 | 6 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.9 | 10.6 | 8.7 | 10.9 | 0.97767
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23072-03C03 | CML-1 | 100-PG-23072-03C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20605 | Rope Access. Line is FFS | 2014-05-25 10:30 | 2014-05-25 11:30 |  |  | Administrator | 2015-09-08 08:11 | [32 empty] | 12.125 | CML-1 | CML: type TBC | 6 | 2099-09-17 | 2086-07-24 | 2014-05-25 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.2 | 12 O'Clock | 100 | 11.13 | 100-PG-23072-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.2 | 11.8 | 13.5 | 12 | 0.97767
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-15 | 50-CG-38476-01C02-H CML-15 | Yes | FPSO 2015 | Pipe Wall Thickness | 23647 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 12.15 | CML-15 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.7 | 6 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 12.6 | 12.5 | 10.7 | 12.8 | 0.97468
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56141-01C02 | CML-5 | 50-DH-56141-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21363 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 19.45 | CML-5 | CML: Reducing Tee | 6 | 2081-02-10 | 2077-04-05 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 18.1 | 9 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.6 |  | 20.3 | 20 | 19.4 | 18.1 | 0.97468
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-2 | 80-CG-38459-09C02-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 24261 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 19.95 | CML-2 | CML: Elbow | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A2: Right Quadrant |  | 11.27 | 7 | 9.135 | 18.6 | 3 O'Clock | 150 | 14.27 | 150-PG-23026-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.6 |  | 20.3 | 18.6 | 20 | 20.9 | 0.97468
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-7 | 200-PL-20008-01C02-H CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8804 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 5.975 | CML-7 | CML: Fitting | 3 | 2023-08-21 | 2023-07-24 | 2015-02-21 07:00 | 2.5 | 0.37641 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 5.9 | 5.7 | 6.3 | 0.25
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-4 | 50-PW-44012-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23163 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.025 | CML-4 | CML: Pipe Length | 3 | 2019-09-11 | 2020-05-15 | 2015-05-11 07:00 | 2.5 | 0.48372 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0.53428 | 5.1 | 5.2 | 5.2 | 4.6 | 0.28723
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-2 | 25-VA-23054-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23359 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 16.125 | CML-2 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2015-07-20 07:00 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 15.3 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 | 6.2317 | 15.6 | 15.3 | 16.1 | 17.5 | 0.97425
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-10 | 50-FG-45024-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12650 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 8.6333 | CML-10 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.8 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.77 |  | 9.7 | 8.4 | 7.8 |  | 0.97125
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-1 | 50-PW-44040-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 1976 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.05 | CML-1 | CML: Elbow | 3 | 2016-05-19 | 2016-09-12 | 2014-03-27 07:00 | 2.5 | 1.0244 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.3 | 5.1 | 5.1 | 0.25166
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13098 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 21.625 | CML-8 | CML: Pipe Length | 3 | 2015-12-23 | 2015-04-30 | 2014-01-10 09:00 | 15.88 | 2.3693 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 3 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 |  | 21.2 | 20.5 | 22.1 | 22.7 | 0.97082
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-10 | 300-PF-20001-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21148 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.65 | CML-10 | CML: Elbow | 6 | 2015-10-16 | 2015-03-17 | 2014-07-16 07:30 | 2.5 | 4.9549 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.7 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.5 | 9.4 | 11 | 8.7 | 0.96782
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-14 | 80-CG-38459-09C02-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23711 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 10.95 | CML-14 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 9.8 | 3 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.5 | 9.8 | 11.7 | 11.8 | 0.96782
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-9 | 50-CG-38470-01C02-P CML-9 | Yes | FPSO 2015 | Pipe Wall Thickness | 23615 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 11.075 | CML-9 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.7 | 12 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 11.8 | 11.7 | 11.1 | 0.96738
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-6 | 250-PW-20039-01C03-P CML-6 | Yes | FPSO 2015 | Pipe Wall Thickness | 22970 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.2 | CML-6 | CML: Elbow | 6 | 2025-07-31 | 2024-11-20 | 2015-05-04 07:00 | 2.5 | 0.55611 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 8.2 | 3 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | 2.094 | 10.1 | 8.2 | 9.8 | 8.7 | 0.89815
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-2 | 50-PW-44015-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22707 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 4.875 | CML-2 | CML: Elbow | 3 | 2019-07-31 | 2020-03-29 | 2015-04-28 07:00 | 2.5 | 0.49275 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0.70674 | 5 | 4.7 | 5.2 | 4.6 | 0.27538
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-23 | 100-FG-45001-09C02 CML-23 | Yes | FPSO 2015 | Pipe Wall Thickness | 23328 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 12.2 | CML-23 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 11.2 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | -0.72362 | 11.2 | 12.2 | 13.5 | 11.9 | 0.96264
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-2 | 300-PG-20048-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21472 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 13.6 | CML-2 | CML: Elbow | 6 | 2019-06-11 | 2018-05-11 | 2014-06-28 09:30 | 4.9 | 1.5534 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.6 | 3 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 13.3 | 12.6 | 13.6 | 14.9 | 0.96264
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-11 | 150-PG-23506-25C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2785 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 23 | CML-11 | CML: Pipe Length | 3 | 2027-01-22 | 2023-08-11 | 2014-03-15 09:00 | 15.88 | 0.44454 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 21.6 | 9 O'Clock | 50 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.72 |  | 23.8 | 23.3 | 23.3 | 21.6 | 0.96264
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-20 | 300-PG-20004-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 6143 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.3 | CML-20 | CML: Pipe Length | 6 | 2024-02-19 | 2022-03-17 | 2014-07-11 07:30 | 4.9 | 0.87352 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 15.6 | 14 | 14.3 | 13.3 | 0.96264
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-13 | 150-WC-40006-01C02 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 20032 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.05 | CML-13 | CML: type TBC | 3 | 2015-02-02 | 2015-04-09 | 2013-11-17 | 2.5 | 1.8142 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.1 | 5.3 | 5.1 | 0.25166
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20069-01C02-P | CML-6 | 100-PL-20069-01C02-P CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 21560 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 5.425 | CML-6 | CML: Elbow | 3 | 2018-04-01 | 2018-05-29 | 2014-07-17 07:30 | 2.5 | 0.72767 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 9 O'Clock | 100 | 6.02 | 100-PL-20069-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.6 | 5.5 | 5.2 | 0.17078
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-5 | 50-PL-20033-01C02 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 2269 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 5.35 | CML-5 | CML: Equal Tee | 3 | 2020-06-23 | 2021-03-27 | 2014-03-16 11:30 | 2.5 | 0.43019 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.3 | 5.2 | 5.4 | 0.1291
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38459-09C02-P | CML-25 | 80-CG-38459-09C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 5693 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 2.916mm/ yr | [34 empty] | Low alarm breach | 15.725 | CML-25 | CML: Cap End | 3 | 2016-04-03 | 2015-01-22 | 2014-06-21 14:00 | 2.5 | 6.6642 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 14.4 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 |  | 16.7 | 15.9 | 15.9 | 14.4 | 0.96047
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20503-03C03-P | CML-1 | 50-PF-20503-03C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7742 |  | 2015-01-10 10:00 | 2015-01-10 12:00 | [36 empty] | 8.775 | CML-1 | CML: Elbow | 6 | 2020-12-01 | 2020-10-09 | 2015-01-10 10:00 | 2.5 | 0.83121 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.4 | 12 O'Clock | 50 | 8.74 | 50-PF-20503-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 8.9 | 9.6 | 9.2 | 0.96047
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-19 | 50-WC-40451-01C02 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10159 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 1.904mm/ yr | [35 empty] | 5.025 | CML-19 | CML: type TBC | 3 | 2015-01-04 | 2015-03-08 | 2013-11-09 | 2.5 | 1.9043 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 4.7 | 5.1 | 5.3 | 0.25
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-7 | 80-PG-20046-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21466 | Protective mesh removed | 2014-06-28 08:00 | 2014-06-28 09:00 | [36 empty] | 12.2 | CML-7 | CML: Elbow | 6 | 2053-09-20 | 2047-07-30 | 2014-06-28 08:00 | 2.5 | 0.21398 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 3 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 12.7 | 10.9 | 12.1 | 13.1 | 0.95917
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-3 | 200-PG-20300-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5868 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | [36 empty] | 12.75 | CML-3 | CML: Elbow | 6 | 2022-07-11 | 2020-11-16 | 2014-06-25 09:30 | 3.3 | 1.0311 | A2: Right Quadrant |  | 6.7 | 3.3 | 5 | 11.6 | 3 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 13.2 | 11.6 | 12.4 | 13.8 | 0.95743
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-1 | 80-PL-44008-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 5738 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 5.95 | CML-1 | CML: Equal Tee | 3 | 2030-01-26 | 2032-01-04 | 2014-06-22 14:00 | 2.5 | 0.17939 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 50 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.3 | 7.1 | 5.6 | 0.79373
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-8 | 300-PG-20049-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21494 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | Check Corrosion Rate of 0.344mm/ yr | 39 | Kirstie Albone | 2017-03-23 13:29 | [32 empty] | 15 | CML-8 | CML: Elbow | 6 | 2040-08-16 | 2035-09-25 | 2014-06-28 10:45 | 4.9 | 0.34412 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 12 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 13.9 | 14.6 | 15.4 | 16.1 | 0.95568
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-2 | 50-PW-44013-01X01 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10316 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.825 | CML-2 | CML: Elbow | 3 | 2014-11-06 | 2015-01-02 | 2013-11-10 | 2.5 | 2.1179 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.2 | 4.7 | 4.8 | 0.263
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-49 | 300-PF-20003-03C03-P CML-49 |  | FPSO 2014 | Pipe Wall Thickness | 21787 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 13.3 | CML-49 | CML: Fitting | 6 | 2019-05-24 | 2018-03-02 | 2014-10-01 07:00 | 4.1 | 1.7003 | A3: Inside Quadrant |  | 8.27 | 4.1 | 6.185 | 12 | 6 O'Clock | 250 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 13.4 | 14.3 | 12 | 13.5 | 0.95568
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-14 | 150-WC-40006-01C02 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 20033 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5 | CML-14 | CML: type TBC | 3 | 2015-02-02 | 2015-04-09 | 2013-11-17 | 2.5 | 1.8142 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 5 | 4.7 | 5.1 | 0.21602
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44513-01C02 | CML-1 | 80-PL-44513-01C02 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 7966 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:05 | [32 empty] | 5.725 | CML-1 | CML: Elbow | 3 | 2039-02-11 | 2042-02-07 | 2015-01-18 10:30 | 2.5 | 0.11627 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.5 | 5.3 | 5.4 | 5.7 | 0.54391
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-1 | 50-PW-44009-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5812 | Protective mesh removed | 2014-06-24 07:00 | 2014-06-24 08:00 | [36 empty] | 9.5 | CML-1 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2014-06-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 10.2 | 9.7 | 8.7 | 9.4 | 0.62716
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23029-25C02-P | CML-2 | 80-PG-23029-25C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20560 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [36 empty] | 15.65 | CML-2 | CML: Elbow | 3 | 2023-05-31 | 2021-07-31 | 2014-07-02 07:00 | 7.5 | 0.77367 | A3: Inside Quadrant |  | 12.24 | 7.5 | 8.9175 | 14.4 | 6 O'Clock | 80 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 15.6 | 16.7 | 14.4 | 15.9 | 0.95394
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-39 | 150-WF-71372-01K01 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 5369 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.675 | CML-39 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.7 | 4.4 | 3.3 | 0.51881
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42042-01S01 | CML-4 | 50-CI-42042-01S01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3451 | Rope Access | 2014-05-13 07:00 | 2014-05-13 08:00 | Check Corrosion Rate of 0.675mm/ yr | [35 empty] | 5.475 | CML-4 | CML: type TBC | 1 | 2017-12-01 | 2016-12-02 | 2014-05-13 07:00 | 2.5 | 0.67458 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-CI-42042-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 5.5 | 6.5 | 0.73201
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-15 | 80-CG-38459-09C02-P CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23712 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 10.425 | CML-15 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 9.6 | 3 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.2 | 9.6 | 10.1 | 11.8 | 0.9535
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-12 | 50-PL-45016-03C03 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10452 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.775 | CML-12 | CML: type TBC | 6 | 2016-03-28 | 2015-12-02 | 2013-11-13 | 0.99 | 2.743 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.5 | 12 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.51 |  | 7.5 | 8.8 | 9 | 9.8 | 0.9535
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-42 | 300-PF-20001-03C03-P CML-42 |  | FPSO 2014 | Pipe Wall Thickness | 21180 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.596mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:49 | [32 empty] | 14.875 | CML-42 | CML: Elbow | 6 | 2029-02-15 | 2026-04-20 | 2014-07-16 07:30 | 4.9 | 0.59601 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 13.6 | 15.1 | 15.9 | 14.9 | 0.9535
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-1 | 300-PG-20502-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 23888 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 13.725 | CML-1 | CML: Reducer | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 12.7 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 12.7 | 13.5 | 15 | 13.7 | 0.9535
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-1 | 300-PG-20502-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20748 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 13.725 | CML-1 | CML: type TBC | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 12.7 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 12.7 | 13.5 | 15 | 13.7 | 0.9535
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-14 | 250-PW-44509-01C03-P CML-14 | Yes | FPSO 2015 | Pipe Wall Thickness | 22999 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.05 | CML-14 | CML: Elbow | 6 | 2025-08-06 | 2024-11-26 | 2015-05-05 07:00 | 2.5 | 0.55532 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.2 | 9 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | 0.55584 | 9.6 | 9.1 | 9.3 | 8.2 | 0.60277
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-7 | 150-PG-23506-25C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2781 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.475 | CML-7 | CML: Pipe Length | 3 | 2027-01-22 | 2023-08-11 | 2014-03-15 09:00 | 15.88 | 0.44454 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 21.6 | 9 O'Clock | 50 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.72 |  | 23.3 | 23.3 | 21.7 | 21.6 | 0.9535
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-1 | 100-DH-56088-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5194 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 10.325 | CML-1 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.9 | 9 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10.7 | 10.8 | 10.9 | 8.9 | 0.9535
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-11 | 50-CG-38452-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 23811 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.475 | CML-11 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8.5 | 8.7 | 9.5 | 7.2 | 0.9535
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-10 | 100-WC-40516-1CG CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 8683 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 | Check Corrosion Rate of 0.328mm/ yr |  | Administrator | 2015-09-08 11:55 | [32 empty] | 9.15 | CML-10 | CML: Pipe Length | 3 | 2031-11-08 | 2027-03-13 | 2015-02-13 07:00 | 2.5 | 0.32846 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 8 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 10.2 | 10 | 8 | 8.4 | 1.1121
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-5 | 50-CG-38488-09C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23594 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 9.325 | CML-5 | CML: Elbow | 3 | 2045-11-25 | 2037-06-19 | 2015-09-15 15:30 | 2.5 | 0.19196 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 3 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | 0.086047 | 9.1 | 8.3 | 9.3 | 10.6 | 0.9535
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-3 | 200-PG-23008-15S01-A CML-3 | Yes | FPSO 2013 | Pipe Wall Thickness | 10089 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 20.875 | CML-3 | CML: Elbow | 1 | 2014-11-28 | 2014-03-31 | 2013-11-07 | 14.06 | 5.9915 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 22.3 | 20.4 | 0.95
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40510-1CG | CML-4 | 100-WC-40510-1CG CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8664 | Material Class Not Selectable. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Feb. 2020). RBI to be updated | 2015-02-12 11:00 | 2015-02-12 12:00 | Check Corrosion Rate of 0.329mm/ yr |  | Administrator | 2015-09-08 12:16 | [32 empty] | 8.45 | CML-4 | CML: Elbow | 3 | 2031-10-30 | 2027-03-07 | 2015-02-12 11:00 | 2.5 | 0.3289 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 8 | 12 O'Clock | 100 | 8.56 | 100-WC-40510-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.9 | 8.4 | 8.5 | 0.36968
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-24 | 50-PF-20300-03C03-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21590 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.525 | CML-24 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.8 | 12 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9.4 | 9 | 10.9 | 0.95
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-38 | 150-WF-71372-01K01 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 5368 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.8 | CML-38 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.8 | 4.4 | 3.7 | 0.45461
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38486-09C02-P |  | 80-CG-38486-09C02-P |  | FPSO 2015 | Pipe Wall Thickness | 23653 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 11.175 | 80-CG-38486-01C02-H | Piping | 3 | 2043-04-25 |  | 2015-10-28 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 9.9 | 3 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 11.3 | 9.9 | 11.3 | 12.2 | 0.95
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-4 | 50-PW-44015-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5714 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 4.85 | CML-4 | CML: Elbow | 3 | 2016-11-01 | 2017-03-15 | 2014-06-22 10:00 | 2.5 | 0.8879 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 4.2287 | 4.7 | 5 | 4.6 | 5.1 | 0.23805
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-9 | 50-CG-38488-09C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23598 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 12.05 | CML-9 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-15 15:30 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 10.7 | 9 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 | 0.68837 | 12.2 | 12.9 | 12.4 | 10.7 | 0.94692
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-11 | 300-PF-20001-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21149 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.65 | CML-11 | CML: Elbow | 6 | 2015-10-31 | 2015-03-29 | 2014-07-16 07:30 | 2.5 | 4.8659 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.8 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.5 | 11 | 9.3 | 8.8 | 0.94692
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-2 | 80-CG-38459-09C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23699 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 15.65 | CML-2 | CML: Reducing Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 14.7 | 12 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.2 |  | 14.7 | 15.2 | 16.9 | 15.8 | 0.94692
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-16 | 80-PL-44008-01C02 CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 5753 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 5.45 | CML-16 | CML: Pipe Length | 3 | 2030-01-26 | 2032-01-04 | 2014-06-22 14:00 | 2.5 | 0.17939 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.9 | 5.3 | 0.3
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56026-01C02 | CML-1 | 80-DH-56026-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3475 | Rope Access | 2014-05-13 13:00 | 2014-05-13 14:00 | [36 empty] | 9.825 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-13 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.6 | 6 O'Clock | 80 | 5.49 | 80-DH-56026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 10.9 | 9.8 | 8.6 | 10 | 0.94648
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-23 | 250-PG-23003-06C02-PA CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 1429 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.729mm/ yr | [35 empty] | 6.775 | CML-23 | CML: type TBC | 3 | 2018-03-28 | 2018-05-25 | 2014-04-07 07:00 | 2.5 | 0.72931 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.9 | 7.4 | 7.4 | 0.94648
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-7 | 80-PL-44008-01C02 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 5744 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 5.425 | CML-7 | CML: Reducing Tee | 3 | 2030-01-26 | 2032-01-04 | 2014-06-22 14:00 | 2.5 | 0.17939 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 40 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.4 | 5.3 | 5.5 | 0.095743
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-7 | 50-PL-20033-01C02 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 21836 |  | 2014-10-12 07:00 | 2014-10-12 12:00 | [36 empty] | 5.525 | CML-7 | CML: Fitting | 3 | 2043-01-15 | 2046-03-21 | 2014-10-12 07:00 | 2.5 | 0.10255 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.17396 | 5.4 | 5.5 | 5.7 | 5.5 | 0.12583
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-22 | 250-PG-23004-06C03-A CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 23389 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.5 | CML-22 | CML: Elbow | 6 | 2359-02-25 | 2293-02-06 | 2015-07-21 07:00 | 8.55 | 0.02807 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.2 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.65 | -0.61286 | 20.2 | 20.2 | 18.2 | 19.4 | 0.94516
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-37 | 100-DC-57036-01C02 CML-37 |  | FPSO 2014 | Pipe Wall Thickness | 1443 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 1.317mm/ yr | [35 empty] | 5.15 | CML-37 | CML: type TBC | 3 | 2016-02-01 | 2016-03-04 | 2014-04-07 07:00 | 2.5 | 1.3175 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 6 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 5.4 | 4.9 | 5.3 | 0.23805
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-11 | 100-DC-57036-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1417 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 1.317mm/ yr | [35 empty] | 5.275 | CML-11 | CML: type TBC | 3 | 2016-02-01 | 2016-03-04 | 2014-04-07 07:00 | 2.5 | 1.3175 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 | 5.6 | 5.6 | 0.37749
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-21 | 150-WF-71372-01K01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 5351 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.9 | CML-21 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 4.3 | 4.3 | 3.7 | 0.4899
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-20 | 150-WF-71372-01K01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 5350 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4 | CML-20 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 4.6 | 4.3 | 3.8 | 0.57155
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57067-01C02 | CML-2 | 50-DC-57067-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1339 | Rope access | 2014-04-04 08:00 | 2014-04-04 09:00 | Check Corrosion Rate of 0.76mm/ yr | [35 empty] | 5.55 | CML-2 | CML: type TBC | 3 | 2017-05-30 | 2017-11-03 | 2014-04-04 08:00 | 2.5 | 0.76009 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DC-57067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 6.5 | 5.5 | 0.68069
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57068-01C02 | CML-9 | 50-DC-57068-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1337 | Rope access | 2014-04-04 07:00 | 2014-04-04 08:00 | Check Corrosion Rate of 0.76mm/ yr | [35 empty] | 5.35 | CML-9 | CML: type TBC | 3 | 2017-05-30 | 2017-11-03 | 2014-04-04 07:00 | 2.5 | 0.76019 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DC-57068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 5.4 | 4.9 | 5.5 | 0.31091
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-16 | 50-DN-56101-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 856 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.375 | CML-16 | CML: Elbow | 3 | 2017-05-22 | 2017-10-25 | 2014-04-02 14:00 | 2.5 | 0.76444 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.5 | 4.9 | 5.8 | 5.3 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-7 | 100-FH-43104-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12758 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 7.9667 | CML-7 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.9 | 12 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 8.7 | 8.3 |  | 0.94516
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56134-01C02 | CML-5 | 50-DN-56134-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1317 |  | 2014-03-31 10:00 | 2014-03-31 10:15 | [36 empty] | 5.45 | CML-5 | CML: type TBC | 3 | 2017-05-12 | 2017-10-13 | 2014-03-31 10:00 | 2.5 | 0.7699 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DN-56134-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.6 | 5.9 | 5.4 | 0.42032
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-7 | 50-DC-57043-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2152 | Rope Access | 2014-03-29 13:00 | 2014-03-29 15:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 5.275 | CML-7 | CML: Elbow | 3 | 2017-05-03 | 2017-10-04 | 2014-03-29 13:00 | 2.5 | 0.77469 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 5.5 | 4.9 | 5.1 | 0.3304
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-4 | 50-DC-57043-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2149 | Rope Access | 2014-03-29 13:00 | 2014-03-29 15:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 5.75 | CML-4 | CML: Pipe Length | 3 | 2017-05-03 | 2017-10-04 | 2014-03-29 13:00 | 2.5 | 0.77469 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.8 | 4.9 | 5.8 | 6.5 | 0.65574
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-3 | 50-DC-57043-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2148 | Rope Access | 2014-03-29 13:00 | 2014-03-29 15:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 5.075 | CML-3 | CML: Elbow | 3 | 2017-05-03 | 2017-10-04 | 2014-03-29 13:00 | 2.5 | 0.77469 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.1 | 5 | 5.3 | 0.17078
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-2 | 50-DC-57043-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2147 | Rope Access | 2014-03-29 13:00 | 2014-03-29 15:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 5.15 | CML-2 | CML: Elbow | 3 | 2017-05-03 | 2017-10-04 | 2014-03-29 13:00 | 2.5 | 0.77469 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 5 | 5.7 | 0.36968
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-7 | 50-DC-57044-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2145 | Rope Access | 2014-03-29 10:30 | 2014-03-29 12:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 5.725 | CML-7 | CML: Pipe Length | 3 | 2017-05-02 | 2017-10-03 | 2014-03-29 10:30 | 2.5 | 0.77495 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.7 | 5.9 | 4.9 | 6.4 | 0.62383
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-7 | 50-DC-57025-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2118 |  | 2014-03-29 07:00 | 2014-03-29 08:00 | Check Corrosion Rate of 0.775mm/ yr | [35 empty] | 5.4 | CML-7 | CML: Elbow | 3 | 2017-05-02 | 2017-10-02 | 2014-03-29 07:00 | 2.5 | 0.77533 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 4.9 | 5.9 | 5.2 | 0.4397
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-8 | 150-WF-71372-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5338 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.575 | CML-8 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.7 | 3.8 | 3.5 | 0.22174
FL01 | Montara_Topside | Yes | Chemical Injection (42) | Pipework | 150-FL-43174-01C02 | CML-5 | 150-FL-43174-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7488 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 1.093mm/ yr | [34 empty] | Low alarm breach | 4.375 | CML-5 | CML: Reducer | 1 | 2016-03-12 | 2015-07-31 | 2015-04-13 07:00 | 2.5 | 1.0929 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.5 | 9 O'Clock | 50 | 5.54 | 50-CI-42045-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4.3 | 5.7 | 4 | 3.5 | 0.94296
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-15 | 50-CG-38487-09C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20854 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.825 | CML-15 | CML: Elbow | 3 | 2221-12-21 | 2167-10-29 | 2014-10-02 07:00 | 2.5 | 0.0299 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 | 3.3692 | 10.2 | 8.7 | 9.5 | 10.9 | 0.94296
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-28 | 50-DC-57020-01C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 2470 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.799mm/ yr | [35 empty] | 5.275 | CML-28 | CML: type TBC | 3 | 2017-03-20 | 2017-08-16 | 2014-03-20 09:30 | 2.5 | 0.79892 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.8 | 5.3 | 4.9 | 5.1 | 0.38622
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-27 | 50-DC-57020-01C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 2469 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.799mm/ yr | [35 empty] | 5 | CML-27 | CML: type TBC | 3 | 2017-03-20 | 2017-08-16 | 2014-03-20 09:30 | 2.5 | 0.79892 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 | 4.9 | 5.2 | 0.14142
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-24 | 50-DC-57020-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 2466 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.799mm/ yr | [35 empty] | 5.15 | CML-24 | CML: type TBC | 3 | 2017-03-20 | 2017-08-16 | 2014-03-20 09:30 | 2.5 | 0.79892 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.1 | 5.5 | 5.1 | 0.25166
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-9 | 50-CG-38487-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20809 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.825 | CML-9 | CML: Elbow | 3 | 2189-07-31 | 2143-11-05 | 2014-07-18 11:00 | 2.5 | 0.0354 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 10.9 | 10.2 | 9.5 | 8.7 | 0.94296
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20070-01C02-P | CML-4 | 100-PL-20070-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21564 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.425 | CML-4 | CML: Elbow | 3 | 2021-01-14 | 2021-04-16 | 2014-07-17 07:30 | 2.5 | 0.46145 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 9 O'Clock | 100 | 6.02 | 100-PL-20070-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 7.1 | 6.7 | 6.4 | 5.5 | 0.68007
FL01 | Montara_Topside | Yes | Chemical Injection (42) | Pipework | 150-FL-43174-01C02 | CML-6 | 150-FL-43174-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7479 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 1.093mm/ yr | [34 empty] | Low alarm breach | 4.575 | CML-6 | CML: Elbow | 1 | 2016-03-12 | 2015-07-31 | 2015-04-13 07:00 | 2.5 | 1.0929 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.5 | 9 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4.5 | 5.8 | 4.5 | 3.5 | 0.94296
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-17 | 80-CG-38459-09C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21426 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 17.4 | CML-17 | CML: Equal Tee | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 16.4 | 3 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.3 |  | 18.1 | 16.4 | 16.8 | 18.3 | 0.94163
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-19 | 80-CG-38459-09C02-P CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 23716 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 15.5 | CML-19 | CML: Reducing Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 14.3 | 6 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.8 |  | 16.6 | 15.6 | 14.3 | 15.5 | 0.94163
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20302-03C03-P | CML-10 | 200-PG-20302-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5864 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 13.9 | CML-10 | CML: Fitting | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 10:30 | 3.3 | 0 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 13.3 | 9 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 15.3 | 13.4 | 13.6 | 13.3 | 0.94163
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-19 | 100-FG-45001-09C02 CML-19 | Yes | FPSO 2015 | Pipe Wall Thickness | 23324 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.6 | CML-19 | CML: type TBC | 3 | 2054-07-05 | 2043-07-19 | 2015-07-11 07:00 | 4.7 | 0.15637 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.8 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | -0.1809 | 10.9 | 10.8 | 12.8 | 11.9 | 0.94163
FH02 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43313-01S01-P | CML-7 | 150-FH-43313-01S01-P CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 20481 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.5 | CML-7 | CML: Elbow | 1 | 2022-02-10 | 2019-07-19 | 2014-10-03 07:00 | 2.5 | 0.52964 | A4: Left Quadrant |  | 6.11 | 2.5 | 3.8606 | 6.4 | 9 O'Clock | 150 | 7.11 | 150-FH-43313-01S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.4 | 8.7 | 7.5 | 6.4 | 0.94163
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-VA-23056-01C02 | CML-2 | 50-VA-23056-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8062 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 6.7 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-22 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-VA-23056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 7.4 | 7.6 | 6.1 | 0.94163
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-14 | 100-FG-45001-09C02 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10429 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 11.25 | CML-14 | CML: type TBC | 3 | 2016-03-27 | 2015-06-26 | 2013-11-13 | 4.7 | 2.2785 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 10.1 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 10.1 | 11.3 | 11.2 | 12.4 | 0.93986
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-7 | 150-WF-71372-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5337 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.975 | CML-7 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.6 | 4.4 | 3.6 | 3.3 | 0.62383
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-4 | 150-WF-71372-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5334 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.675 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 3 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 3.3 | 3.6 | 4.4 | 0.49917
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13094 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 21.7 | CML-4 | CML: Pipe Length | 3 | 2015-12-23 | 2015-04-30 | 2014-01-10 09:00 | 15.88 | 2.3693 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 3 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 |  | 22.1 | 20.5 | 21.5 | 22.7 | 0.93808
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-19 | 50-PW-44040-01C02 CML-19 | yes | FPSO 2015 | Pipe Wall Thickness | 23254 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5 | CML-19 | CML: Elbow | 3 | 2020-06-10 | 2021-03-13 | 2015-05-11 07:00 | 2.5 | 0.43226 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.089024 | 4.7 | 5.3 | 5 | 5 | 0.24495
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-39 | 300-PF-20501-03C03-P CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 23535 | Re-check | 2015-07-29 07:00 | 2015-07-29 12:00 | [36 empty] | 13.9 | CML-39 | CML: type TBC | 6 | 2028-03-05 | 2025-07-09 | 2015-07-29 07:00 | 4.9 | 0.63435 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 12.9 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | -13.6875 | 15.1 | 14.1 | 13.5 | 12.9 | 0.93808
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-2 | 50-PL-23516-03C03 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7790 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:02 | [32 empty] | 13.675 | CML-2 | CML: Equal Tee | 6 | 2075-10-24 | 2074-08-12 | 2015-01-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 12.8 | 12 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.3 |  | 12.8 | 13.5 | 15 | 13.4 | 0.93586
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1369 | Rope access | 2014-04-05 09:30 | 2014-04-05 10:30 | [36 empty] | 18.05 | CML-2 | CML: type TBC | 3 | 2031-10-01 | 2033-09-19 | 2014-04-05 09:30 | 2.5 | 0.1657 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DC-57042-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 7.3 | 5.4 | 5.4 | 5.5 | 0.93452
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20302-03C03-P | CML-4 | 200-PG-20302-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5857 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 12.7 | CML-4 | CML: Elbow | 6 | 2020-07-28 | 2019-04-12 | 2014-06-25 10:30 | 3.3 | 1.3121 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 11.3 | 9 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 13.1 | 13.2 | 13.2 | 11.3 | 0.93452
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-2 | 50-CG-38474-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23626 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 10.65 | CML-2 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.9 | 6 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.5 | 10.2 | 9.9 | 12 | 0.93274
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-1 | 50-PW-44015-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22706 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 4.85 | CML-1 | CML: Elbow | 3 | 2019-07-31 | 2020-03-29 | 2015-04-28 07:00 | 2.5 | 0.49275 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | -0.47116 | 4.6 | 5 | 4.8 | 5 | 0.19149
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-1 | 300-PG-20506-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13215 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.675 | CML-1 | CML: type TBC | 6 | 2024-08-09 | 2022-08-05 | 2014-02-04 15:00 | 4.9 | 0.8368 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 3 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 15.9 | 13.7 | 14.3 | 14.8 | 0.93229
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40510-1CG | CML-5 | 100-WC-40510-1CG CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8665 | Material Class Not Selectable.Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Feb. 2020). RBI to be updated | 2015-02-12 11:00 | 2015-02-12 12:00 | Check Corrosion Rate of 0.329mm/ yr |  | Administrator | 2015-09-08 12:17 | [32 empty] | 8.3 | CML-5 | CML: Elbow | 3 | 2031-10-30 | 2027-03-07 | 2015-02-12 11:00 | 2.5 | 0.3289 | A2: Right Quadrant |  | 5.56 | 2.5 | 4.03 | 8 | 3 O'Clock | 100 | 8.56 | 100-WC-40510-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.6 | 8 | 8.4 | 8.2 | 0.2582
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-11 | 250-PW-20022-01C03-P CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 23109 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 8.7 | CML-11 | CML: Elbow | 6 | 2025-09-07 | 2024-12-26 | 2015-05-10 07:00 | 2.5 | 0.5514 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 8.2 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | 1.3419 | 8.8 | 8.2 | 8.6 | 9.2 | 0.41633
FG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-FG-45024-01C02 | CML-5 | 50-FG-45024-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2551 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 10.175 | CML-5 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 12 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.6 | 10.7 | 11.2 | 0.93229
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-18 | 50-DH-56137-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23446 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 18.8 | CML-18 | CML: Elbow | 3 | 2024-11-15 | 2020-01-20 | 2015-07-23 07:00 | 2.5 | 1.6517 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 17.9 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 | -0.82806 | 18.5 | 20.1 | 18.7 | 17.9 | 0.93095
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-10 | 200-PG-23505-09C02-A CML-10 | no | FPSO 2015 | Pipe Wall Thickness | 23411 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 17.95 | CML-10 | CML: Pipe Length | 3 | 2022-10-10 | 2021-06-08 | 2015-07-22 07:00 | 14.06 | 0.44849 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.3 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.24 | 0.08753 | 17.3 | 18.3 | 18.2 | 18 | 0.45092
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56087-01C02 | CML-2 | 100-DH-56087-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8032 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:30 | [32 empty] | 7.275 | CML-2 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-20 14:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 12 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 8 | 8.1 | 6.8 | 0.92871
FH01 | Montara_Topside | Yes | Chemical Injection (42) | Pipework | 150-FH-43141-01C02 | CML-4 | 150-FH-43141-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 7487 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | Check Corrosion Rate of 1.147mm/ yr | [34 empty] | Low alarm breach | 4.325 | CML-4 | CML: Elbow | 1 | 2016-01-24 | 2015-06-24 | 2015-04-13 07:00 | 2.5 | 1.1465 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 3.4 | 12 O'Clock | 50 | 5.54 | 50-CI-42045-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 4.3 | 5.6 | 4 | 0.92871
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23018-09C03-A | CML-7 | 200-PG-23018-09C03-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13068 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 21.575 | CML-7 | CML: type TBC | 6 | 2042-06-15 | 2036-04-09 | 2014-01-10 07:00 | 10.17 | 0.35962 | A1: Outside Quadrant |  | 14.62 | 10.17 | 12.395 | 20.4 | 12 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.23 |  | 20.4 | 22.5 | 22.1 | 21.3 | 0.92871
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-35 | 150-PG-23506-25C02 CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 20089 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.725 | CML-35 | CML: Pipe Length | 3 | 2019-02-24 | 2017-09-12 | 2014-05-29 07:00 | 15.88 | 1.0578 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 20.9 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.02 | 36.5001 | 22.8 | 22.2 | 21 | 20.9 | 0.92871
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-10 | 200-PG-23505-09C02-A CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2691 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.475 | CML-10 | CML: Pipe Length | 3 | 2017-09-19 | 2017-02-07 | 2014-03-12 09:00 | 14.06 | 0.97547 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.5 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.44 | 0 | 17.5 | 18.7 | 18.7 | 19 | 0.66521
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-13 | 50-CG-38487-09C02-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23582 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 12.425 | CML-13 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 11.5 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 | 0.53207 | 11.5 | 12.1 | 12.4 | 13.7 | 0.92871
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20045-03C03-P | CML-3 | 80-PG-20045-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21459 | Protective mesh removed | 2014-06-29 11:00 | 2014-06-29 12:00 | [36 empty] | 21.1 | CML-3 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-06-29 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 20.2 | 12 O'Clock | 80 | 11.13 | 80-PG-20045-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 |  | 20.2 | 20.9 | 22.4 | 20.9 | 0.92736
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20031-01C03-P | CML-3 | 150-PG-20031-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 23865 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.45 | CML-3 | CML: Elbow | 6 | 2022-12-22 | 2021-07-31 | 2014-09-26 07:00 | 2.5 | 0.88546 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 9.8 | 3 O'Clock | 150 | 10.97 | 150-PG-20031-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.9 | 9.8 | 10.3 | 11.8 | 0.92556
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-7 | 50-CG-38488-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20825 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 11.35 | CML-7 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 10.5 | 9 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 12.1 | 12.2 | 10.6 | 10.5 | 0.92556
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-11 | 400-FH-43500-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5647 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 7.65 | CML-11 | CML: type TBC | 3 | 2019-08-18 | 2018-10-23 | 2014-06-21 07:00 | 2.5 | 0.87155 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7 | 3 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 9 | 7 | 7.5 | 7.1 | 0.92556
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-3 | 50-PW-44012-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2017 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 5.2 | CML-3 | CML: Elbow | 3 | 2016-05-19 | 2016-09-12 | 2014-03-27 09:30 | 2.5 | 1.0241 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.4 | 4.7 | 5.1 | 5.6 | 0.39158
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-43 | 150-WF-71372-01K01 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 5373 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.55 | CML-43 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.6 | 3.5 | 3.7 | 0.1291
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-2 | 50-PW-44009-01C03-P CML-2 | Yes | FPSO 2015 | Pipe Wall Thickness | 22809 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 8.725 | CML-2 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2015-04-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | 0.58871 | 8.9 | 8.9 | 8.2 | 8.9 | 0.35
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-3 | 300-PG-20049-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21489 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | Check Corrosion Rate of 0.53mm/ yr | 39 | Kirstie Albone | 2017-03-23 13:24 | [32 empty] | 14.225 | CML-3 | CML: Fitting | 6 | 2031-01-29 | 2027-11-26 | 2014-06-28 10:45 | 4.9 | 0.53013 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 9 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 15.6 | 13.9 | 13.7 | 13.7 | 0.9215
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-57 | 300-PF-20001-03C03-P CML-57 |  | FPSO 2016 | Pipe Wall Thickness | 24488 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 13.275 | CML-57 | CML: Elbow | 6 | 2026-09-28 | 2024-01-04 | 2016-07-09 07:00 | 4.1 | 0.76263 | A1: Outside Quadrant |  | 8.27 | 4.1 | 6.185 | 11.9 | 12 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 | 0.20977 | 11.9 | 13.8 | 13.8 | 13.6 | 0.9215
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-26 | 300-PF-20500-03C03-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 21646 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 17.625 | CML-26 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 16.9 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12 |  | 18.9 | 17.7 | 16.9 | 17 | 0.9215
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-14 | 100-PG-23028-25C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 453 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.375 | CML-14 | CML: Elbow | 3 | 2063-07-03 | 2048-03-11 | 2014-03-12 09:00 | 9.4 | 0.15402 | A4: Left Quadrant |  | 14.12 | 9.4 | 11.76 | 17 | 9 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 18.7 | 18.9 | 18.9 | 17 | 0.9215
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-3 | 200-PG-23008-15S01-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22325 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 5.8 | CML-3 | CML: type TBC | 3 | 2019-11-01 | 2020-07-09 | 2014-05-06 07:00 | 2.5 | 0.47334 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 7.1 | 5.8 | 5.2 | 5.1 | 0.92014
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-3 | 200-PG-23008-15S01-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1845 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 5.8 | CML-3 | CML: type TBC | 3 | 2019-11-01 | 2020-07-09 | 2014-05-06 07:00 | 2.5 | 0.47334 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 7.1 | 5.8 | 5.2 | 5.1 | 0.92014
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-4 | 50-PW-44040-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 23239 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 4.975 | CML-4 | CML: Elbow | 3 | 2020-06-10 | 2021-03-13 | 2015-05-11 07:00 | 2.5 | 0.43226 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.26707 | 4.7 | 5.1 | 4.9 | 5.2 | 0.22174
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-32 | 150-WF-71372-01K01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 5362 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.9 | CML-32 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 4.3 | 4.1 | 3.8 | 0.39158
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-7 | 250-PG-23004-06C03-A CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23374 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.5 | CML-7 | CML: Elbow | 6 | 2359-02-25 | 2293-02-06 | 2015-07-21 07:00 | 8.55 | 0.02807 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.2 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.65 | -0.78812 | 18.2 | 19.5 | 20.2 | 20.1 | 0.92014
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-2 | 50-PW-44009-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5813 | Protective mesh removed | 2014-06-24 07:00 | 2014-06-24 08:00 | [36 empty] | 9.075 | CML-2 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2014-06-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.7 | 12 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 8.9 | 9.8 | 8.9 | 0.49244
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-25 | 150-WF-71372-01K01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 5355 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.05 | CML-25 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 4.2 | 4.8 | 3.8 | 0.59722
SD01 | Montara_Topside | No | Steam (55) | Pipework | 150-SL-55001-01C02-H | CML-2 | 150-SL-55001-01C02-H CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23603 |  | 2015-09-28 07:00 | 2015-09-28 15:00 | [36 empty] | 5.35 | CML-2 | CML: Equal Tee | 3 | 2018-06-30 | 2018-02-05 | 2015-09-28 07:00 | 2.5 | 0.90681 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 5 | 9 O'Clock | 50 | 7.11 | 150-SL-55001-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5.5 | 5.5 | 5 | 0.23805
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-8 | 100-WC-40516-1CG CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8681 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 | Check Corrosion Rate of 0.328mm/ yr |  | Administrator | 2015-09-08 11:55 | [32 empty] | 8.25 | CML-8 | CML: Pipe Length | 3 | 2031-11-08 | 2027-03-13 | 2015-02-13 07:00 | 2.5 | 0.32846 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 8 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.6 | 8 | 8.2 | 0.25166
PL03 | Montara_Topside | Yes | Wellstream (57) | Pipework | 50-PL-57066-01C03 | CML-3 | 50-PL-57066-01C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22109 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 9.3 | CML-3 | CML: type TBC | 6 | 2032-12-29 | 2032-08-14 | 2014-10-18 07:00 | 2.5 | 0.31847 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 6 O'Clock | 50 | 8.74 | 50-PF-57066-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 10.5 | 9.4 | 8.3 | 9 | 0.92014
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-47 | 150-WF-71372-01K01 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 5377 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.825 | CML-47 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.6 | 3.8 | 4.4 | 3.5 | 0.40311
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-12 | 80-FH-43158-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12893 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 6.375 | CML-12 | CML: type TBC | 3 | 2034-10-31 | 2037-04-29 | 2014-01-22 11:00 | 2.5 | 0.13952 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 7.6 | 6.4 | 5.4 | 0.91788
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-6 | 50-PL-23515-01C03 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8655 |  | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:50 | [32 empty] | 9.475 | CML-6 | CML: Elbow | 6 | 2278-10-11 | 2273-09-03 | 2015-02-12 07:00 | 2.5 | 0.0235 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.7 | 6 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 10.8 | 9.3 | 8.7 | 9.1 | 0.91788
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-12 | 200-PG-23007-09C03-PA CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20699 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 20.675 | CML-12 | CML: Fitting | 6 | 2029-01-06 | 2025-09-19 | 2014-06-30 13:00 | 10.22 | 0.66609 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 19.9 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.68 |  | 20.3 | 20.5 | 22 | 19.9 | 0.91788
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-9 | 100-FH-43507-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8595 | Line is FFS. Current RBI frequency is 36m. Action: CML’s to Inspect in 48m. RBI to be updated | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-08 14:58 | [32 empty] | 8.475 | CML-9 | CML: Equal Tee | 3 | 2063-07-07 | 2057-06-06 | 2015-02-08 11:00 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.5 | 3 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.16 |  | 8.5 | 7.5 | 8.2 | 9.7 | 0.91788
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-19 | 300-PG-20005-03C03-P CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 22781 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 15.425 | CML-19 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.5 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 | 2.1252 | 16 | 14.8 | 16.4 | 14.5 | 0.91788
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-27 | 150-PG-23506-25C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 2801 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.875 | CML-27 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.1 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.22 |  | 22.1 | 22.1 | 23.9 | 23.4 | 0.91788
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-3 | 80-CG-38459-09C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23700 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 6.55 | CML-3 | CML: Elbow | 3 | 2051-05-21 | 2055-10-22 | 2015-10-30 07:00 | 2.5 | 0.07869 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.7 | 5.3 | 6.7 | 7.5 | 0.91469
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-37 | 150-WF-71372-01K01 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 5367 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.6 | CML-37 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.6 | 3.6 | 3.7 | 3.5 | 0.08165
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-29 | 150-WF-71372-01K01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 5359 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.625 | CML-29 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 6 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.7 | 3.7 | 3.5 | 3.6 | 0.095743
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-12 | 150-WF-71372-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5342 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.9 | CML-12 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 3 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4.2 | 3.5 | 4.3 | 3.6 | 0.40825
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-9 | 150-WF-71372-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5339 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.9 | CML-9 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 3 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.6 | 3.5 | 4.2 | 4.3 | 0.40825
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-3 | 50-DC-57043-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23128 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.125 | CML-3 | CML: Elbow | 3 | 2024-05-01 | 2025-07-03 | 2015-05-10 07:00 | 2.5 | 0.27828 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.089736 | 5 | 5.2 | 5 | 5.3 | 0.15
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-3 | 50-DC-57044-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23121 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.275 | CML-3 | CML: Elbow | 3 | 2024-05-01 | 2025-07-03 | 2015-05-10 07:00 | 2.5 | 0.27828 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.26914 | 5.3 | 5.5 | 5 | 5.3 | 0.20616
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-10 | 50-DC-57013-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22934 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.05 | CML-10 | CML: Elbow | 3 | 2024-03-17 | 2025-05-14 | 2015-05-02 07:00 | 2.5 | 0.28145 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -1.6023 | 5 | 5 | 5.1 | 5.1 | 0.057735
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-8 | 50-DC-57013-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22932 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.125 | CML-8 | CML: Elbow | 3 | 2024-03-17 | 2025-05-14 | 2015-05-02 07:00 | 2.5 | 0.28145 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.9614 | 5 | 5.1 | 5.1 | 5.3 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-5 | 50-DC-57013-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22929 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.625 | CML-5 | CML: Equal Tee | 3 | 2024-03-17 | 2025-05-14 | 2015-05-02 07:00 | 2.5 | 0.28145 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 3.2047 | 5.6 | 6.2 | 5.7 | 5 | 0.49244
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-3 | 80-CG-38459-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10953 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 18.25 | CML-3 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A4: Left Quadrant |  | 8.27 | 5.22 | 6.745 | 17.1 | 9 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.88 |  | 18.1 | 19.3 | 18.5 | 17.1 | 0.91469
FL02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-FL-43454-01C02-P | CML-20 | 50-FL-43454-01C02-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 2439 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | [36 empty] | 10.1 | CML-20 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-20 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.1 | 12 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.6 | 10.6 | 11.1 | 0.91287
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-8 | 50-CG-38488-09C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23597 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 11.8 | CML-8 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-15 15:30 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 10.5 | 9 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | 0.51628 | 11.9 | 12.6 | 12.2 | 10.5 | 0.91287
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-39 | 50-DH-56070-01C02 CML-39 |  | FPSO 2014 | Pipe Wall Thickness | 3255 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.65 | CML-39 | CML: type TBC | 3 | 2025-04-14 | 2026-07-23 | 2014-05-09 07:00 | 2.5 | 0.25592 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 7.2 | 5.3 | 6.9 | 7.2 | 0.91104
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23048-09C02 | CML-3 | 50-PG-23048-09C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20585 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.625 | CML-3 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.8 | 9 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 10.9 | 9.6 | 9.2 | 8.8 | 0.91059
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-9 | 100-WC-40516-1CG CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8682 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 | Check Corrosion Rate of 0.328mm/ yr |  | Administrator | 2015-09-08 11:55 | [32 empty] | 8.15 | CML-9 | CML: Pipe Length | 3 | 2031-11-08 | 2027-03-13 | 2015-02-13 07:00 | 2.5 | 0.32846 | A4: Left Quadrant |  | 5.56 | 2.5 | 4.03 | 8 | 9 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.2 | 8.3 | 8.1 | 8 | 0.1291
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-2 | 50-PL-23021-03C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10234 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 14.5333 | CML-2 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 13.7 | 3 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.2 |  | 15.5 | 13.7 |  | 14.4 | 0.90738
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-44 | 150-WF-71372-01K01 CML-44 |  | FPSO 2015 | Pipe Wall Thickness | 5374 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.975 | CML-44 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 6 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 4.4 | 3.6 | 3.6 | 4.3 | 0.43493
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-36 | 150-WF-71372-01K01 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 5366 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.725 | CML-36 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.9 | 3.7 | 3.6 | 0.12583
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-31 | 150-WF-71372-01K01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 5361 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.675 | CML-31 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.7 | 3.7 | 3.7 | 0.05
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-30 | 150-WF-71372-01K01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 5360 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.925 | CML-30 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 4.3 | 3.6 | 4.2 | 3.6 | 0.37749
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-17 | 100-PG-23503-03C03-A CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2733 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 12.675 | CML-17 | CML: Elbow | 6 | 2068-02-11 | 2070-10-05 | 2014-03-13 09:00 | 5.66 | 0 | A3: Inside Quadrant |  | 5.13 | 5.66 | 5.395 | 11.6 | 6 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.94 |  | 12.5 | 13.8 | 11.6 | 12.8 | 0.90692
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-5 | 300-PF-20500-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21625 | Protective mesh removed | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.475 | CML-5 | CML: Elbow | 6 | 2039-10-17 | 2035-01-19 | 2014-09-27 07:00 | 4.9 | 0.35496 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14 | 15.8 | 14.3 | 13.8 | 0.90692
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-22 | 150-WF-71372-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 5352 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.9 | CML-22 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.9 | 4.1 | 4 | 3.6 | 0.21602
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67301-01E01 | CML-1 | 25-GN-67301-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22495 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.275 | CML-1 | CML: Elbow | 3 | 2018-10-15 | 2018-10-01 | 2015-04-20 07:00 | 2.5 | 0.7159 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 12 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.6 | 5.3 | 5.2 | 0.25
FH02 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43313-01S01-P | CML-5 | 150-FH-43313-01S01-P CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 20479 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.525 | CML-5 | CML: Elbow | 1 | 2022-02-10 | 2019-07-19 | 2014-10-03 07:00 | 2.5 | 0.52964 | A4: Left Quadrant |  | 6.11 | 2.5 | 3.8606 | 6.4 | 9 O'Clock | 150 | 7.11 | 150-FH-43313-01S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.7 | 8.6 | 7.4 | 6.4 | 0.90692
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-10 | 50-PW-44015-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22715 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.175 | CML-10 | CML: Elbow | 3 | 2020-04-24 | 2021-01-20 | 2015-04-28 07:00 | 2.5 | 0.44033 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.23558 | 5.5 | 5.3 | 4.7 | 5.2 | 0.34034
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-7 | 80-CG-38459-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2742 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 15.9 | CML-7 | CML: Elbow | 3 | 2096-09-16 | 2070-01-23 | 2014-03-13 09:00 | 2.8 | 0 | A1: Outside Quadrant |  | 8.13 | 2.8 | 5.465 | 14.9 | 12 O'Clock | 80 | 11.13 | 80-PG-23050-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.1 |  | 14.9 | 16.2 | 17 | 15.5 | 0.90554
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71337-01K01 | CML-3 | 100-WF-71337-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6405 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 5.2 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 5 | 3 O'Clock | 100 | 3 | 100-WF-71337-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5.4 | 5.2 | 0.1633
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71352-01K01 | CML-6 | 100-WF-71352-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6116 |  | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 5.625 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 5 | 9 O'Clock | 100 | 3 | 100-WF-71352-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.6 | 5.8 | 6.1 | 5 | 0.46458
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-8 | 0200-DC-57L9006-AC21-00 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5048 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.732mm/ yr | [34 empty] | Low alarm breach | 5.3 | CML-8 | CML: type TBC | 3 | 2016-08-13 | 2015-12-30 | 2015-03-05 07:00 | 2.5 | 1.7317 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 5 | 12 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.7 | 5.3 | 5.2 | 0.29439
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-5 | 0200-DC-57L9006-AC21-00 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5045 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.732mm/ yr | [34 empty] | Low alarm breach | 5.05 | CML-5 | CML: type TBC | 3 | 2016-08-13 | 2015-12-30 | 2015-03-05 07:00 | 2.5 | 1.7317 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 5 | 6 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5 | 5.1 | 0.057735
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-21 | 50-GN-67002-01E01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 9080 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.9 | CML-21 | CML: type TBC | 3 | 2023-04-03 | 2024-04-23 | 2015-03-01 09:30 | 2.5 | 0.30874 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.4 | 6.4 | 5.8 | 5 | 0.66332
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-22 | 50-AU-63015-01E01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 9053 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | Check Corrosion Rate of 0.309mm/ yr | [35 empty] | 5 | CML-22 | CML: type TBC | 3 | 2023-04-03 | 2024-04-22 | 2015-03-01 07:00 | 2.5 | 0.30879 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5 | 5 | 0
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-8 | 50-AU-63015-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 9039 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | Check Corrosion Rate of 0.309mm/ yr | [35 empty] | 5.3 | CML-8 | CML: type TBC | 3 | 2023-04-03 | 2024-04-22 | 2015-03-01 07:00 | 2.5 | 0.30879 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 5.3 | 5.6 | 0.24495
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-15 | 50-AI-63004-01E01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 9006 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | Check Corrosion Rate of 0.309mm/ yr | [35 empty] | 5.525 | CML-15 | CML: type TBC | 3 | 2023-03-28 | 2024-04-16 | 2015-02-28 07:00 | 2.5 | 0.30928 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 6.5 | 5 | 5.4 | 0.6702
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-61 | 50-AI-63007-01E01 CML-61 |  | FPSO 2015 | Pipe Wall Thickness | 8985 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.1 | CML-61 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 5.1 | 5 | 0.14142
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-57 | 50-AI-63007-01E01 CML-57 |  | FPSO 2015 | Pipe Wall Thickness | 8981 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.25 | CML-57 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5.1 | 5.8 | 0.36968
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-55 | 50-AI-63007-01E01 CML-55 |  | FPSO 2015 | Pipe Wall Thickness | 8979 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.275 | CML-55 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.3 | 5 | 5.7 | 0.30957
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-54 | 50-AI-63007-01E01 CML-54 |  | FPSO 2015 | Pipe Wall Thickness | 8978 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.6 | CML-54 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.5 | 6 | 5.9 | 0.45461
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-45 | 50-AI-63007-01E01 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 8969 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.15 | CML-45 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5.2 | 5.2 | 0.1
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-37 | 50-AI-63007-01E01 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 8961 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.3 | CML-37 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.7 | 5.1 | 5.4 | 5 | 0.31623
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-23 | 50-AI-63007-01E01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 8947 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.275 | CML-23 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.1 | 5.8 | 0.3594
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-14 | 50-AI-63007-01E01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8938 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.175 | CML-14 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5 | 5.3 | 5.3 | 0.15
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-7 | 50-AI-63007-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8931 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.35 | CML-7 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.6 | 5.8 | 5 | 0.41231
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-6 | 50-AI-63007-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8930 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | Check Corrosion Rate of 0.31mm/ yr | [35 empty] | 5.425 | CML-6 | CML: type TBC | 3 | 2023-03-17 | 2024-04-04 | 2015-02-26 09:00 | 2.5 | 0.31021 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6 | 5.3 | 5 | 5.4 | 0.41932
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-23 | 50-AU-63018-01E01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 8919 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | Check Corrosion Rate of 0.311mm/ yr | [35 empty] | 5.225 | CML-23 | CML: type TBC | 3 | 2023-03-13 | 2024-03-30 | 2015-02-25 13:00 | 2.5 | 0.31062 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.5 | 5 | 5.3 | 0.22174
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-1 | 50-AU-63018-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8897 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | Check Corrosion Rate of 0.311mm/ yr | [35 empty] | 5.275 | CML-1 | CML: type TBC | 3 | 2023-03-13 | 2024-03-30 | 2015-02-25 13:00 | 2.5 | 0.31062 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5.2 | 5.1 | 5 | 0.3594
SD02 | Montara_Topside | No | Steam (55) | Pipework | 50-SL-55006-01C02-P | CML-2 | 50-SL-55006-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8860 |  | 2015-02-24 13:00 | 2015-02-24 14:00 | [36 empty] | 5.1 | CML-2 | CML: type TBC | 3 | 2023-03-07 | 2024-03-24 | 2015-02-24 13:00 | 2.5 | 0.31111 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-SL-55006-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5 | 5.2 | 0.11547
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-15 | 50-WC-40452-01C02 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10612 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 1.814mm/ yr | [35 empty] | 4.925 | CML-15 | CML: type TBC | 3 | 2015-02-02 | 2015-04-09 | 2013-11-17 | 2.5 | 1.8142 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 4.8 | 5.1 | 5.1 | 0.20616
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63034-01E01 | CML-1 | 50-AI-63034-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8573 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | Check Corrosion Rate of 0.321mm/ yr | [35 empty] | 16.925 | CML-1 | CML: type TBC | 3 | 2022-11-13 | 2023-11-19 | 2015-02-04 07:30 | 2.5 | 0.32137 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-AI-63034-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 52 | 5 | 5.6 | 23.3848
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71321-01K01 | CML-9 | 100-WF-71321-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8543 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.1 | CML-9 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-02-04 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 5 | 6 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.1 | 5 | 5.1 | 0.08165
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38486-09C02-P | CML-26 | 80-CG-38486-09C02-P CML-26 |  | FPSO 2016 | Pipe Wall Thickness | 24431 | Re-check as requested by N.Sequera, Pipe material class 1CG | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.641mm/ yr | [34 empty] | Low alarm breach | 16.65 | CML-26 | CML: Elbow | 3 | 2023-04-04 | 2019-02-11 | 2016-07-02 07:00 | 2.5 | 1.9233 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 15.5 | 3 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13 | 0.74058 | 17.7 | 15.5 | 16.6 | 16.8 | 0.9037
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63020-01E01 | CML-4 | 50-AU-63020-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8484 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | Check Corrosion Rate of 0.322mm/ yr | [35 empty] | 5.25 | CML-4 | CML: type TBC | 3 | 2022-11-02 | 2023-11-06 | 2015-02-02 07:30 | 2.5 | 0.32242 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-AU-63020-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 5.4 | 5.3 | 0.17321
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-32 | 300-PF-20003-03C03-P CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 21770 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.575 | CML-32 | CML: Reducing Tee | 6 | 2040-01-05 | 2035-03-25 | 2014-10-01 07:00 | 4.9 | 0.35205 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 6 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 15.8 | 14 | 13.8 | 14.7 | 0.90323
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62001-01C02 | CML-5 | 50-DO-62001-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8045 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.15 | CML-5 | CML: type TBC | 3 | 2022-08-26 | 2023-08-23 | 2015-01-21 07:30 | 2.5 | 0.32888 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DO-62001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5.3 | 5.2 | 0.1291
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62001-01C02 | CML-1 | 50-DO-62001-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8041 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.25 | CML-1 | CML: type TBC | 3 | 2022-08-26 | 2023-08-23 | 2015-01-21 07:30 | 2.5 | 0.32888 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DO-62001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.4 | 5.4 | 5 | 0.19149
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-15 | 80-CG-38459-09C02-P CML-15 |  | FPSO 2016 | Pipe Wall Thickness | 24470 | Re-check as requested by N.Sequera | 2016-07-07 07:00 | 2016-07-07 15:00 | [36 empty] | 10.075 | CML-15 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2016-07-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.9 | 3 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | 1.0179 | 10.1 | 8.9 | 10.2 | 11.1 | 0.90323
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-29 | 300-PG-20004-03C03-P CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 6152 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14 | CML-29 | CML: Pipe Length | 6 | 2024-02-19 | 2022-03-17 | 2014-07-11 07:30 | 4.9 | 0.87352 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 15.3 | 13.5 | 13.9 | 13.3 | 0.90185
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43129-01C02 | CML-5 | 50-FH-43129-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1784 | Rope access | 2014-04-28 08:00 | 2014-04-28 09:00 | [36 empty] | 8.15 | CML-5 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-28 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.7 | 9 O'Clock | 50 | 5.54 | 50-FH-43129-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9.5 | 7.7 | 7.7 | 7.7 | 0.9
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-23 | 50-WC-40451-01C02 CML-23 |  | FPSO 2013 | Pipe Wall Thickness | 10163 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 1.904mm/ yr | [35 empty] | 4.95 | CML-23 | CML: type TBC | 3 | 2015-01-04 | 2015-03-08 | 2013-11-09 | 2.5 | 1.9043 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 5.1 | 4.9 | 4.7 | 0.19149
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-12 | 100-FG-45001-09C02 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10427 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 11.025 | CML-12 | CML: type TBC | 3 | 2016-11-30 | 2015-12-25 | 2013-11-13 | 4.7 | 1.8361 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 10.3 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 10.3 | 10.5 | 11 | 12.3 | 0.89954
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-12 | 100-WC-40516-1CG CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8685 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:56 | [32 empty] | 8.775 | CML-12 | CML: Pipe Length | 3 | 2042-02-04 | 2034-11-08 | 2015-02-13 07:00 | 2.5 | 0.21116 | A2: Right Quadrant |  | 5.56 | 2.5 | 4.03 | 8.2 | 3 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 10.2 | 8.2 | 8.4 | 8.3 | 0.9535
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-21 | 50-WC-40071-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 7734 |  | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.335mm/ yr |  | Administrator | 2015-09-08 09:37 | [32 empty] | 5.275 | CML-21 | CML: Reducer | 3 | 2022-06-21 | 2023-06-11 | 2015-01-09 13:00 | 2.5 | 0.33547 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 2.5247 | 5.4 | 5.2 | 5.5 | 5 | 0.22174
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-16 | 50-WC-40071-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 7729 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.335mm/ yr |  | Administrator | 2015-09-08 09:35 | [32 empty] | 5.25 | CML-16 | CML: Pipe Length | 3 | 2022-06-21 | 2023-06-11 | 2015-01-09 13:00 | 2.5 | 0.33547 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.63117 | 5 | 5.4 | 5.4 | 5.2 | 0.19149
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-15 | 50-WC-40071-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 7728 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 | Check Corrosion Rate of 0.335mm/ yr |  | Administrator | 2015-09-08 09:35 | [32 empty] | 5.35 | CML-15 | CML: Elbow | 3 | 2022-06-21 | 2023-06-11 | 2015-01-09 13:00 | 2.5 | 0.33547 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 1.0099 | 5 | 5 | 5.6 | 5.8 | 0.41231
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-2 | 50-CG-38487-09C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23571 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 12.375 | CML-2 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 11.7 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 | -2.6603 | 11.7 | 13.6 | 11.7 | 12.5 | 0.89954
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-3 | 50-DC-57013-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7668 | Re-check | 2015-01-08 09:30 | 2015-01-08 12:00 | Check Corrosion Rate of 0.336mm/ yr |  | Administrator | 2015-09-08 12:38 | [32 empty] | 5.225 | CML-3 | CML: Elbow | 3 | 2022-06-15 | 2023-06-04 | 2015-01-08 09:30 | 2.5 | 0.33612 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -1.5265 | 5 | 5.3 | 5.2 | 5.4 | 0.17078
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57048-03C02 | CML-1 | 50-DC-57048-03C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7613 |  | 2015-01-07 07:00 | 2015-01-07 08:00 | Check Corrosion Rate of 0.337mm/ yr | [35 empty] | 5.25 | CML-1 | CML: Equal Tee | 3 | 2022-06-08 | 2022-05-18 | 2015-01-07 07:00 | 2.5 | 0.33676 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 9 O'Clock | 50 | 5.54 | 50-DC-57048-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.6 | 5 | 0.3
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-19 | 200-PG-23013-09C03-A CML-19 | yes | FPSO 2014 | Pipe Wall Thickness | 20003 | Rope Access | 2014-01-10 | 2014-01-10 | [35 empty] | Low alarm breach | 14.325 | CML-19 | CML: type TBC | 6 | 2014-04-01 | 2014-01-26 | 2014-01-10 | 10.22 | 12.4722 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 13 | 12 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.78 |  | 13 | 14.7 | 14.6 | 15 | 0.89954
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-3 | 150-PG-23043-06C02-P CML-3 | Yes | FPSO 2015 | Pipe Wall Thickness | 23459 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 12.775 | CML-3 | CML: Equal Tee | 3 | 2076-02-10 | 2066-08-14 | 2015-07-24 07:00 | 4.7 | 0 | A3: Inside Quadrant |  | 7.97 | 4.7 | 5.6494 | 12.1 | 6 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 | 1.0842 | 12.4 | 12.5 | 12.1 | 14.1 | 0.89954
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-19 | 250-PG-23004-06C03-A CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 23386 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.025 | CML-19 | CML: Elbow | 6 | 2143-01-24 | 2118-04-19 | 2015-07-21 07:00 | 8.55 | 0.07484 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 18.1 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.55 | 0.26275 | 18.5 | 20.1 | 19.4 | 18.1 | 0.89954
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-15 | 50-PL-23516-03C03 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 7803 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 15:58 | [32 empty] | 9.125 | CML-15 | CML: Elbow | 6 | 2027-01-25 | 2026-10-21 | 2015-01-13 07:00 | 2.5 | 0.4568 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 10.2 | 9.1 | 9.2 | 8 | 0.89954
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-8 | 300-PG-20037-03C03-PA CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21383 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | [36 empty] | 16.625 | CML-8 | CML: Elbow | 6 | 2102-10-24 | 2088-02-10 | 2014-06-29 13:00 | 5.33 | 0 | A3: Inside Quadrant |  | 8.27 | 5.33 | 6.8 | 15.5 | 6 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.17 |  | 16.7 | 17.7 | 15.5 | 16.6 | 0.89954
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-3 | 50-PW-44009-01C03-P CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 5814 | Protective mesh removed | 2014-06-24 07:00 | 2014-06-24 08:00 | [36 empty] | 9.125 | CML-3 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2014-06-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 10.2 | 9 | 8.2 | 9.1 | 0.82209
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-3 | 50-PW-44009-01C03-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22810 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 8.875 | CML-3 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2015-04-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.4 | 6 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | -0.23548 | 9.3 | 9.2 | 8.4 | 8.6 | 0.44253
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40047-01C02 | CML-5 | 50-WC-40047-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1705 | Rope Access | 2014-04-13 10:15 | 2014-04-13 11:15 | Check Corrosion Rate of 0.854mm/ yr | [35 empty] | 5.425 | CML-5 | CML: Elbow | 3 | 2016-12-21 | 2017-05-10 | 2014-04-13 10:15 | 2.5 | 0.85359 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-WC-40047-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 4.8 | 5.8 | 5.8 | 0.47871
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-5 | 250-PW-20022-01C03-P CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23103 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.425 | CML-5 | CML: Equal Tee | 6 | 2028-07-03 | 2027-08-25 | 2015-05-10 07:00 | 2.5 | 0.44833 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 8.4 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 3.6679 | 10.4 | 8.4 | 10 | 8.9 | 0.93229
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-9 | 80-CG-38459-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 13070 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 23.65 | CML-9 | CML: type TBC | 6 | 2117-11-29 | 2095-08-30 | 2014-01-10 07:00 | 10.17 | 0 | A1: Outside Quadrant |  | 14.62 | 10.17 | 12.395 | 22.7 | 12 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.53 |  | 22.7 | 24.6 | 23.1 | 24.2 | 0.89629
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-21 | 300-FL-43070-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 12714 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 11.65 | CML-21 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.7 | 12 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.7 | 12.6 | 12.2 | 11.1 | 0.89629
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-9 | 50-CG-38452-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2273 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 7.6667 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-16 11:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 3 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8.7 | 7.1 |  | 7.2 | 0.89629
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-11 | 50-DC-57450-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20327 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | Check Corrosion Rate of 0.401mm/ yr | [35 empty] | 5.275 | CML-11 | CML: Elbow | 3 | 2020-12-26 | 2021-10-19 | 2014-10-05 07:00 | 2.5 | 0.40119 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.1 | 5.5 | 5 | 0.263
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-18 | 150-WF-71372-01K01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5348 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.925 | CML-18 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 4.1 | 3.7 | 4.3 | 3.6 | 0.3304
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-10 | 150-WF-71372-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5340 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.775 | CML-10 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 6 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.7 | 3.6 | 4.2 | 0.28723
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-3 | 50-CG-38465-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20866 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.375 | CML-3 | CML: Elbow | 3 | 2020-12-21 | 2021-10-13 | 2014-10-04 07:00 | 2.5 | 0.40201 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5.9 | 5.3 | 5 | 0.37749
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38462-01C02 | CML-5 | 50-CG-38462-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20833 | Reviewed on 20/11/14. FFS. This line has not been RBI assessed. CML to be rechecked Oct. 18 based on other line on this circuit which are a 48m interval | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 15:57 | [32 empty] | 5.225 | CML-5 | CML: Reducing Tee | 3 | 2020-12-21 | 2021-10-13 | 2014-10-04 07:00 | 2.5 | 0.40201 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-CG-38462-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5.2 | 5.3 | 5 | 0.17078
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38462-01C02 | CML-3 | 50-CG-38462-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20831 | Reviewed on 20/11/14. FFS. This line has not been RBI assessed. CML to be rechecked Oct. 18 based on other line on this circuit which are a 48m interval | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 15:40 | [32 empty] | 5.625 | CML-3 | CML: Elbow | 3 | 2020-12-21 | 2021-10-13 | 2014-10-04 07:00 | 2.5 | 0.40201 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-CG-38462-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.2 | 5 | 6.1 | 5.2 | 0.61305
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-5 | 150-WF-71372-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5335 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.65 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 3 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.6 | 3.7 | 3.7 | 0.057735
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-1 | 150-WF-71372-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5331 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.775 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 6 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 4.2 | 3.6 | 3.6 | 3.7 | 0.28723
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-16 | 50-DH-56137-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 5457 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 4.789mm/ yr | [34 empty] | Low alarm breach | 17.975 | CML-16 | CML: Straight | 3 | 2017-05-14 | 2015-09-15 | 2014-05-28 07:00 | 2.5 | 4.7886 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 16.7 | 3 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.2 |  | 18 | 16.7 | 18.6 | 18.6 | 0.89582
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-24 | 80-CG-38459-09C02-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 20008 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 23.925 | CML-24 | CML: type TBC | 6 | 2117-05-30 | 2095-05-30 | 2014-01-10 | 10.22 | 0 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 22.7 | 12 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.48 |  | 22.7 | 24.8 | 23.9 | 24.3 | 0.89582
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-16 | 25-VA-23054-01C02 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10062 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 20.025 | CML-16 | CML: Elbow | 6 | 2110-01-05 | 2091-09-17 | 2013-11-06 | 8.6 | 0 | A2: Right Quadrant |  | 12.26 | 8.6 | 10.43 | 18.9 | 3 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.3 |  | 20.4 | 18.9 | 21 | 19.8 | 0.89582
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-45 | 150-WF-71372-01K01 CML-45 |  | FPSO 2015 | Pipe Wall Thickness | 5375 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.025 | CML-45 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 6 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.1 | 3.7 | 3.7 | 4.6 | 0.4272
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-14 | 150-WF-71372-01K01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5344 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.1 | CML-14 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 6 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 4.8 | 3.7 | 4 | 0.48305
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-13 | 150-WF-71372-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5343 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.025 | CML-13 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 3.8 | 4.3 | 4.3 | 0.32016
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-2 | 50-PW-44013-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22721 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.125 | CML-2 | CML: Elbow | 3 | 2020-04-24 | 2021-01-20 | 2015-04-28 07:00 | 2.5 | 0.44033 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | -0.47135 | 5.4 | 5.2 | 4.7 | 5.2 | 0.29861
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-6 | 250-PG-20036-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21364 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 9.275 | CML-6 | CML: Elbow | 6 | 2021-03-20 | 2020-10-09 | 2014-07-14 07:30 | 2.5 | 0.86711 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.3 | 9 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.7 | 8.8 | 10.3 | 8.3 | 0.89582
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-2 | 80-CG-38486-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21360 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 17.125 | CML-2 | CML: Reducing Tee | 6 | 2081-02-10 | 2077-04-05 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 15.8 | 9 O'Clock | 150 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.3 |  | 17.4 | 17.7 | 17.6 | 15.8 | 0.89209
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-13 | 50-WC-40452-01C02 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10610 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 1.598mm/ yr | [35 empty] | 5.175 | CML-13 | CML: type TBC | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5.4 | 5.3 | 4.8 | 0.263
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-10 | 200-PG-23505-09C02-A CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 380 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 18.475 | CML-10 | CML: Pipe Length | 3 | 2017-09-17 | 2017-02-05 | 2014-03-12 | 14.06 | 0.97676 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.5 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.44 |  | 17.5 | 18.7 | 18.7 | 19 | 0.66521
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-11 | 150-WF-71372-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5341 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.275 | CML-11 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.1 | 3 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.6 |  | 4.2 | 4.1 | 4.4 | 4.4 | 0.15
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-41 | 150-WF-71372-01K01 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 5371 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.3 | CML-41 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 12 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 4.4 | 4.3 | 4.3 | 0.08165
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57301-01C02 | CML-6 | 50-DC-57301-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5666 | Rope access | 2014-06-21 13:00 | 2014-06-21 14:00 | Check Corrosion Rate of 0.511mm/ yr | [35 empty] | 5.175 | CML-6 | CML: Elbow | 3 | 2019-05-11 | 2019-12-30 | 2014-06-21 13:00 | 2.5 | 0.51123 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5.1 | 5.5 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57301-01C02 | CML-4 | 50-DC-57301-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5664 | Rope access | 2014-06-21 13:00 | 2014-06-21 14:00 | Check Corrosion Rate of 0.511mm/ yr | [35 empty] | 5.375 | CML-4 | CML: Elbow | 3 | 2019-05-11 | 2019-12-30 | 2014-06-21 13:00 | 2.5 | 0.51123 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-DC-57301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5.4 | 5 | 5.8 | 0.3304
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-17 | 150-WF-71372-01K01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5347 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 4.625 | CML-17 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 4.2 | 6 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.7 | 4.8 | 4.2 | 4.8 | 0.28723
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-6 | 150-WF-71372-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5336 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 5.075 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.6 | 3 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.7 | 4.6 | 5.1 | 4.9 | 0.46458
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57007-01C02 | CML-2 | 80-DC-57007-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20266 | Rope access | 2014-06-02 11:00 | 2014-06-02 12:00 | Check Corrosion Rate of 0.488mm/ yr | [35 empty] | 5.475 | CML-2 | CML: type TBC | 3 | 2019-07-16 | 2020-04-01 | 2014-06-02 11:00 | 2.5 | 0.48805 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 3 O'Clock | 80 | 5.49 | 80-DC-57007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5 | 5.9 | 5.5 | 0.36856
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-14 | 80-PL-44008-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 5751 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 6.15 | CML-14 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.9 | 6.2 | 5.5 | 6 | 0.58023
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-19 | 25-FG-45455-01C02-E CML-19 |  | FPSO 2016 | Pipe Wall Thickness | 24364 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.15 | CML-19 | CML: Elbow | 3 | 2022-01-05 | 2021-12-13 | 2016-06-06 07:00 | 2.5 | 0.44743 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 12 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 7.1 | 6.5 | 6 | 0.88882
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-2 | 100-PW-20021-01C02-P CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 22820 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 4.975 | CML-2 | CML: Elbow | 3 | 2018-07-07 | 2018-09-06 | 2015-04-30 07:00 | 2.5 | 0.68997 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.7 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.54478 | 5.1 | 4.9 | 4.7 | 5.2 | 0.22174
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45044-03C02 | CML-27 | 50-FG-45044-03C02 CML-27 | yes | FPSO 2014 | Pipe Wall Thickness | 3025 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.925 | CML-27 | CML: Elbow | 6 | 2020-08-16 | 2021-10-03 | 2014-05-01 07:00 | 3.61 | 0.63328 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 7.6 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.99 | 0 | 9.5 | 9.3 | 7.6 | 9.3 | 0.88835
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45044-03C02 | CML-27 | 50-FG-45044-03C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 22304 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.925 | CML-27 | CML: Elbow | 6 | 2020-08-16 | 2021-10-03 | 2014-05-01 07:00 | 3.61 | 0.63328 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 7.6 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.99 |  | 9.5 | 9.3 | 7.6 | 9.3 | 0.88835
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-12 | 250-PG-20036-01C03-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23399 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 9.225 | CML-12 | CML: Elbow | 6 | 2030-01-14 | 2029-02-03 | 2015-07-21 07:00 | 2.5 | 0.40696 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.4 | 12 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | -0.49062 | 8.4 | 9.4 | 10.4 | 8.7 | 0.88835
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-15 | 250-PW-20022-01C03-P CML-15 | yes | FPSO 2015 | Pipe Wall Thickness | 23113 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.125 | CML-15 | CML: Pipe Length | 6 | 2028-07-03 | 2027-08-25 | 2015-05-10 07:00 | 2.5 | 0.44833 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.4 | 12 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 1.6998 | 8.4 | 9.9 | 8.8 | 9.4 | 0.66018
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-10 | 50-PL-23040-03C03 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10195 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.075 | CML-10 | CML: type TBC | 6 | 2018-06-23 | 2018-05-19 | 2013-11-08 | 2.5 | 1.2319 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 3 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 9 | 8.2 | 8.8 | 10.3 | 0.88459
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-5 | 50-CG-38487-09C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23574 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 9.5 | CML-5 | CML: Elbow | 3 | 2055-03-09 | 2044-05-04 | 2015-09-10 07:00 | 2.5 | 0.14929 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 0 | 9.8 | 8.4 | 9.3 | 10.5 | 0.88318
FH01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FH-43507-01C02 | CML-26 | 100-FH-43507-01C02 CML-26 | Yes | FPSO 2015 | Pipe Wall Thickness | 23331 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.8 | CML-26 |  | 3 | 2072-05-16 | 2056-08-24 | 2015-07-11 07:00 | 4.7 | 0.10898 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.9 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 11.5 | 10.9 | 11.8 | 13 | 0.88318
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38471-01C02-P | CML-3 | 50-CG-38471-01C02-P CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 23622 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 4.35 | CML-3 | CML: Elbow | 3 | 2016-09-06 | 2017-01-12 | 2015-10-28 07:00 | 2.5 | 0.92984 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.3 | 3 O'Clock | 50 | 5.54 | 50-CG-38471-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.6 | 3.3 | 4.1 | 5.4 | 0.88129
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-7 | 250-PW-44004-01C02 CML-7 | yes | FPSO 2015 | Pipe Wall Thickness | 22751 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 5.725 | CML-7 | CML: Elbow | 3 | 2018-02-26 | 2018-02-14 | 2015-04-29 07:00 | 2.5 | 0.81135 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.8 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 1.1671 | 4.8 | 6.2 | 6.1 | 5.8 | 0.63966
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-12 | 250-PW-44509-01C03-P CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 22997 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.175 | CML-12 | CML: Elbow | 6 | 2028-05-25 | 2027-07-19 | 2015-05-05 07:00 | 2.5 | 0.45152 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.4 | 9 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 2.5939 | 9.7 | 9 | 9.6 | 8.4 | 0.60208
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-9 | 150-PG-20507-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2853 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.85 | CML-9 | CML: type TBC | 6 | 2019-02-17 | 2018-04-18 | 2014-03-16 07:00 | 2.5 | 1.4813 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 9.8 | 12 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 9.8 | 11.9 | 11.1 | 10.6 | 0.88129
FG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 25-FG-45455-01C02-E | CML-17 | 25-FG-45455-01C02-E CML-17 | High Priority | FPSO 2013 | Pipe Wall Thickness | 10273 | Deck Level | 2013-11-09 | 2013-11-09 | High alarm WT breach | [35 empty] | 7.05 | CML-17 | CML: Elbow | 3 | 2015-04-05 | 2014-12-09 | 2013-11-09 | 2.5 | 2.4938 | A1: Outside Quadrant |  | 4.1 | 2.5 | 3.3 | 6 | 12 O'Clock | 40 | 7.1 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 7.5 | 6.7 | 8 | 0.88129
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-11 | 80-PL-44008-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5748 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 6.075 | CML-11 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.6 | 6.1 | 5.5 | 6.1 | 0.45
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45044-03C02 | CML-16 | 50-FG-45044-03C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21692 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.975 | CML-16 | CML: Elbow | 6 | 2035-03-19 | 2031-04-17 | 2014-09-28 07:00 | 4.9 | 0.4296 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 15.1 | 15.6 | 13.7 | 15.5 | 0.87702
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-9 | 50-CG-38452-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2290 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 8.025 | CML-9 | CML: type TBC | 3 | 2018-08-26 | 2017-12-17 | 2014-03-17 08:00 | 2.5 | 1.0345 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 7.1 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.5 | 8.5 | 9 | 7.1 | 0.87702
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-18 | 300-FL-43070-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 12711 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 11.175 | CML-18 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.2 | 12 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.2 | 12.1 | 11.7 | 10.7 | 0.87702
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-3 | 50-PL-23515-01C03 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 8652 | Line is FFS despite the High CR on CML-3 &1. They are all in the same spool. Current RBI frequency is 48m. RBI frequency to stay at 48m. Action: to recheck CML-1 to 6 in a year to confirm CR. RBI frequency to stay at 48m | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:50 | [32 empty] | 8.8 | CML-3 | CML: Elbow | 6 | 2022-09-22 | 2022-07-19 | 2015-02-12 07:00 | 2.5 | 0.66973 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.6 | 6 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 9.4 | 8.7 | 7.6 | 9.5 | 0.8756
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-9 | 50-DH-56070-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 3225 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 7.7 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 8.4 | 8.5 | 7.1 | 0.8756
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-13 | 50-CG-38466-01C02 CML-13 | yes | FPSO 2014 | Pipe Wall Thickness | 2527 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.45 | CML-13 | CML: type TBC | 3 | 2016-11-07 | 2017-03-21 | 2014-04-02 13:00 | 2.5 | 0.884 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 4.8 | 5.4 | 4.9 | 4.8 | 6.7 | 0.87369
PL03 | Montara_Topside | Yes | Flare (43) | Pipework | 50-PL-57066-01C03 | CML-18 | 50-PL-57066-01C03 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 12658 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 9.2333 | CML-18 | CML: Fitting | 3 | 2074-03-18 | 2063-04-04 | 2014-01-22 07:00 | 1.03 | 0 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 8.5 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.47 |  | 10.2 | 8.5 | 9 |  | 0.87369
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 20023 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.125 | CML-4 | CML: type TBC | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5.3 | 4.8 | 5.2 | 0.22174
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56067-01C02 | CML-1 | 50-DH-56067-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3400 | Rope Access | 2014-05-10 14:00 | 2014-05-10 15:00 | [36 empty] | 8.375 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-10 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.7 | 7.6 | 9.4 | 8.8 | 0.87321
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-8 | 200-FH-43131-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2829 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 8.475 | CML-8 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.7 | 3 O'Clock | 200 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.36 |  | 9.5 | 7.7 | 7.8 | 8.9 | 0.87321
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-11 | 300-PG-20005-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 6167 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.975 | CML-11 | CML: Elbow | 6 | 2161-12-15 | 2135-03-31 | 2014-07-11 07:30 | 4.9 | 0.06304 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.2 | 16 | 15.4 | 14.3 | 0.87321
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-7 | 50-PW-44015-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22712 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 4.975 | CML-7 | CML: Elbow | 3 | 2020-04-24 | 2021-01-20 | 2015-04-28 07:00 | 2.5 | 0.44033 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.23558 | 4.8 | 5.3 | 4.7 | 5.1 | 0.27538
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-23 | 100-WC-40516-1CG CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 8696 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:58 | [32 empty] | 9.025 | CML-23 | CML: Elbow | 3 | 2053-02-15 | 2043-02-06 | 2015-02-13 07:00 | 2.5 | 0.1525 | A4: Left Quadrant |  | 5.56 | 2.5 | 4.03 | 8.3 | 9 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.5 | 10.4 | 8.9 | 8.3 | 0.95
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-4 | 50-PL-23040-03C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10189 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.525 | CML-4 | CML: type TBC | 6 | 2015-08-15 | 2015-07-30 | 2013-11-08 | 2.5 | 2.8287 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 7.5 | 9 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.3 | 8.7 | 9.6 | 7.5 | 0.87321
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-16 | 100-PG-23503-03C03-A CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 5515 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 11.25 | CML-16 | CML: Elbow | 6 | 2020-11-28 | 2021-04-09 | 2014-06-01 07:00 | 5.66 | 0.72942 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.4 | 12 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.74 | 0 | 10.4 | 10.6 | 12 | 12 | 0.86987
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45044-03C02 | CML-4 | 50-FG-45044-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21742 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.25 | CML-4 | CML: Pipe Length | 6 | 2027-10-14 | 2025-03-14 | 2014-10-01 07:00 | 4.9 | 0.65166 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 14.4 | 13.8 | 15.4 | 13.4 | 0.86987
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-41 | 300-PF-20001-03C03-P CML-41 |  | FPSO 2014 | Pipe Wall Thickness | 21179 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.418mm/ yr | 40 | Kirstie Albone | 2017-03-23 16:09 | [32 empty] | 14.95 | CML-41 | CML: Fitting | 6 | 2035-10-24 | 2031-10-14 | 2014-07-16 07:30 | 4.9 | 0.4181 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 15.4 | 15.8 | 14.8 | 13.8 | 0.86987
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-8 | 250-PW-20022-01C03-P CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 23106 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.275 | CML-8 | CML: Pipe Length | 6 | 2028-07-03 | 2027-08-25 | 2015-05-10 07:00 | 2.5 | 0.44833 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.4 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 0.17892 | 9.6 | 9.5 | 9.6 | 8.4 | 0.58523
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-8 | 300-PG-20506-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13222 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.425 | CML-8 | CML: type TBC | 6 | 2021-09-12 | 2020-03-17 | 2014-02-04 15:00 | 4.9 | 1.1304 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 12 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 13.5 | 14 | 15.5 | 14.7 | 0.86939
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38456-01C02-H | CML-1 | 50-CG-38456-01C02-H CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 23692 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 3.9 | CML-1 | CML: Elbow | 3 | 2016-03-11 | 2016-06-28 | 2015-10-30 07:00 | 2.5 | 1.0934 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 2.9 | 3 O'Clock | 50 | 5.54 | 50-CG-38456-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 4 | 2.9 | 3.7 | 5 | 0.86795
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-1 | 80-FH-43007-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12562 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 8.15 | CML-1 | CML: Pipe Length | 3 | 2062-11-29 | 2056-08-05 | 2014-01-18 07:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 7.1 | 12 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.56 |  | 7.1 | 8.7 | 7.8 | 9 | 0.86603
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-23 | 50-CG-38452-09C02-P CML-23 |  | FPSO 2013 | Pipe Wall Thickness | 10137 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.325 | CML-23 | CML: type TBC | 6 | 2015-01-30 | 2015-01-19 | 2013-11-08 | 2.5 | 3.7412 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 7.1 | 9 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 9.1 | 8.4 | 8.7 | 7.1 | 0.86554
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-9 | 50-PL-23021-03C03 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10241 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.925 | CML-9 | CML: type TBC | 6 | 2016-04-28 | 2016-04-07 | 2013-11-08 | 2.5 | 2.1444 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.8 | 6 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 9.7 | 9.5 | 7.8 | 8.7 | 0.86554
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-10 | 300-PF-20003-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21748 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 9.375 | CML-10 | CML: Elbow | 6 | 2016-02-03 | 2015-06-08 | 2014-10-01 07:00 | 2.5 | 4.3968 | A2: Right Quadrant |  | 8.27 | 2.5 | 5.385 | 8.4 | 3 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.7 | 8.4 | 10.4 | 9 | 0.86554
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-2 | 80-PW-44016-01C02-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 21934 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.7 | CML-2 | CML: Elbow | 3 | 2019-04-21 | 2019-12-27 | 2014-10-10 07:00 | 2.5 | 0.50746 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 6.1 | 5.8 | 6.1 | 0.61644
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-12 | 250-PG-20036-01C03-P CML-12 |  | FPSO 2016 | Pipe Wall Thickness | 24416 | Re-check as requested by N.Sequera | 2016-07-06 07:00 | 2016-07-06 15:00 | Check Corrosion Rate of 0.345mm/ yr | 41 | Kirstie Albone | 2017-03-23 15:17 | [32 empty] | 9.275 | CML-12 | CML: Elbow | 6 | 2033-01-04 | 2031-11-24 | 2016-07-06 07:00 | 2.5 | 0.34522 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.2 | 12 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | 0.20798 | 8.2 | 9.2 | 9.4 | 10.3 | 0.86168
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-46 | 150-PG-23506-25C02 CML-46 |  | FPSO 2014 | Pipe Wall Thickness | 2820 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.775 | CML-46 | CML: Pipe Length | 3 | 2017-03-27 | 2016-04-08 | 2014-03-15 09:00 | 15.88 | 1.5877 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.7 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.82 |  | 21.9 | 21.7 | 20.7 | 22.8 | 0.86168
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-11 | 50-DH-56137-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23055 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 17.225 | CML-11 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2015-05-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 16.2 | 3 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.7 |  | 18.3 | 16.2 | 17.3 | 17.1 | 0.86168
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-21 | 100-WC-40516-1CG CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 8694 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:58 | [32 empty] | 9.4 | CML-21 | CML: Elbow | 3 | 2053-02-15 | 2043-02-06 | 2015-02-13 07:00 | 2.5 | 0.1525 | A2: Right Quadrant |  | 5.56 | 2.5 | 4.03 | 8.3 | 3 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9 | 8.3 | 10.3 | 10 | 0.92014
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-11 | 50-PL-23300-09C03 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 13127 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 11.675 | CML-11 | CML: type TBC | 6 | 2093-08-18 | 2082-08-28 | 2014-02-04 07:00 | 2.81 | 0.1029 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 11 | 6 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.19 |  | 11.9 | 11 | 11 | 12.8 | 0.86168
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-1 | 200-PG-23013-09C03-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10985 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 20.725 | CML-1 | CML: Pipe Length | 6 | 2025-08-17 | 2023-01-16 | 2014-01-10 | 10.22 | 0.85112 | A2: Right Quadrant |  | 14.62 | 10.22 | 12.42 | 20.1 | 3 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.88 |  | 20.4 | 20.1 | 22 | 20.4 | 0.86168
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-16 | 50-FL-43454-01C02-P CML-16 | Yes | FPSO 2014 | Pipe Wall Thickness | 20519 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 7.175 | CML-16 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 40 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 8.3 | 6.5 | 7.4 | 6.5 | 0.86168
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56065-01C02 | CML-5 | 50-DH-56065-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3413 | Rope Access | 2014-05-11 09:30 | 2014-05-11 11:00 | [36 empty] | 5.6 | CML-5 | CML: type TBC | 3 | 2016-10-29 | 2017-03-12 | 2014-05-11 09:30 | 2.5 | 0.89025 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DH-56065-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.8 | 6.7 | 5.2 | 0.86023
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-10 | 80-PL-44008-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5747 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 6.075 | CML-10 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6 | 6.5 | 6.3 | 0.43493
FL02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-FL-43454-01C02-P | CML-4 | 50-FL-43454-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8702 | Material Class Not Selectable. Line is FFS. Action: to recheck in two year(Feb. 2017) to confirm CR | 2015-02-13 14:00 | 2015-02-13 15:00 | Check Corrosion Rate of 1.096mm/ yr | 36 | Administrator | 2015-09-08 11:50 | [32 empty] | 10.2 | CML-4 | CML: Elbow | 3 | 2021-02-18 | 2018-08-23 | 2015-02-13 14:00 | 2.5 | 1.0963 | A4: Left Quadrant |  | 7.97 | 2.5 | 5.235 | 9.1 | 9 O'Clock | 150 | 10.97 | 150-WC-40509-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 11.2 | 10.2 | 10.3 | 9.1 | 0.86023
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-16 | 150-WF-71372-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 5346 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 5.125 | CML-16 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.8 | 9 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 4.8 | 5.9 | 4.8 | 0.5252
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71372-01K01 | CML-3 | 150-WF-71372-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5333 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 5.3 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.9 | 3 O'Clock | 150 | 3 | 150-WF-71372-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.5 | 4.9 | 5.5 | 5.3 | 0.28284
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-3 | 150-WF-71374-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5138 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.15 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.1 | 9 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.3 | 3.1 | 3.1 | 0.1
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-25 | 150-WF-71374-01K01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 5160 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.775 | CML-25 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 3 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.7 | 3.2 | 3.8 | 4.4 | 0.49244
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56075-01C02 | CML-1 | 50-DN-56075-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3491 | Rope Access | 2014-05-14 14:00 | 2014-05-14 15:00 | [36 empty] | 5.2 | CML-1 | CML: type TBC | 3 | 2018-10-09 | 2019-05-07 | 2014-05-14 14:00 | 2.5 | 0.56706 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DN-56075-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5.2 | 5.6 | 0.28284
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-20 | 150-WF-71374-01K01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 5155 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.55 | CML-20 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 12 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.2 | 3.6 | 3.6 | 3.8 | 0.25166
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-7 | 50-DH-56137-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5448 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 4.182mm/ yr | [34 empty] | Low alarm breach | 18.4 | CML-7 | CML: Straight | 3 | 2017-12-09 | 2016-01-14 | 2014-05-28 07:00 | 2.5 | 4.1825 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.3 | 6 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 |  | 18.4 | 18.5 | 17.3 | 19.4 | 0.86023
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-24 | 300-PF-20501-03C03-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21700 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 15.25 | CML-24 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.6 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 16.5 | 14.6 | 14.8 | 15.1 | 0.85829
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-33 | 300-PF-20501-03C03-P CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 21709 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.55 | CML-33 | CML: type TBC | 6 | 2039-11-06 | 2035-02-04 | 2014-09-28 07:00 | 4.9 | 0.35423 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14.9 | 15.6 | 13.8 | 13.9 | 0.85829
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-9 | 200-PG-23505-09C02-A CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 2690 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.55 | CML-9 | CML: Pipe Length | 3 | 2019-04-03 | 2018-06-03 | 2014-03-12 09:00 | 14.06 | 0.71877 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.7 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.64 | 0 | 17.7 | 18.6 | 19.2 | 18.7 | 0.6245
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-11 | 300-FL-43080-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2390 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 10.875 | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.1 | 3 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.7 | 10.1 | 12.1 | 10.6 | 0.85781
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38002-09C02-P | CML-7 | 50-CG-38002-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20798 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 |  |  | Administrator | 2015-09-07 11:00 | [32 empty] | 9.375 | CML-7 | CML: Elbow | 3 | 2029-06-06 | 2025-04-09 | 2014-07-18 11:00 | 2.5 | 0.38937 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-CG-38002-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 10.4 | 9.4 | 9.4 | 8.3 | 0.85781
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-2 | 150-PG-20507-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2846 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.95 | CML-2 | CML: type TBC | 6 | 2018-09-05 | 2017-11-29 | 2014-03-16 07:00 | 2.5 | 1.6079 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 9.7 | 12 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 11.5 | 11.5 | 11.1 | 0.8544
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44025-01X01 | CML-1 | 50-PW-44025-01X01 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10340 | Deck Level | 2013-11-11 | 2013-11-11 | [36 empty] | 4.95 | CML-1 | CML: Pipe Length | 3 | 2015-01-11 | 2015-03-16 | 2013-11-11 | 2.5 | 1.881 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 4.8 | 4.7 | 5.3 | 0.26458
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-14 | 150-WF-71374-01K01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 5149 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.775 | CML-14 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.2 | 3 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.7 |  | 3.7 | 3.2 | 3.8 | 4.4 | 0.49244
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-10 | 50-CG-38487-09C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23579 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 12.55 | CML-10 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-10 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 11.5 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 | -3.086 | 12.3 | 13.5 | 12.9 | 11.5 | 0.8544
PL03 | Montara_Topside | Yes | Wellstream (57) | Pipework | 50-PL-57066-01C03 | CML-1 | 50-PL-57066-01C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22107 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 8.85 | CML-1 | CML: type TBC | 6 | 2021-09-12 | 2021-07-16 | 2014-10-18 07:00 | 2.5 | 0.75274 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.7 | 6 O'Clock | 50 | 8.74 | 50-PF-57066-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9.5 | 9.5 | 7.7 | 8.7 | 0.8544
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-24 | 50-DH-56062-01C02 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 9111 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.925 | CML-24 | CML: type TBC | 3 | 2023-04-08 | 2024-04-29 | 2015-03-02 07:00 | 2.5 | 0.30831 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.7 | 5 | 6.6 | 5.4 | 0.85391
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-4 | 50-PW-44009-01C03-P CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 22811 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 29.1 | CML-4 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.3 | 12 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | 0.11774 | 8.3 | 9.2 | 9 | 8.9 | 0.3873
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-10 | 300-PG-20037-03C03-PA CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21373 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | [36 empty] | 16.875 | CML-10 | CML: Elbow | 6 | 2102-10-24 | 2088-02-10 | 2014-06-29 13:00 | 5.33 | 0 | A1: Outside Quadrant |  | 8.27 | 5.33 | 6.8 | 16 | 12 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.67 |  | 16 | 17 | 16.5 | 18 | 0.85391
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20503-03C03-P | CML-4 | 50-PF-20503-03C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7745 |  | 2015-01-10 10:00 | 2015-01-10 12:00 | [36 empty] | 9.175 | CML-4 | CML: Elbow | 6 | 2025-05-20 | 2025-02-25 | 2015-01-10 10:00 | 2.5 | 0.52106 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 12 O'Clock | 50 | 8.74 | 50-PF-20503-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 9.6 | 9.7 | 9.5 | 0.85391
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-9 | 200-PG-23505-09C02-A CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 379 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 18.55 | CML-9 | CML: Pipe Length | 3 | 2019-04-01 | 2018-05-31 | 2014-03-12 | 14.06 | 0.71972 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.7 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.64 |  | 17.7 | 18.6 | 19.2 | 18.7 | 0.6245
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-1 | 100-FH-43104-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12752 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 5.7 | CML-1 | CML: type TBC | 3 | 2015-02-26 | 2015-03-19 | 2014-01-25 07:00 | 2.5 | 2.0219 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.7 | 12 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.4 | 6.7 | 6 | 0.85245
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-9 | 50-PL-45016-03C03 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10449 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.75 | CML-9 | CML: type TBC | 6 | 2017-08-01 | 2017-02-10 | 2013-11-13 | 0.99 | 1.8582 | A4: Left Quadrant |  | 2.74 | 0.99 | 1.865 | 7.9 | 9 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.91 |  | 9.9 | 8.8 | 8.4 | 7.9 | 0.85049
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-4 | 50-PW-44009-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5815 | Protective mesh removed | 2014-06-24 07:00 | 2014-06-24 08:00 | [36 empty] | 9.125 | CML-4 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2014-06-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.4 | 12 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9 | 9.6 | 9.5 | 0.55
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43116-01C02 | CML-7 | 150-FH-43116-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7871 | Line is FFS. It has been check twice. The higher values reported here are from the data collected in Apr. 2014. The rechecked CR’s from data from Jan. 2015 are lower. Current RBI frequency is 48m. Action: to recheck line in a 24m (Jan. 2017) to confirm CR. | 2015-01-14 09:30 | 2015-01-14 10:30 |  |  | Administrator | 2015-09-07 17:07 | [32 empty] | 7.875 | CML-7 | CML: Elbow | 3 | 2031-08-26 | 2030-03-23 | 2015-01-14 09:30 | 2.5 | 0.25262 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 12 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 8.2 | 7.9 | 8.7 | 0.85
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-10 | 50-DH-56070-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 3226 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.775 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.6 | 6.2 | 7.4 | 5.9 | 0.85
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-4 | 80-PW-44016-01C02-P CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 22906 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.425 | CML-4 | CML: Elbow | 3 | 2021-09-21 | 2022-09-09 | 2015-05-02 07:00 | 2.5 | 0.35964 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.35784 | 4.8 | 5.2 | 6 | 5.7 | 0.53151
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-10 | 50-CG-38487-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20810 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 11.3 | CML-10 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.3 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 11.9 | 10.9 | 10.3 | 12.1 | 0.84853
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45028-03C02-E | CML-2 | 80-FG-45028-03C02-E CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24326 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.775 | CML-2 | CML: Elbow | 3 | 2028-09-22 | 2026-10-08 | 2016-06-01 07:00 | 1.46 | 0.26302 | A3: Inside Quadrant |  | 2.49 | 1.46 | 1.975 | 4.7 | 6 O'Clock | 80 | 5.49 | 80-FG-45028-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.24 |  | 5.6 | 6.7 | 4.7 | 6.1 | 0.84607
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-6 | 50-PW-44012-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23165 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5 | CML-6 | CML: Pipe Length | 3 | 2020-06-10 | 2021-03-13 | 2015-05-11 07:00 | 2.5 | 0.43226 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.35619 | 5 | 5.1 | 4.7 | 5.2 | 0.21602
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-26 | 100-DC-57036-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 1432 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 1.2mm/ yr | [35 empty] | 5.6 | CML-26 | CML: type TBC | 3 | 2016-05-06 | 2016-06-11 | 2014-04-07 07:00 | 2.5 | 1.1998 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.1 | 6 | 5.3 | 5 | 0.53541
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-12 | 100-DC-57036-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1418 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 1.2mm/ yr | [35 empty] | 5.5 | CML-12 | CML: type TBC | 3 | 2016-05-06 | 2016-06-11 | 2014-04-07 07:00 | 2.5 | 1.1998 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.7 | 5.9 | 5.4 | 5 | 0.39158
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57051-01C02 | CML-1 | 50-DC-57051-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1394 | Rope access | 2014-04-05 14:00 | 2014-04-05 15:00 | Check Corrosion Rate of 0.639mm/ yr | [35 empty] | 5.275 | CML-1 | CML: type TBC | 3 | 2018-03-04 | 2018-09-06 | 2014-04-05 14:00 | 2.5 | 0.63873 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.2 | 5.5 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57063-01C02 | CML-8 | 50-DC-57063-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1393 | Rope access | 2014-04-05 13:00 | 2014-04-05 14:00 | Check Corrosion Rate of 0.639mm/ yr | [35 empty] | 5.45 | CML-8 | CML: type TBC | 3 | 2018-03-03 | 2018-09-06 | 2014-04-05 13:00 | 2.5 | 0.63881 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.3 | 5.6 | 5.9 | 0.3873
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57063-01C02 | CML-7 | 50-DC-57063-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1392 | Rope access | 2014-04-05 13:00 | 2014-04-05 14:00 | Check Corrosion Rate of 0.639mm/ yr | [35 empty] | 5.125 | CML-7 | CML: type TBC | 3 | 2018-03-03 | 2018-09-06 | 2014-04-05 13:00 | 2.5 | 0.63881 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DC-57063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.2 | 5.2 | 5 | 0.095743
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57014-01C02 | CML-6 | 50-DC-57014-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1367 | Rope access | 2014-04-04 13:00 | 2014-04-04 15:00 | Check Corrosion Rate of 0.641mm/ yr | [35 empty] | 5.35 | CML-6 | CML: type TBC | 3 | 2018-02-26 | 2018-08-31 | 2014-04-04 13:00 | 2.5 | 0.64089 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.1 | 5.6 | 5.7 | 0.35119
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-26 | 150-WF-71374-01K01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 5161 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.725 | CML-26 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 12 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.7 | 4.2 | 3.7 | 0.36856
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-22 | 150-WF-71374-01K01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 5157 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.8 | CML-22 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 3 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.6 | 3.3 | 3.9 | 4.4 | 0.46904
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-18 | 150-WF-71374-01K01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 5153 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.75 | CML-18 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 6 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.1 | 3.8 | 3.3 | 3.8 | 0.33166
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-15 | 150-WF-71374-01K01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 5150 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.575 | CML-15 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 3 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.8 | 3.3 | 3.6 | 3.6 | 0.20616
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-19 | 50-DN-56101-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 859 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.15 | CML-19 | CML: Elbow | 3 | 2018-02-15 | 2018-08-18 | 2014-04-02 14:00 | 2.5 | 0.645 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5 | 5.4 | 0.19149
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-13 | 50-DN-56101-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 853 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.15 | CML-13 | CML: Elbow | 3 | 2018-02-15 | 2018-08-18 | 2014-04-02 14:00 | 2.5 | 0.645 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.3 | 5.1 | 0.1291
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-10 | 50-DN-56101-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 850 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.5 | CML-10 | CML: Elbow | 3 | 2018-02-15 | 2018-08-18 | 2014-04-02 14:00 | 2.5 | 0.645 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.6 | 5.8 | 5.6 | 5 | 0.34641
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-5 | 50-DN-56101-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 845 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.1 | CML-5 | CML: Elbow | 3 | 2018-02-15 | 2018-08-18 | 2014-04-02 14:00 | 2.5 | 0.645 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5 | 5.2 | 5.1 | 0.08165
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-17 | 50-WC-40452-01C02 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10614 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 1.598mm/ yr | [35 empty] | 5.075 | CML-17 | CML: type TBC | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.2 | 5 | 5.3 | 0.22174
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-38 | 300-PF-20003-03C03-P CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 21776 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.375 | CML-38 | CML: Reducing Tee | 6 | 2026-04-21 | 2023-12-26 | 2014-10-01 07:00 | 4.9 | 0.72657 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 6 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 14.2 | 15.3 | 13.3 | 14.7 | 0.84607
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-40 | 150-PG-23506-25C02 CML-40 |  | FPSO 2014 | Pipe Wall Thickness | 2814 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.55 | CML-40 | CML: Pipe Length | 3 | 2016-12-14 | 2016-01-22 | 2014-03-15 09:00 | 15.88 | 1.7147 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.6 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.72 |  | 20.6 | 21.1 | 22.4 | 22.1 | 0.84261
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56097-01C02 | CML-5 | 50-DN-56097-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1327 |  | 2014-04-01 07:00 | 2014-04-01 08:00 | [36 empty] | 5.25 | CML-5 | CML: type TBC | 3 | 2018-02-08 | 2018-08-10 | 2014-04-01 07:00 | 2.5 | 0.64773 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DN-56097-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5 | 5.5 | 5.1 | 0.23805
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56097-01C02 | CML-3 | 50-DN-56097-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1325 |  | 2014-04-01 07:00 | 2014-04-01 08:00 | [36 empty] | 5.35 | CML-3 | CML: type TBC | 3 | 2018-02-08 | 2018-08-10 | 2014-04-01 07:00 | 2.5 | 0.64773 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-DN-56097-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.7 | 5 | 5.5 | 0.31091
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56134-01C02 | CML-2 | 50-DN-56134-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1314 |  | 2014-03-31 10:00 | 2014-03-31 10:15 | [36 empty] | 5.525 | CML-2 | CML: type TBC | 3 | 2018-02-03 | 2018-08-05 | 2014-03-31 10:00 | 2.5 | 0.6496 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DN-56134-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.7 | 5 | 5.5 | 5.9 | 0.38622
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56096-01C02 | CML-1 | 50-DN-56096-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1310 |  | 2014-03-31 09:30 | 2014-03-31 10:00 | [36 empty] | 5.325 | CML-1 | CML: type TBC | 3 | 2018-02-03 | 2018-08-05 | 2014-03-31 09:30 | 2.5 | 0.64965 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DN-56096-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.2 | 5.7 | 0.29861
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56095-01C02 | CML-3 | 50-DN-56095-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1309 |  | 2014-03-31 08:00 | 2014-03-31 09:00 | [36 empty] | 5.45 | CML-3 | CML: type TBC | 3 | 2018-02-02 | 2018-08-04 | 2014-03-31 08:00 | 2.5 | 0.64978 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DN-56095-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.7 | 5.5 | 5.6 | 5 | 0.31091
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-12 | 350-FL-43511-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2293 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 8.225 | CML-12 | CML: type TBC | 3 | 2021-09-02 | 2020-07-31 | 2014-03-17 08:00 | 2.5 | 0.65599 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 12 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 9 | 8.9 | 7.6 | 0.84212
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-7 | 250-PW-20039-01C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5839 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 8.95 | CML-7 | CML: Elbow | 6 | 2021-09-10 | 2021-03-22 | 2014-06-24 13:00 | 2.5 | 0.81729 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.4 | 12 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 8.9 | 9.3 | 9.2 | 0.40415
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-6 | 50-DC-57044-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2144 | Rope Access | 2014-03-29 10:30 | 2014-03-29 12:00 | Check Corrosion Rate of 0.654mm/ yr | [35 empty] | 5.325 | CML-6 | CML: Pipe Length | 3 | 2018-01-22 | 2018-07-24 | 2014-03-29 10:30 | 2.5 | 0.65387 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.2 | 5.7 | 0.29861
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-7 | 150-WF-71374-01K01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 5142 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.825 | CML-7 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 3 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.9 | 3.3 | 3.7 | 4.4 | 0.45735
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-4 | 150-WF-71374-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5139 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.95 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 12 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.8 | 4.5 | 4.2 | 0.51962
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-5 | 50-PG-44022-01C03-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22980 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 12.175 | CML-5 | CML: Reducer | 6 | 2075-10-24 | 2074-08-12 | 2015-05-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 11.2 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 | 2.2157 | 13.1 | 12.6 | 11.2 | 11.8 | 0.84212
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-12 | 50-PW-44015-01X01 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10295 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.875 | CML-12 | CML: Elbow | 3 | 2015-01-08 | 2015-03-12 | 2013-11-10 | 2.5 | 1.8926 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 4.8 | 4.7 | 4.9 | 0.17078
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-2 | 200-PG-23505-09C02-A CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 2683 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.2 | CML-2 | CML: Pipe Length | 3 | 2019-04-03 | 2018-06-03 | 2014-03-12 09:00 | 14.06 | 0.71877 | A3: Inside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.7 | 6 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.64 | 0 | 18.7 | 18.6 | 17.7 | 17.8 | 0.52281
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-21 | 150-WF-71374-01K01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 5156 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.6 | CML-21 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 9 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.6 | 3.7 | 3.7 | 3.4 | 0.14142
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-19 | 150-WF-71374-01K01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 5154 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.85 | CML-19 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 12 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.4 | 3.8 | 4.5 | 3.7 | 0.46547
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-9 | 150-WF-71374-01K01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 5144 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.575 | CML-9 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 6 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.7 | 3.5 | 3.4 | 3.7 | 0.15
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-8 | 150-WF-71374-01K01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 5143 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.575 | CML-8 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 3 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.5 | 3.4 | 3.7 | 3.7 | 0.15
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-17 | 150-WF-71374-01K01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 5152 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.75 | CML-17 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 9 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.8 | 3.9 | 3.8 | 3.5 | 0.17321
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-23 | 100-PW-20021-01C02-P CML-23 | yes | FPSO 2015 | Pipe Wall Thickness | 22841 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.425 | CML-23 | CML: Elbow | 3 | 2018-12-06 | 2019-02-11 | 2015-04-30 07:00 | 2.5 | 0.6377 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 1.6343 | 5.9 | 5.7 | 5.3 | 4.8 | 0.48563
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22326 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 6.075 | CML-4 | CML: type TBC | 3 | 2033-08-02 | 2035-10-02 | 2014-05-06 07:00 | 2.5 | 0.15061 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 7.3 | 5.8 | 0.83815
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1846 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 6.075 | CML-4 | CML: type TBC | 3 | 2033-08-02 | 2035-10-02 | 2014-05-06 07:00 | 2.5 | 0.15061 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 7.3 | 5.8 | 0.83815
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-12 | 25-FG-45455-01C02-E CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1692 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 7.125 | CML-12 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.4 | 7.1 | 6 | 8 | 0.83815
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-3 | 80-CG-38486-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21451 | Protective mesh removed | 2014-06-29 09:30 | 2014-06-29 11:00 | [36 empty] | 16.175 | CML-3 | CML: Equal Tee | 6 | 2099-09-17 | 2086-07-24 | 2014-06-29 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 15.4 | 9 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.9 |  | 16.3 | 17.3 | 15.7 | 15.4 | 0.83815
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-14 | 100-FG-45001-09C02 CML-14 | Yes | FPSO 2015 | Pipe Wall Thickness | 23319 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.725 | CML-14 | CML: type TBC | 3 | 2039-01-01 | 2032-03-05 | 2015-07-11 07:00 | 4.7 | 0.25114 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.6 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | -0.30151 | 11.6 | 10.6 | 12.2 | 12.5 | 0.83815
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-26 | 50-DC-57020-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 2468 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.674mm/ yr | [35 empty] | 5.4 | CML-26 | CML: type TBC | 3 | 2017-12-03 | 2018-05-28 | 2014-03-20 09:30 | 2.5 | 0.67409 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.6 | 5.8 | 0.36515
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56130-01C02 | CML-2 | 50-DH-56130-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21054 | Rope Access | 2014-05-15 13:00 | 2014-05-15 14:00 | [36 empty] | 7.725 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-15 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 12 O'Clock | 50 | 5.54 | 50-DH-56130-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 8.6 | 8 | 7.7 | 0.83815
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-11 | 50-DH-56137-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23439 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 18.125 | CML-11 | CML: Pipe Length | 3 | 2022-07-21 | 2018-09-15 | 2015-07-23 07:00 | 2.5 | 2.0716 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 17 | 6 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.5 | 0.64405 | 19 | 18.4 | 17 | 18.1 | 0.83815
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-1 | 300-PG-23002-03C03-A CML-1 | Yes | FPSO 2013 | Pipe Wall Thickness | 10097 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 13.525 | CML-1 | CML: Elbow | 6 | 2016-02-04 | 2015-08-23 | 2013-11-07 | 5.22 | 3.3745 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 12.8 | 9 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.58 |  | 14.3 | 14.2 | 12.8 | 12.8 | 0.83815
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-4 | 300-PG-23002-03C03-A CML-4 | Yes | FPSO 2013 | Pipe Wall Thickness | 10100 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 13.5 | CML-4 | CML: Elbow | 6 | 2016-02-04 | 2015-08-23 | 2013-11-07 | 5.22 | 3.3745 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 12.8 | 12 O'Clock | 40 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.58 |  | 12.8 | 14.6 | 13.7 | 12.9 | 0.83666
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-1 | 80-CG-38459-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20766 | No pipe schedule provided | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 15.2 | CML-1 | CML: Pipe Length | 6 | 2098-02-09 | 2085-10-05 | 2014-10-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 14.5 | 6 O'Clock | 150 | 10.97 | 100-PG-23409-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12 |  | 15.1 | 14.8 | 14.5 | 16.4 | 0.83666
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-18 | 200-PG-24001-09C02 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10274 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 18.2 | CML-18 | CML: Pipe Length | 3 | 2016-11-09 | 2015-09-15 | 2013-11-09 | 9.2 | 2.6298 | A1: Outside Quadrant |  | 15.26 | 9.2 | 12.23 | 17.1 | 12 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 17.1 | 18.9 | 18.8 | 18 | 0.83666
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-34 | 50-DH-56062-01C02 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 9121 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 6.05 | CML-34 | CML: type TBC | 3 | 2035-08-02 | 2037-12-18 | 2015-03-02 07:00 | 2.5 | 0.13703 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 7 | 6.5 | 5.4 | 5.3 | 0.83467
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-18 | 300-PF-20003-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21756 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 9.35 | CML-18 | CML: Elbow | 6 | 2016-02-03 | 2015-06-08 | 2014-10-01 07:00 | 2.5 | 4.3968 | A2: Right Quadrant |  | 8.27 | 2.5 | 5.385 | 8.4 | 3 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.1 | 8.4 | 9.5 | 10.4 | 0.83467
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-3 | 350-FL-43511-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2284 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 7.75 | CML-3 | CML: type TBC | 3 | 2016-12-07 | 2016-06-20 | 2014-03-17 08:00 | 2.5 | 1.5391 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 6.7 | 12 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 8.2 | 7.5 | 8.6 | 0.83467
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-14 | 250-PW-44509-01C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 22049 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.4 | CML-14 | CML: Elbow | 6 | 2025-08-08 | 2024-11-28 | 2014-10-20 07:00 | 2.5 | 0.55511 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.5 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10.3 | 9.2 | 8.5 | 9.6 | 0.75277
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-5 | 50-PW-44015-01X01 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10288 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.9 | CML-5 | CML: Pipe Length | 3 | 2015-01-08 | 2015-03-12 | 2013-11-10 | 2.5 | 1.8926 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 5 | 5 | 4.7 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-16 | 50-WC-40451-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 3078 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 0.803mm/ yr | [35 empty] | 5.025 | CML-16 | CML: Elbow | 3 | 2017-03-13 | 2017-08-08 | 2014-05-03 08:00 | 2.5 | 0.80307 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 6.4534 | 4.9 | 5.1 | 4.8 | 5.3 | 0.22174
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-20 | 200-PL-20019-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21271 | Reviewed on 27/11/14. FFS. recheck on Sep.15 | 2014-09-30 07:00 | 2014-09-30 15:00 |  |  | Nestor | 2014-11-27 15:58 | [32 empty] | 5.9 | CML-20 | CML: Fitting | 3 | 2019-06-12 | 2019-05-27 | 2014-09-30 07:00 | 2.5 | 0.63799 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 3 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 5.5 | 5.8 | 6.4 | 0.37417
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-20 | 250-PG-23004-06C03-A CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23387 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.525 | CML-20 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2015-07-21 07:00 | 8.55 | 0 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.4 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.85 | 0.065687 | 19.4 | 20.2 | 18.4 | 20.1 | 0.83016
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-12 | 150-WF-71374-01K01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5147 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.6 | CML-12 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 9 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.7 | 3.7 | 3.5 | 3.5 | 0.11547
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-11 | 150-WF-71374-01K01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5146 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.6 | CML-11 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 12 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.5 | 3.6 | 3.7 | 3.6 | 0.08165
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-10 | 150-WF-71374-01K01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 5145 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.6 | CML-10 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.5 | 6 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.6 | 3.7 | 3.5 | 3.6 | 0.08165
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-12 | 50-CG-24002-09C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2558 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 9.175 | CML-12 | CML: type TBC | 3 | 2035-03-28 | 2029-07-27 | 2014-04-03 13:00 | 2.5 | 0.28577 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 3 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10.3 | 8.5 | 8.6 | 9.3 | 0.83016
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43119-01C02 | CML-1 | 80-FH-43119-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12828 |  | 2014-01-18 10:00 | 2014-01-18 11:30 | [36 empty] | 8.175 | CML-1 | CML: Reducer | 3 | 2062-11-29 | 2056-08-05 | 2014-01-18 10:00 | 0.54 | 0 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 7.3 | 12 O'Clock | 50 | 5.49 | 80-FH-43119-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.76 |  | 7.3 | 8.1 | 8 | 9.3 | 0.83016
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-11 | 150-PG-20507-01C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2855 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.825 | CML-11 | CML: type TBC | 6 | 2018-09-05 | 2017-11-29 | 2014-03-16 07:00 | 2.5 | 1.6079 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 9.7 | 6 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 11.4 | 10.7 | 9.7 | 11.5 | 0.83016
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-36 | 300-PF-20501-03C03-P CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 21712 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.575 | CML-36 | CML: type TBC | 6 | 2029-07-20 | 2026-08-25 | 2014-09-28 07:00 | 4.9 | 0.58033 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 15.5 | 14.8 | 13.5 | 14.5 | 0.83016
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-44 | 300-PF-20003-03C03-P CML-44 | yes | FPSO 2014 | Pipe Wall Thickness | 21782 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [35 empty] | Low alarm breach | 7.375 | CML-44 | CML: Elbow | 6 | 2015-06-09 | 2014-12-10 | 2014-10-01 07:00 | 2.5 | 5.82 | A2: Right Quadrant |  | 8.27 | 2.5 | 5.385 | 6.5 | 3 O'Clock | 40 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.2 | 6.5 | 8.5 | 7.3 | 0.83016
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-2 | 200-PG-23505-09C02-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 372 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 18.2 | CML-2 | CML: Pipe Length | 3 | 2019-04-01 | 2018-05-31 | 2014-03-12 | 14.06 | 0.71972 | A3: Inside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.7 | 6 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.64 |  | 18.7 | 18.6 | 17.7 | 17.8 | 0.52281
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-7 | 50-PG-44022-01C03-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22982 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 11.9 | CML-7 | CML: Equal Tee | 6 | 2075-10-24 | 2074-08-12 | 2015-05-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 10.7 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 | 4.6645 | 12.5 | 12.4 | 10.7 | 12 | 0.82865
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-5 | 50-CG-38487-09C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20805 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.8 | CML-5 | CML: Elbow | 3 | 2189-07-31 | 2143-11-05 | 2014-07-18 11:00 | 2.5 | 0.0354 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 10.7 | 9.8 | 10 | 8.7 | 0.82865
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20069-01C02-P | CML-4 | 100-PL-20069-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21558 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 5.75 | CML-4 | CML: Elbow | 3 | 2021-01-14 | 2021-04-16 | 2014-07-17 07:30 | 2.5 | 0.46145 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 3 O'Clock | 100 | 6.02 | 100-PL-20069-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.5 | 6.2 | 5.8 | 0.33166
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-6 | 50-CG-38487-09C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23575 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 9.15 | CML-6 | CML: Elbow | 3 | 2072-08-03 | 2057-03-24 | 2015-09-10 07:00 | 2.5 | 0.10538 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 0.42566 | 9.2 | 8.5 | 8.6 | 10.3 | 0.82664
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-11 | 250-PG-23004-06C03-A CML-11 |  | FPSO 2016 | Pipe Wall Thickness | 24454 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | Check Corrosion Rate of 0.568mm/ yr |  | John Wilson | 2017-03-23 14:59 | Loss within CA no further action required. | [31 empty] | 17.65 | CML-11 | CML: Elbow | 6 | 2030-06-27 | 2027-03-24 | 2016-07-05 07:00 | 8.55 | 0.56835 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 16.5 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.95 | 0.93857 | 16.5 | 18.3 | 18.2 | 17.6 | 0.82664
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-9 | 50-WC-40452-01C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10606 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 1.598mm/ yr | [35 empty] | 5.075 | CML-9 | CML: type TBC | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.1 | 5.1 | 5.3 | 0.20616
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43112-01C02 | CML-1 | 80-FH-43112-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20427 | Rope Access | 2014-05-25 13:00 | 2014-05-25 14:00 | [36 empty] | 6.175 | CML-1 | CML: type TBC | 3 | 2019-05-28 | 2020-02-07 | 2014-05-25 13:00 | 2.5 | 0.49883 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-FH-43112-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 6.2 | 6.8 | 6.7 | 0.82614
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-10 | 300-PG-23001-03C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10960 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.175 | CML-10 | CML: Elbow | 6 | 2021-08-16 | 2020-03-29 | 2014-01-09 | 5.22 | 1.1016 | A2: Right Quadrant |  | 8.27 | 5.22 | 6.745 | 13.6 | 3 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.38 |  | 13.8 | 13.6 | 13.9 | 15.4 | 0.82614
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20069-01C02-P | CML-2 | 100-PL-20069-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21556 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.2 | CML-2 | CML: Elbow | 3 | 2022-11-08 | 2023-03-02 | 2014-07-17 07:30 | 2.5 | 0.37271 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-PL-20069-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 7.1 | 6.2 | 5.6 | 0.64807
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20042 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.4 | CML-4 | CML: Pipe Length | 3 | 2017-07-26 | 2016-07-08 | 2014-05-29 07:00 | 15.88 | 1.4608 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 3 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 | 0 | 22.1 | 20.5 | 22.1 | 20.9 | 0.82462
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-6 | 50-PW-44015-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22711 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 4.775 | CML-6 | CML: Elbow | 3 | 2020-04-24 | 2021-01-20 | 2015-04-28 07:00 | 2.5 | 0.44033 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | -0.23558 | 4.8 | 4.9 | 4.7 | 4.7 | 0.095743
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-6 | 200-PW-44019-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23034 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 5.85 | CML-6 | CML: Fitting | 3 | 2018-03-16 | 2018-03-03 | 2015-05-06 07:00 | 2.5 | 0.80329 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.8 | 9 O'Clock | 200 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 1.0237 | 6.5 | 6.5 | 5.6 | 4.8 | 0.81854
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-5 | 300-PL-20011-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23489 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 6.175 | CML-5 | CML: Fitting | 3 | 2024-06-19 | 2024-05-20 | 2015-07-27 07:00 | 2.5 | 0.34815 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 40 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0.71803 | 6.8 | 5.9 | 5.6 | 6.4 | 0.53151
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23041 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 5.85 | CML-4 | CML: Fitting | 3 | 2018-03-16 | 2018-03-03 | 2015-05-06 07:00 | 2.5 | 0.80329 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.8 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 1.1376 | 6 | 6.1 | 4.8 | 6.5 | 0.73258
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-2 | 250-PW-20022-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2045 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 9.05 | CML-2 | CML: Elbow | 6 | 2020-08-23 | 2020-03-26 | 2014-03-28 07:00 | 2.5 | 0.93592 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.5 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.8 | 9.2 | 8.7 | 8.5 | 0.58023
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-16 | 100-PG-23503-03C03-A CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2732 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 11.275 | CML-16 | CML: Elbow | 6 | 2019-04-09 | 2019-07-21 | 2014-03-13 09:00 | 5.66 | 0.93368 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.4 | 12 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.74 |  | 10.4 | 10.8 | 12.2 | 11.7 | 0.82209
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23048-09C02 | CML-1 | 50-PG-23048-09C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20583 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.8 | CML-1 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9 | 9 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.4 | 10.9 | 9.9 | 9 | 0.82057
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-24 | 150-WF-71374-01K01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 5159 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.625 | CML-24 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 9 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.6 | 3.6 | 3.6 | 0.05
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-23 | 150-WF-71374-01K01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 5158 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.675 | CML-23 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 6 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.7 | 3.6 | 3.7 | 0.05
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56063-01C02 | CML-2 | 50-DH-56063-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3362 | Rope Access | 2014-05-10 07:00 | 2014-05-10 08:00 | [36 empty] | 7.2 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-DH-56063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 7.1 | 8 | 7.6 | 0.82057
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-15 | 50-DH-56137-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23443 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | Check Corrosion Rate of 0.317mm/ yr |  | John Wilson | 2017-03-23 11:35 | Loss within CA include this CML in the next inspection | [30 empty] | Low alarm breach | 17.9 | CML-15 | CML: Pipe Length | 3 | 2022-02-27 | 2018-06-24 | 2015-07-23 07:00 | 2.5 | 2.1649 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 16.8 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.3 | 0.55204 | 18.7 | 18.3 | 17.8 | 16.8 | 0.82057
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-28 | 250-PW-44006-01X01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 23199 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.575 | CML-28 | CML: Fitting | 3 | 2018-03-28 | 2018-03-15 | 2015-05-11 07:00 | 2.5 | 0.79763 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.8 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 2.3031 | 6 | 5.5 | 4.8 | 6 | 0.56789
FG03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-FG-45055-06S01-E | CML-1 | 50-FG-45055-06S01-E CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24385 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.45 | CML-1 | CML: Elbow | 1 | 2035-06-01 | 2029-05-31 | 2016-06-07 07:00 | 1.71 | 0 | A4: Left Quadrant |  | 2.91 | 1.71 | 2.31 | 4.3 | 9 O'Clock | 50 | 3.91 | 50-FG-45055-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.59 |  | 4.5 | 4.4 | 4.6 | 4.3 | 0.1291
FG03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-FG-45054-06S01-E | CML-2 | 50-FG-45054-06S01-E CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24384 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.575 | CML-2 | CML: Elbow | 1 | 2035-06-01 | 2029-05-31 | 2016-06-07 07:00 | 1.71 | 0 | A2: Right Quadrant |  | 2.91 | 1.71 | 2.31 | 4.3 | 3 O'Clock | 50 | 3.91 | 50-FG-45054-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.59 |  | 4.9 | 4.3 | 4.5 | 4.6 | 0.25
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-11 | 300-PG-23001-03C03 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10961 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.825 | CML-11 | CML: Elbow | 6 | 2023-01-24 | 2021-06-09 | 2014-01-09 | 5.22 | 0.93716 | A2: Right Quadrant |  | 8.27 | 5.22 | 6.745 | 13.7 | 3 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.48 |  | 15.6 | 13.7 | 15.2 | 14.8 | 0.81803
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-3 | 400-FH-43508-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 6552 | Rope Access. Line is FFS. Action: to recheck in a year (Mar. 2016) to confirm CR. | 2015-03-30 07:00 | 2015-03-30 15:00 |  |  | Administrator | 2015-09-07 16:09 | [32 empty] | 7.325 | CML-3 | CML: Elbow | 3 | 2019-03-04 | 2018-05-31 | 2015-03-30 07:00 | 2.5 | 0.94082 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 6.2 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.3 | 6.2 | 8.1 | 7.7 | 0.81803
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-21 | 50-PL-23020-01C03 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10135 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.6 | CML-21 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 9 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 9.8 | 8.4 | 8.2 | 8 | 0.8165
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-3 | 300-PG-20004-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6126 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 15 | CML-3 | CML: Elbow | 6 | 2035-07-16 | 2031-07-24 | 2014-07-11 07:30 | 4.9 | 0.42325 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 15.2 | 15.4 | 15.6 | 13.8 | 0.8165
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-13 | 150-WF-71374-01K01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 5148 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.675 | CML-13 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 9 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.7 | 3.8 | 3.6 | 0.095743
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-5 | 150-WF-71374-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5140 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.7 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 3 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 3.6 | 3.8 | 3.7 | 0.08165
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-2 | 150-WF-71374-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5137 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.85 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.6 | 6 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.7 | 4.3 | 3.6 | 3.8 | 0.31091
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-2 | 25-PW-44028-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10308 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 6.4 | CML-2 | CML: Equal Tee | 3 | 2016-07-09 | 2016-06-30 | 2013-11-10 | 2.5 | 1.2392 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 20 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6 | 6.2 | 7.6 | 0.8165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-23 | 400-FH-43508-01C02 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 6572 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 |  |  | Administrator | 2015-09-07 16:09 | [32 empty] | 7.425 | CML-23 | CML: Elbow | 3 | 2020-05-21 | 2019-06-20 | 2015-03-30 07:00 | 2.5 | 0.77672 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 6.5 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.1 | 6.5 | 8.4 | 7.7 | 0.81394
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23070-01C03-P | CML-1 | 300-PG-23070-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20598 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 10.425 | CML-1 | CML: Pipe Length | 6 | 2028-02-11 | 2026-05-30 | 2014-07-25 07:30 | 2.5 | 0.53099 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 3 O'Clock | 300 | 10.31 | 300-PG-23070-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.9 | 9.7 | 11.5 | 10.6 | 0.81394
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-16 | 50-PL-23514-01C03 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8649 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:23 | [32 empty] | 9 | CML-16 | CML: Elbow | 6 | 2033-01-05 | 2032-08-20 | 2015-02-10 11:30 | 2.5 | 0.31817 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 12 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 8.5 | 9.3 | 10 | 0.8124
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-16 | 150-WF-71374-01K01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 5151 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 3.85 | CML-16 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 3.7 | 9 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.8 | 3.7 | 4.2 | 3.7 | 0.23805
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38486-09C02-P | CML-18 | 80-CG-38486-09C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 20818 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 16.5 | CML-18 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 15.7 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.2 |  | 16 | 15.7 | 16.8 | 17.5 | 0.8124
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-38 | 300-PF-20001-03C03-P CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 21176 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.7 | CML-38 | CML: Elbow | 6 | 2015-12-22 | 2015-05-07 | 2014-07-16 07:30 | 2.5 | 4.5991 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 9.1 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 10.9 | 9.4 | 9.4 | 9.1 | 0.8124
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-11 | 50-PL-23020-01C03 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10125 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9 | CML-11 | CML: type TBC | 6 | 2021-06-15 | 2021-04-20 | 2013-11-08 | 2.5 | 0.77562 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 10.2 | 8.4 | 8.7 | 8.7 | 0.8124
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-3 | 80-PL-44008-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5740 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 6.2 | CML-3 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.5 | 6.5 | 6.2 | 0.42426
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-38 | 150-PG-23506-25C02 CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 2812 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.05 | CML-38 | CML: Pipe Length | 3 | 2017-12-18 | 2016-10-24 | 2014-03-15 09:00 | 15.88 | 1.3336 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.9 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.02 |  | 22.2 | 20.9 | 22.8 | 22.3 | 0.81035
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-18 | 50-CG-24002-09C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2564 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 10.55 | CML-18 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9.5 | 9 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 11.4 | 10.4 | 10.9 | 9.5 | 0.81035
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3371 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.55 | CML-3 | CML: type TBC | 3 | 2018-10-02 | 2018-12-05 | 2014-05-10 09:30 | 2.5 | 0.65901 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 3 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 7.3 | 5.4 | 6.7 | 6.8 | 0.81035
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-4 | 200-PG-23505-09C02-A CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 2685 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.125 | CML-4 | CML: Pipe Length | 3 | 2020-07-10 | 2019-07-05 | 2014-03-12 09:00 | 14.06 | 0.59042 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.8 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.74 | 0 | 17.8 | 18.1 | 17.9 | 18.7 | 0.40311
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-9 | 250-PW-20039-01C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5841 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 9.175 | CML-9 | CML: Reducing Tee | 6 | 2022-10-08 | 2022-03-27 | 2014-06-24 13:00 | 2.5 | 0.72335 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.5 | 6 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.6 | 8.9 | 8.5 | 9.7 | 0.57373
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-10 | 50-DH-56062-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 9097 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.725 | CML-10 | CML: type TBC | 3 | 2020-08-09 | 2021-05-18 | 2015-03-02 07:00 | 2.5 | 0.4225 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6.5 | 6.3 | 5.3 | 4.8 | 0.80984
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-38 | 250-PW-44006-01X01 CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 1935 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 5.35 | CML-38 | CML: Elbow | 3 | 2015-06-11 | 2015-06-06 | 2014-03-26 07:00 | 2.5 | 1.8966 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.8 | 12 O'Clock | 50 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.6 | 5.6 | 5.4 | 0.37859
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-12 | 50-WC-40452-01C02 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10609 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 1.598mm/ yr | [35 empty] | 5.025 | CML-12 | CML: type TBC | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.1 | 4.8 | 5.1 | 5.1 | 0.15
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-18 | 100-WC-40516-1CG CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8691 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:57 | [32 empty] | 8.675 | CML-18 | CML: Pipe Length | 3 | 2053-02-15 | 2043-02-06 | 2015-02-13 07:00 | 2.5 | 0.1525 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.3 | 12 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.9 | 9.1 | 8.4 | 0.38622
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20070-01C02-P | CML-6 | 100-PL-20070-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21566 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 5.85 | CML-6 | CML: Elbow | 3 | 2022-11-08 | 2023-03-02 | 2014-07-17 07:30 | 2.5 | 0.37271 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-PL-20070-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.7 | 6.4 | 5.6 | 0.36968
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 20020 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.875 | CML-1 | CML: type TBC | 3 | 2015-04-26 | 2015-07-09 | 2013-11-17 | 2.5 | 1.5982 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.9 | 4.8 | 5 | 0.095743
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 24240 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.425 | CML-2 | CML: Elbow | 3 | 2032-09-16 | 2029-08-14 | 2014-09-24 07:00 | 7.9 | 0.37238 | A1: Outside Quadrant |  | 12.09 | 7.9 | 9.0519 | 14.6 | 12 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 14.6 | 16.3 | 15.9 | 14.9 | 0.80571
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-1 | 150-WF-71374-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5136 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 5 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.4 | 3 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5.3 | 4.4 | 5.6 | 4.7 | 0.54772
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-5 | 50-DC-57044-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23123 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.9 | CML-5 | CML: Elbow | 3 | 2026-10-24 | 2028-04-01 | 2015-05-10 07:00 | 2.5 | 0.22674 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.17943 | 6.9 | 5.7 | 5.1 | 5.9 | 0.74833
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56084-01C02 | CML-3 | 100-DH-56084-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3345 | Rope Access | 2014-05-08 13:00 | 2014-05-08 14:00 | [36 empty] | 9.125 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8 | 12 O'Clock | 100 | 6.02 | 100-DH-56084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 9.1 | 9.6 | 9.8 | 0.80571
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-33 | 50-DH-56070-01C02 CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 3249 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 7.625 | CML-33 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 8.1 | 8.5 | 7.1 | 0.80571
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-23 | 50-CG-38452-09C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 23823 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 8.325 | CML-23 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 9.1 | 8.6 | 8.4 | 7.2 | 0.80571
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-25 | 250-PG-23004-06C03-A CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 23392 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.425 | CML-25 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2015-07-21 07:00 | 8.55 | 0 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 18.3 | 3 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.75 | 0.19706 | 19.9 | 18.3 | 19.4 | 20.1 | 0.80571
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-1 | 300-PG-20048-03C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23344 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.525 | CML-1 | CML: Elbow | 6 | 2036-05-24 | 2032-04-05 | 2015-07-20 07:00 | 4.9 | 0.40749 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 | -0.094341 | 13.4 | 14.5 | 15 | 15.2 | 0.80571
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-4 | 200-PG-23505-09C02-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 374 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 18.125 | CML-4 | CML: Pipe Length | 3 | 2020-07-07 | 2019-07-02 | 2014-03-12 | 14.06 | 0.5912 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.8 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.74 |  | 17.8 | 18.1 | 17.9 | 18.7 | 0.40311
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-3 | 25-PW-44028-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5696 |  | 2014-06-22 07:00 | 2014-06-22 08:00 | [36 empty] | 6.775 | CML-3 | CML: Elbow | 3 | 2025-01-18 | 2024-12-18 | 2014-06-22 07:00 | 2.5 | 0.33071 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 25 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 5.533 | 6 | 6.7 | 7.9 | 6.5 | 0.80571
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-19 | 50-DH-56137-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21103 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.275 | CML-19 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.6 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 7.4 | 6.3 | 5.8 | 5.6 | 0.80571
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71374-01K01 | CML-6 | 150-WF-71374-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5141 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 5.175 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 4.7 | 3 O'Clock | 150 | 3 | 150-WF-71374-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.7 | 4.7 | 5.2 | 5.1 | 0.4113
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71517-01F01 | CML-1 | 150-WF-71517-01F01 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 2122 |  | 2016-02-18 | 2016-02-18 | [36 empty] | 12.575 | CML-1 | CML: Elbow | 3 | 2098-02-09 |  | 2016-02-18 |  | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 11.7 | 6 O'Clock | 150 | 10.97 | 150-WF-71517-01F01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 12.7 | 13.3 | 11.7 | 12.6 | 0.66018
Marine | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71517-01F01 | CML-2 | 150-WF-71517-01F01 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 2123 |  | 2016-02-18 | 2016-02-18 | [36 empty] | 12.825 | CML-2 | CML: Fitting | 3 | 2098-02-09 |  | 2016-02-18 |  | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 12.5 | 6 O'Clock | 150 | 10.97 | 150-WF-71517-01F01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 12.8 | 12.8 | 12.5 | 13.2 | 0.28723
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 0400-WF-71L9001-AK11-00 | CML-4 | 0400-WF-71L9001-AK11-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22569 | Rope Access | 2015-04-24 07:00 | 2015-04-24 15:00 | [36 empty] | 5.2 | CML-4 | CML: Reducer | 0.5 | 2013-01-06 | 2017-01-28 | 2015-04-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.0938 | 5.1 | 12 O'Clock | 100 | 2.5 | 0400-WF-71L9001-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 5.2 | 5.2 | 0.08165
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67301-01E01 | CML-12 | 25-GN-67301-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22506 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.175 | CML-12 | CML: Elbow | 3 | 2019-03-21 | 2019-03-06 | 2015-04-20 07:00 | 2.5 | 0.66287 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.1 | 12 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.2 | 5.2 | 5.2 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-7 | 50-WC-40452-01C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10604 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 1.382mm/ yr | [35 empty] | 5.3 | CML-7 | CML: type TBC | 3 | 2015-08-12 | 2015-11-06 | 2013-11-17 | 2.5 | 1.3822 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 5.9 | 5.2 | 4.9 | 0.42426
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 40-WF-71361-01K01 | CML-1 | 40-WF-71361-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6634 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 5.175 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 5.1 | 9 O'Clock | 40 | 2.5 | 40-WF-71361-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 5.2 | 5.1 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-WC-40059-01C02 | CML-4 | 80-WC-40059-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3153 |  | 2014-05-02 11:30 | 2014-05-02 12:00 | Check Corrosion Rate of 0.642mm/ yr | [35 empty] | 5.3 | CML-4 | CML: Elbow | 3 | 2018-01-26 | 2018-08-12 | 2014-05-02 11:30 | 2.5 | 0.64192 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-WC-40059-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 5.2 | 4.9 | 5.7 | 0.33665
CG04 | Montara_Topside | Yes | Chemical Injection (42) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7492 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.9 | CML-3 | CML: type TBC | 1 | 2059-10-24 | 2046-01-28 | 2015-04-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 6.14 | 2.5 | 3.8737 | 7.2 | 3 O'Clock | 40 | 7.14 | 40-CI-42310-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8.9 | 7.2 | 7.3 | 8.2 | 0.80416
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-4 | 50-PL-23023-03C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10204 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.6 | CML-4 | CML: type TBC | 6 | 2016-01-17 | 2015-12-29 | 2013-11-08 | 2.5 | 2.3725 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.7 | 3 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.3 | 7.7 | 9.6 | 8.8 | 0.80416
CG03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-CG-38459-09C02-P | CML-7 | 80-CG-38459-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5850 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 15.4667 | CML-7 | CML: Equal Tee | 6 | 2075-10-24 | 2074-08-12 | 2014-06-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 14.7 | 3 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.2 |  | 15.4 | 14.7 | 16.3 |  | 0.80208
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-33 | 300-PG-20004-03C03-P CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 6156 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 9.55 | CML-33 | CML: Elbow | 6 | 2015-11-23 | 2015-04-15 | 2014-07-11 07:30 | 2.5 | 4.7458 | A2: Right Quadrant |  | 8.27 | 2.5 | 5.385 | 9 | 9 O'Clock | 50 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 10.7 | 9 | 9.5 | 9 | 0.80208
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71335-01K01 | CML-1 | 150-WF-71335-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6399 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 5.325 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 5.1 | 3 O'Clock | 150 | 3 | 150-WF-71335-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.1 | 5.3 | 5.5 | 0.17078
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-4 | 0200-DC-57L9006-AC21-00 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5044 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.685mm/ yr | [34 empty] | Low alarm breach | 5.175 | CML-4 | CML: type TBC | 3 | 2016-09-18 | 2016-01-29 | 2015-03-05 07:00 | 2.5 | 1.6854 | A2: Right Quadrant |  | 5.74 | 2.5 | 3.5737 | 5.1 | 9 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.1 | 5.2 | 5.1 | 0.095743
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-18 | 50-GN-67002-01E01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 9077 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.325 | CML-18 | CML: type TBC | 3 | 2025-06-28 | 2026-10-15 | 2015-03-01 09:30 | 2.5 | 0.25157 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.1 | 5.4 | 5.4 | 0.15
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-15 | 50-GN-67002-01E01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 9074 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.55 | CML-15 | CML: type TBC | 3 | 2025-06-28 | 2026-10-15 | 2015-03-01 09:30 | 2.5 | 0.25157 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.2 | 6.1 | 5.8 | 0.47958
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-28 | 50-AU-63015-01E01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 9059 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.525 | CML-28 | CML: type TBC | 3 | 2025-06-28 | 2026-10-14 | 2015-03-01 07:00 | 2.5 | 0.25161 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.2 | 5.7 | 6.1 | 0.46458
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-11 | 50-AI-63004-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 9002 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.2 | CML-11 | CML: type TBC | 3 | 2025-06-21 | 2026-10-06 | 2015-02-28 07:00 | 2.5 | 0.252 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.2 | 5.1 | 5.3 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-7 | 50-AI-63004-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8998 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.35 | CML-7 | CML: type TBC | 3 | 2025-06-21 | 2026-10-06 | 2015-02-28 07:00 | 2.5 | 0.252 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.2 | 5.2 | 5.9 | 0.36968
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-62 | 50-AI-63007-01E01 CML-62 |  | FPSO 2015 | Pipe Wall Thickness | 8986 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.35 | CML-62 | CML: type TBC | 3 | 2025-06-07 | 2026-09-21 | 2015-02-26 09:00 | 2.5 | 0.25276 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.4 | 5.4 | 5.5 | 0.17321
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-59 | 50-AI-63007-01E01 CML-59 |  | FPSO 2015 | Pipe Wall Thickness | 8983 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.25 | CML-59 | CML: type TBC | 3 | 2025-06-07 | 2026-09-21 | 2015-02-26 09:00 | 2.5 | 0.25276 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 5.4 | 5.2 | 0.1291
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-48 | 50-AI-63007-01E01 CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 8972 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.475 | CML-48 | CML: type TBC | 3 | 2025-06-07 | 2026-09-21 | 2015-02-26 09:00 | 2.5 | 0.25276 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.8 | 5.1 | 5.9 | 5.1 | 0.43493
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-36 | 50-AI-63007-01E01 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 8960 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.4 | CML-36 | CML: type TBC | 3 | 2025-06-07 | 2026-09-21 | 2015-02-26 09:00 | 2.5 | 0.25276 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.3 | 5.1 | 5.6 | 0.24495
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-28 | 50-AI-63007-01E01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 8952 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.275 | CML-28 | CML: type TBC | 3 | 2025-06-07 | 2026-09-21 | 2015-02-26 09:00 | 2.5 | 0.25276 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.4 | 5.1 | 5.3 | 0.12583
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-25 | 50-AI-63007-01E01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 8949 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.275 | CML-25 | CML: type TBC | 3 | 2025-06-07 | 2026-09-21 | 2015-02-26 09:00 | 2.5 | 0.25276 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.1 | 5.4 | 5.4 | 0.15
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-25 | 50-AU-63018-01E01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 8921 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.225 | CML-25 | CML: type TBC | 3 | 2025-06-02 | 2026-09-15 | 2015-02-25 13:00 | 2.5 | 0.2531 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 5.1 | 5.4 | 0.15
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-14 | 50-AU-63018-01E01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8910 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.225 | CML-14 | CML: type TBC | 3 | 2025-06-02 | 2026-09-15 | 2015-02-25 13:00 | 2.5 | 0.2531 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.3 | 5.1 | 5.2 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-13 | 50-AU-63018-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8909 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.2 | CML-13 | CML: type TBC | 3 | 2025-06-02 | 2026-09-15 | 2015-02-25 13:00 | 2.5 | 0.2531 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.2 | 5.1 | 5.2 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-12 | 50-AU-63018-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8908 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.15 | CML-12 | CML: type TBC | 3 | 2025-06-02 | 2026-09-15 | 2015-02-25 13:00 | 2.5 | 0.2531 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.1 | 5.2 | 5.2 | 0.057735
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-7 | 50-AU-63018-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8903 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.375 | CML-7 | CML: type TBC | 3 | 2025-06-02 | 2026-09-15 | 2015-02-25 13:00 | 2.5 | 0.2531 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.2 | 5.2 | 6 | 0.41932
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-18 | 50-AI-63005-01E01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8894 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.3 | CML-18 | CML: type TBC | 3 | 2025-06-01 | 2026-09-14 | 2015-02-25 09:30 | 2.5 | 0.25315 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.1 | 5.5 | 5.4 | 0.18257
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-12 | 50-AI-63005-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8888 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.5 | CML-12 | CML: type TBC | 3 | 2025-06-01 | 2026-09-14 | 2015-02-25 09:30 | 2.5 | 0.25315 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.3 | 5.4 | 5.2 | 5.1 | 0.54772
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63019-01E01 | CML-4 | 50-AU-63019-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8872 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 08:00 | 2015-02-25 09:00 | [36 empty] | 5.425 | CML-4 | CML: type TBC | 3 | 2025-05-31 | 2026-09-14 | 2015-02-25 08:00 | 2.5 | 0.25318 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-AU-63019-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.3 | 5.1 | 6.1 | 0.45735
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-2 | 80-SC-55002-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8832 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 5.875 | CML-2 | CML: type TBC | 3 | 2026-09-16 | 2028-04-03 | 2015-02-24 07:00 | 2.5 | 0.22478 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.5 | 5.9 | 5.1 | 6 | 0.57951
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67011-01E01 | CML-12 | 50-GN-67011-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8770 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.85 | CML-12 | CML: type TBC | 3 | 2025-03-24 | 2026-06-29 | 2015-02-15 09:30 | 2.5 | 0.25721 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.2 | 5.1 | 6 | 6.1 | 0.50662
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67011-01E01 | CML-6 | 50-GN-67011-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8764 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.225 | CML-6 | CML: type TBC | 3 | 2025-03-24 | 2026-06-29 | 2015-02-15 09:30 | 2.5 | 0.25721 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.2 | 5.1 | 5.5 | 0.1893
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-18 | 50-DH-56062-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 9105 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.625 | CML-18 | CML: type TBC | 3 | 2019-01-28 | 2019-09-07 | 2015-03-02 07:00 | 2.5 | 0.53669 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 6.4 | 5.4 | 6.1 | 4.6 | 0.80156
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63038-01E01 | CML-1 | 50-AI-63038-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8567 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.25 | CML-1 | CML: type TBC | 3 | 2025-01-06 | 2026-04-06 | 2015-02-04 07:30 | 2.5 | 0.26186 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-AI-63038-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.2 | 5.1 | 5.3 | 0.1291
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63020-01E01 | CML-2 | 50-AU-63020-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8482 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 5.95 | CML-2 | CML: type TBC | 3 | 2024-12-23 | 2026-03-21 | 2015-02-02 07:30 | 2.5 | 0.26271 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-AU-63020-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.1 | 6.3 | 5.1 | 6.3 | 0.57446
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-10 | 50-WD-53011-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8286 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.775 | CML-10 | CML: type TBC | 3 | 2024-11-05 | 2026-01-27 | 2015-01-26 07:30 | 2.5 | 0.26576 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 6.3 | 5.5 | 6.2 | 0.57373
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62005-01C02 | CML-3 | 50-DO-62005-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8056 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.45 | CML-3 | CML: type TBC | 3 | 2024-10-01 | 2025-12-20 | 2015-01-21 07:30 | 2.5 | 0.26797 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DO-62005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.5 | 5.1 | 5.9 | 0.34157
RP01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 15-CI-42001-T |  | 15-CI-42001-T |  | FPSO 2016 | Pipe Wall Thickness | 24276 |  | 2016-04-27 11:20 |  | Low WT | [35 empty] | 1.2 | 15-CI-42001-T | Piping |  |  |  | 2016-04-27 11:20 |  | 0 | A1: Outside Quadrant |  |  |  |  | 1.2 |  | 15 |  | Pipework | [7 empty] | 1.2 | 1.2 |  |  | 0
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-14 | 50-WC-40451-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 3076 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 0.695mm/ yr | [35 empty] | 5.4 | CML-14 | CML: Elbow | 3 | 2017-10-15 | 2018-04-05 | 2014-05-03 08:00 | 2.5 | 0.69455 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.41635 | 4.9 | 5.6 | 5.5 | 5.6 | 0.33665
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-11 | 50-CG-38470-01C02-P CML-11 | Yes | FPSO 2015 | Pipe Wall Thickness | 23617 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 3.975 | CML-11 | CML: Elbow | 3 | 2016-02-01 | 2016-05-16 | 2015-10-28 07:00 | 2.5 | 1.1374 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 2.8 | 6 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.3 |  | 4.3 | 4.2 | 2.8 | 4.6 | 0.80156
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-27 | 300-FL-43070-01C02 CML-27 | yes | FPSO 2014 | Pipe Wall Thickness | 12720 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.025 | CML-27 | CML: type TBC | 3 | 2015-05-01 | 2015-04-26 | 2014-02-01 09:00 | 2.5 | 2.0082 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 12 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 6.5 | 6.8 | 5.8 | 0.80156
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-17 | 300-FL-43070-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12710 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 11.5 | CML-17 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.7 | 12 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.7 | 11.5 | 12.3 |  | 0.8
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-1 | 300-PG-20049-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21487 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | [36 empty] | 14.875 | CML-1 | CML: Elbow | 6 | 2050-09-14 | 2043-12-31 | 2014-06-28 10:45 | 4.9 | 0.25112 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 9 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 14.4 | 15.5 | 15.6 | 14 | 0.79739
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-7 | 50-WC-40071-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7720 |  | 2015-01-09 13:00 | 2015-01-09 15:00 |  |  | Administrator | 2015-09-08 09:33 | [32 empty] | 5.3 | CML-7 | CML: Pipe Length | 3 | 2024-07-12 | 2025-09-21 | 2015-01-09 13:00 | 2.5 | 0.27334 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.7574 | 5.1 | 5.4 | 5.5 | 5.2 | 0.18257
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-2 | 50-WC-40071-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7715 | Line is FFS. It has been check twice. The higher values reported here are from the latest data collected in Jan. 2015. Action: to recheck in two year (Jan. 2017) to confirm CR. | 2015-01-09 13:00 | 2015-01-09 15:00 |  |  | Administrator | 2015-09-08 09:32 | [32 empty] | 5.45 | CML-2 | CML: Pipe Length | 3 | 2024-07-12 | 2025-09-21 | 2015-01-09 13:00 | 2.5 | 0.27334 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.3787 | 5.7 | 5.6 | 5.4 | 5.1 | 0.26458
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20068-01C02-P | CML-3 | 100-PL-20068-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21551 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.025 | CML-3 | CML: Elbow | 3 | 2022-11-08 | 2023-03-02 | 2014-07-17 07:30 | 2.5 | 0.37271 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-PL-20068-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.4 | 6.2 | 5.9 | 5.6 | 0.35
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56106-01C02 | CML-6 | 80-DH-56106-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2032 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 11.35 | CML-6 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-27 14:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 10.5 | 6 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 12.4 | 11.1 | 10.5 | 11.4 | 0.79373
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-5 | 200-PW-44019-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23033 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 5.225 | CML-5 | CML: Elbow | 3 | 2018-03-16 | 2018-03-03 | 2015-05-06 07:00 | 2.5 | 0.80329 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.8 | 6 O'Clock | 20 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.22749 | 5.5 | 5.4 | 4.8 | 5.2 | 0.30957
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23034-01C03 | CML-3 | 50-PL-23034-01C03 CML-3 | no | FPSO 2014 | Pipe Wall Thickness | 20571 | Reviewed on 26/11/14.FFS. Repeat Oct.19 | 2014-10-12 07:00 | 2014-10-12 12:00 |  |  | Nestor | 2014-11-26 16:19 | [32 empty] | 8.65 | CML-3 | CML: Elbow | 6 | 2023-07-20 | 2023-05-10 | 2014-10-12 07:00 | 2.5 | 0.6153 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 3 O'Clock | 50 | 8.74 | 50-PL-23034-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.1 | 7.9 | 9 | 9.6 | 0.79373
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56139-01C02 | CML-3 | 50-DH-56139-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21066 | Rope Access | 2014-05-15 11:00 | 2014-05-15 12:00 | [36 empty] | 6.65 | CML-3 | CML: type TBC | 3 | 2085-12-02 | 2093-09-13 | 2014-05-15 11:00 | 2.5 | 0.0419 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DH-56139-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 7.3 | 7 | 6.8 | 5.5 | 0.79373
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-4 | 50-PW-44013-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5728 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 5.15 | CML-4 | CML: Elbow | 3 | 2017-10-05 | 2018-03-25 | 2014-06-22 13:00 | 2.5 | 0.69876 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 1.6255 | 5 | 5.4 | 4.8 | 5.4 | 0.3
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-5 | 200-PG-23505-09C02-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2686 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.075 | CML-5 | CML: Pipe Length | 3 | 2022-07-01 | 2021-03-14 | 2014-03-12 09:00 | 14.06 | 0.46207 | A4: Left Quadrant |  | 15.26 | 14.06 | 14.66 | 17.9 | 9 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.84 | 0 | 18 | 18.4 | 18 | 17.9 | 0.22174
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-5 | 200-PG-23505-09C02-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 375 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 18.075 | CML-5 | CML: Pipe Length | 3 | 2022-06-27 | 2021-03-11 | 2014-03-12 | 14.06 | 0.46268 | A4: Left Quadrant |  | 15.26 | 14.06 | 14.66 | 17.9 | 9 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.84 |  | 18 | 18.4 | 18 | 17.9 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40062-01C02 | CML-8 | 100-WC-40062-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 832 |  | 2014-04-02 08:00 | 2014-04-02 09:00 | Check Corrosion Rate of 1.339mm/ yr | [35 empty] | 5.25 | CML-8 | CML: Elbow | 3 | 2016-01-16 | 2016-02-17 | 2014-04-02 08:00 | 2.5 | 1.3389 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 6 O'Clock | 100 | 6.02 | 100-WC-40062-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.3 | 5.4 | 4.9 | 5.4 | 0.23805
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56057-01C02 | CML-1 | 50-DH-56057-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3169 | Rope Access | 2014-05-07 08:00 | 2014-05-07 09:00 | [36 empty] | 8.225 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56057-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.7 | 8.8 | 9 | 0.7932
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-1 | 50-DH-56056-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20121 | Rope Access | 2014-05-07 08:00 | 2014-05-07 09:00 | [36 empty] | 8.225 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | -23652.0197 | 7.4 | 7.7 | 8.8 | 9 | 0.7932
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-30 | 400-FH-43508-01C02 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 6579 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.675 | CML-30 | CML: Elbow | 3 | 2021-07-13 | 2020-06-17 | 2015-03-30 07:00 | 2.5 | 0.66732 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 6.7 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 8.5 | 8.1 | 7.4 | 6.7 | 0.7932
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-1 | 200-FH-43003-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12524 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.775 | CML-1 | CML: Pipe Length | 3 | 2022-06-27 | 2021-05-21 | 2014-01-18 11:30 | 1.34 | 0.55189 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 6 | 9 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 7.3 | 6.2 | 7.6 | 6 | 0.7932
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-19 | 300-PF-20001-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21157 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 14.65 | CML-19 | CML: Fitting | 6 | 2052-05-26 | 2045-05-22 | 2014-07-16 07:30 | 4.9 | 0.24018 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 6 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 14 | 15.6 | 14 | 15 | 0.78951
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1397 | Rope access | 2014-04-05 14:00 | 2014-04-05 15:00 | [36 empty] | 6.575 | CML-4 | CML: type TBC | 3 | 2031-10-05 | 2033-09-23 | 2014-04-05 14:00 | 2.5 | 0.1656 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.9 | 7.1 | 5.4 | 6.9 | 0.78899
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-56 | 300-PF-20001-03C03-P CML-56 |  | FPSO 2014 | Pipe Wall Thickness | 21194 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.534mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:51 | [32 empty] | 13.225 | CML-56 | CML: Pipe Length | 6 | 2018-09-05 | 2017-08-07 | 2014-07-16 07:30 | 4.1 | 1.9304 | A4: Left Quadrant |  | 8.27 | 4.1 | 6.185 | 12.1 | 9 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 13.3 | 13.9 | 13.6 | 12.1 | 0.78899
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-21 | 50-CG-38001-09C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 10935 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.775 | CML-21 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.7176 | A3: Inside Quadrant |  | 5.74 |  |  | 7.7 | 6 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.7 | 8.7 | 9.2 | 7.7 | 9.5 | 0.78899
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-2 | 150-PG-23506-25C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2776 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.4 | CML-2 | CML: Pipe Length | 3 | 2022-02-05 | 2019-11-26 | 2014-03-15 09:00 | 15.88 | 0.69856 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.4 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.52 |  | 23.3 | 22.3 | 21.4 | 22.6 | 0.7874
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-12 | 150-PG-23506-25C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2786 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.6 | CML-12 | CML: Pipe Length | 3 | 2032-07-08 | 2027-09-08 | 2014-03-15 09:00 | 15.88 | 0.31753 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.7 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.82 |  | 21.7 | 23.6 | 22.7 | 22.4 | 0.7874
PL03 | Montara_Topside | Yes | Wellstream (57) | Pipework | 50-PL-57066-01C03 | CML-4 | 50-PL-57066-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22110 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 9.3 | CML-4 | CML: type TBC | 6 | 2038-10-03 | 2038-04-08 | 2014-10-18 07:00 | 2.5 | 0.24609 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-PF-57066-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.4 | 10.3 | 9.1 | 0.7874
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-2 | 50-WC-40452-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10599 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 1.382mm/ yr | [35 empty] | 5.1 | CML-2 | CML: type TBC | 3 | 2015-08-12 | 2015-11-06 | 2013-11-17 | 2.5 | 1.3822 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 5.3 | 4.9 | 0.23094
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-4 | 300-PF-20001-03C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23484 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 13.9 | CML-4 | CML: Pipe Length | 6 | 2028-02-20 | 2025-06-28 | 2015-07-27 07:00 | 4.9 | 0.63596 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.9 | 3 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | 0.38832 | 14.8 | 12.9 | 13.8 | 14.1 | 0.7874
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-45 | 300-PF-20001-03C03-P CML-45 |  | FPSO 2016 | Pipe Wall Thickness | 24486 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 15 | CML-45 | CML: Elbow | 6 | 2184-08-02 | 2153-10-21 | 2016-07-09 07:00 | 4.9 | 0.0547 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 | 0.20977 | 15.1 | 16 | 14.8 | 14.1 | 0.7874
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-3 | 50-PW-44014-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23148 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.075 | CML-3 | CML: Elbow | 3 | 2021-05-19 | 2022-03-28 | 2015-05-10 07:00 | 2.5 | 0.38134 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.17854 | 5.4 | 4.8 | 5 | 5.1 | 0.25
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-9 | 50-PW-44013-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22728 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.125 | CML-9 | CML: Elbow | 3 | 2021-03-31 | 2022-02-01 | 2015-04-28 07:00 | 2.5 | 0.38791 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | -0.35351 | 4.8 | 5.3 | 5.1 | 5.3 | 0.23629
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-5 | 50-WC-40452-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10602 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 1.382mm/ yr | [35 empty] | 5.025 | CML-5 | CML: type TBC | 3 | 2015-08-12 | 2015-11-06 | 2013-11-17 | 2.5 | 1.3822 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 4.9 | 5.2 | 5.1 | 0.15
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-1 | 50-CG-38487-09C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23570 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 9.05 | CML-1 | CML: Elbow | 3 | 2055-03-09 | 2044-05-04 | 2015-09-10 07:00 | 2.5 | 0.14929 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 0.31924 | 8.4 | 8.5 | 9.2 | 10.1 | 0.78528
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-40 | 150-PG-23506-25C02 CML-40 |  | FPSO 2014 | Pipe Wall Thickness | 20093 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.55 | CML-40 | CML: Pipe Length | 3 | 2018-03-26 | 2017-01-05 | 2014-05-29 07:00 | 15.88 | 1.2593 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.7 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.82 | 109.5004 | 20.7 | 21.1 | 22 | 22.4 | 0.78528
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20508-03C03-P | CML-3 | 300-PF-20508-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6512 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 17.65 | CML-3 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-24 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 17 | 3 O'Clock | 300 | 14.27 | 300-PF-20508-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.1 |  | 17.1 | 17 | 17.8 | 18.7 | 0.78528
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56028-01C02 | CML-2 | 80-DH-56028-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20899 | Rope Access | 2014-05-22 07:00 | 2014-05-22 08:00 | [36 empty] | 5.65 | CML-2 | CML: Elbow | 3 | 2017-08-18 | 2018-02-13 | 2014-05-22 07:00 | 2.5 | 0.70885 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 9 O'Clock | 80 | 5.49 | 80-DH-56028-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 6.1 | 6.5 | 4.8 | 0.78528
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-5 | 50-PW-44012-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23164 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.1 | CML-5 | CML: Elbow | 3 | 2021-05-23 | 2022-04-01 | 2015-05-11 07:00 | 2.5 | 0.3808 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.44524 | 5.1 | 5.3 | 4.8 | 5.2 | 0.21602
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20057-01C02-P | CML-5 | 100-PW-20057-01C02-P CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 22818 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.375 | CML-5 | CML: Elbow | 3 | 2018-12-06 | 2019-02-11 | 2015-04-30 07:00 | 2.5 | 0.6377 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 9 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 2.9495 | 5.8 | 5.5 | 5.4 | 4.8 | 0.41932
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-18 | 50-WC-40451-01C02 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10158 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 1.451mm/ yr | [35 empty] | 5 | CML-18 | CML: Pipe Length | 3 | 2015-07-05 | 2015-09-25 | 2013-11-09 | 2.5 | 1.4509 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 |  | 5.1 | 0.1
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-3 | 200-PG-23006-09C02-PA CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 23836 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 20.475 | CML-3 | CML: Elbow | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A4: Left Quadrant |  | 15.26 | 9.3 | 12.28 | 19.3 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 20.8 | 20.9 | 20.9 | 19.3 | 0.78475
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-5 | 80-FL-43015-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20410 | Reviewed on 20/11/14. Line is FFS. Repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-20 11:26 | [32 empty] | 6.2 | CML-5 | CML: Elbow | 3 | 2027-04-24 | 2028-12-05 | 2014-10-06 07:00 | 2.5 | 0.21501 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6 | 6.6 | 7 | 0.78316
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43035-01C02 | CML-4 | 100-FH-43035-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12663 |  | 2014-01-22 10:00 | 2014-01-22 11:00 | [36 empty] | 20.9 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-01-22 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 20 | 3 O'Clock | 100 | 6.02 | 100-FH-43035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.5 |  | 21.4 | 20 | 21.3 |  | 0.78102
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-2 | 50-PW-44012-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23161 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.1 | CML-2 | CML: Pipe Length | 3 | 2021-05-23 | 2022-04-01 | 2015-05-11 07:00 | 2.5 | 0.3808 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.53428 | 5.1 | 5.2 | 4.8 | 5.3 | 0.21602
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-6 | 50-PW-44015-01X01 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10289 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.05 | CML-6 | CML: Elbow | 3 | 2015-03-28 | 2015-06-07 | 2013-11-10 | 2.5 | 1.6673 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5 | 5.1 | 5.3 | 0.20817
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-7 | 25-FG-45455-01C02-E CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1687 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 6.675 | CML-7 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 7.8 | 6 | 6.5 | 0.78049
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-11 | 100-DH-56561-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 7943 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 10.125 | CML-11 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-17 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9 | 12 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 10.4 | 10.8 | 10.3 | 0.78049
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20965 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 8.325 | CML-6 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 12 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 8.9 | 8.8 | 8.4 | 0.78049
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-4 | 80-PL-44008-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5741 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 6.325 | CML-4 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 6.2 | 7.6 | 0.87702
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-3 | 150-PG-23506-25C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2777 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 23.875 | CML-3 | CML: Elbow | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 23.3 | 12 O'Clock | 50 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.42 |  | 23.3 | 23.4 | 23.8 | 25 | 0.78049
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23047-09C02-P | CML-1 | 150-PG-23047-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 24257 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 16.125 | CML-1 | CML: Elbow | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A3: Inside Quadrant |  | 11.27 | 7 | 9.135 | 15 | 6 O'Clock | 150 | 14.27 | 150-PG-23047-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 16.2 | 16.6 | 15 | 16.7 | 0.78049
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20504-03C03-P | CML-3 | 50-PF-20504-03C03-P CML-3 | Yes | FPSO 2015 | Pipe Wall Thickness | 7748 |  | 2015-01-10 13:00 | 2015-01-10 16:00 | [36 empty] | 8.025 | CML-3 | CML: Elbow | 6 | 2018-11-17 | 2018-10-10 | 2015-01-10 13:00 | 2.5 | 1.1411 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 6.9 | 12 O'Clock | 50 | 8.74 | 50-PF-20504-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 8.2 | 8.7 | 8.3 | 0.78049
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-6 | 50-PF-20300-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21572 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.625 | CML-6 | CML: type TBC | 6 | 2038-12-31 | 2038-07-04 | 2014-05-26 09:30 | 2.5 | 0.24374 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 6 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10.1 | 9.7 | 8.5 | 10.2 | 0.78049
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-15 | 100-WC-40516-1CG CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8688 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:56 | [32 empty] | 8.325 | CML-15 | CML: Pipe Length | 3 | 2053-02-15 | 2043-02-06 | 2015-02-13 07:00 | 2.5 | 0.1525 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.3 | 9 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.3 | 8.4 | 8.3 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40022-01C02 | CML-19 | 400-WC-40022-01C02 CML-19 | yes | FPSO 2014 | Pipe Wall Thickness | 1113 | Rope Access | 2014-03-21 09:30 | 2014-03-21 11:30 | Check Corrosion Rate of 3.508mm/ yr | [35 empty] | 6.725 | CML-19 | CML: type TBC | 3 | 2014-12-06 | 2014-09-28 | 2014-03-21 09:30 | 2.6 | 3.5082 | A1: Outside Quadrant |  | 4.92 | 2.6 | 3.265 | 5.1 | 12 O'Clock | 400 | 7.92 | 400-WC-40022-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 7.4 | 7 | 7.4 | 1.0996
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-10 | 50-PW-44013-01X01 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10324 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.925 | CML-10 | CML: Reducer | 3 | 2015-03-28 | 2015-06-07 | 2013-11-10 | 2.5 | 1.6673 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.8 | 5.2 | 4.9 | 0.1893
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-5 | 50-PW-44009-01C03-P CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 5816 | Protective mesh removed | 2014-06-24 07:00 | 2014-06-24 08:00 | [36 empty] | 9.05 | CML-5 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2014-06-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.3 | 6 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 10.3 | 8.6 | 8.3 | 9 | 0.88129
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-1 | 50-CG-38488-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20819 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 10.4 | CML-1 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9.5 | 9 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 11.4 | 10.4 | 10.3 | 9.5 | 0.77889
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-3 | 50-PW-44015-01X01 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10286 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.05 | CML-3 | CML: Elbow | 3 | 2015-03-28 | 2015-06-07 | 2013-11-10 | 2.5 | 1.6673 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 5.1 | 5.1 | 4.8 | 0.17321
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-11 | 300-PF-20003-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21749 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.15 | CML-11 | CML: Fitting | 6 | 2032-01-27 | 2028-09-19 | 2014-10-01 07:00 | 4.9 | 0.50186 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 13.8 | 15.3 | 13.9 | 13.6 | 0.77675
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56024-01C02 | CML-2 | 80-DH-56024-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3489 | Rope Access | 2014-05-14 13:00 | 2014-05-14 14:00 | [36 empty] | 7.45 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-14 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.5 | 9 O'Clock | 80 | 5.49 | 80-DH-56024-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.5 | 7.4 | 8.4 | 6.5 | 0.77675
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-9 | 50-PG-44022-01C03-P CML-9 | Yes | FPSO 2015 | Pipe Wall Thickness | 22984 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 8.95 | CML-9 | CML: Elbow | 6 | 2029-08-18 | 2029-04-26 | 2015-05-04 07:00 | 2.5 | 0.3846 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 12 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 | 0.46645 | 8 | 9 | 9.9 | 8.9 | 0.77675
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-15 | 50-PL-23020-01C03 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10129 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.15 | CML-15 | CML: type TBC | 6 | 2018-06-23 | 2018-05-19 | 2013-11-08 | 2.5 | 1.2319 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 9 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 10.1 | 9.2 | 9.1 | 8.2 | 0.77675
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-1 | 200-PG-23505-09C02-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2682 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.725 | CML-1 | CML: Pipe Length | 3 | 2033-11-07 | 2030-12-07 | 2014-03-12 09:00 | 14.06 | 0.20536 | A4: Left Quadrant |  | 15.26 | 14.06 | 14.66 | 18.1 | 9 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.04 | 0 | 19.1 | 19.3 | 18.4 | 18.1 | 0.56789
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-1 | 200-PG-23505-09C02-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 371 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 18.725 | CML-1 | CML: Pipe Length | 3 | 2033-10-29 | 2030-11-29 | 2014-03-12 | 14.06 | 0.20563 | A4: Left Quadrant |  | 15.26 | 14.06 | 14.66 | 18.1 | 9 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.04 |  | 19.1 | 19.3 | 18.4 | 18.1 | 0.56789
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-3 | 50-PW-44013-01X01 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10317 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.975 | CML-3 | CML: Elbow | 3 | 2015-03-28 | 2015-06-07 | 2013-11-10 | 2.5 | 1.6673 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 4.8 | 5 | 4.9 | 0.17078
FH01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FH-43141-01C02 | CML-4 | 150-FH-43141-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 23695 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.425 | CML-4 | CML: Elbow | 3 | 2016-11-03 | 2017-03-18 | 2015-10-30 07:00 | 2.5 | 0.88631 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.4 | 3 O'Clock | 50 | 5.54 | 50-CG-38456-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 4.8 | 3.4 | 4.3 | 5.2 | 0.77621
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-10 | 50-WC-40451-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 3072 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 0.586mm/ yr | [35 empty] | 5.375 | CML-10 | CML: Fitting | 3 | 2018-08-07 | 2019-02-26 | 2014-05-03 08:00 | 2.5 | 0.58603 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0 | 5.1 | 5.7 | 5.7 | 5 | 0.37749
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-6 | 200-PG-24001-09C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10262 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 18.175 | CML-6 | CML: Pipe Length | 3 | 2017-03-08 | 2015-12-03 | 2013-11-09 | 9.2 | 2.4031 | A1: Outside Quadrant |  | 15.26 | 9.2 | 12.23 | 17.2 | 12 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 17.2 | 17.9 | 18.8 | 18.8 | 0.77621
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-14 | 250-PW-20022-01C03-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23112 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.1 | CML-14 | CML: Pipe Length | 6 | 2030-06-19 | 2029-06-30 | 2015-05-10 07:00 | 2.5 | 0.3968 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.5 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 1.6998 | 9.4 | 8.8 | 9.7 | 8.5 | 0.54772
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-12 | 250-PW-20022-01C03-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23110 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.2 | CML-12 | CML: Pipe Length | 6 | 2030-06-19 | 2029-06-30 | 2015-05-10 07:00 | 2.5 | 0.3968 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.5 | 6 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 1.0735 | 9.2 | 9.7 | 8.5 | 9.4 | 0.5099
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56118-01C02 | CML-1 | 50-DH-56118-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21020 | Rope Access | 2014-05-19 11:00 | 2014-05-19 12:00 | [36 empty] | 5.65 | CML-1 | CML: type TBC | 3 | 2017-05-18 | 2017-10-21 | 2014-05-19 11:00 | 2.5 | 0.76633 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 6.4 | 6.2 | 4.8 | 0.77244
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38486-09C02-P | CML-1 | 80-CG-38486-09C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8627 | Rope Access / Material Class Not Selectable. Line is FFS. Only one CM-3 is showing high CR. Current RBI frequency is 48m Action: NIL. RBI to stay at 48m | 2015-02-10 08:00 | 2015-02-10 09:00 |  |  | Administrator | 2015-09-08 10:30 | [32 empty] | 15.95 | CML-1 | CML: Pipe Length | 3 | 2139-04-24 | 2091-05-12 | 2015-02-10 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 12.09 | 2.5 | 7.295 | 15.5 | 9 O'Clock | 250 | 15.09 | 250-WC-40505-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13 |  | 17.1 | 15.5 | 15.7 | 15.5 | 0.77244
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-12 | 50-PW-44012-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23171 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.025 | CML-12 | CML: Elbow | 3 | 2021-05-23 | 2022-04-01 | 2015-05-11 07:00 | 2.5 | 0.3808 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.97952 | 5 | 5.1 | 4.8 | 5.2 | 0.17078
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-17 | 300-PG-20005-03C03-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23361 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.05 | CML-17 | CML: Reducing Tee | 6 | 2034-01-09 | 2030-04-27 | 2015-07-20 07:00 | 4.9 | 0.45432 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | 1.7805 | 15.1 | 13.3 | 13.7 | 14.1 | 0.77244
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56053-01C02 | CML-2 | 80-DH-56053-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20941 | Rope Access | 2014-05-21 14:00 | 2014-05-21 15:00 | [36 empty] | 5.65 | CML-2 | CML: Elbow | 3 | 2018-05-02 | 2018-11-28 | 2014-05-21 14:00 | 2.5 | 0.60733 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-DH-56053-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.1 | 6.1 | 6.5 | 0.77244
DH01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-DH-56004-01C02 | CML-2 | 80-DH-56004-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 23693 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.075 | CML-2 | CML: Elbow | 3 | 2016-09-09 | 2017-01-15 | 2015-10-30 07:00 | 2.5 | 0.92773 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.3 | 3 O'Clock | 50 | 5.54 | 50-CG-38456-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4.4 | 3.3 | 3.6 | 5 | 0.7719
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-15 | 300-PF-20003-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21753 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 9.325 | CML-15 | CML: Elbow | 6 | 2016-03-08 | 2015-07-04 | 2014-10-01 07:00 | 2.5 | 4.247 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.6 | 9 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 10.4 | 9.3 | 9 | 8.6 | 0.7719
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-7 | 50-PW-44015-01X01 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10290 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 4.975 | CML-7 | CML: Elbow | 3 | 2015-03-28 | 2015-06-07 | 2013-11-10 | 2.5 | 1.6673 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 5.1 | 4.8 | 5 | 0.12583
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-13 | 250-FH-43303-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12951 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.925 | CML-13 | CML: type TBC | 3 | 2030-04-23 | 2030-03-09 | 2014-01-27 10:00 | 2.5 | 0.22773 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 8 | 6.2 | 6.6 | 6.9 | 0.7719
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-10 | 250-PG-20036-01C03-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23398 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 8.425 | CML-10 | CML: Elbow | 6 | 2022-08-17 | 2022-02-07 | 2015-07-21 07:00 | 2.5 | 0.7344 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.7 | 12 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 | 0.19625 | 7.7 | 9.5 | 8.1 | 8.4 | 0.7719
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23037-25C02-A | CML-12 | 150-PG-23037-25C02-A CML-12 | Yes | FPSO 2014 | Pipe Wall Thickness | 13102 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 20.675 | CML-12 | CML: Pipe Length | 3 | 2015-07-15 | 2014-12-31 | 2014-01-10 09:00 | 15.88 | 2.8595 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.2 | 6 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.32 |  | 21 | 20.2 | 20.2 | 21.3 | 0.56199
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-6 | 200-FH-43025-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2479 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 10.075 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 10.4 | 9.6 | 11 | 9.3 | 0.7719
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-WC-40059-01C02 | CML-3 | 80-WC-40059-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3152 |  | 2014-05-02 11:30 | 2014-05-02 12:00 | Check Corrosion Rate of 0.533mm/ yr | [35 empty] | 5.35 | CML-3 | CML: Elbow | 3 | 2019-01-08 | 2019-09-03 | 2014-05-02 11:30 | 2.5 | 0.53312 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-WC-40059-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.7 | 5.4 | 5.3 | 0.28868
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-5 | 200-PW-44018-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5582 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 5.875 | CML-5 | CML: Fitting | 3 | 2016-03-15 | 2016-03-07 | 2014-06-19 10:30 | 2.5 | 1.3803 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.9 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0 | 6.4 | 5.6 | 4.9 | 6.6 | 0.78049
FG02 | Montara_Topside | Yes | Potable Water (53) | Pipework | 25-FG-45455-01C02-E | CML-12 | 25-FG-45455-01C02-E CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8255 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 7 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 7.5 | 7.7 | 6.8 | 0.77028
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1154 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.7 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | -4.1814 | 6.5 | 6 | 7.8 | 6.5 | 0.77028
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23017-03C03-A | CML-1 | 250-PG-23017-03C03-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10975 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 12.3 | CML-1 | CML: Pipe Length | 6 | 2017-08-14 | 2017-01-13 | 2014-01-09 | 4.4 | 1.973 | A3: Inside Quadrant |  | 6.7 | 4.4 | 5.55 | 11.5 | 6 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 12.8 | 13.1 | 11.5 | 11.8 | 0.77028
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-5 | 100-DC-57036-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1411 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 1.082mm/ yr | [35 empty] | 5.25 | CML-5 | CML: type TBC | 3 | 2016-08-31 | 2016-10-09 | 2014-04-07 07:00 | 2.5 | 1.0822 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 3 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.1 | 5.3 | 5.3 | 0.1
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57014-01C02 | CML-5 | 50-DC-57014-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1366 | Rope access | 2014-04-04 13:00 | 2014-04-04 15:00 | Check Corrosion Rate of 0.522mm/ yr | [35 empty] | 5.425 | CML-5 | CML: type TBC | 3 | 2019-03-26 | 2019-11-09 | 2014-04-04 13:00 | 2.5 | 0.52221 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DC-57014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.5 | 5.1 | 5.4 | 5.7 | 0.25
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57067-01C02 | CML-4 | 50-DC-57067-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1341 | Rope access | 2014-04-04 08:00 | 2014-04-04 09:00 | Check Corrosion Rate of 0.523mm/ yr | [35 empty] | 5.425 | CML-4 | CML: type TBC | 3 | 2019-03-25 | 2019-11-08 | 2014-04-04 08:00 | 2.5 | 0.52256 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DC-57067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.5 | 5.1 | 5.7 | 0.25
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57068-01C02 | CML-5 | 50-DC-57068-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1333 | Rope access | 2014-04-04 07:00 | 2014-04-04 08:00 | Check Corrosion Rate of 0.523mm/ yr | [35 empty] | 5.35 | CML-5 | CML: type TBC | 3 | 2019-03-25 | 2019-11-07 | 2014-04-04 07:00 | 2.5 | 0.52263 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DC-57068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.7 | 5.1 | 5.2 | 0.26458
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57068-01C02 | CML-3 | 50-DC-57068-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1331 | Rope access | 2014-04-04 07:00 | 2014-04-04 08:00 | Check Corrosion Rate of 0.523mm/ yr | [35 empty] | 6.1 | CML-3 | CML: type TBC | 3 | 2019-03-25 | 2019-11-07 | 2014-04-04 07:00 | 2.5 | 0.52263 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DC-57068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.1 | 5.3 | 8.8 | 1.8019
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-3 | 50-DN-56101-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 843 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.7 | CML-3 | CML: Elbow | 3 | 2019-03-13 | 2019-10-25 | 2014-04-02 14:00 | 2.5 | 0.52555 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.1 | 6.3 | 5.7 | 0.4899
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-15 | 80-PL-44008-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 5752 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 6.15 | CML-15 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.2 | 6.9 | 5.8 | 0.54467
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-3 | 300-PG-20048-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21473 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | Check Corrosion Rate of 0.344mm/ yr | 38 | Kirstie Albone | 2017-03-23 12:55 | [32 empty] | 14.475 | CML-3 | CML: Fitting | 6 | 2040-08-15 | 2035-09-24 | 2014-06-28 09:30 | 4.9 | 0.34417 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 9 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.1 | 14.3 | 15.6 | 13.9 | 0.76757
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-5 | 200-PW-44018-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21891 |  | 2014-06-19 10:30 | 2014-06-19 11:30 | [36 empty] | 5.875 | CML-5 | CML: Fitting | 3 | 2016-03-15 | 2016-03-07 | 2014-06-19 10:30 | 2.5 | 1.3803 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.9 | 6 O'Clock | 200 | 6.35 | 200-PW-44018-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 6.4 | 5.6 | 4.9 | 6.6 | 0.78049
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43079-01C02 | CML-3 | 50-FL-43079-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3046 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 6.125 | CML-3 | CML: type TBC | 3 | 2025-01-28 | 2026-04-30 | 2014-05-03 07:00 | 2.5 | 0.26049 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.8 | 7.1 | 6.3 | 0.76757
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-22 | 250-PG-23003-06C02-PA CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 3238 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6 | CML-22 | CML: type TBC | 3 | 2033-10-06 | 2035-12-13 | 2014-05-09 07:00 | 2.5 | 0.14929 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.2 | 7 | 5.4 | 0.76594
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56133-01C02 | CML-5 | 50-DN-56133-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1322 |  | 2014-03-31 10:15 | 2014-03-31 10:30 | [36 empty] | 5.35 | CML-5 | CML: type TBC | 3 | 2019-02-26 | 2019-10-09 | 2014-03-31 10:15 | 2.5 | 0.52929 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-DN-56133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 5.7 | 5.3 | 0.25166
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56133-01C02 | CML-2 | 50-DN-56133-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1319 |  | 2014-03-31 10:15 | 2014-03-31 10:30 | [36 empty] | 5.375 | CML-2 | CML: type TBC | 3 | 2019-02-26 | 2019-10-09 | 2014-03-31 10:15 | 2.5 | 0.52929 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DN-56133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.3 | 5.4 | 5.1 | 0.25
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56095-01C02 | CML-1 | 50-DN-56095-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1307 |  | 2014-03-31 08:00 | 2014-03-31 09:00 | [36 empty] | 5.35 | CML-1 | CML: type TBC | 3 | 2019-02-25 | 2019-10-08 | 2014-03-31 08:00 | 2.5 | 0.52945 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DN-56095-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.6 | 5.1 | 5.6 | 0.28868
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-5 | 50-DC-57043-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2150 | Rope Access | 2014-03-29 13:00 | 2014-03-29 15:00 | Check Corrosion Rate of 0.533mm/ yr | [35 empty] | 5.5333 | CML-5 | CML: Equal Tee | 3 | 2019-02-13 | 2019-09-24 | 2014-03-29 13:00 | 2.5 | 0.5326 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  |  | 5.4 | 6.1 | 5.1 | 0.51316
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-10 | 50-PW-44015-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5720 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 5.425 | CML-10 | CML: Elbow | 3 | 2018-06-10 | 2018-12-24 | 2014-06-22 10:00 | 2.5 | 0.60453 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.48793 | 5.6 | 5.8 | 4.9 | 5.4 | 0.38622
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-5 | 50-FH-43137-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12857 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 8.1667 | CML-5 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-01-23 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 6 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8 | 9 | 7.5 |  | 0.76376
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-25 | 300-PF-20001-03C03-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 21163 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.625 | CML-25 | CML: Elbow | 6 | 2015-09-30 | 2015-03-05 | 2014-07-16 07:30 | 2.5 | 5.0438 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.6 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 10.1 | 9.5 | 10.3 | 8.6 | 0.76322
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-5 | 100-WC-40027-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23425 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 |  |  | Nestor | 2016-04-01 | [32 empty] | 5.4 | CML-5 | CML: Elbow | 3 | 2020-10-21 | 2021-01-18 | 2015-07-23 07:00 | 2.5 | 0.47591 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 6 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.15307 | 5.5 | 5.5 | 5 | 5.6 | 0.2708
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40062-01C02 | CML-1 | 100-WC-40062-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 825 |  | 2014-04-02 08:00 | 2014-04-02 09:00 | Check Corrosion Rate of 1.219mm/ yr |  | Dearne Gaebler | 2016-04-05 11:42 | Test Reviewed comment | [31 empty] | 5.35 | CML-1 | CML: Elbow | 3 | 2016-04-19 | 2016-05-24 | 2014-04-02 08:00 | 2.5 | 1.2193 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 3 O'Clock | 100 | 6.02 | 100-WC-40062-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.6 | 5 | 5.5 | 5.3 | 0.26458
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-12 | 50-PF-20300-03C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21578 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.425 | CML-12 | CML: type TBC | 6 | 2038-12-31 | 2038-07-04 | 2014-05-26 09:30 | 2.5 | 0.24374 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10.1 | 10 | 9.1 | 8.5 | 0.76322
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-7 | 50-PW-44015-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5717 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 5.2 | CML-7 | CML: Elbow | 3 | 2018-06-10 | 2018-12-24 | 2014-06-22 10:00 | 2.5 | 0.60453 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.16264 | 5 | 5.3 | 4.9 | 5.6 | 0.31623
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-14 | 200-PG-23006-09C02-PA CML-14 | Yes | FPSO 2014 | Pipe Wall Thickness | 23847 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 17.975 | CML-14 | CML: Fitting | 3 | 2025-09-18 | 2021-08-16 | 2014-09-25 07:00 | 9.3 | 0.72804 | A4: Left Quadrant |  | 15.26 | 9.3 | 12.28 | 17.3 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 18.1 | 17.5 | 19 | 17.3 | 0.76322
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-8 | 50-PL-23041-06C03 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10221 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 11.475 | CML-8 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 1.5284 | A3: Inside Quadrant |  | 5.07 |  |  | 10.4 | 6 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 12.2 | 11.6 | 10.4 | 11.7 | 0.76322
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-17 | 50-CG-38487-09C02-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23586 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 9 | CML-17 | CML: Elbow | 3 | 2030-04-28 | 2025-12-07 | 2015-09-10 07:00 | 2.5 | 0.36882 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 7.9 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | -0.42566 | 9.6 | 7.9 | 9.1 | 9.4 | 0.76158
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-30 | 50-PF-20300-03C03-P CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 21596 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 8.1 | CML-30 | CML: type TBC | 6 | 2018-05-14 | 2018-04-09 | 2014-05-26 09:30 | 2.5 | 1.2593 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.5 | 3 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.7 | 7.5 | 8 | 9.2 | 0.76158
FL02 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FL-43454-01C02-P | CML-38 | 50-FL-43454-01C02-P CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 21658 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 17.4 | CML-38 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 16.8 | 3 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 |  | 18.5 | 16.8 | 17 | 17.3 | 0.76158
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-7 | 50-PL-23515-01C03 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8656 |  | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:51 | [32 empty] | 9.2 | CML-7 | CML: Elbow | 6 | 2044-08-19 | 2044-01-13 | 2015-02-12 07:00 | 2.5 | 0.19975 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.3 | 10.2 | 8.9 | 0.76158
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-12 | 25-VA-23054-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21375 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | [36 empty] | 16.3 | CML-12 | CML: Elbow | 6 | 2102-10-24 | 2088-02-10 | 2014-06-29 13:00 | 5.33 | 0 | A2: Right Quadrant |  | 8.27 | 5.33 | 6.8 | 15.7 | 3 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.37 |  | 15.9 | 15.7 | 16.2 | 17.4 | 0.76158
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-18 | 350-FL-43511-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2299 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 8.55 | CML-18 | CML: type TBC | 3 | 2026-10-31 | 2025-01-23 | 2014-03-17 08:00 | 2.5 | 0.40369 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.6 | 6 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 9.3 | 8.3 | 7.6 | 9 | 0.75939
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-6 | 50-PL-20033-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2270 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 6.2 | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-16 11:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.1 | 5.7 | 6.2 | 6.8 | 0.45461
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20069-01C02-P | CML-3 | 100-PL-20069-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21557 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.275 | CML-3 | CML: Elbow | 3 | 2025-10-20 | 2026-03-18 | 2014-07-17 07:30 | 2.5 | 0.28397 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-PL-20069-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.7 | 6.3 | 6.4 | 5.7 | 0.41932
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23048-09C02 | CML-2 | 50-PG-23048-09C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20584 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.65 | CML-2 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9 | 9 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 10.7 | 9.7 | 9.2 | 9 | 0.75939
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-3 | 200-PG-20300-03C03-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23358 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 12.25 | CML-3 | CML: Elbow | 6 | 2030-02-16 | 2027-02-08 | 2015-07-20 07:00 | 3.3 | 0.56205 | A3: Inside Quadrant |  | 6.7 | 3.3 | 5 | 11.5 | 6 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 | 0.093615 | 12.5 | 11.8 | 11.5 | 13.2 | 0.75939
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-1 | 100-WC-40027-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 833 |  | 2014-04-02 09:00 | 2014-04-02 10:00 | Check Corrosion Rate of 1.219mm/ yr |  | Nestor | 2016-04-01 | This is where reviewed description will go. | [31 empty] | 5.325 | CML-1 | CML: Elbow | 3 | 2016-04-19 | 2016-05-24 | 2014-04-02 09:00 | 2.5 | 1.2192 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.4 | 5.5 | 0.22174
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-4 | 80-FL-43015-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22947 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 6.375 | CML-4 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | -0.17548 | 7.4 | 6.4 | 5.6 | 6.1 | 0.75884
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-3 | 50-PL-20033-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21832 |  | 2014-10-12 07:00 | 2014-10-12 12:00 | [36 empty] | 6.15 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 0.52189 | 6.1 | 5.7 | 6.2 | 6.6 | 0.36968
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-2 | 80-PL-44008-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23770 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 5.95 | CML-2 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2015-04-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 9 O'Clock | 50 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 2.1921 | 5.7 | 6.1 | 6.3 | 5.7 | 0.3
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-6 | 100-WC-40516-1CG CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8679 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:55 | [32 empty] | 9.625 | CML-6 | CML: Elbow | 3 | 2077-12-11 | 2061-08-26 | 2015-02-13 07:00 | 2.5 | 0.09385 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.4 | 12 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.4 | 10.4 | 10.3 | 0.93229
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-11 | 300-PG-20506-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 13225 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 13.7333 | CML-11 | CML: type TBC | 6 | 2019-05-18 | 2018-04-21 | 2014-02-04 15:00 | 4.9 | 1.5708 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 3 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 14.6 | 13.2 | 13.4 |  | 0.75719
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-16 | 300-PG-20005-03C03-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 22778 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14 | CML-16 | CML: Reducing Tee | 6 | 2026-06-22 | 2024-02-15 | 2015-04-29 07:00 | 4.9 | 0.71713 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.9 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | 1.6251 | 14.1 | 12.9 | 14.5 | 14.5 | 0.75719
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-13 | 100-DH-56088-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5206 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 6.4 | CML-13 | CML: Reducing Tee | 3 | 2041-10-15 | 2042-09-22 | 2014-05-20 07:00 | 2.5 | 0.12398 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.3 | 7.5 | 5.9 | 5.9 | 0.75719
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-16 | 300-PG-20048-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21486 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | Check Corrosion Rate of 0.53mm/ yr | 38 | Kirstie Albone | 2017-03-23 12:47 | [32 empty] | 14.75 | CML-16 | CML: Fitting | 6 | 2031-01-28 | 2027-11-25 | 2014-06-28 09:30 | 4.9 | 0.5302 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 3 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 15.3 | 13.7 | 15.3 | 14.7 | 0.75498
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-6 | 50-PL-23040-03C03 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10191 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.05 | CML-6 | CML: type TBC | 6 | 2018-06-23 | 2018-05-19 | 2013-11-08 | 2.5 | 1.2319 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 6 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 9.2 | 10 | 8.2 | 8.8 | 0.75498
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-13 | 250-PG-20036-01C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21371 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 9.65 | CML-13 | CML: Pipe Length | 6 | 2041-06-12 | 2039-11-07 | 2014-07-14 07:30 | 2.5 | 0.24136 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 10.2 | 9 | 10.4 | 0.75498
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45024-01C02 | CML-41 | 50-FG-45024-01C02 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 23498 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 14.35 | CML-41 | CML: Elbow | 6 | 2056-05-01 | 2048-08-12 | 2015-07-27 07:00 | 4.9 | 0.21818 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 | -0.72277 | 14.4 | 13.8 | 13.8 | 15.4 | 0.75498
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38002-09C02-P | CML-1 | 50-CG-38002-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20792 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 |  |  | Administrator | 2015-09-07 10:58 | [32 empty] | 9.75 | CML-1 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.8 | 9 O'Clock | 50 | 8.74 | 50-CG-38002-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 10.6 | 9.6 | 10 | 8.8 | 0.75498
CG03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-CG-38459-09C02-P | CML-14 | 80-CG-38459-09C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21856 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 14.95 | CML-14 | CML: Reducing Tee | 6 | 2091-07-06 | 2082-06-18 | 2014-10-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 14.3 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.8 |  | 15.7 | 14.3 | 14.3 | 15.5 | 0.75498
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-11 | 300-PG-20037-03C03-PA CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21374 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | [36 empty] | 14.375 | CML-11 | CML: Fitting | 6 | 2039-06-13 | 2035-03-03 | 2014-06-29 13:00 | 5.33 | 0.34317 | A2: Right Quadrant |  | 8.27 | 5.33 | 6.8 | 13.9 | 3 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.57 |  | 14 | 13.9 | 15.5 | 14.1 | 0.75443
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-18 | 250-PG-23004-06C03-A CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23385 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 18.1 | CML-18 | CML: Pipe Length | 6 | 2032-12-25 | 2029-03-31 | 2015-07-21 07:00 | 8.55 | 0.49584 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 17.2 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.65 | -0.1751 | 19 | 18.3 | 17.9 | 17.2 | 0.75277
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-18 | 250-PW-20022-01C03-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23116 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 8.85 | CML-18 | CML: Fitting | 6 | 2030-06-19 | 2029-06-30 | 2015-05-10 07:00 | 2.5 | 0.3968 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.5 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 0.98407 | 8.9 | 9.1 | 8.9 | 8.5 | 0.25166
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-11 | 250-PW-20039-01C03-P CML-11 | Yes | FPSO 2015 | Pipe Wall Thickness | 22975 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 8.725 | CML-11 | CML: Reducing Tee | 6 | 2030-04-27 | 2029-05-11 | 2015-05-04 07:00 | 2.5 | 0.40019 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.5 | 9 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 0.349 | 8.8 | 9 | 8.6 | 8.5 | 0.22174
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20069-01C02-P | CML-1 | 100-PL-20069-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21555 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6 | CML-1 | CML: Fitting | 3 | 2025-10-20 | 2026-03-18 | 2014-07-17 07:30 | 2.5 | 0.28397 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 3 O'Clock | 100 | 6.02 | 100-PL-20069-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.7 | 6.2 | 6.3 | 0.29439
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1855 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 6 | CML-6 | CML: type TBC | 3 | 2033-08-03 | 2035-10-03 | 2014-05-06 08:00 | 2.5 | 0.15059 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 7.1 | 5.7 | 5.4 | 5.8 | 0.75277
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22335 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 6 | CML-6 | CML: type TBC | 3 | 2033-08-03 | 2035-10-03 | 2014-05-06 08:00 | 2.5 | 0.15059 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 7.1 | 5.7 | 5.4 | 5.8 | 0.75277
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1400 | Rope access | 2014-04-05 15:00 | 2014-04-05 16:00 | [36 empty] | 6.35 | CML-1 | CML: type TBC | 3 | 2031-10-06 | 2033-09-24 | 2014-04-05 15:00 | 2.5 | 0.16557 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DC-57027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.9 | 7 | 6.1 | 0.75056
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-25 | 300-PG-20005-03C03-P CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 22787 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 13.35 | CML-25 | CML: Elbow | 6 | 2024-10-22 | 2022-10-05 | 2015-04-29 07:00 | 4.9 | 0.82182 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 12.7 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 | 1.1251 | 14 | 12.7 | 12.7 | 14 | 0.75056
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-8 | 50-CG-38487-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20847 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 11.475 | CML-8 | CML: Reducer | 3 | 2075-10-24 | 2059-08-12 | 2014-10-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.7 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 | -1.444 | 12.3 | 11.9 | 10.7 | 11 | 0.75
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45024-01C02 | CML-17 | 50-FG-45024-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21155 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.575 | CML-17 | CML: Elbow | 6 | 2015-09-30 | 2015-03-05 | 2014-07-16 07:30 | 2.5 | 5.0438 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.6 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 10.4 | 9.5 | 9.8 | 8.6 | 0.75
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-7 | 50-PF-20301-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22284 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.975 | CML-7 | CML: Elbow | 6 | 2036-08-26 | 2040-04-15 | 2014-05-01 07:00 | 3.61 | 0.19653 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.39 |  | 8.9 | 9.8 | 9.2 | 8 | 0.75
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-48 | 300-PF-20001-03C03-P CML-48 |  | FPSO 2014 | Pipe Wall Thickness | 21186 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 21.275 | CML-48 | CML: Reducer | 6 | 2090-02-10 | 2081-10-05 | 2014-07-16 07:30 | 6.6 | 0 | A3: Inside Quadrant |  | 8.27 | 6.6 | 7.435 | 20.5 | 6 O'Clock | 400 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.9 |  | 22.3 | 21.2 | 20.5 | 21.1 | 0.75
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-8 | 200-PG-23505-09C02-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2689 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.475 | CML-8 | CML: Pipe Length | 3 | 2055-05-31 | 2049-05-31 | 2014-03-12 09:00 | 14.06 | 0 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 19.1 | 9 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.04 | 0 | 19.7 | 19.1 | 20 | 19.1 | 0.45
DH01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-DH-56004-01C02 | CML-3 | 80-DH-56004-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 23694 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.125 | CML-3 | CML: Elbow | 3 | 2016-09-09 | 2017-01-15 | 2015-10-30 07:00 | 2.5 | 0.92773 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.3 | 3 O'Clock | 50 | 5.54 | 50-CG-38456-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.9 | 3.3 | 4.2 | 5.1 | 0.75
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-36 | 50-DH-56070-01C02 CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 3252 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.675 | CML-36 | CML: type TBC | 3 | 2017-11-12 | 2018-05-06 | 2014-05-09 07:00 | 2.5 | 0.68246 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 4.9 | 5.5 | 6.7 | 0.75
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-8 | 200-PG-23505-09C02-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 378 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 19.475 | CML-8 | CML: Pipe Length | 3 | 2055-05-31 | 2049-05-31 | 2014-03-12 | 14.06 | 0 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 19.1 | 9 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.04 |  | 19.7 | 19.1 | 20 | 19.1 | 0.45
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23037-25C02-A | CML-9 | 150-PG-23037-25C02-A CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 20046 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.85 | CML-9 | CML: Elbow | 3 | 2019-10-02 | 2018-02-24 | 2014-05-29 07:00 | 15.88 | 0.9571 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 21 | 9 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.12 | 0.52549 | 24.2 | 21 | 21.2 | 21 | 1.5695
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56061-01C02 | CML-2 | 50-DH-56061-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3366 | Rope Access | 2014-05-10 08:00 | 2014-05-10 09:00 | [36 empty] | 8.275 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-10 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 12 O'Clock | 50 | 5.54 | 50-DH-56061-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 8.1 | 9 | 8.7 | 0.75
PL03 | Montara_Topside | Yes | Flare (43) | Pipework | 50-PL-57066-01C03 | CML-6 | 50-PL-57066-01C03 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23505 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 9.025 | CML-6 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2015-07-28 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 8.4 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.37 | 0.26449 | 8.4 | 9.9 | 8.4 | 9.4 | 0.75
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-34 | 300-PF-20501-03C03-P CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 21710 | Protective mesh removed. Reviewed on 1/12/14. FFS. Recheck on Sep.15 | 2014-09-28 07:00 | 2014-09-28 15:00 |  |  | Nestor | 2014-12-01 08:53 | [32 empty] | 14.125 | CML-34 | CML: type TBC | 6 | 2026-03-23 | 2023-12-02 | 2014-09-28 07:00 | 4.9 | 0.73107 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 13.7 | 14.6 | 14.9 | 13.3 | 0.75
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-8 | 250-PW-20022-01C03-P CML-8 | yes | FPSO 2014 | Pipe Wall Thickness | 2051 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 9.35 | CML-8 | CML: Pipe Length | 6 | 2021-09-21 | 2021-04-01 | 2014-03-28 07:00 | 2.5 | 0.81437 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.6 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.4 | 10.8 | 8.6 | 1.0376
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-37 | 250-PW-44006-01X01 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 8029 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 5.25 | CML-37 | CML: Elbow | 3 | 2017-10-06 | 2017-09-25 | 2015-01-20 08:30 | 2.5 | 0.88451 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 4.9 | 12 O'Clock | 50 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.24328 | 4.9 | 5.2 | 5.6 | 5.3 | 0.28868
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20504-03C03-P | CML-4 | 50-PF-20504-03C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7749 |  | 2015-01-10 13:00 | 2015-01-10 16:00 | [36 empty] | 8.2 | CML-4 | CML: Elbow | 6 | 2019-12-11 | 2019-10-26 | 2015-01-10 13:00 | 2.5 | 0.95507 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.2 | 12 O'Clock | 50 | 8.74 | 50-PF-20504-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 8.4 | 9 | 8.2 | 0.74833
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-11 | 50-PW-44013-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22730 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.2 | CML-11 | CML: Elbow | 3 | 2022-06-21 | 2023-06-11 | 2015-04-28 07:00 | 2.5 | 0.33549 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | -0.82486 | 4.9 | 5.3 | 5.1 | 5.5 | 0.2582
PL03 | Montara_Topside | Yes | Wellstream (57) | Pipework | 50-PL-57066-01C03 | CML-2 | 50-PL-57066-01C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22108 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 9.675 | CML-2 | CML: type TBC | 6 | 2074-12-15 | 2073-10-08 | 2014-10-18 07:00 | 2.5 | 0.10133 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-PF-57066-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.8 | 10.3 | 10 | 0.74554
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40054-01C02 | CML-3 | 50-WC-40054-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2094 |  | 2014-03-28 11:30 | 2014-03-28 12:00 | Check Corrosion Rate of 0.656mm/ yr | [35 empty] | 5.325 | CML-3 | CML: type TBC | 3 | 2018-01-17 | 2018-07-18 | 2014-03-28 11:30 | 2.5 | 0.65595 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-WC-40054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.4 | 5.4 | 5 | 0.22174
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40021-01C02 | CML-5 | 50-WC-40021-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2100 | Rope Access | 2014-03-28 13:00 | 2014-03-28 14:00 | Check Corrosion Rate of 0.656mm/ yr | [35 empty] | 5.3 | CML-5 | CML: type TBC | 3 | 2018-01-17 | 2018-07-18 | 2014-03-28 13:00 | 2.5 | 0.65582 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-WC-40021-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5 | 5.3 | 5.5 | 0.21602
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-20 | 250-PW-20022-01C03-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23118 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.25 | CML-20 | CML: Fitting | 6 | 2033-01-03 | 2031-11-23 | 2015-05-10 07:00 | 2.5 | 0.34527 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 8.6 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 1.2525 | 8.9 | 8.6 | 10.3 | 9.2 | 0.74162
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-6 | 50-CG-38488-09C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23595 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 11.875 | CML-6 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2015-09-15 15:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.8 | 12 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 | 0.51628 | 10.8 | 12.5 | 12.2 | 12 | 0.74554
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56142-01C02 | CML-3 | 25-DH-56142-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7524 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 6.3 | CML-3 | CML: Elbow | 3 | 2022-12-28 | 2022-12-02 | 2015-04-13 07:00 | 2.5 | 0.40181 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 3 O'Clock | 25 | 6.35 | 25-DH-56142-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 7.3 | 5.6 | 5.9 | 6.4 | 0.74386
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20023-01C03-P | CML-2 | 250-PW-20023-01C03-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 5599 |  | 2014-06-20 07:00 | 2014-06-20 08:00 | [36 empty] | 9.25 | CML-2 | CML: Elbow | 6 | 2024-01-18 | 2023-06-11 | 2014-06-20 07:00 | 2.5 | 0.63637 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.6 | 12 O'Clock | 250 | 9.27 | 250-PW-20023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.3 | 9.3 | 9.8 | 0.49329
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20070-01C02-P | CML-2 | 100-PL-20070-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21562 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.075 | CML-2 | CML: Elbow | 3 | 2025-10-20 | 2026-03-18 | 2014-07-17 07:30 | 2.5 | 0.28397 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-PL-20070-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 6.3 | 6.3 | 5.7 | 0.28723
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-7 | 200-PG-23006-09C02-PA CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 23840 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 18.2 | CML-7 | CML: Fitting | 3 | 2024-07-21 | 2020-11-06 | 2014-09-25 07:00 | 9.3 | 0.80388 | A4: Left Quadrant |  | 15.26 | 9.3 | 12.28 | 17.2 | 9 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 18.6 | 18.9 | 18.1 | 17.2 | 0.74386
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-7 | 50-PW-44013-01X01 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10321 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.1 | CML-7 | CML: Equal Tee | 3 | 2015-07-10 | 2015-10-01 | 2013-11-10 | 2.5 | 1.442 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.2 | 4.9 | 5.1 | 5.2 | 0.14142
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-14 | 50-PL-45016-03C03 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10454 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.5 | CML-14 | CML: type TBC | 6 | 2016-03-28 | 2015-12-02 | 2013-11-13 | 0.99 | 2.743 | A3: Inside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.5 | 6 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.51 |  | 8.9 | 9.2 | 7.5 | 8.4 | 0.74386
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1753 | Rope access | 2014-04-27 07:00 | 2014-04-27 08:00 | [36 empty] | 5.65 | CML-4 | CML: Equal Tee | 3 | 2017-02-16 | 2017-07-12 | 2014-04-27 07:00 | 2.5 | 0.81776 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-FH-43117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.5 | 6.6 | 5.7 | 0.74162
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-3 | 50-PF-20301-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3001 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.35 | CML-3 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.5 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.89 | 0 | 10.3 | 9.4 | 8.5 | 9.2 | 0.74162
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-3 | 50-PF-20301-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22280 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.35 | CML-3 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.5 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.89 |  | 10.3 | 9.4 | 8.5 | 9.2 | 0.74162
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-7 | 250-PW-20039-01C03-P CML-7 | Yes | FPSO 2015 | Pipe Wall Thickness | 22971 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 8.825 | CML-7 | CML: Elbow | 6 | 2032-11-04 | 2031-09-27 | 2015-05-04 07:00 | 2.5 | 0.34822 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.6 | 12 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | -0.23267 | 8.6 | 8.7 | 9.1 | 8.9 | 0.22174
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-17 | 300-PF-20003-03C03-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21755 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 9.35 | CML-17 | CML: Elbow | 6 | 2016-03-26 | 2015-07-18 | 2014-10-01 07:00 | 2.5 | 4.1721 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.7 | 9 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9 | 9.3 | 10.4 | 8.7 | 0.74162
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-6 | 200-PG-23013-09C03-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10990 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 20.45 | CML-6 | CML: Elbow | 6 | 2019-01-31 | 2017-11-19 | 2014-01-10 | 10.22 | 1.8332 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 19.5 | 6 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.28 |  | 20.4 | 21.3 | 19.5 | 20.6 | 0.74162
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-19 | 100-DH-56086-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 20978 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 5.95 | CML-19 | CML: type TBC | 3 | 2018-02-03 | 2018-04-01 | 2014-05-16 13:00 | 2.5 | 0.75184 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.9 | 7 | 5.3 | 0.74162
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-2 | 50-PW-44014-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23147 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.025 | CML-2 | CML: Pipe Length | 3 | 2022-08-17 | 2023-08-13 | 2015-05-10 07:00 | 2.5 | 0.32981 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.44635 | 5.2 | 5 | 4.9 | 5 | 0.12583
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40021-01C02 | CML-1 | 50-WC-40021-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2096 | Rope Access | 2014-03-28 13:00 | 2014-03-28 14:00 | Check Corrosion Rate of 0.656mm/ yr | [35 empty] | 5.2 | CML-1 | CML: type TBC | 3 | 2018-01-17 | 2018-07-18 | 2014-03-28 13:00 | 2.5 | 0.65582 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-WC-40021-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.4 | 5.3 | 5 | 0.18257
WC01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-WC-40006-01C02 | CML-15 | 150-WC-40006-01C02 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10543 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.175 | CML-15 | CML: type TBC | 3 | 2016-01-02 | 2015-12-27 | 2013-11-16 | 2.5 | 1.1732 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.1 | 5 | 5.4 | 0.17078
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-12 | 200-PL-20010-01C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 23812 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.475 | CML-12 | CML: Fitting | 3 | 2022-08-22 | 2022-07-28 | 2014-09-25 07:00 | 2.5 | 0.41711 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.9 | 6.4 | 5.8 | 6.8 | 0.49917
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1278 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | Check Corrosion Rate of 0.432mm/ yr | [35 empty] | 7.025 | CML-2 | CML: type TBC | 3 | 2022-04-24 | 2022-03-31 | 2014-03-23 09:30 | 2.5 | 0.43247 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7 | 7.7 | 6 | 7.4 | 0.74106
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-3 | 100-PG-23503-03C03-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2719 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 11.575 | CML-3 | CML: Elbow | 6 | 2020-03-13 | 2020-07-11 | 2014-03-13 09:00 | 5.66 | 0.80578 | A4: Left Quadrant |  | 5.13 | 5.66 | 5.395 | 10.5 | 9 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.84 |  | 11.8 | 11.8 | 12.2 | 10.5 | 0.74106
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-5 | 200-PW-44019-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21896 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 5.75 | CML-5 | CML: Elbow | 3 | 2016-05-29 | 2016-05-21 | 2014-06-19 09:30 | 2.5 | 1.2852 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 3 O'Clock | 20 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 6.2 | 6.5 | 0.71414
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23037-25C02-A | CML-7 | 150-PG-23037-25C02-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20044 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 22.575 | CML-7 | CML: Elbow | 3 | 2019-10-02 | 2018-02-24 | 2014-05-29 07:00 | 15.88 | 0.9571 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21 | 12 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.12 | 0.52549 | 21 | 23.5 | 23.8 | 22 | 1.3124
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-1 | 80-CG-38459-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 24260 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 19.975 | CML-1 | CML: Elbow | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A2: Right Quadrant |  | 11.27 | 7 | 9.135 | 19.2 | 3 O'Clock | 150 | 14.27 | 150-PG-23026-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.2 |  | 20.2 | 19.2 | 20.9 | 19.6 | 0.74106
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-37 | 300-PF-20500-03C03-P CML-37 |  | FPSO 2014 | Pipe Wall Thickness | 21657 | Reviewed on 27/11/14. FFS. Recheck on Sep. 15 | 2014-09-27 07:00 | 2014-09-27 15:00 |  |  | Nestor | 2014-11-27 17:39 | [32 empty] | 14.1 | CML-37 | CML: Pipe Length | 6 | 2025-01-01 | 2022-12-02 | 2014-09-27 07:00 | 4.9 | 0.8081 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 3 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 14.8 | 13.2 | 13.8 | 14.6 | 0.73937
FG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FG-45044-03C02 | CML-1 | 50-FG-45044-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21910 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 9.5 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.6 | 12 O'Clock | 250 | 6.35 | 250-PW-44030-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 10.4 | 9.4 | 9.6 | 0.73937
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-22 | 100-DH-56082-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 3390 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 8.4 | CML-22 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.3 | 9 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.7 | 8.9 | 8.7 | 7.3 | 0.73937
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-8 | 50-CG-38488-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20826 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 11.6 | CML-8 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 11.1 | 3 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.3 | 11.1 | 11.3 | 12.7 | 0.73937
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-9 | 250-PG-23005-06C03 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10055 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 18.3 | CML-9 | CML: Elbow | 6 | 2022-07-02 | 2020-10-11 | 2013-11-06 | 8.6 | 1.0627 | A1: Outside Quadrant |  | 12.26 | 8.6 | 10.43 | 17.8 | 12 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 17.8 | 18 | 18 | 19.4 | 0.73937
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-4 | 50-FH-43016-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12603 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 7.525 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-01-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 12 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 8.4 | 7.6 | 7.5 | 0.73655
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-35 | 150-PG-23506-25C02 CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 2809 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.425 | CML-35 | CML: Pipe Length | 3 | 2017-12-18 | 2016-10-24 | 2014-03-15 09:00 | 15.88 | 1.3336 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 20.9 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.02 |  | 21 | 22.5 | 21.3 | 20.9 | 0.73655
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-13 | 200-PL-20018-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 23885 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.2 | CML-13 | CML: Fitting | 3 | 2022-08-29 | 2022-08-04 | 2014-09-26 07:00 | 2.5 | 0.41624 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0 | 5.8 | 5.9 | 6.4 | 6.7 | 0.42426
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-5 | 50-PW-44009-01C03-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22812 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 9.025 | CML-5 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2015-04-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.3 | 6 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | 0 | 9.2 | 9.6 | 8.3 | 9 | 0.54391
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44019-01X01 | CML-5 | 200-PW-44019-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5571 |  | 2014-06-19 09:30 | 2014-06-19 10:30 | [36 empty] | 5.75 | CML-5 | CML: Elbow | 3 | 2016-05-29 | 2016-05-21 | 2014-06-19 09:30 | 2.5 | 1.2852 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 3 O'Clock | 20 | 6.35 | 200-PW-44019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 6.2 | 6.5 | 0.71414
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-13 | 200-PL-20018-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21249 | Protective mesh removed. Reviewed on 27/11/14. FFS. Recheck on Sep. 15 | 2014-09-26 07:00 | 2014-09-26 15:00 |  |  | Nestor | 2014-11-27 15:00 | [32 empty] | 6.2 | CML-13 | CML: Fitting | 3 | 2022-08-29 | 2022-08-04 | 2014-09-26 07:00 | 2.5 | 0.41624 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 6.4 | 6.7 | 0.42426
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-13 | 50-PL-23514-01C03 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8646 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:22 | [32 empty] | 9.675 | CML-13 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2015-02-10 11:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.8 | 6 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.4 | 10.5 | 8.8 | 10 | 0.73655
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-13 | 150-PG-20507-01C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2857 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.825 | CML-13 | CML: type TBC | 6 | 2019-08-31 | 2018-10-02 | 2014-03-16 07:00 | 2.5 | 1.3547 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 9.9 | 3 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.8 | 9.9 | 11.7 | 10.9 | 0.73655
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-19 | 100-FG-45001-09C02 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10434 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.9 | CML-19 | CML: type TBC | 3 | 2018-01-10 | 2016-10-17 | 2013-11-13 | 4.7 | 1.3936 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 10.5 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 10.5 | 10.6 | 10.5 | 12 | 0.73485
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-15 | 150-PG-20507-01C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2859 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 11 | CML-15 | CML: type TBC | 6 | 2021-02-05 | 2019-12-24 | 2014-03-16 07:00 | 2.5 | 1.1015 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.1 | 6 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.7 | 11.6 | 10.1 | 11.6 | 0.73485
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-2 | 200-PG-23006-09C02-PA CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 23835 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 18.9 | CML-2 | CML: Elbow | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 18.3 | 3 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 18.3 | 18.3 | 19.8 | 19.2 | 0.73485
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20002-03C03-P | CML-1 | 300-PF-20002-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6513 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 16.9 | CML-1 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-24 07:30 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 15.8 | 9 O'Clock | 300 | 14.27 | 300-PF-20002-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 17.3 | 17.2 | 17.3 | 15.8 | 0.73485
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56069-01C02 | CML-3 | 50-DH-56069-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3398 | Rope Access | 2014-05-10 13:00 | 2014-05-10 14:00 | [36 empty] | 8.3 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-10 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.7 | 3 O'Clock | 50 | 5.54 | 50-DH-56069-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.7 | 9.2 | 8.6 | 0.73485
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-4 | 250-PW-44509-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22039 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.5 | CML-4 | CML: Elbow | 6 | 2029-11-17 | 2028-12-10 | 2014-10-20 07:00 | 2.5 | 0.41093 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.7 | 9 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.5 | 10 | 9.8 | 8.7 | 0.57155
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-25 | 250-PW-44006-01X01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 23196 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.65 | CML-25 | CML: Elbow | 3 | 2018-12-14 | 2018-11-30 | 2015-05-11 07:00 | 2.5 | 0.69471 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 4.6062 | 5.1 | 6.1 | 5 | 6.4 | 0.70475
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-2 | 200-PG-20300-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5867 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | [36 empty] | 12.45 | CML-2 | CML: Elbow | 6 | 2023-06-09 | 2021-08-16 | 2014-06-25 09:30 | 3.3 | 0.93735 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 11.7 | 9 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 12.8 | 13.3 | 12 | 11.7 | 0.73258
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23012-25C02-A | CML-2 | 150-PG-23012-25C02-A CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 13028 |  | 2014-01-11 09:00 | 2014-01-11 10:30 | [36 empty] | 22.275 | CML-2 | CML: Reducer | 3 | 2017-10-20 | 2016-09-10 | 2014-01-11 09:00 | 15.88 | 1.3827 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.1 | 6 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 |  | 21.1 | 21.2 | 21.1 | 25.7 | 2.2838
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-25 | 50-PF-20300-03C03-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 21591 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.35 | CML-25 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 10.3 | 9.5 | 9 | 8.6 | 0.73258
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43175-01C02 | CML-3 | 150-FL-43175-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12914 |  | 2014-02-03 07:00 | 2014-02-03 08:00 | [36 empty] | 7.15 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 3 O'Clock | 100 | 6.02 | 100-FL-43175-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7.6 | 6.1 | 7.2 | 7.7 | 0.73258
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-10 | 50-WC-40451-01C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10150 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 1.224mm/ yr | [35 empty] | 5.125 | CML-10 | CML: Fitting | 3 | 2015-11-24 | 2016-02-29 | 2013-11-09 | 2.5 | 1.2242 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.3 | 5 | 5 | 0.15
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-7 | 100-WC-40027-01C02 CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24420 | Re-check as requested by N.Sequera | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.33mm/ yr |  | John Wilson | 2017-03-23 10:29 | Loss within CA CML on 12 monthly schedule. | [31 empty] | 5.175 | CML-7 | CML: Elbow | 3 | 2024-01-25 | 2024-06-01 | 2016-07-02 07:00 | 2.5 | 0.33026 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 3 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.1058 | 5.3 | 5 | 5.2 | 5.2 | 0.12583
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-4 | 250-PW-44509-01C03-P CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 22989 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.325 | CML-4 | CML: Elbow | 6 | 2036-04-14 | 2034-12-26 | 2015-05-05 07:00 | 2.5 | 0.29582 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.7 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 | 0 | 9.2 | 9.9 | 8.7 | 9.5 | 0.5058
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-8 | 250-PG-20036-01C03-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23396 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 7.975 | CML-8 | CML: Elbow | 6 | 2021-02-23 | 2020-09-16 | 2015-07-21 07:00 | 2.5 | 0.87474 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.4 | 12 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | 0.49062 | 7.4 | 9 | 7.5 | 8 | 0.73201
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-5 | 25-VA-23054-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20587 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 13.725 | CML-5 | CML: Equal Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 13.1 | 6 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.6 |  | 14.5 | 13.1 | 13.1 | 14.2 | 0.73201
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-18 | 250-PG-23003-06C02-PA CML-18 | High Priority | FPSO 2015 | Pipe Wall Thickness | 23528 | Re-check on line as Per RBI 2014 Report | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 14.425 | CML-18 | CML: Elbow | 3 | 2022-08-02 | 2021-02-11 | 2015-07-28 07:00 | 7.9 | 0.78351 | A1: Outside Quadrant |  | 12.09 | 7.9 | 9.0519 | 13.4 | 12 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 | -0.23779 | 13.4 | 14.9 | 15 | 14.4 | 0.73201
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-47 | 50-DH-56070-01C02 CML-47 |  | FPSO 2014 | Pipe Wall Thickness | 3263 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 7.025 | CML-47 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.5 | 6.4 | 6.4 | 7.8 | 0.73201
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-2 | 100-WC-40027-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23422 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 |  |  | Nestor | 2016-04-01 | [32 empty] | 5.075 | CML-2 | CML: Elbow | 3 | 2020-10-21 | 2021-01-18 | 2015-07-23 07:00 | 2.5 | 0.47591 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 6 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.2296 | 5 | 5.2 | 5 | 5.1 | 0.095743
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-1 | 200-PG-24001-09C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10257 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 19.425 | CML-1 | CML: Elbow | 3 | 2104-01-05 | 2073-09-17 | 2013-11-09 | 9.2 | 0 | A1: Outside Quadrant |  | 15.26 | 9.2 | 12.23 | 18.9 | 12 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 18.9 | 19.1 | 19.2 | 20.5 | 0.72744
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43091-01C02 | CML-5 | 80-FL-43091-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5830 | Rope access | 2014-06-24 10:30 | 2014-06-24 12:00 | [36 empty] | 6.375 | CML-5 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-06-24 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-FL-43091-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 6.1 | 7.4 | 0.72744
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-7 | 80-FH-43158-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12888 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 6.325 | CML-7 | CML: type TBC | 3 | 2023-07-24 | 2024-09-27 | 2014-01-22 11:00 | 2.5 | 0.29453 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 12 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 7 | 6.6 | 6.4 | 0.72744
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-16 | 300-PG-20506-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 13230 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 13.875 | CML-16 | CML: type TBC | 6 | 2019-05-18 | 2018-04-21 | 2014-02-04 15:00 | 4.9 | 1.5708 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 6 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 14.6 | 14.4 | 13.2 | 13.3 | 0.72744
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56032-01C02 | CML-2 | 80-DH-56032-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20913 | Rope Access | 2014-05-21 13:00 | 2014-05-21 14:00 | [36 empty] | 5.525 | CML-2 | CML: Elbow | 3 | 2017-08-15 | 2018-02-10 | 2014-05-21 13:00 | 2.5 | 0.71035 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 6 O'Clock | 80 | 5.49 | 80-DH-56032-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5 | 6.2 | 4.8 | 6.1 | 0.72744
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-8 | 100-FL-43455-01C02-P CML-8 | Yes | FPSO 2014 | Pipe Wall Thickness | 20491 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 6.025 | CML-8 | CML: Reducer | 3 | 2019-12-19 | 2020-03-07 | 2014-10-03 07:00 | 2.5 | 0.5371 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 9 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.7 | 6.6 | 5.5 | 5.3 | 0.72744
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-3 | 50-FG-45024-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2568 | Rope Access | 2014-04-08 07:30 | 2014-04-08 08:30 | [36 empty] | 9.9 | CML-3 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-04-08 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 9.2 | 6 O'Clock | 150 | 7.11 | 150-FL-43084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.9 | 9.9 | 9.2 | 9.6 | 0.72572
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23009-09C02 | CML-3 | 200-PG-23009-09C02 CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 10913 | Deck Level | 2014-01-06 | 2014-01-06 | [36 empty] | 17.2 | CML-3 | CML: type TBC | 3 | 2016-06-19 | 2015-06-15 | 2014-01-06 | 9.3 | 2.9333 | A4: Left Quadrant |  | 15.26 | 9.3 | 12.28 | 16.5 | 9 O'Clock | 200 | 18.26 | 200-PG-23009-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 16.9 | 18.2 | 17.2 | 16.5 | 0.72572
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-19 | 50-PW-44040-01C02 CML-19 | yes | FPSO 2014 | Pipe Wall Thickness | 1994 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.2 | CML-19 | CML: Elbow | 3 | 2016-10-12 | 2017-02-21 | 2014-03-27 07:00 | 2.5 | 0.90246 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.6 | 5.3 | 5.1 | 0.33665
FL02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-FL-43454-01C02-P | CML-1 | 50-FL-43454-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8661 | Material Class Not Selectable. | 2015-02-12 11:00 | 2015-02-12 12:00 |  |  | Administrator | 2015-09-08 12:16 | [32 empty] | 9.95 | CML-1 | CML: Elbow | 3 | 2074-01-04 | 2058-09-17 | 2015-02-12 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 9.1 | 6 O'Clock | 100 | 8.56 | 100-WC-40510-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.7 | 10.2 | 9.1 | 10.8 | 0.72342
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43308-01C02-E | CML-2 | 200-PL-43308-01C02-E CML-2 | Yes | FPSO 2015 | Pipe Wall Thickness | 8795 | LAGGING REMOVAL REQUIRED | 2015-02-15 13:00 | 2015-02-15 15:00 | [36 empty] | 5.9 | CML-2 | CML: Elbow | 3 | 2023-07-18 | 2023-06-21 | 2015-02-15 13:00 | 2.5 | 0.37988 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 9 O'Clock | 200 | 6.35 | 200-PL-43308-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 6 | 5.9 | 5.7 | 0.14142
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-5 | 50-PL-23022-03C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1861 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.825 | CML-5 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 12 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9.6 | 10.4 | 10.4 | 0.72284
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23018-09C03-A | CML-5 | 200-PG-23018-09C03-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13066 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 21.775 | CML-5 | CML: type TBC | 6 | 2117-11-29 | 2095-08-30 | 2014-01-10 07:00 | 10.17 | 0 | A1: Outside Quadrant |  | 14.62 | 10.17 | 12.395 | 21.2 | 6 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.03 |  | 21.2 | 22.7 | 21.2 | 22 | 0.72284
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-7 | 50-CG-38452-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12970 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 9.8 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 9 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  |  | 9.6 | 10.6 | 9.2 | 0.72111
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-5 | 80-DH-56140-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21076 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 8.75 | CML-5 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 8.2 | 12 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 9.8 | 8.4 | 8.6 | 0.7188
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20031-01C03-P | CML-6 | 150-PG-20031-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 23868 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.35 | CML-6 | CML: Elbow | 6 | 2022-03-22 | 2020-12-08 | 2014-09-26 07:00 | 2.5 | 0.96114 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 9.7 | 9 O'Clock | 150 | 10.97 | 150-PG-20031-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.9 | 11.3 | 10.5 | 9.7 | 0.7188
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-3 | 80-FH-43158-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12884 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 6.25 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-22 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 6.4 | 5.6 | 7.2 | 0.7188
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-11 | 80-DH-56140-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21082 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 8.05 | CML-11 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 7.4 | 3 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.6 | 7.4 | 8.2 | 9 | 0.7188
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23018-09C03-A | CML-6 | 200-PG-23018-09C03-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13067 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 20.55 | CML-6 | CML: type TBC | 6 | 2019-09-05 | 2018-05-06 | 2014-01-10 07:00 | 10.17 | 1.6673 | A3: Inside Quadrant |  | 14.62 | 10.17 | 12.395 | 19.6 | 6 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.43 |  | 20.4 | 21.2 | 19.6 | 21 | 0.7188
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-19 | 150-PG-23506-25C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2793 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 24.225 | CML-19 | CML: Elbow | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 23.8 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.92 |  | 23.9 | 23.8 | 23.9 | 25.3 | 0.71822
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-24 | 250-PG-23004-06C03-A CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 23391 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 18.725 | CML-24 | CML: Pipe Length | 6 | 2093-03-13 | 2077-12-15 | 2015-07-21 07:00 | 8.55 | 0.12162 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 18 | 3 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.45 | -0.26266 | 19.6 | 18 | 19 | 18.3 | 0.71822
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-16 | 100-WC-40516-1CG CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8689 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:57 | [32 empty] | 9.375 | CML-16 | CML: Pipe Length | 3 | 2077-12-11 | 2061-08-26 | 2015-02-13 07:00 | 2.5 | 0.09385 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.4 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.8 | 10.1 | 8.4 | 10.2 | 0.91059
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-24 | 50-WC-40451-01C02 CML-24 |  | FPSO 2013 | Pipe Wall Thickness | 10164 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 1.224mm/ yr | [35 empty] | 5.05 | CML-24 | CML: type TBC | 3 | 2015-11-24 | 2016-02-29 | 2013-11-09 | 2.5 | 1.2242 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.1 | 5 | 5 | 0.057735
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-8 | 50-CG-24002-09C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2554 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 9.875 | CML-8 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.8 | 12 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 10.3 | 10.2 | 10.2 | 0.71822
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56130-01C02 | CML-7 | 50-DH-56130-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21059 | Rope Access | 2014-05-15 13:00 | 2014-05-15 14:00 | [36 empty] | 5.375 | CML-7 | CML: type TBC | 3 | 2016-07-02 | 2016-10-31 | 2014-05-15 13:00 | 2.5 | 0.98439 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56130-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.1 | 4.6 | 5.5 | 6.3 | 0.71822
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45044-03C02 | CML-4 | 50-FG-45044-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21362 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | Check Corrosion Rate of 0.599mm/ yr | 41 | Kirstie Albone | 2017-03-23 15:00 | [32 empty] | 9.3 | CML-4 | CML: Fitting | 6 | 2024-09-16 | 2024-01-26 | 2014-07-14 07:30 | 2.5 | 0.59893 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.6 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 10.3 | 9.2 | 8.6 | 9.1 | 0.71647
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-4 | 100-PW-20021-01C02-P CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 22822 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.125 | CML-4 | CML: Elbow | 3 | 2018-12-06 | 2019-02-11 | 2015-04-30 07:00 | 2.5 | 0.6377 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 3 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.72637 | 5.4 | 4.8 | 5.4 | 4.9 | 0.32016
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-14 | 250-PG-23004-06C03-A CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23381 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 19.5 | CML-14 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2015-07-21 07:00 | 8.55 | 0 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.5 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.95 | -0.52531 | 18.5 | 19.7 | 20.2 | 19.6 | 0.71647
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-5 | 80-FH-43151-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2239 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 7.5 | CML-5 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.7 | 12 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.1 | 8.2 | 8 | 0.71647
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-20 | 250-PW-44006-01X01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23191 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.675 | CML-20 | CML: Elbow | 3 | 2018-12-14 | 2018-11-30 | 2015-05-11 07:00 | 2.5 | 0.69471 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 9 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.32901 | 6.1 | 6.4 | 5.2 | 5 | 0.68007
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-36 | 150-PG-23506-25C02 CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 20090 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 20.45 | CML-36 | CML: Elbow | 3 | 2016-05-08 | 2015-08-11 | 2014-05-29 07:00 | 15.88 | 2.0653 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 19.9 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.02 | 401.5016 | 20.2 | 20.2 | 21.5 | 19.9 | 0.71414
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-50 | 300-PF-20003-03C03-P CML-50 |  | FPSO 2014 | Pipe Wall Thickness | 21788 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 17.45 | CML-50 | CML: Equal Tee | 6 | 2115-02-10 | 2094-04-05 | 2014-10-01 07:00 | 4.1 | 0 | A1: Outside Quadrant |  | 8.27 | 4.1 | 6.185 | 16.9 | 12 O'Clock | 250 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.8 |  | 16.9 | 17.2 | 17.2 | 18.5 | 0.71414
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-9 | 50-PW-44014-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2011 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 5.475 | CML-9 | CML: Pipe Length | 3 | 2018-01-11 | 2018-07-11 | 2014-03-27 10:00 | 2.5 | 0.65828 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.3 | 5 | 5.1 | 5.5 | 0.5909
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-24 | 250-PW-44006-01X01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 23195 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.7 | CML-24 | CML: Pipe Length | 3 | 2018-12-14 | 2018-11-30 | 2015-05-11 07:00 | 2.5 | 0.69471 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.65803 | 6.1 | 5.8 | 5 | 5.9 | 0.48305
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44009-01C03-P | CML-6 | 50-PW-44009-01C03-P CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 5817 | Protective mesh removed | 2014-06-24 07:00 | 2014-06-24 08:00 | [36 empty] | 9.1 | CML-6 | CML: Elbow | 6 | 2043-10-24 | 2058-08-12 | 2014-06-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | -0.46 | 2.5 | 1.02 | 8.1 | 12 O'Clock | 50 | 5.54 | 50-PW-44009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 9.2 | 10.3 | 8.8 | 0.92014
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45003-03C02 | CML-2 | 150-FG-45003-03C02 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24368 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 8.45 | CML-2 | CML: Equal Tee | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 3.305 | 7.7 | 3 O'Clock | 150 | 7.11 | 150-FG-45003-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9.2 | 7.7 | 8 | 8.9 | 0.71414
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57300-01C02 | CML-2 | 50-DC-57300-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20292 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 5.375 | CML-2 | CML: Elbow | 3 | 2025-09-26 | 2027-01-21 | 2014-10-17 07:00 | 2.5 | 0.24658 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DC-57300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.7 | 5.3 | 5.2 | 0.22174
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-15 | 50-PG-23074-01C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20637 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 7.35 | CML-15 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-07-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 40 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.6 | 6.4 | 7.3 | 8.1 | 0.71414
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38002-09C02-P | CML-2 | 50-CG-38002-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20793 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 |  |  | Administrator | 2015-09-07 10:59 | [32 empty] | 9.65 | CML-2 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.9 | 9 O'Clock | 50 | 8.74 | 50-CG-38002-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10.6 | 9.4 | 9.7 | 8.9 | 0.71414
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-5 | 100-FG-45043-03C02-E CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22651 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 10.45 | CML-5 | CML: Reducing Tee | 3 | 2054-10-24 | 2049-02-10 | 2015-04-27 07:00 | 1.88 | 0 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 9.4 | 12 O'Clock | 100 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.52 |  | 9.4 | 10.7 | 10.7 | 11 | 0.71414
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-12 | 50-DH-56109-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21001 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.775 | CML-12 | CML: Equal Tee | 3 | 2018-01-23 | 2018-07-25 | 2014-05-24 10:30 | 2.5 | 0.65354 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 4.9 | 6.6 | 6 | 0.71356
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56067-01C02 | CML-2 | 50-DH-56067-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3401 | Rope Access | 2014-05-10 14:00 | 2014-05-10 15:00 | [36 empty] | 8.125 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-10 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 12 O'Clock | 50 | 5.54 | 50-DH-56067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.8 | 8.9 | 8.5 | 0.71356
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-1 | 50-PW-44014-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2003 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 5.525 | CML-1 | CML: Elbow | 3 | 2018-01-11 | 2018-07-11 | 2014-03-27 10:00 | 2.5 | 0.65828 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.7 | 5.9 | 5.5 | 5 | 0.38622
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-51 | 300-PF-20001-03C03-P CML-51 |  | FPSO 2016 | Pipe Wall Thickness | 24487 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.708mm/ yr | 40 | [34 empty] | 11.525 | CML-51 | CML: Elbow | 6 | 2021-10-16 | 2020-01-28 | 2016-07-09 07:00 | 4.1 | 1.2131 | A2: Right Quadrant |  | 8.27 | 4.1 | 6.185 | 10.5 | 3 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | 0.20977 | 11.9 | 10.5 | 12.1 | 11.6 | 0.71356
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-7 | 200-FH-43012-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2837 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.575 | CML-7 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 7 | 3 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.66 |  | 8.6 | 7 | 7.2 | 7.5 | 0.71356
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-13 | 250-PW-44509-01C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 22048 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.55 | CML-13 | CML: Elbow | 6 | 2033-05-19 | 2032-03-31 | 2014-10-20 07:00 | 2.5 | 0.33884 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.8 | 9 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.7 | 9.6 | 10.1 | 8.8 | 0.54467
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-19 | 50-WC-40452-01C02 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10616 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 1.166mm/ yr | [35 empty] | 5.025 | CML-19 | CML: type TBC | 3 | 2016-01-08 | 2016-04-19 | 2013-11-17 | 2.5 | 1.1663 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5.1 | 5 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-10 | 50-DC-57450-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20326 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.35 | CML-10 | CML: Elbow | 3 | 2025-06-10 | 2026-09-25 | 2014-10-05 07:00 | 2.5 | 0.2526 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.4 | 5.2 | 5.5 | 0.1291
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-9 | 50-DC-57450-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20325 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.4 | CML-9 | CML: Elbow | 3 | 2025-06-10 | 2026-09-25 | 2014-10-05 07:00 | 2.5 | 0.2526 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.7 | 5.4 | 5.3 | 0.21602
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-46 | 150-PG-23506-25C02 CML-46 |  | FPSO 2014 | Pipe Wall Thickness | 20095 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.675 | CML-46 | CML: Pipe Length | 3 | 2018-03-26 | 2017-01-05 | 2014-05-29 07:00 | 15.88 | 1.2593 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.7 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.82 | -146.0003 | 21.9 | 21.7 | 20.7 | 22.4 | 0.71356
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38488-09C02-P | CML-10 | 50-CG-38488-09C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23599 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 9.125 | CML-10 | CML: Elbow | 3 | 2055-06-15 | 2044-07-16 | 2015-09-15 15:30 | 2.5 | 0.14833 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 0.68837 | 8.9 | 8.4 | 9.1 | 10.1 | 0.71356
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-16 | 300-PF-20003-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21754 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 9.625 | CML-16 | CML: Elbow | 6 | 2016-05-04 | 2015-08-16 | 2014-10-01 07:00 | 2.5 | 4.0223 | A1: Outside Quadrant |  | 8.27 | 2.5 | 5.385 | 8.9 | 12 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9.4 | 10.6 | 9.6 | 0.71356
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FH-43308-01C02 | CML-5 | 50-FH-43308-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20442 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.35 | CML-5 | CML: Pipe Length | 3 | 2023-09-14 | 2024-10-22 | 2014-07-26 07:00 | 2.5 | 0.29527 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-FH-43308-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 5.5 | 5.4 | 0.1291
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FH-43308-01C02 | CML-2 | 50-FH-43308-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20439 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.4 | CML-2 | CML: Elbow | 3 | 2023-09-14 | 2024-10-22 | 2014-07-26 07:00 | 2.5 | 0.29527 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FH-43308-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.5 | 5.4 | 5.2 | 0.14142
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-5 | 200-PG-23007-09C03-PA CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20692 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 |  |  | John Wilson | 2017-03-23 09:55 | [32 empty] | 21.025 | CML-5 | CML: Fitting | 6 | 2048-07-09 | 2041-02-04 | 2014-06-30 13:00 | 10.22 | 0.29604 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 20.3 | 6 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.08 |  | 20.8 | 22 | 20.3 | 21 | 0.71356
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-14 | 300-PG-23001-03C03 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 10964 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 17.475 | CML-14 | CML: Pipe Length | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 16.5 | 6 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.28 |  | 17.5 | 18.2 | 16.5 | 17.7 | 0.71356
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-11 | 250-PW-20039-01C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5843 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 9.1 | CML-11 | CML: Reducing Tee | 6 | 2028-09-26 | 2027-11-13 | 2014-06-24 13:00 | 2.5 | 0.44152 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.8 | 12 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9.5 | 8.9 | 9.2 | 0.31623
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-9 | 80-PG-23025-06C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 13080 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 19.675 | CML-9 | CML: Elbow | 6 | 2096-09-16 | 2085-01-22 | 2014-02-07 11:00 | 2.8 | 0 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 18.8 | 12 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16 |  | 18.8 | 19.9 | 20.5 | 19.5 | 0.71356
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-20 | 80-PW-44016-01C02-P CML-20 | yes | FPSO 2015 | Pipe Wall Thickness | 22922 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.225 | CML-20 | CML: Elbow | 3 | 2021-09-21 | 2022-09-09 | 2015-05-02 07:00 | 2.5 | 0.35964 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.35784 | 4.8 | 5.4 | 5.4 | 5.3 | 0.28723
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2398 | Rope Access | 2014-03-19 09:30 | 2014-03-19 11:00 | [36 empty] | 6.6 | CML-4 | CML: type TBC | 3 | 2022-03-11 | 2022-02-15 | 2014-03-19 09:30 | 2.5 | 0.43841 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 300 | 6.35 | 300-FL-43509-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.4 | 7 | 6 | 6 | 0.71181
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43121-01C02 | CML-3 | 150-FH-43121-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1766 | Rope access | 2014-04-27 09:30 | 2014-04-27 11:00 | [36 empty] | 7.8 | CML-3 | CML: Elbow | 3 | 2026-11-13 | 2025-10-24 | 2014-04-27 09:30 | 2.5 | 0.34247 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.8 | 12 O'Clock | 150 | 7.11 | 150-FH-43121-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 8.4 | 8.2 | 7.8 | 0.71181
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-29 | 300-PF-20500-03C03-P CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 21649 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.7 | CML-29 | CML: Pipe Length | 6 | 2086-05-06 | 2073-03-25 | 2014-09-27 07:00 | 4.9 | 0.12839 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 14.1 | 15.1 | 14.1 | 15.5 | 0.71181
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7708 |  | 2015-01-09 07:00 | 2015-01-09 10:00 | [36 empty] | 7 | CML-4 | CML: Elbow | 3 | 2031-02-07 | 2030-12-22 | 2015-01-09 07:00 | 2.5 | 0.21752 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 200 | 6.35 | 200-WC-40036-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.6 | 7.4 | 7 | 6 | 0.71181
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-20 | 200-PL-20019-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23481 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 6.25 | CML-20 | CML: Fitting | 3 | 2028-06-05 | 2028-04-25 | 2015-07-24 07:00 | 2.5 | 0.25629 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | -0.36869 | 6.1 | 5.8 | 6.6 | 6.5 | 0.36968
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45044-03C02 | CML-1 | 50-FG-45044-03C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23590 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 9.2 | CML-1 | CML: Elbow | 3 | 2115-07-07 | 2089-01-02 | 2015-09-15 15:30 | 2.5 | 0.06108 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 0.77442 | 9.2 | 8.8 | 8.6 | 10.2 | 0.71181
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-9 | 150-PG-23506-25C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2783 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.9 | CML-9 | CML: Elbow | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 22.3 | 6 O'Clock | 50 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.42 |  | 23.7 | 22.3 | 22.3 | 23.3 | 0.71181
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-8 | 250-PW-20039-01C03-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22972 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.05 | CML-8 | CML: Elbow | 6 | 2041-02-09 | 2039-07-15 | 2015-05-04 07:00 | 2.5 | 0.24427 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 8.8 | 3 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 | 0.58167 | 9.1 | 8.8 | 8.9 | 9.4 | 0.26458
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23012-25C02-A | CML-2 | 150-PG-23012-25C02-A CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 20536 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 22.2 | CML-2 | CML: Reducer | 3 | 2020-07-09 | 2018-09-21 | 2014-05-30 09:30 | 15.88 | 0.85375 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.1 | 6 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 | 0 | 21.1 | 21.1 | 21.1 | 25.5 | 2.2
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23012-25C02-A | CML-6 | 150-PG-23012-25C02-A CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 13032 |  | 2014-01-11 09:00 | 2014-01-11 10:30 | [36 empty] | 21.375 | CML-6 | CML: Pipe Length | 3 | 2017-10-20 | 2016-09-10 | 2014-01-11 09:00 | 15.88 | 1.3827 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.1 | 9 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 |  | 21.1 | 22.1 | 21.2 | 21.1 | 0.48563
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H |  | 50-CG-38454-01C02-H |  | FPSO 2015 | Pipe Wall Thickness | 23683 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 7.075 | 50-CG-38454-01C02-H | Piping | 3 | 2043-10-24 |  | 2015-10-30 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.1 | 3 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7.2 | 6.1 | 7.2 | 7.8 | 0.70887
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23040-03C03 | CML-15 | 50-PL-23040-03C03 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10200 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.525 | CML-15 | CML: type TBC | 6 | 2016-09-01 | 2016-08-09 | 2013-11-08 | 2.5 | 1.9163 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 6 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9.4 | 8.8 | 7.9 | 8 | 0.70887
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-24 | 100-WC-40516-1CG CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 8697 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:58 | [32 empty] | 9.075 | CML-24 | CML: Elbow | 3 | 2077-12-11 | 2061-08-26 | 2015-02-13 07:00 | 2.5 | 0.09385 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.4 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.8 | 8.7 | 8.4 | 10.4 | 0.89954
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57301-01C02 | CML-8 | 50-DC-57301-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5668 | Rope access | 2014-06-21 13:00 | 2014-06-21 14:00 | Check Corrosion Rate of 0.322mm/ yr | [35 empty] | 5.275 | CML-8 | CML: Elbow | 3 | 2022-11-08 | 2023-11-13 | 2014-06-21 13:00 | 2.5 | 0.32188 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DC-57301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.2 | 5.3 | 0.095743
PG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45306-03C03-P | CML-4 | 80-FG-45306-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22088 | Protective mesh removed | 2014-07-02 11:00 | 2014-07-02 12:00 | [36 empty] | 10.575 | CML-4 | CML: Pipe Length | 6 | 2019-12-19 | 2018-12-20 | 2014-07-02 11:00 | 2.5 | 1.3165 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 9.7 | 6 O'Clock | 80 | 11.13 | 80-FG-45306-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 11.1 | 11.2 | 9.7 | 10.3 | 0.70887
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-4 | 100-FG-45304-03C02 CML-4 | no | FPSO 2014 | Pipe Wall Thickness | 22060 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 5.225 | CML-4 | CML: type TBC | 3 | 2017-08-17 | 2017-04-25 | 2014-05-25 07:00 | 2.5 | 0.83535 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.2 | 6 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.2 | 5.3 | 0.05
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-1 | 100-FG-45304-03C02 CML-1 | no | FPSO 2014 | Pipe Wall Thickness | 22057 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 5.525 | CML-1 | CML: type TBC | 3 | 2017-08-17 | 2017-04-25 | 2014-05-25 07:00 | 2.5 | 0.83535 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.76 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.2 | 5.5 | 5.7 | 0.23629
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43142-01C02 | CML-1 | 100-FH-43142-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10519 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 8.375 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-15 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.4 | 12 O'Clock | 100 | 6.02 | 100-FH-43142-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 9.1 | 8.5 | 8.5 | 0.70887
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-4 | 50-CG-38474-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23628 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 4.775 | CML-4 | CML: Elbow | 3 | 2017-08-15 | 2018-01-27 | 2015-10-28 07:00 | 2.5 | 0.72229 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.8 | 3 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 5.3 | 3.8 | 4.7 | 5.3 | 0.70887
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-1 | 50-PL-20033-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21830 |  | 2014-10-12 07:00 | 2014-10-12 12:00 | [36 empty] | 6.075 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0 | 5.8 | 6 | 6.6 | 5.9 | 0.3594
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-17 | 300-PW-44003-01C03 CML-17 | yes | FPSO 2014 | Pipe Wall Thickness | 21859 | Reviewed 21/11/14. FFS. Recheck in Oct. 18. | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 9.675 | CML-17 | CML: Elbow | 6 | 2021-01-28 | 2020-03-10 | 2014-10-19 07:00 | 2.5 | 1.0185 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 8.9 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.6 | 10.7 | 8.9 | 9.5 | 0.75
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-12 | 50-WC-40451-01C02 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10152 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 1.224mm/ yr | [35 empty] | 5.025 | CML-12 | CML: Reducer | 3 | 2015-11-24 | 2016-02-29 | 2013-11-09 | 2.5 | 1.2242 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5 | 5.1 | 5 | 0.05
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-13 | 250-PW-44509-01C03-P CML-13 | yes | FPSO 2015 | Pipe Wall Thickness | 22998 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.45 | CML-13 | CML: Elbow | 6 | 2048-08-24 | 2046-08-23 | 2015-05-05 07:00 | 2.5 | 0.19203 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.9 | 12 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | -0.18528 | 8.9 | 9.3 | 9.3 | 10.3 | 0.59722
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-32 | 50-CG-38452-09C02-P CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 20086 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.3 | CML-32 | CML: Pipe Length | 3 | 2017-07-26 | 2016-07-08 | 2014-05-29 07:00 | 15.88 | 1.4608 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 | 182.5007 | 20.5 | 21.1 | 22.2 | 21.4 | 0.70711
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-32 | 50-CG-38452-09C02-P CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 2806 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.3 | CML-32 | CML: Pipe Length | 3 | 2016-09-16 | 2015-11-16 | 2014-03-15 09:00 | 15.88 | 1.8417 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 |  | 20.5 | 21.1 | 22.2 | 21.4 | 0.70711
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38471-01C02-P | CML-4 | 50-CG-38471-01C02-P CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 23623 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 3.75 | CML-4 | CML: Pipe Length | 3 | 2016-05-31 | 2016-09-26 | 2015-10-28 07:00 | 2.5 | 1.0129 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.1 | 9 O'Clock | 50 | 5.54 | 50-CG-38471-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 4.5 | 4.2 | 3.2 | 3.1 | 0.70475
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-11 | 80-PW-44016-01C02-P CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 22913 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5 | CML-11 | CML: Equal Tee | 3 | 2021-09-21 | 2022-09-09 | 2015-05-02 07:00 | 2.5 | 0.35964 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 1.0735 | 4.8 | 5 | 4.8 | 5.4 | 0.28284
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-10 | 250-PG-20036-01C03-P CML-10 | yes | FPSO 2016 | Pipe Wall Thickness | 24415 | Re-check as requested by N.Sequera | 2016-07-06 07:00 | 2016-07-06 15:00 | Check Corrosion Rate of 0.603mm/ yr | 41 | [34 empty] | 8.45 | CML-10 | CML: Elbow | 6 | 2024-08-17 | 2023-12-28 | 2016-07-06 07:00 | 2.5 | 0.60334 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.4 | 12 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | 0.31197 | 7.4 | 8.7 | 8.8 | 8.9 | 0.70475
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-11 | 150-FH-43518-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2711 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.25 | CML-11 | CML: Elbow | 3 | 2018-06-12 | 2017-08-05 | 2014-03-12 09:00 | 1.23 | 1.168 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.2 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.97 | 0 | 6.2 | 7.7 | 7.6 | 7.5 | 0.70475
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-17 | 50-DH-56137-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 13088 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 18.85 | CML-17 | CML: Pipe Length | 6 | 2096-09-16 | 2085-01-22 | 2014-02-07 11:00 | 2.8 | 0 | A4: Left Quadrant |  | 5.13 | 2.8 | 3.965 | 17.8 | 9 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15 |  | 19.2 | 19.1 | 19.3 | 17.8 | 0.70475
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-15 | 50-PL-23514-01C03 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8648 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:23 | [32 empty] | 9.45 | CML-15 | CML: Elbow | 6 | 2057-07-06 | 2056-08-30 | 2015-02-10 11:30 | 2.5 | 0.14141 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 6 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.5 | 10.2 | 8.5 | 9.6 | 0.70475
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-17 | 80-CG-38459-09C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21401 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 17.15 | CML-17 | CML: Equal Tee | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A3: Inside Quadrant |  | 6.7 | 4.1 | 5.4 | 16.3 | 6 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.2 |  | 17.3 | 17 | 16.3 | 18 | 0.70475
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-28 | 300-PF-20003-03C03-P CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 21766 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 18.85 | CML-28 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 18 | 12 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.1 |  | 18 | 19.7 | 19 | 18.7 | 0.70475
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56012-01C02 | CML-7 | 80-DH-56012-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3473 | Rope Access | 2014-05-13 10:30 | 2014-05-13 12:00 | [36 empty] | 5.65 | CML-7 | CML: type TBC | 3 | 2019-03-15 | 2019-11-17 | 2014-05-13 10:30 | 2.5 | 0.51625 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 6 O'Clock | 80 | 5.49 | 80-DH-56012-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 6.1 | 5 | 6.4 | 0.70475
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-12 | 50-PW-44015-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5722 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 5.3 | CML-12 | CML: Elbow | 3 | 2019-05-16 | 2020-01-04 | 2014-06-22 10:00 | 2.5 | 0.51007 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.48793 | 5 | 5.5 | 5.1 | 5.6 | 0.29439
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38477-01C02-P | CML-10 | 50-CG-38477-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5507 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 18.425 | CML-10 | CML: Pipe Length | 3 | 2018-04-15 | 2017-08-03 | 2014-05-31 07:00 | 14.06 | 0.86167 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.4 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.34 | 0 | 17.4 | 18.6 | 18.7 | 19 | 0.70415
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38477-01C02-P | CML-10 | 50-CG-38477-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20655 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 18.425 | CML-10 | CML: Pipe Length | 3 | 2018-04-15 | 2017-08-03 | 2014-05-31 07:00 | 14.06 | 0.86167 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.4 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.34 | 0.45673 | 17.4 | 18.6 | 18.7 | 19 | 0.70415
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-1 | 50-PL-20033-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2265 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 6.1 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-16 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 6.6 | 6.1 | 0.3559
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-5 | 150-PG-20054-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21516 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 12.875 | CML-5 | CML: Equal Tee | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 12.3 | 3 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 12.6 | 12.3 | 13.9 | 12.7 | 0.70415
FH02 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43313-01S01-P | CML-6 | 150-FH-43313-01S01-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20480 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.825 | CML-6 | CML: Elbow | 1 | 2042-10-28 | 2034-02-21 | 2014-10-03 07:00 | 2.5 | 0.15666 | A4: Left Quadrant |  | 6.11 | 2.5 | 3.8606 | 6.9 | 9 O'Clock | 150 | 7.11 | 150-FH-43313-01S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 8 | 8.6 | 7.8 | 6.9 | 0.70415
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-55 | 300-PF-20001-03C03-P CML-55 |  | FPSO 2014 | Pipe Wall Thickness | 21193 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.801mm/ yr | 40 | Kirstie Albone | 2017-03-23 13:49 | [32 empty] | 12.575 | CML-55 | CML: Elbow | 6 | 2018-01-15 | 2017-02-03 | 2014-07-16 07:30 | 4.1 | 2.1972 | A4: Left Quadrant |  | 8.27 | 4.1 | 6.185 | 11.8 | 9 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 13.5 | 12.6 | 12.4 | 11.8 | 0.70415
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-9 | 400-FH-43500-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5645 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 9.7 | CML-9 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 9 | 3 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 10.4 | 9 | 10.2 | 9.2 | 0.70238
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-1 | 100-WC-40027-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23421 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | Check Corrosion Rate of 0.476mm/ yr |  | Nestor | 2016-04-01 | asd vdsf f svadf | [31 empty] | 5 | CML-1 | CML: Elbow | 3 | 2020-10-21 | 2021-01-18 | 2015-07-23 07:00 | 2.5 | 0.47591 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 9 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0 | 5 | 5 | 5 | 5 | 0
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-19 | 300-PF-20003-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21757 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.05 | CML-19 | CML: Fitting | 6 | 2025-02-05 | 2022-12-30 | 2014-10-01 07:00 | 4.9 | 0.80147 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 14.8 | 13.8 | 14.4 | 13.2 | 0.7
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-7 | 300-PG-20037-03C03-PA CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23342 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.45 | CML-7 | CML: Fitting | 6 | 2046-11-17 | 2041-05-17 | 2015-07-20 07:00 | 5.33 | 0.26697 | A1: Outside Quadrant |  | 8.27 | 5.33 | 6.8 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.37 | 0 | 13.7 | 15.3 | 14.7 | 14.1 | 0.7
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-4 | 200-FH-43003-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12527 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 10.2 | CML-4 | CML: Tee | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 11:30 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 9.7 | 3 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.36 |  | 9.9 | 9.7 | 11 |  | 0.7
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43517-01C02 | CML-2 | 150-FH-43517-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20470 | Rope Access | 2014-05-27 14:00 | 2014-05-27 15:00 | [36 empty] | 7.35 | CML-2 | CML: type TBC | 3 |  |  | 2014-05-27 14:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.5 | 3 O'Clock | 150 |  | 150-FH-43517-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.1 | 6.5 | 7.7 | 8.1 | 0.7
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-10 | 50-PW-44012-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2024 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 5.35 | CML-10 | CML: Elbow | 3 | 2018-01-11 | 2018-07-11 | 2014-03-27 09:30 | 2.5 | 0.65833 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 5.5 | 5.6 | 0.26458
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-23 | 300-PF-20501-03C03-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21699 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 15.025 | CML-23 | CML: Elbow | 6 | 2086-07-01 | 2073-05-09 | 2014-09-28 07:00 | 4.9 | 0.12813 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 15.1 | 15.8 | 14.1 | 15.1 | 0.6994
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-29 | 50-DH-56137-01C02 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 21113 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 5.675 | CML-29 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 6.6 | 5.8 | 5 | 0.6994
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-2 | 80-PW-44016-01C02-P CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 22904 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.175 | CML-2 | CML: Elbow | 3 | 2021-09-21 | 2022-09-09 | 2015-05-02 07:00 | 2.5 | 0.35964 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0 | 4.8 | 5.3 | 5.4 | 5.2 | 0.263
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-1 | 150-PG-23506-25C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2775 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.375 | CML-1 | CML: Pipe Length | 3 | 2027-01-22 | 2023-08-11 | 2014-03-15 09:00 | 15.88 | 0.44454 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 21.6 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.72 |  | 22.3 | 21.6 | 22.3 | 23.3 | 0.6994
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20044-03C03-P | CML-7 | 80-PG-20044-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21455 | Protective mesh removed | 2014-06-29 09:30 | 2014-06-29 11:00 | [36 empty] | 11.225 | CML-7 | CML: Elbow | 6 | 2024-08-12 | 2022-11-28 | 2014-06-29 09:30 | 2.5 | 0.77009 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 10.3 | 3 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 11.9 | 10.3 | 11.1 | 11.6 | 0.6994
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-5 | 300-PF-20001-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21143 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.685mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:45 | [32 empty] | 14.275 | CML-5 | CML: Pipe Length | 6 | 2027-02-01 | 2024-08-17 | 2014-07-16 07:30 | 4.9 | 0.68497 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 6 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 15.2 | 14.2 | 13.5 | 14.2 | 0.6994
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56066-01C02 | CML-2 | 50-DH-56066-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3279 | Rope Access | 2014-05-09 14:00 | 2014-05-09 15:00 | [36 empty] | 6 | CML-2 | CML: type TBC | 3 | 2021-10-20 | 2022-09-13 | 2014-05-09 14:00 | 2.5 | 0.36225 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DH-56066-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.9 | 5.9 | 5.2 | 6 | 0.69761
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38494-01C02 | CML-4 | 25-CG-38494-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10387 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.4 | CML-4 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 12 O'Clock | 25 | 6.35 | 25-CG-38494-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.6 | 6.1 | 6.7 | 7.2 | 0.69761
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-4 | 80-DH-56140-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5056 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 10.4 | CML-4 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 9.5 | 6 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.9 | 10.2 | 9.5 | 11 | 0.69761
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-26 | 300-PF-20001-03C03-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 21164 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.329mm/ yr | 40 | Kirstie Albone | 2017-03-23 16:16 | [32 empty] | 14.8 | CML-26 | CML: Fitting | 6 | 2041-11-11 | 2036-09-30 | 2014-07-16 07:30 | 4.9 | 0.32914 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 15.4 | 14.6 | 15.3 | 13.9 | 0.69761
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-19 | 400-FH-43508-01C02 CML-19 | yes | FPSO 2015 | Pipe Wall Thickness | 6568 | Rope Access.Line is FFS. Action: to recheck in a year (Mar. 2016) to confirm CR. | 2015-03-30 07:00 | 2015-03-30 15:00 |  |  | Administrator | 2015-09-07 16:18 | [32 empty] | 7.4 | CML-19 | CML: Elbow | 3 | 2020-11-30 | 2019-12-05 | 2015-03-30 07:00 | 2.5 | 0.72202 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 6.6 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.7 | 8.2 | 7.1 | 6.6 | 0.69761
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-12 | 50-PW-44015-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22717 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.35 | CML-12 | CML: Elbow | 3 | 2024-02-23 | 2025-04-19 | 2015-04-28 07:00 | 2.5 | 0.28307 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0 | 5.6 | 5.5 | 5 | 5.3 | 0.26458
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-18 | 100-DC-57036-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1424 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.965mm/ yr | [35 empty] | 5.35 | CML-18 | CML: type TBC | 3 | 2017-01-22 | 2017-03-07 | 2014-04-07 07:00 | 2.5 | 0.96458 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.3 | 5.6 | 5.2 | 0.17321
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-10 | 100-DC-57036-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1416 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.965mm/ yr | [35 empty] | 5.975 | CML-10 | CML: type TBC | 3 | 2017-01-22 | 2017-03-07 | 2014-04-07 07:00 | 2.5 | 0.96458 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.2 | 5.5 | 7.6 | 1.0966
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57042-01C02 | CML-3 | 50-DC-57042-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1370 | Rope access | 2014-04-05 09:30 | 2014-04-05 10:30 | Check Corrosion Rate of 0.402mm/ yr | [35 empty] | 5.475 | CML-3 | CML: type TBC | 3 | 2020-12-18 | 2021-10-10 | 2014-04-05 09:30 | 2.5 | 0.4024 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DC-57042-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.8 | 5.3 | 5.2 | 5.6 | 0.27538
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57042-01C02 | CML-1 | 50-DC-57042-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1368 | Rope access | 2014-04-05 09:30 | 2014-04-05 10:30 | Check Corrosion Rate of 0.402mm/ yr | [35 empty] | 5.475 | CML-1 | CML: type TBC | 3 | 2020-12-18 | 2021-10-10 | 2014-04-05 09:30 | 2.5 | 0.4024 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DC-57042-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.6 | 5.5 | 5.2 | 0.1893
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45044-03C02 | CML-6 | 50-FG-45044-03C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21208 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 9.6 | CML-6 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.6 | 3 O'Clock | 200 | 6.35 | 200-PL-20012-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.7 | 8.6 | 9.9 | 10.2 | 0.69761
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57067-01C02 | CML-1 | 50-DC-57067-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1338 | Rope access | 2014-04-04 08:00 | 2014-04-04 09:00 | Check Corrosion Rate of 0.404mm/ yr | [35 empty] | 5.85 | CML-1 | CML: type TBC | 3 | 2020-12-08 | 2021-09-29 | 2014-04-04 08:00 | 2.5 | 0.4038 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DC-57067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 6.7 | 5.2 | 5.9 | 0.63509
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57068-01C02 | CML-4 | 50-DC-57068-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1332 | Rope access | 2014-04-04 07:00 | 2014-04-04 08:00 | Check Corrosion Rate of 0.404mm/ yr | [35 empty] | 5.3 | CML-4 | CML: type TBC | 3 | 2020-12-08 | 2021-09-29 | 2014-04-04 07:00 | 2.5 | 0.40385 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 5.4 | 5.3 | 0.08165
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57068-01C02 | CML-2 | 50-DC-57068-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1330 | Rope access | 2014-04-04 07:00 | 2014-04-04 08:00 | Check Corrosion Rate of 0.404mm/ yr | [35 empty] | 5.375 | CML-2 | CML: type TBC | 3 | 2020-12-08 | 2021-09-29 | 2014-04-04 07:00 | 2.5 | 0.40385 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-DC-57068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.2 | 5.6 | 5.4 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-32 | 50-DH-56070-01C02 CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 3248 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.1 | CML-32 | CML: type TBC | 3 | 2021-10-17 | 2022-09-10 | 2014-05-09 07:00 | 2.5 | 0.36256 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.9 | 6.6 | 6.7 | 5.2 | 0.69761
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40013-01C02 | CML-2 | 50-WC-40013-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1557 | Rope Access | 2014-04-09 10:00 | 2014-04-09 11:00 | Check Corrosion Rate of 0.514mm/ yr | [35 empty] | 5.825 | CML-2 | CML: Pipe Length | 3 | 2019-04-29 | 2019-12-17 | 2014-04-09 10:00 | 2.5 | 0.51406 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-WC-40013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.6 | 5.9 | 5.7 | 5.1 | 0.61847
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-22 | 300-PG-20005-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 6178 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.2 | CML-22 | CML: Reducing Tee | 6 | 2025-05-14 | 2023-03-21 | 2014-07-11 07:30 | 4.9 | 0.78347 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 15.1 | 13.4 | 14.2 | 14.1 | 0.69761
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56039-01C02 | CML-2 | 80-DH-56039-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20919 | Rope Access | 2014-05-21 11:00 | 2014-05-21 12:00 | [36 empty] | 5.35 | CML-2 | CML: Elbow | 3 | 2017-02-01 | 2017-07-07 | 2014-05-21 11:00 | 2.5 | 0.81349 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 3 O'Clock | 80 | 5.49 | 80-DH-56039-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.8 | 4.7 | 5.9 | 6 | 0.69522
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56097-01C02 | CML-6 | 50-DN-56097-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1328 |  | 2014-04-01 07:00 | 2014-04-01 08:00 | [36 empty] | 5.575 | CML-6 | CML: type TBC | 3 | 2020-11-11 | 2021-08-30 | 2014-04-01 07:00 | 2.5 | 0.40783 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DN-56097-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.6 | 5.9 | 5.6 | 0.28723
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56134-01C02 | CML-4 | 50-DN-56134-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1316 |  | 2014-03-31 10:00 | 2014-03-31 10:15 | [36 empty] | 5.325 | CML-4 | CML: type TBC | 3 | 2020-11-03 | 2021-08-22 | 2014-03-31 10:00 | 2.5 | 0.40901 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-DN-56134-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.6 | 5.3 | 0.1893
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56134-01C02 | CML-3 | 50-DN-56134-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1315 |  | 2014-03-31 10:00 | 2014-03-31 10:15 | [36 empty] | 5.525 | CML-3 | CML: type TBC | 3 | 2020-11-03 | 2021-08-22 | 2014-03-31 10:00 | 2.5 | 0.40901 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DN-56134-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.5 | 5.2 | 5.8 | 0.25
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56095-01C02 | CML-2 | 50-DN-56095-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1308 |  | 2014-03-31 08:00 | 2014-03-31 09:00 | [36 empty] | 5.55 | CML-2 | CML: type TBC | 3 | 2020-11-03 | 2021-08-21 | 2014-03-31 08:00 | 2.5 | 0.40912 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DN-56095-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.6 | 5.7 | 5.7 | 0.23805
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56094-01C02 | CML-2 | 50-DN-56094-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1305 |  | 2014-03-31 07:00 | 2014-03-31 08:00 | [36 empty] | 5.6 | CML-2 | CML: type TBC | 3 | 2020-11-02 | 2021-08-20 | 2014-03-31 07:00 | 2.5 | 0.40918 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-DN-56094-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.2 | 6.1 | 5.5 | 0.37417
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56094-01C02 | CML-1 | 50-DN-56094-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1304 |  | 2014-03-31 07:00 | 2014-03-31 08:00 | [36 empty] | 5.425 | CML-1 | CML: type TBC | 3 | 2020-11-02 | 2021-08-20 | 2014-03-31 07:00 | 2.5 | 0.40918 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DN-56094-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.6 | 5.2 | 5.6 | 0.20616
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-16 | 200-PG-23007-09C03-PA CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20703 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 19.55 | CML-16 | CML: Fitting | 6 | 2019-12-12 | 2018-07-25 | 2014-06-30 13:00 | 10.22 | 1.5912 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 18.9 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.68 |  | 19.6 | 20.5 | 19.2 | 18.9 | 0.69522
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-2 | 150-PG-20054-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21513 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 12.65 | CML-2 | CML: Elbow | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 12 | 6 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 13.2 | 13.3 | 12 | 12.1 | 0.69522
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H |  | 50-CG-38454-01C02-H |  | FPSO 2015 | Pipe Wall Thickness | 23684 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 6.85 | 50-CG-38454-01C02-H | Piping | 3 | 2043-10-24 |  | 2015-10-30 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5.9 | 3 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.5 | 5.9 | 6.8 | 7.2 | 0.69522
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56130-01C02 | CML-5 | 50-DH-56130-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21057 | Rope Access | 2014-05-15 13:00 | 2014-05-15 14:00 | [36 empty] | 6.55 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-15 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56130-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 5.9 | 7.5 | 6.6 | 0.69522
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-12 | 100-FG-45001-09C02 CML-12 | Yes | FPSO 2015 | Pipe Wall Thickness | 23317 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.75 | CML-12 | CML: type TBC | 3 | 2054-07-05 | 2043-07-19 | 2015-07-11 07:00 | 4.7 | 0.15637 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 10.8 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | -0.30151 | 10.8 | 11.7 | 12.4 | 12.1 | 0.69522
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56019-01C02 | CML-6 | 80-DH-56019-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3466 | Rope Access | 2014-05-13 09:30 | 2014-05-13 10:30 | [36 empty] | 5.75 | CML-6 | CML: type TBC | 3 | 2018-03-22 | 2018-10-12 | 2014-05-13 09:30 | 2.5 | 0.62169 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-DH-56019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 6.6 | 4.9 | 5.7 | 5.8 | 0.69522
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-1 | 250-PW-44509-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22986 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.7 | CML-1 | CML: Pipe Length | 6 | 2048-08-24 | 2046-08-23 | 2015-05-05 07:00 | 2.5 | 0.19203 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.9 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | 0.18528 | 9.7 | 10.3 | 8.9 | 9.9 | 0.58878
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-3 | 50-FG-45501-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 6586 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 6.375 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-03-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 7.4 | 6.2 | 5.9 | 0.69462
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43175-01C02 | CML-1 | 150-FL-43175-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12912 |  | 2014-02-03 07:00 | 2014-02-03 08:00 | [36 empty] | 7.325 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.3 | 3 O'Clock | 100 | 6.02 | 100-FL-43175-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.8 | 6.3 | 7.5 | 7.7 | 0.69462
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-8 | 150-FH-43518-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2708 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.575 | CML-8 | CML: Pipe Length | 3 | 2022-05-23 | 2020-11-14 | 2014-03-12 09:00 | 1.23 | 0.65459 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 | 0 | 7.9 | 7.6 | 6.6 | 8.2 | 0.69462
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-8 | 150-FH-43518-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 347 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.575 | CML-8 | CML: Pipe Length | 3 | 2022-05-19 | 2020-11-10 | 2014-03-12 | 1.23 | 0.65546 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 |  | 7.9 | 7.6 | 6.6 | 8.2 | 0.69462
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21206 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 8.225 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 9 O'Clock | 200 | 6.35 | 200-PL-20012-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8.4 | 8.6 | 8.7 | 7.2 | 0.69462
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-8 | 80-PW-44035-01C02-P CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 23272 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.025 | CML-8 | CML: Elbow | 3 | 2021-11-03 | 2022-10-28 | 2015-05-12 07:00 | 2.5 | 0.35457 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 3 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.16977 | 5 | 4.8 | 5.2 | 5.1 | 0.17078
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-3 | 150-PG-20507-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2847 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.775 | CML-3 | CML: type TBC | 6 | 2019-02-17 | 2018-04-18 | 2014-03-16 07:00 | 2.5 | 1.4813 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 9.8 | 3 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.8 | 9.8 | 11.4 | 11.1 | 0.69462
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-17 | 50-DH-56137-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23445 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 18.325 | CML-17 | CML: Elbow | 3 | 2023-09-17 | 2019-05-19 | 2015-07-23 07:00 | 2.5 | 1.8383 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.5 | 12 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15 | 0.092007 | 17.5 | 18.3 | 19.2 | 18.3 | 0.69462
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-3 | 80-PW-44035-01C02-P CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 23267 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.575 | CML-3 | CML: Elbow | 3 | 2023-04-09 | 2024-06-01 | 2015-05-12 07:00 | 2.5 | 0.30319 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 20 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.67907 | 6 | 4.9 | 5.2 | 6.2 | 0.62383
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-9 | 50-WC-40071-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1944 | Rope Access. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Mar. 2020). RBI to be updated | 2014-03-26 09:30 | 2014-03-26 10:30 | Check Corrosion Rate of 0.416mm/ yr |  | Administrator | 2015-09-08 12:57 | [32 empty] | 5.45 | CML-9 | CML: Pipe Length | 3 | 2020-09-20 | 2021-07-03 | 2014-03-26 09:30 | 2.5 | 0.41589 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.4 | 5.6 | 5.2 | 0.19149
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-5 | 250-PW-44010-01C03-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23027 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 9.4 | CML-5 | CML: Reducing Tee | 6 | 2028-06-02 | 2027-07-26 | 2015-05-06 07:00 | 2.5 | 0.45088 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.4 | 12 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 0.80881 | 8.4 | 9.6 | 9.6 | 10 | 0.69282
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-6 | 50-DC-57056-03C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1138 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | Check Corrosion Rate of 0.423mm/ yr |  | Emilyn Chan | 2017-05-10 02:21 | [32 empty] | 5.475 | CML-6 | CML: type TBC | 3 | 2020-08-05 | 2020-07-19 | 2014-03-21 07:00 | 2.5 | 0.42313 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.8 | 5.2 | 5.4 | 0.25
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-3 | 100-DC-57075-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2422 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 1.024mm/ yr | [35 empty] | 5.875 | CML-3 | CML: type TBC | 3 | 2016-11-06 | 2016-12-18 | 2014-03-20 07:00 | 2.5 | 1.024 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.3 | 5.2 | 6 | 6 | 0.4717
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-2 | 100-DC-57037-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2353 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | Check Corrosion Rate of 1.03mm/ yr | [35 empty] | 6.025 | CML-2 | CML: type TBC | 3 | 2016-10-30 | 2016-12-10 | 2014-03-18 13:00 | 2.5 | 1.0301 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 6 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.4 | 6.7 | 5.2 | 5.8 | 0.66521
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20302-03C03-P | CML-1 | 200-PG-20302-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5854 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 12.725 | CML-1 | CML: Pipe Length | 6 | 2023-06-09 | 2021-08-16 | 2014-06-25 10:30 | 3.3 | 0.93725 | A2: Right Quadrant |  | 6.7 | 3.3 | 5 | 11.7 | 3 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 13.2 | 11.7 | 13 | 13 | 0.68981
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-8 | 100-WC-40027-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 840 |  | 2014-04-02 09:00 | 2014-04-02 10:00 | Check Corrosion Rate of 1.1mm/ yr |  | Nestor | 2016-04-01 | [32 empty] | 5.275 | CML-8 | CML: Elbow | 3 | 2016-08-12 | 2016-09-19 | 2014-04-02 09:00 | 2.5 | 1.0996 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 9 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 5.6 | 5.2 | 5.1 | 0.22174
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20015-01C02-P | CML-3 | 200-PL-20015-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23461 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 6.1 | CML-3 | CML: Fitting | 3 | 2028-06-05 | 2028-04-25 | 2015-07-24 07:00 | 2.5 | 0.25629 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 40 | 6.35 | 200-PL-20015-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.38935 | 6.1 | 6 | 5.8 | 6.5 | 0.29439
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-4 | 50-PL-23052-09C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10168 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 11.125 | CML-4 | CML: type TBC | 6 | 2017-08-07 | 2017-01-10 | 2013-11-09 | 2.81 | 1.9724 | A4: Left Quadrant |  | 5.07 | 2.81 | 3.94 | 10.2 | 9 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.39 |  | 11.6 | 11 | 11.7 | 10.2 | 0.68981
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-6 | 80-FL-43015-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20411 | Reviewed on 20/11/14. Line is FFS. Repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-20 11:27 | [32 empty] | 6.275 | CML-6 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 3 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.8 | 6 | 7.3 | 0.68981
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43303-01C02 | CML-3 | 50-FL-43303-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20459 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 6.375 | CML-3 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-FL-43303-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 7.3 | 6.5 | 5.9 | 5.8 | 0.68981
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43175-01C02 | CML-2 | 150-FL-43175-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12913 |  | 2014-02-03 07:00 | 2014-02-03 08:00 | [36 empty] | 7.575 | CML-2 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-03 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 9 O'Clock | 100 | 6.02 | 100-FL-43175-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.3 | 8.6 | 7.3 | 7.1 | 0.68981
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56108-01C02 | CML-3 | 50-DH-56108-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20989 | Rope Access | 2014-05-24 09:30 | 2014-05-24 10:30 | [36 empty] | 5.2 | CML-3 | CML: Elbow | 3 | 2016-12-15 | 2017-05-03 | 2014-05-24 09:30 | 2.5 | 0.85787 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-DH-56108-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 6.2 | 4.7 | 5.1 | 4.8 | 0.68799
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-11 | 250-PW-44509-01C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 22046 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.425 | CML-11 | CML: Elbow | 6 | 2038-10-11 | 2037-05-02 | 2014-10-20 07:00 | 2.5 | 0.26674 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.9 | 9 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.1 | 9.5 | 10.2 | 8.9 | 0.57373
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-13 | 300-PG-20005-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 6169 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 13.1 | CML-13 | CML: Reducing Tee | 6 | 2019-08-23 | 2018-07-10 | 2014-07-11 07:30 | 4.9 | 1.5039 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.6 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 12.6 | 12.7 | 13 | 14.1 | 0.68799
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-6 | 50-PW-44014-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23151 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.2 | CML-6 | CML: Pipe Length | 3 | 2024-05-01 | 2025-07-03 | 2015-05-10 07:00 | 2.5 | 0.27828 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0 | 5.5 | 5 | 5.2 | 5.1 | 0.21602
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-22 | 100-PW-20021-01C02-P CML-22 | yes | FPSO 2014 | Pipe Wall Thickness | 21825 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.475 | CML-22 | CML: Elbow | 3 | 2017-09-10 | 2017-11-01 | 2014-10-11 07:00 | 2.5 | 0.82205 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.9 | 5.3 | 5.8 | 0.46458
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20036 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 9.15 | CML-2 | CML: Equal Tee | 6 | 2015-10-22 | 2016-01-09 | 2014-05-29 07:00 | 5.22 | 2.1258 | A2: Right Quadrant |  | 4.31 | 5.22 | 4.765 | 8.2 | 3 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.98 | -0.47454 | 9.1 | 8.2 | 9.7 | 9.6 | 0.68557
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-31 | 50-DH-56137-01C02 CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 21115 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.15 | CML-31 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.5 | 6 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 7 | 6.4 | 5.5 | 5.7 | 0.68557
FH02 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43313-01S01-P | CML-4 | 150-FH-43313-01S01-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20478 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.45 | CML-4 | CML: Elbow | 1 | 2023-07-16 | 2020-07-20 | 2014-10-03 07:00 | 2.5 | 0.45505 | A2: Right Quadrant |  | 6.11 | 2.5 | 3.8606 | 6.5 | 3 O'Clock | 150 | 7.11 | 150-FH-43313-01S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.9 | 6.5 | 7.4 | 8 | 0.68557
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-17 | 100-DH-56009-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 3440 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 7.25 | CML-17 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.6 | 9 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 8.1 | 7.5 | 6.8 | 6.6 | 0.68557
FG01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-FG-45024-01C02 | CML-2 | 50-FG-45024-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5195 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 10.05 | CML-2 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.2 | 9 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.7 | 10.5 | 9.8 | 9.2 | 0.68557
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-12 | 250-PG-23005-06C03 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10058 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 16.75 | CML-12 | CML: Elbow | 6 | 2015-06-11 | 2015-01-22 | 2013-11-06 | 8.6 | 4.7589 | A4: Left Quadrant |  | 12.26 | 8.6 | 10.43 | 16.2 | 9 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 17.7 | 16.3 | 16.8 | 16.2 | 0.68557
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-3 | 50-PW-44015-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5713 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 5.225 | CML-3 | CML: Elbow | 3 | 2019-05-16 | 2020-01-04 | 2014-06-22 10:00 | 2.5 | 0.51007 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.32529 | 5.4 | 5.4 | 5 | 5.1 | 0.20616
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44027-01X01 | CML-1 | 50-PW-44027-01X01 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10338 | Deck Level | 2013-11-11 | 2013-11-11 | [36 empty] | 5.25 | CML-1 | CML: Pipe Length | 3 | 2015-12-05 | 2016-03-13 | 2013-11-11 | 2.5 | 1.2092 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-PW-44027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.4 | 5 | 5.4 | 0.19149
FG01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-FG-45024-01C02 | CML-27 | 50-FG-45024-01C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 3395 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 10.175 | CML-27 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.2 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 10.3 | 10.4 | 10.8 | 0.68496
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-2 | 50-PL-23041-06C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10215 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.475 | CML-2 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 4.4941 | A1: Outside Quadrant |  | 5.07 |  |  | 9.1 | 3 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 9.1 | 9.1 | 9.2 | 10.5 | 0.68496
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-5 | 100-WC-40027-01C02 CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24419 | Re-check as requested by N.Sequera | 2016-07-02 07:00 | 2016-07-02 15:00 | [36 empty] | 5.3 | CML-5 | CML: Elbow | 3 | 2025-03-23 | 2025-08-12 | 2016-07-02 07:00 | 2.5 | 0.29788 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 3 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | -0.1058 | 5.3 | 5.1 | 5.5 | 5.3 | 0.1633
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40062-01C02 | CML-5 | 100-WC-40062-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 829 |  | 2014-04-02 08:00 | 2014-04-02 09:00 | Check Corrosion Rate of 1.1mm/ yr | [35 empty] | 5.275 | CML-5 | CML: Elbow | 3 | 2016-08-12 | 2016-09-19 | 2014-04-02 08:00 | 2.5 | 1.0998 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 3 O'Clock | 100 | 6.02 | 100-WC-40062-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.1 | 5.2 | 5.4 | 0.15
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-14 | 50-CG-38476-01C02-H CML-14 | Yes | FPSO 2015 | Pipe Wall Thickness | 23646 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 9.125 | CML-14 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.5 | 6 O'Clock | 100 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.5 | 9.9 | 8.5 | 8.6 | 0.68496
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43302-01C02 | CML-20 | 250-FH-43302-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 12936 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.475 | CML-20 | CML: type TBC | 3 | 2016-05-19 | 2016-05-11 | 2014-01-26 07:00 | 2.5 | 1.2965 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 6 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.5 | 6.9 | 5.5 | 7 | 0.68496
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-34 | 300-PF-20003-03C03-P CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 21772 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.325 | CML-34 | CML: Reducing Tee | 6 | 2040-01-05 | 2035-03-25 | 2014-10-01 07:00 | 4.9 | 0.35205 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 6 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 15.3 | 14.3 | 13.8 | 13.9 | 0.68496
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-5 | 250-PW-20039-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5837 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 9.425 | CML-5 | CML: Elbow | 6 | 2032-11-17 | 2031-10-09 | 2014-06-24 13:00 | 2.5 | 0.34758 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.9 | 6 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10.1 | 9.6 | 8.9 | 9.1 | 0.53774
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-3 | 200-PG-20300-03C03-P CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24483 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.418mm/ yr |  | Kirstie Albone | 2017-03-23 10:10 | Loss within CA no further action required, include in next inspection | [31 empty] | 12.025 | CML-3 | CML: Elbow | 6 | 2035-11-14 | 2031-10-23 | 2016-07-09 07:00 | 3.3 | 0.41832 | A2: Right Quadrant |  | 6.7 | 3.3 | 5 | 11.4 | 3 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 | 0.10282 | 13 | 11.4 | 11.9 | 11.8 | 0.68496
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-14 | 250-PG-23005-06C03 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10060 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 16.525 | CML-14 | CML: Pipe Length | 6 | 2014-12-06 | 2014-08-23 | 2013-11-06 | 8.6 | 6.3759 | A2: Right Quadrant |  | 12.26 | 8.6 | 10.43 | 15.5 | 3 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 16.9 | 15.5 | 16.9 | 16.8 | 0.68496
PL03 | Montara_Topside | Yes | Flare (43) | Pipework | 50-PL-57066-01C03 | CML-19 | 50-PL-57066-01C03 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 5528 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 9.575 | CML-19 | CML: Reducing Tee | 3 | 2074-03-18 | 2063-04-04 | 2014-06-01 07:00 | 1.03 | 0 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 8.8 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.77 | -5.0538 | 10.1 | 8.8 | 9.2 | 10.2 | 0.68496
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-6 | 80-PG-20046-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21465 | Protective mesh removed | 2014-06-28 08:00 | 2014-06-28 09:00 | [36 empty] | 16.1 | CML-6 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-06-28 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 15.2 | 6 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.7 |  | 16 | 16.8 | 15.2 | 16.4 | 0.68313
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56108-01C02 | CML-2 | 50-DH-56108-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20988 | Rope Access | 2014-05-24 09:30 | 2014-05-24 10:30 | [36 empty] | 6.6 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-24 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-DH-56108-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.5 | 5.9 | 6.7 | 6.3 | 0.68313
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-21 | 50-PW-44040-01C02 CML-21 | yes | FPSO 2014 | Pipe Wall Thickness | 1996 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.45 | CML-21 | CML: Pipe Length | 3 | 2017-04-22 | 2017-09-22 | 2014-03-27 07:00 | 2.5 | 0.78051 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.9 | 5.7 | 5.3 | 0.44347
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38002-09C02-P | CML-6 | 50-CG-38002-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20797 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 |  |  | Administrator | 2015-09-07 10:59 | [32 empty] | 9.55 | CML-6 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 9 | 9 O'Clock | 50 | 8.74 | 50-CG-38002-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 10.4 | 9 | 9.8 | 9 | 0.68069
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23047-09C02-P | CML-2 | 150-PG-23047-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20582 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 14.95 | CML-2 | CML: Pipe Length | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A2: Right Quadrant |  | 11.27 | 7 | 9.135 | 14.3 | 3 O'Clock | 150 | 14.27 | 150-PG-23047-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 | 0 | 14.7 | 14.3 | 14.9 | 15.9 | 0.68069
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23047-09C02-P | CML-2 | 150-PG-23047-09C02-P CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 24258 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 14.95 | CML-2 | CML: Pipe Length | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A2: Right Quadrant |  | 11.27 | 7 | 9.135 | 14.3 | 3 O'Clock | 150 | 14.27 | 150-PG-23047-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 14.7 | 14.3 | 14.9 | 15.9 | 0.68069
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-7 | 100-WC-40027-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23427 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 |  |  | Nestor | 2016-04-01 | [32 empty] | 5.3 | CML-7 | CML: Elbow | 3 | 2021-08-11 | 2021-11-17 | 2015-07-23 07:00 | 2.5 | 0.42925 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 6 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.15307 | 5.4 | 5.3 | 5.1 | 5.4 | 0.14142
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40062-01C02 | CML-7 | 100-WC-40062-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 831 |  | 2014-04-02 08:00 | 2014-04-02 09:00 | Check Corrosion Rate of 0.98mm/ yr | [35 empty] | 5.65 | CML-7 | CML: Elbow | 3 | 2017-01-01 | 2017-02-13 | 2014-04-02 08:00 | 2.5 | 0.98024 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-WC-40062-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.1 | 5.2 | 6 | 5.3 | 0.46547
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-4 | 50-CG-38474-01C02-P CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24466 | Re-check as requested by N.Sequera | 2016-07-07 07:00 | 2016-07-07 15:00 | Check Corrosion Rate of 0.658mm/ yr | [35 empty] | 4.425 | CML-4 | CML: Elbow | 3 | 2018-01-13 | 2018-07-13 | 2016-07-07 07:00 | 2.5 | 0.6576 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.5 | 12 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 | 0.43281 | 3.5 | 4.7 | 4.4 | 5.1 | 0.68007
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-6 | 50-PW-44014-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2008 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 5.15 | CML-6 | CML: Pipe Length | 3 | 2018-01-11 | 2018-07-11 | 2014-03-27 10:00 | 2.5 | 0.65828 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.3 | 5 | 5.2 | 5.1 | 0.1291
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44025-01X01 | CML-1 | 50-PW-44025-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22741 |  | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.1 | CML-1 | CML: Pipe Length | 3 | 2024-02-23 | 2025-04-19 | 2015-04-28 07:00 | 2.5 | 0.28307 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-PW-44025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 5.015 | 5 | 5.2 | 5.2 | 5 | 0.11547
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-3 | 50-PW-44014-01X01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2005 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 5.15 | CML-3 | CML: Elbow | 3 | 2018-01-11 | 2018-07-11 | 2014-03-27 10:00 | 2.5 | 0.65828 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.2 | 5.2 | 0.1
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-13 | 200-PL-20010-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 23813 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.2 | CML-13 | CML: Fitting | 3 | 2022-08-22 | 2022-07-28 | 2014-09-25 07:00 | 2.5 | 0.41711 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 5.8 | 6.3 | 6.2 | 0.29439
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-15 | 50-PF-20300-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21581 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.225 | CML-15 | CML: type TBC | 6 | 2027-05-15 | 2027-02-06 | 2014-05-26 09:30 | 2.5 | 0.44686 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.9 | 9.5 | 9.2 | 8.3 | 0.68007
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20002-03C03-P | CML-4 | 300-PF-20002-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6516 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:10 | [32 empty] | 14.425 | CML-4 | CML: Pipe Length | 6 | 2027-05-09 | 2024-11-04 | 2014-07-24 07:30 | 4.9 | 0.67187 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 3 O'Clock | 300 | 14.27 | 300-PF-20002-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 15.1 | 13.5 | 14.7 | 14.4 | 0.68007
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-21 | 250-PG-23004-06C03-A CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 23388 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 18.775 | CML-21 | CML: Elbow | 6 | 2143-01-24 | 2118-04-19 | 2015-07-21 07:00 | 8.55 | 0.07484 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.1 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.55 | 0.19706 | 18.8 | 18.5 | 18.1 | 19.7 | 0.68007
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56028-01C02 | CML-9 | 80-DH-56028-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20906 | Rope Access | 2014-05-22 07:00 | 2014-05-22 08:00 | [36 empty] | 5.4 | CML-9 | CML: Elbow | 3 | 2017-02-04 | 2017-07-11 | 2014-05-22 07:00 | 2.5 | 0.81159 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 12 O'Clock | 80 | 5.49 | 80-DH-56028-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5 | 6.2 | 5.7 | 0.67823
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56071-01C02 | CML-3 | 50-DH-56071-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3418 | Rope Access | 2014-05-11 13:00 | 2014-05-11 14:00 | [36 empty] | 7.6 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-11 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.3 | 8 | 8.3 | 0.67823
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-13 | 50-WC-40451-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 3075 | Deck Level | 2014-05-03 08:00 | 2014-05-03 09:00 | Check Corrosion Rate of 0.369mm/ yr | [35 empty] | 5.475 | CML-13 | CML: Fitting | 3 | 2021-08-25 | 2022-07-13 | 2014-05-03 08:00 | 2.5 | 0.36898 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 6.4534 | 5.8 | 5.3 | 5.2 | 5.6 | 0.27538
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23012-25C02-A | CML-4 | 150-PG-23012-25C02-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13030 |  | 2014-01-11 09:00 | 2014-01-11 10:30 | [36 empty] | 21.475 | CML-4 | CML: Pipe Length | 3 | 2017-10-20 | 2016-09-10 | 2014-01-11 09:00 | 15.88 | 1.3827 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.1 | 9 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 |  | 22.1 | 21.6 | 21.1 | 21.1 | 0.47871
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57008-01C02 | CML-5 | 80-DC-57008-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23277 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 6.05 | CML-5 | CML: Elbow | 3 | 2044-01-07 | 2047-08-01 | 2015-05-12 07:00 | 2.5 | 0.09764 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 12 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.8 | 6.5 | 6.6 | 0.61373
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57008-01C02 | CML-14 | 80-DC-57008-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23286 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.55 | CML-14 | CML: Pipe Length | 3 | 2044-01-07 | 2047-08-01 | 2015-05-12 07:00 | 2.5 | 0.09764 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.5 | 5.6 | 5.3 | 0.20817
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-21 | 300-PF-20500-03C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21641 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.6 | CML-21 | CML: Pipe Length | 6 | 2086-05-06 | 2073-03-25 | 2014-09-27 07:00 | 4.9 | 0.12839 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 15.6 | 14.3 | 14.1 | 14.4 | 0.67823
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-9 | 50-PW-44015-01X01 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10292 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.15 | CML-9 | CML: Equal Tee | 3 | 2015-11-30 | 2016-03-06 | 2013-11-10 | 2.5 | 1.2167 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 5.2 | 5.2 | 0.1
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-2 | 250-PG-23015-06C03-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13034 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 14.15 | CML-2 | CML: Elbow | 6 | 2014-08-23 | 2014-05-29 | 2014-01-11 13:00 | 8.55 | 7.9001 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 13.4 | 12 O'Clock | 100 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.85 |  | 13.4 | 14.9 | 13.8 | 14.5 | 0.67577
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-8 | 50-DC-57043-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23133 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.525 | CML-8 | CML: Pipe Length | 3 | 2037-12-23 | 2040-08-12 | 2015-05-10 07:00 | 2.5 | 0.12368 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0.53841 | 5.3 | 5.8 | 5.6 | 5.4 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-6 | 50-DC-57044-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23124 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.375 | CML-6 | CML: Pipe Length | 3 | 2037-12-23 | 2040-08-12 | 2015-05-10 07:00 | 2.5 | 0.12368 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | -0.26914 | 5.5 | 5.3 | 5.3 | 5.4 | 0.095743
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-8 | 80-PW-44035-01C02-P CML-8 | yes | FPSO 2014 | Pipe Wall Thickness | 21931 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 5.3 | CML-8 | CML: Elbow | 3 | 2020-04-15 | 2021-02-01 | 2014-10-09 07:00 | 2.5 | 0.43479 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.5 | 4.9 | 5 | 5.8 | 0.42426
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-4 | 50-PG-23063-09C02 CML-4 | Yes | FPSO 2013 | Pipe Wall Thickness | 10730 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.925 | CML-4 | CML: type TBC | 3 | 2020-01-21 | 2018-05-01 | 2013-11-19 | 2.5 | 0.93918 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 12 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.1 | 9.8 | 8.5 | 0.67515
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-5 | 100-WC-40027-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 837 |  | 2014-04-02 09:00 | 2014-04-02 10:00 | Check Corrosion Rate of 0.98mm/ yr |  | Nestor | 2016-04-01 | [32 empty] | 5.5 | CML-5 | CML: Elbow | 3 | 2017-01-01 | 2017-02-14 | 2014-04-02 09:00 | 2.5 | 0.98011 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 6 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 2 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.7 | 5.2 | 5.6 | 0.21602
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-14 | 50-DH-56137-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21098 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.5 | CML-14 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.7 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.3 | 7.3 | 6.7 | 5.7 | 0.6733
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-3 | 50-DC-57025-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22937 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.825 | CML-3 | CML: Elbow | 3 | 2037-09-13 | 2040-04-22 | 2015-05-02 07:00 | 2.5 | 0.12509 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0.18296 | 6 | 6.1 | 5.3 | 5.9 | 0.3594
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40021-01C02 | CML-4 | 50-WC-40021-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2099 | Rope Access | 2014-03-28 13:00 | 2014-03-28 14:00 | Check Corrosion Rate of 0.413mm/ yr | [35 empty] | 5.4 | CML-4 | CML: type TBC | 3 | 2020-10-09 | 2021-07-24 | 2014-03-28 13:00 | 2.5 | 0.41292 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40021-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.3 | 5.2 | 5.6 | 0.18257
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-5 | 100-FG-45001-09C02 CML-5 | High Priority | FPSO 2015 | Pipe Wall Thickness | 23310 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.625 | CML-5 | CML: type TBC | 3 | 2044-12-13 | 2036-07-16 | 2015-07-11 07:00 | 4.7 | 0.20375 | A4: Left Quadrant |  | 8.13 | 4.7 | 6.415 | 10.7 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | -2.1106 | 11.8 | 12.3 | 11.7 | 10.7 | 0.6702
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-16 | 50-PW-44040-01C02 CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 1991 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.45 | CML-16 | CML: Elbow | 3 | 2017-04-22 | 2017-09-22 | 2014-03-27 07:00 | 2.5 | 0.78051 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.8 | 5.6 | 4.9 | 5.5 | 0.3873
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-12 | 200-PL-20010-01C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23525 | Re-check on line as Per RBI 2014 Report | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 6.175 | CML-12 | CML: Fitting | 3 | 2028-07-03 | 2028-05-23 | 2015-07-28 07:00 | 2.5 | 0.25499 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0 | 6.2 | 6.5 | 6.2 | 5.8 | 0.28723
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-20 | 150-PG-20507-01C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 2864 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 10.125 | CML-20 | CML: type TBC | 6 | 2018-04-18 | 2017-08-01 | 2014-03-16 07:00 | 2.5 | 1.7345 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 9.6 | 3 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.6 | 9.6 | 11 | 10.3 | 0.6702
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67301-01E01 | CML-11 | 25-GN-67301-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22505 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.325 | CML-11 | CML: Elbow | 3 | 2020-04-28 | 2020-04-10 | 2015-04-20 07:00 | 2.5 | 0.55681 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 9 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.4 | 5.3 | 0.05
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67301-01E01 | CML-10 | 25-GN-67301-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22504 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.3 | CML-10 | CML: Elbow | 3 | 2020-04-28 | 2020-04-10 | 2015-04-20 07:00 | 2.5 | 0.55681 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 9 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.3 | 5.3 | 0
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67301-01E01 | CML-9 | 25-GN-67301-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22503 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.625 | CML-9 | CML: Pipe Length | 3 | 2020-04-28 | 2020-04-10 | 2015-04-20 07:00 | 2.5 | 0.55681 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 3 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 6 | 5.9 | 0.37749
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-3 | 50-WC-40452-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10600 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 0.734mm/ yr | [35 empty] | 5.3 | CML-3 | CML: type TBC | 3 | 2017-07-21 | 2017-12-30 | 2013-11-17 | 2.5 | 0.73432 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.4 | 5.2 | 0.11547
FG01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-FG-45024-01C02 | CML-14 | 50-FG-45024-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 5207 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 10.175 | CML-14 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.2 | 9 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.3 | 10.7 | 10.5 | 9.2 | 0.6702
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-13 | 400-FH-43500-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5649 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 12.825 | CML-13 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 12.3 | 6 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.8 |  | 13.8 | 12.5 | 12.3 | 12.7 | 0.6702
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-8 | 80-DH-56140-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21079 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 10.975 | CML-8 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 10 | 3 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 11.3 | 10 | 11.1 | 11.5 | 0.6702
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-14 | 50-WC-40452-01C02 CML-14 |  | FPSO 2013 | Pipe Wall Thickness | 10611 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 0.734mm/ yr | [35 empty] | 5.25 | CML-14 | CML: type TBC | 3 | 2017-07-21 | 2017-12-30 | 2013-11-17 | 2.5 | 0.73432 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.2 | 5.2 | 0.1
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71336-01K01 | CML-5 | 100-WF-71336-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6414 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 5.525 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 5.3 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 5.4 | 5.9 | 0.263
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71329-01K01 | CML-1 | 50-WF-71329-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6250 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 5.75 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 5.3 | 6 O'Clock | 50 | 2.5 | 50-WF-71329-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 6.3 | 5.3 | 5.8 | 0.42032
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71333-01K01 | CML-2 | 50-WF-71333-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6229 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 5.775 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 5.3 | 6 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.9 | 5.3 | 6 | 0.32016
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 50-WF-71333-01K01 | CML-1 | 50-WF-71333-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6228 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 5.65 | CML-1 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 5.3 | 6 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.8 | 5.3 | 5.7 | 0.23805
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 100-WF-71359-01K01 | CML-2 | 100-WF-71359-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6211 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 5.65 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 5.3 | 3 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.3 | 5.9 | 5.5 | 0.3
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 250-WF-71306-01K01 | CML-4 | 250-WF-71306-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5183 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 6.525 | CML-4 | CML: type TBC | 0.5 | 2023-06-01 | 2020-11-30 | 2015-03-12 07:00 | 3.5 | 0 | A1: Outside Quadrant |  | 4 | 3.5 | 3.75 | 6.3 | 12 O'Clock | 250 | 4.5 | 250-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.3 | 6.6 | 6.4 | 6.8 | 0.22174
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71315-01K01 | CML-5 | 150-WF-71315-01K01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5134 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 5.35 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 5.3 | 6 O'Clock | 150 | 3 | 150-WF-71315-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.3 | 5.4 | 0.057735
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-22 | 50-GN-67002-01E01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 9081 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.475 | CML-22 | CML: type TBC | 3 | 2035-07-22 | 2037-12-06 | 2015-03-01 09:30 | 2.5 | 0.13722 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 5.4 | 5.8 | 0.22174
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-11 | 50-GN-67002-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 9070 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.725 | CML-11 | CML: type TBC | 3 | 2035-07-22 | 2037-12-06 | 2015-03-01 09:30 | 2.5 | 0.13722 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.1 | 6.1 | 5.4 | 0.43493
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-9 | 50-AU-63015-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 9040 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.375 | CML-9 | CML: type TBC | 3 | 2035-07-21 | 2037-12-04 | 2015-03-01 07:00 | 2.5 | 0.13724 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.6 | 5.3 | 0.15
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-20 | 50-AI-63004-01E01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 9011 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.95 | CML-20 | CML: type TBC | 3 | 2035-07-08 | 2037-11-20 | 2015-02-28 07:00 | 2.5 | 0.13746 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.4 | 6.1 | 6 | 5.3 | 0.46547
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-13 | 50-AI-63004-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 9004 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.6 | CML-13 | CML: type TBC | 3 | 2035-07-08 | 2037-11-20 | 2015-02-28 07:00 | 2.5 | 0.13746 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.3 | 5.6 | 5.6 | 0.24495
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-12 | 50-AI-63004-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 9003 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.55 | CML-12 | CML: type TBC | 3 | 2035-07-08 | 2037-11-20 | 2015-02-28 07:00 | 2.5 | 0.13746 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 6 | 5.5 | 0.31091
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-2 | 50-AI-63004-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8993 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.4 | CML-2 | CML: type TBC | 3 | 2035-07-08 | 2037-11-20 | 2015-02-28 07:00 | 2.5 | 0.13746 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.4 | 5.5 | 5.3 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-58 | 50-AI-63007-01E01 CML-58 |  | FPSO 2015 | Pipe Wall Thickness | 8982 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.65 | CML-58 | CML: type TBC | 3 | 2035-06-14 | 2037-10-24 | 2015-02-26 09:00 | 2.5 | 0.13787 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 6 | 5.9 | 5.3 | 0.35119
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-49 | 50-AI-63007-01E01 CML-49 |  | FPSO 2015 | Pipe Wall Thickness | 8973 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.525 | CML-49 | CML: type TBC | 3 | 2035-06-14 | 2037-10-24 | 2015-02-26 09:00 | 2.5 | 0.13787 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.5 | 5.8 | 5.3 | 0.20616
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-43 | 50-AI-63007-01E01 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 8967 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.425 | CML-43 | CML: type TBC | 3 | 2035-06-14 | 2037-10-24 | 2015-02-26 09:00 | 2.5 | 0.13787 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.5 | 5.5 | 5.3 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-41 | 50-AI-63007-01E01 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 8965 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.55 | CML-41 | CML: type TBC | 3 | 2035-06-14 | 2037-10-24 | 2015-02-26 09:00 | 2.5 | 0.13787 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.4 | 5.3 | 6 | 0.31091
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-40 | 50-AI-63007-01E01 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 8964 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.8 | CML-40 | CML: type TBC | 3 | 2035-06-14 | 2037-10-24 | 2015-02-26 09:00 | 2.5 | 0.13787 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 6.3 | 6.1 | 5.3 | 0.4761
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-24 | 50-AI-63007-01E01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 8948 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.575 | CML-24 | CML: type TBC | 3 | 2035-06-14 | 2037-10-24 | 2015-02-26 09:00 | 2.5 | 0.13787 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 6.2 | 5.3 | 0.4272
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-2 | 50-AI-63007-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8926 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.65 | CML-2 | CML: type TBC | 3 | 2035-06-14 | 2037-10-24 | 2015-02-26 09:00 | 2.5 | 0.13787 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6 | 6 | 5.3 | 5.3 | 0.40415
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-15 | 50-AU-63018-01E01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8911 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.375 | CML-15 | CML: type TBC | 3 | 2035-06-03 | 2037-10-13 | 2015-02-25 13:00 | 2.5 | 0.13805 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.4 | 5.3 | 5.4 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-17 | 50-AI-63005-01E01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8893 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.525 | CML-17 | CML: type TBC | 3 | 2035-06-01 | 2037-10-11 | 2015-02-25 09:30 | 2.5 | 0.13808 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.5 | 6 | 5.3 | 0.3304
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-15 | 50-AI-63005-01E01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8891 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.65 | CML-15 | CML: type TBC | 3 | 2035-06-01 | 2037-10-11 | 2015-02-25 09:30 | 2.5 | 0.13808 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.3 | 5.3 | 6.2 | 0.43589
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-9 | 50-AI-63005-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8885 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.55 | CML-9 | CML: type TBC | 3 | 2035-06-01 | 2037-10-11 | 2015-02-25 09:30 | 2.5 | 0.13808 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 6.2 | 5.4 | 0.43589
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-4 | 50-AI-63005-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8880 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.525 | CML-4 | CML: type TBC | 3 | 2035-06-01 | 2037-10-11 | 2015-02-25 09:30 | 2.5 | 0.13808 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6 | 5.3 | 5.5 | 0.3304
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-3 | 50-AI-63005-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8879 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.525 | CML-3 | CML: type TBC | 3 | 2035-06-01 | 2037-10-11 | 2015-02-25 09:30 | 2.5 | 0.13808 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.2 | 5.3 | 5.3 | 5.3 | 0.45
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63023-01E01 | CML-4 | 50-AU-63023-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8865 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 07:00 | 2015-02-25 08:00 | [36 empty] | 5.525 | CML-4 | CML: type TBC | 3 | 2035-05-31 | 2037-10-09 | 2015-02-25 07:00 | 2.5 | 0.13811 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-AU-63023-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 5.4 | 6 | 0.32016
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67011-01E01 | CML-1 | 50-GN-67011-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8759 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.55 | CML-1 | CML: type TBC | 3 | 2035-01-26 | 2037-05-23 | 2015-02-15 09:30 | 2.5 | 0.1403 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6 | 5.4 | 5.5 | 0.31091
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-13 | 50-GN-67006-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8758 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.575 | CML-13 | CML: type TBC | 3 | 2035-01-24 | 2037-05-22 | 2015-02-15 07:00 | 2.5 | 0.14032 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 6.1 | 5.4 | 0.3594
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-3 | 50-GN-67006-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8748 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.55 | CML-3 | CML: type TBC | 3 | 2035-01-24 | 2037-05-22 | 2015-02-15 07:00 | 2.5 | 0.14032 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 6 | 5.4 | 0.31091
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-16 | 50-GN-67004-01E01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8621 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.425 | CML-16 | CML: type TBC | 3 | 2034-11-09 | 2037-02-27 | 2015-02-09 07:30 | 2.5 | 0.14168 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 5.5 | 5.5 | 0.095743
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-4 | 50-GN-67004-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8609 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.575 | CML-4 | CML: type TBC | 3 | 2034-11-09 | 2037-02-27 | 2015-02-09 07:30 | 2.5 | 0.14168 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.5 | 5.4 | 6.1 | 0.3594
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63035-01E01 | CML-5 | 50-AI-63035-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8586 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-07 14:00 | 2015-02-07 16:00 | [36 empty] | 5.85 | CML-5 | CML: type TBC | 3 | 2034-10-19 | 2037-02-03 | 2015-02-07 14:00 | 2.5 | 0.14207 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-AI-63035-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.5 | 5.3 | 5.7 | 5.9 | 0.5
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63035-01E01 | CML-3 | 50-AI-63035-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8584 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-07 14:00 | 2015-02-07 16:00 | [36 empty] | 5.75 | CML-3 | CML: type TBC | 3 | 2034-10-19 | 2037-02-03 | 2015-02-07 14:00 | 2.5 | 0.14207 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-AI-63035-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.3 | 6.1 | 5.8 | 0.33166
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-5 | 50-FL-43454-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21922 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 9.775 | CML-5 | CML: Reducing Tee | 6 | 2055-10-06 | 2053-05-09 | 2014-06-24 09:30 | 2.5 | 0.15976 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.1 | 6 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.6 | 10.7 | 9.1 | 9.7 | 0.6702
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-5 | 50-FL-43454-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5824 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 9.775 | CML-5 | CML: Reducing Tee | 6 | 2055-10-06 | 2053-05-09 | 2014-06-24 09:30 | 2.5 | 0.15976 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.1 | 6 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.6 | 10.7 | 9.1 | 9.7 | 0.6702
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-2 | 80-PG-20046-03C03-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23338 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-19 07:00 | 2015-07-19 15:00 | [36 empty] | 11.775 | CML-2 | CML: Elbow | 6 | 2069-02-20 | 2060-08-25 | 2015-07-19 07:00 | 2.5 | 0.15476 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.8 | 12 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 | -0.18914 | 10.8 | 11.9 | 12.3 | 12.1 | 0.6702
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-12 | 50-AI-63450-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8331 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.75 | CML-12 | CML: type TBC | 3 | 2034-06-10 | 2036-09-12 | 2015-01-28 07:30 | 2.5 | 0.14448 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.7 | 5.3 | 6.4 | 0.46547
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63044-01E01 | CML-1 | 50-AI-63044-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8304 |  | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 5.85 | CML-1 | CML: type TBC | 3 | 2034-05-30 | 2036-08-30 | 2015-01-27 09:45 | 2.5 | 0.1447 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-AI-63044-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6 | 5.9 | 5.3 | 6.2 | 0.3873
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-21 | 50-WD-53010-01E01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 8264 | Reducing Hose Coupling | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.35 | CML-21 | CML: type TBC | 3 | 2034-05-16 | 2036-08-15 | 2015-01-26 07:30 | 2.5 | 0.14496 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.7 | 6.7 | 6.7 | 0.7
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53015-01E01 | CML-6 | 50-WD-53015-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8232 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.5 | CML-6 | CML: type TBC | 3 | 2034-05-03 | 2036-08-01 | 2015-01-25 07:30 | 2.5 | 0.1452 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.5 | 5.6 | 5.3 | 0.14142
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53015-01E01 | CML-5 | 50-WD-53015-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8231 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.875 | CML-5 | CML: type TBC | 3 | 2034-05-03 | 2036-08-01 | 2015-01-25 07:30 | 2.5 | 0.1452 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.4 | 5.9 | 5.9 | 0.45
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62003-01C02 | CML-1 | 50-DO-62003-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8049 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.4 | CML-1 | CML: type TBC | 3 | 2034-03-14 | 2036-06-05 | 2015-01-21 07:30 | 2.5 | 0.14617 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DO-62003-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.4 | 5.6 | 0.14142
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62001-01C02 | CML-8 | 50-DO-62001-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8048 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.45 | CML-8 | CML: type TBC | 3 | 2034-03-14 | 2036-06-05 | 2015-01-21 07:30 | 2.5 | 0.14617 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DO-62001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.3 | 5.3 | 5.4 | 0.23805
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20062-01C03-P | CML-2 | 250-PG-20062-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21539 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 13.325 | CML-2 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2014-07-13 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 12.4 | 3 O'Clock | 150 | 9.27 | 250-PG-20062-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 13.5 | 12.4 | 13.4 | 14 | 0.6702
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-5 | 25-VA-23054-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5606 |  | 2014-06-20 08:00 | 2014-06-20 09:00 | [36 empty] | 13.575 | CML-5 | CML: Equal Tee | 6 | 2098-02-09 | 2085-10-05 | 2014-06-20 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 12.9 | 3 O'Clock | 150 | 10.97 | 150-PG-23403-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 13.5 | 12.9 | 13.4 | 14.5 | 0.6702
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-11 | 100-WC-40516-1CG CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8684 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:56 | [32 empty] | 9.025 | CML-11 | CML: Pipe Length | 3 | 2077-12-11 | 2061-08-26 | 2015-02-13 07:00 | 2.5 | 0.09385 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.4 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 10.1 | 8.6 | 8.4 | 9 | 0.75884
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-12 | 100-DH-56086-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20971 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 5.525 | CML-12 | CML: type TBC | 3 | 2015-10-15 | 2015-11-13 | 2014-05-16 13:00 | 2.5 | 1.4828 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.6 | 3 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.7 | 4.6 | 5.6 | 6.2 | 0.6702
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-15 | 80-CG-38459-09C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 13047 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 21.3 | CML-15 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 13:00 | 8.55 | 0 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 20.4 | 6 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.85 |  | 21.3 | 22 | 20.4 | 21.5 | 0.66833
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-10 | 300-PG-20004-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 6133 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.2 | CML-10 | CML: Pipe Length | 6 | 2023-02-18 | 2021-05-21 | 2014-07-11 07:30 | 4.9 | 0.96358 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 13.2 | 14.5 | 14.6 | 14.5 | 0.66833
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56555-01C02 | CML-2 | 50-DH-56555-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21124 | Reviewed 20/11/14. FFS. Re check Oct.18. Review RBI to include this line. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-20 16:43 | [32 empty] | 8.2 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-08 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56555-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.2 | 7.3 | 8.9 | 8.4 | 0.66833
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38489-01C02-P | CML-1 | 50-CG-38489-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20858 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.6 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 9 | 3 O'Clock | 50 | 5.54 | 50-CG-38489-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.1 | 9 | 9.9 | 10.4 | 0.66833
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-6 | 80-DH-56140-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21077 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 6.3 | CML-6 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.5 | 9 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.8 | 6.9 | 6 | 5.5 | 0.66833
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-17 | 50-WC-40071-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 7730 |  | 2015-01-09 13:00 | 2015-01-09 15:00 |  |  | Administrator | 2015-09-08 09:36 | [32 empty] | 5.575 | CML-17 | CML: Pipe Length | 3 | 2033-10-16 | 2035-12-23 | 2015-01-09 13:00 | 2.5 | 0.1491 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0.50494 | 6 | 5.4 | 5.6 | 5.3 | 0.30957
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43129-01C02 | CML-2 | 50-FH-43129-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1781 | Rope access | 2014-04-28 08:00 | 2014-04-28 09:00 | [36 empty] | 6 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-28 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-FH-43129-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 7 | 5.7 | 0.66833
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-2 | 400-FH-43508-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 6551 | Rope Access.Line is FFS. Action: to recheck in a year (Mar. 2016) to confirm CR. | 2015-03-30 07:00 | 2015-03-30 15:00 |  |  | Administrator | 2015-09-07 16:18 | [32 empty] | 7.1 | CML-2 | CML: Elbow | 3 | 2020-05-21 | 2019-06-20 | 2015-03-30 07:00 | 2.5 | 0.77672 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 6.5 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.2 | 8 | 6.7 | 6.5 | 0.66833
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57030-01C02 | CML-3 | 50-DC-57030-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20279 | Reviewed on 24/11/14. FFS. Repeat on Oct.19 | 2014-10-16 07:00 | 2014-10-14 15:00 |  |  | Nestor | 2014-11-24 09:31 | [32 empty] | 5.775 | CML-3 | CML: Elbow | 3 | 2030-11-01 | 2032-09-14 | 2014-10-16 07:00 | 2.5 | 0.1744 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57030-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.1 | 5.5 | 5.3 | 6.2 | 0.44253
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57006-01C02 | CML-1 | 80-DC-57006-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20263 | Reviewed on 24/11/14. FFS. Repeat Oct.19 | 2014-10-11 07:00 | 2014-10-11 15:00 |  |  | Nestor | 2014-11-24 09:49 | [32 empty] | 5.925 | CML-1 | CML: Elbow | 3 | 2034-11-03 | 2037-05-02 | 2014-10-11 07:00 | 2.5 | 0.13946 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-DC-57006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 6.5 | 6.4 | 5.3 | 0.61305
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-10 | 50-PW-44014-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2012 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 6.35 | CML-10 | CML: Elbow | 3 | 2019-01-29 | 2019-09-08 | 2014-03-27 10:00 | 2.5 | 0.53638 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.6 | 5.1 | 7.5 | 6.2 | 0.99499
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-14 | 50-PL-23516-03C03 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7802 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 15:58 | [32 empty] | 9.2 | CML-14 | CML: Elbow | 6 | 2036-05-16 | 2035-12-07 | 2015-01-13 07:00 | 2.5 | 0.27161 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.9 | 9.4 | 9.2 | 8.3 | 0.66833
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-32 | 250-PW-44006-01X01 CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 1929 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6 | CML-32 | CML: Pipe Length | 3 | 2015-12-06 | 2015-11-30 | 2014-03-26 07:00 | 2.5 | 1.5295 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.1 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.5 | 6.8 | 5.1 | 5.6 | 0.7874
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43113-01C02 | CML-3 | 80-FH-43113-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20430 | Rope Access | 2014-05-25 14:00 | 2014-05-25 15:00 | [36 empty] | 6.3 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-25 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 3 O'Clock | 80 | 5.49 | 80-FH-43113-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.7 | 6.6 | 7.1 | 0.66833
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-20 | 250-PW-44006-01X01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 8012 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.075 | CML-20 | CML: Elbow | 3 | 2018-06-17 | 2018-06-04 | 2015-01-20 08:30 | 2.5 | 0.76251 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.1 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 2.3112 | 6.5 | 6.4 | 5.1 | 6.3 | 0.65511
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-14 | 50-FG-45019-03C02 CML-14 | yes | FPSO 2013 | Pipe Wall Thickness | 10496 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.8 | CML-14 | CML: type TBC | 3 | 2014-04-06 | 2014-04-04 | 2013-11-15 | 2.5 | 3.5844 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 3.9 | 6 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 5.4 | 5.2 | 3.9 | 4.7 | 0.66833
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-40 | 300-PF-20003-03C03-P CML-40 |  | FPSO 2014 | Pipe Wall Thickness | 21778 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.35 | CML-40 | CML: Fitting | 6 | 2040-01-05 | 2035-03-25 | 2014-10-01 07:00 | 4.9 | 0.35205 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 3 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14 | 13.8 | 14.3 | 15.3 | 0.66583
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-1 | 80-CG-38459-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10951 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 17.95 | CML-1 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 17 | 6 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.78 |  | 18 | 18.3 | 17 | 18.5 | 0.66583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-8 | 50-DC-57450-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20324 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.4 | CML-8 | CML: Elbow | 3 | 2030-06-15 | 2032-04-12 | 2014-10-05 07:00 | 2.5 | 0.17831 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.5 | 5.5 | 0.11547
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-5 | 50-DC-57450-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20321 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.85 | CML-5 | CML: Reducer | 3 | 2030-06-15 | 2032-04-12 | 2014-10-05 07:00 | 2.5 | 0.17831 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.1 | 5.8 | 6.2 | 5.3 | 0.40415
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-5 | 200-PW-44018-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2116 |  | 2014-03-29 07:00 | 2014-03-29 08:00 | Check Corrosion Rate of 0.533mm/ yr | [35 empty] | 5.8 | CML-5 | CML: Elbow | 3 | 2019-02-11 | 2019-09-23 | 2014-03-29 07:00 | 2.5 | 0.53304 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.8 | 5.1 | 6.3 | 6 | 0.5099
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FH-43309-01C02 | CML-5 | 50-FH-43309-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20447 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.375 | CML-5 | CML: Pipe Length | 3 | 2027-12-28 | 2029-07-22 | 2014-07-26 07:00 | 2.5 | 0.20843 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-FH-43309-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.4 | 5.4 | 0.05
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FH-43309-01C02 | CML-1 | 50-FH-43309-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20443 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.375 | CML-1 | CML: Pipe Length | 3 | 2027-12-28 | 2029-07-22 | 2014-07-26 07:00 | 2.5 | 0.20843 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-FH-43309-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.4 | 5.4 | 0.05
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45024-01C02 | CML-1 | 50-FG-45024-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 23801 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 9.75 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 12 O'Clock | 250 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.7 | 10.7 | 9.4 | 0.66583
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-17 | 250-PG-23004-06C03-A CML-17 |  | FPSO 2016 | Pipe Wall Thickness | 24455 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | [36 empty] | 18.275 | CML-17 | CML: Pipe Length | 6 | 2052-12-13 | 2045-05-26 | 2016-07-05 07:00 | 8.55 | 0.24542 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 17.5 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.95 | -0.10429 | 18.4 | 19.1 | 18.1 | 17.5 | 0.66521
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-3 | 200-PG-23013-09C03-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10987 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 20.725 | CML-3 | CML: Elbow | 6 | 2022-03-27 | 2020-05-14 | 2014-01-10 | 10.22 | 1.1785 | A2: Right Quadrant |  | 14.62 | 10.22 | 12.42 | 19.9 | 3 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.68 |  | 20.5 | 19.9 | 21.4 | 21.1 | 0.66521
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-1 | 80-PW-44016-01C02-P CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 21933 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.45 | CML-1 | CML: Elbow | 3 | 2020-04-20 | 2021-02-06 | 2014-10-10 07:00 | 2.5 | 0.43392 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.7 | 5.7 | 5.5 | 0.37859
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23012-25C02-A | CML-4 | 150-PG-23012-25C02-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20538 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 21.325 | CML-4 | CML: Pipe Length | 3 | 2020-07-09 | 2018-09-21 | 2014-05-30 09:30 | 15.88 | 0.85375 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 21.1 | 9 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 | 0 | 22 | 21.1 | 21.1 | 21.1 | 0.45
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23012-25C02-A | CML-5 | 150-PG-23012-25C02-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13031 |  | 2014-01-11 09:00 | 2014-01-11 10:30 | [36 empty] | 21.1333 | CML-5 | CML: Tee | 3 | 2017-10-20 | 2016-09-10 | 2014-01-11 09:00 | 15.88 | 1.3827 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.1 | 3 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 |  | 21.1 | 21.1 | 21.2 |  | 0.057735
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-FH-43507-01C02 | CML-5 | 100-FH-43507-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13095 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 22.575 | CML-5 | CML: Elbow | 3 | 2074-02-10 | 2058-10-06 | 2014-01-10 09:00 | 15.88 | 0 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 22 | 6 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.12 |  | 22.2 | 22.6 | 22 | 23.5 | 0.66521
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-6 | 50-PW-44013-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22725 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.6 | CML-6 | CML: Elbow | 3 | 2026-08-02 | 2028-01-01 | 2015-04-28 07:00 | 2.5 | 0.23065 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.11784 | 5.1 | 6.1 | 5.3 | 5.9 | 0.4761
FG02 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 25-FG-45455-01C02-E | CML-18 | 25-FG-45455-01C02-E CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8139 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.525 | CML-18 | CML: type TBC | 1 | 2303-03-05 | 2230-06-04 | 2015-01-23 07:30 | 2.5 | 0.01214 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.3 | 7.5 | 6.3 | 0.66521
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-15 | 80-CG-38459-09C02-P CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 22777 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 17.625 | CML-15 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 16.8 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 | 0.75005 | 18 | 16.8 | 18.3 | 17.4 | 0.66521
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43176-01C02 | CML-6 | 300-FL-43176-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20436 | Protective mesh removed/Rope access | 2014-06-27 10:30 | 2014-06-27 12:00 | [36 empty] | 6.725 | CML-6 | CML: Elbow | 3 | 2029-12-02 | 2029-10-19 | 2014-06-27 10:30 | 2.5 | 0.23312 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 300 | 6.35 | 300-FL-43176-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7.3 | 6.1 | 7.3 | 6.2 | 0.66521
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-28 | 400-FH-43508-01C02 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 6577 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.425 | CML-28 | CML: Elbow | 3 | 2022-04-04 | 2021-02-02 | 2015-03-30 07:00 | 2.5 | 0.61263 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 6.8 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 8 | 8 | 6.9 | 6.8 | 0.66521
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-4 | 150-FH-43136-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2765 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.075 | CML-4 | CML: Pipe Length | 3 | 2021-03-15 | 2019-10-19 | 2014-03-13 09:00 | 1.03 | 0.7802 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.5 | 12 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.47 |  | 6.5 | 6.7 | 7.1 | 8 | 0.66521
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-5 | 400-FH-43500-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5641 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 9.825 | CML-5 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 9 | 6 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 10.6 | 10 | 9 | 9.7 | 0.66521
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23012-25C02-A | CML-5 | 150-PG-23012-25C02-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20539 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 21.1 | CML-5 | CML: Tee | 3 | 2020-07-09 | 2018-09-21 | 2014-05-30 09:30 | 15.88 | 0.85375 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.1 | 6 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 | 0 | 21.1 | 21.1 | 21.1 |  | 0
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23037-25C02-A | CML-9 | 150-PG-23037-25C02-A CML-9 | yes | FPSO 2014 | Pipe Wall Thickness | 13099 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 22.275 | CML-9 | CML: Elbow | 3 | 2018-05-13 | 2017-02-10 | 2014-01-10 09:00 | 15.88 | 1.2255 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 21.2 | 6 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.32 |  | 24.6 | 21.2 | 21.2 | 22.1 | 1.607
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-9 | 250-PW-20039-01C03-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22973 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.2 | CML-9 | CML: Reducing Tee | 6 | 2048-08-06 | 2046-08-06 | 2015-05-04 07:00 | 2.5 | 0.1923 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.9 | 9 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | -0.46534 | 9 | 10 | 8.9 | 8.9 | 0.53541
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56127-01C02 | CML-2 | 80-DH-56127-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21050 | Rope Access | 2014-05-22 14:00 | 2014-05-22 15:00 | [36 empty] | 5.3 | CML-2 | CML: Pipe Length | 3 | 2017-08-19 | 2018-02-15 | 2014-05-22 14:00 | 2.5 | 0.70827 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 9 O'Clock | 80 | 5.49 | 80-DH-56127-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6.2 | 4.8 | 5.4 | 4.8 | 0.66332
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57301-01C02 | CML-5 | 50-DC-57301-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5665 | Rope access | 2014-06-21 13:00 | 2014-06-21 14:00 | [36 empty] | 5.325 | CML-5 | CML: Elbow | 3 | 2026-10-14 | 2028-03-21 | 2014-06-21 13:00 | 2.5 | 0.22721 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.3 | 5.4 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-4 | 80-DC-57005-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20250 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 5.55 | CML-4 | CML: type TBC | 3 | 2029-03-17 | 2031-01-17 | 2014-06-02 13:00 | 2.5 | 0.1892 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.5 | 5.3 | 5.6 | 0.20817
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-20 | 25-FG-45455-01C02-E CML-20 |  | FPSO 2016 | Pipe Wall Thickness | 24365 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 9.4 | CML-20 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 12 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 9.3 | 10.3 | 9.3 | 0.66332
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38452-09C02-P | CML-13 | 50-CG-38452-09C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 22353 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.9 | CML-13 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8.8 | 7.8 | 7.8 | 7.2 | 0.66332
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-2 | 50-PL-23023-03C03 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10202 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.7 | CML-2 | CML: type TBC | 6 | 2016-04-28 | 2016-04-07 | 2013-11-08 | 2.5 | 2.1444 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.8 | 6 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.8 | 8.8 | 7.8 | 9.4 | 0.66332
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-36 | 300-PF-20500-03C03-P CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 21656 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.8 | CML-36 | CML: Pipe Length | 6 | 2046-12-04 | 2040-11-24 | 2014-09-27 07:00 | 4.9 | 0.27944 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 15.3 | 15.3 | 13.9 | 14.7 | 0.66332
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-3 | 200-PG-24001-09C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10259 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 20.3 | CML-3 | CML: Elbow | 3 | 2104-01-05 | 2073-09-17 | 2013-11-09 | 9.2 | 0 | A2: Right Quadrant |  | 15.26 | 9.2 | 12.23 | 19.8 | 6 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.6 |  | 20.4 | 19.8 | 19.8 | 21.2 | 0.66332
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-51 | 200-PL-20019-01C02 CML-51 |  | FPSO 2014 | Pipe Wall Thickness | 21302 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.175 | CML-51 | CML: Pipe Length | 3 | 2022-09-26 | 2022-09-01 | 2014-09-30 07:00 | 2.5 | 0.41282 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.2 | 5.8 | 6.3 | 0.263
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-23 | 200-PW-44018-01X01 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 1998 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.475 | CML-23 | CML: Elbow | 3 | 2019-01-28 | 2019-09-07 | 2014-03-27 07:00 | 2.5 | 0.5366 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 6 | 5.1 | 5.7 | 0.45
CG04 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23213 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 7.95 | CML-4 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2015-05-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.2 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 | 2.445 | 7.2 | 8.4 | 8.6 | 7.6 | 0.66081
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40452-01C02 | CML-21 | 50-WC-40452-01C02 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10618 | Deck Level | 2013-11-17 | 2013-11-17 | Check Corrosion Rate of 0.734mm/ yr | [35 empty] | 5.275 | CML-21 | CML: type TBC | 3 | 2017-07-21 | 2017-12-30 | 2013-11-17 | 2.5 | 0.73432 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40452-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.2 | 5.3 | 0.095743
WC01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10379 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.05 | CML-4 | CML: type TBC | 3 | 2015-01-23 | 2015-01-18 | 2013-11-12 | 2.5 | 2.3369 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 12 O'Clock | 25 | 6.35 | 25-CG-38482-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 5.3 | 5.3 | 6.3 | 5.6 | 7 | 0.75939
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-15 | 50-CG-38452-09C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 3383 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 7.85 | CML-15 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 3 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.4 | 7.2 | 8.6 | 8.2 | 0.66081
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-22 | 50-DH-56137-01C02 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 23450 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 17.75 | CML-22 | CML: Pipe Length | 3 | 2022-10-05 | 2018-10-30 | 2015-07-23 07:00 | 2.5 | 2.025 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 17.1 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.6 | 2.9442 | 17.3 | 18.1 | 18.5 | 17.1 | 0.66081
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-6 | 100-DH-56082-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3374 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.025 | CML-6 | CML: type TBC | 3 | 2018-01-04 | 2018-03-01 | 2014-05-10 09:30 | 2.5 | 0.7653 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.8 | 5.7 | 6.3 | 0.66018
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-10 | 250-PW-20039-01C03-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22974 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.35 | CML-10 | CML: Elbow | 6 | 2048-08-06 | 2046-08-06 | 2015-05-04 07:00 | 2.5 | 0.1923 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.9 | 12 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | 0.46534 | 8.9 | 9.3 | 9.5 | 9.7 | 0.34157
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-11 | 150-PG-20054-01C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21522 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 12.825 | CML-11 | CML: Fitting | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 12.1 | 6 O'Clock | 200 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 13.6 | 13.1 | 12.1 | 12.5 | 0.66018
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44037-01C03 | CML-1 | 300-PW-44037-01C03 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 22954 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 10.175 | CML-1 | CML: Reducing Tee | 6 | 2042-11-10 | 2039-06-13 | 2015-05-04 07:00 | 2.5 | 0.26506 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.8 | 6 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 | 0.73 | 10.7 | 10.1 | 9.8 | 10.1 | 0.37749
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20020-01C02-P | CML-2 | 200-PL-20020-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21306 | Reviewed on 27/11/14. FFS. recheck on Sep.18 | 2014-09-28 07:00 | 2014-09-28 15:00 |  |  | Nestor | 2014-11-27 16:33 | [32 empty] | 6.1 | CML-2 | CML: Fitting | 3 | 2022-09-12 | 2022-08-18 | 2014-09-28 07:00 | 2.5 | 0.41452 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 20 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 6.3 | 5.8 | 6 | 0.24495
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-21 | 50-PF-20301-03C03-P CML-21 | yes | FPSO 2014 | Pipe Wall Thickness | 3019 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.1 | CML-21 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.3 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.69 | 0 | 8.3 | 9 | 9.9 | 9.2 | 0.65828
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-21 | 50-PF-20301-03C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 22298 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.1 | CML-21 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.3 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.69 |  | 8.3 | 9 | 9.9 | 9.2 | 0.65828
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-VA-23056-01C02 | CML-1 | 50-VA-23056-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8061 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 11.6 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-22 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.8 | 12 O'Clock | 50 | 5.54 | 50-VA-23056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 12.4 | 11.7 | 11.5 | 0.65828
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-2 | 250-PW-44509-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22037 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.225 | CML-2 | CML: Elbow | 6 | 2038-10-11 | 2037-05-02 | 2014-10-20 07:00 | 2.5 | 0.26674 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.9 | 9 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.3 | 9.5 | 9.2 | 8.9 | 0.25
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-17 | 100-PW-20021-01C02-P CML-17 | yes | FPSO 2015 | Pipe Wall Thickness | 22835 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.3 | CML-17 | CML: Elbow | 3 | 2019-06-04 | 2019-08-16 | 2015-04-30 07:00 | 2.5 | 0.58543 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.9 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.18159 | 4.9 | 5.3 | 5.3 | 5.7 | 0.3266
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-12 | 80-PW-44016-01C02-P CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 22914 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.225 | CML-12 | CML: Elbow | 3 | 2023-02-17 | 2024-04-06 | 2015-05-02 07:00 | 2.5 | 0.30751 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.17892 | 4.9 | 5.1 | 5.4 | 5.5 | 0.27538
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-14 | 350-FL-43511-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2295 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 8.15 | CML-14 | CML: type TBC | 3 | 2026-10-31 | 2025-01-23 | 2014-03-17 08:00 | 2.5 | 0.40369 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.6 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.9 | 8.5 | 7.6 | 7.6 | 0.65574
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-2 | 50-FL-43454-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23501 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 8.25 | CML-2 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2015-07-28 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.3 | 12 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.27 | 0.72736 | 7.3 | 8.4 | 8.8 | 8.5 | 0.65574
WC01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-WC-40006-01C02 | CML-11 | 150-WC-40006-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12997 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 6.175 | CML-11 | CML: type TBC | 3 | 2021-07-04 | 2022-05-17 | 2014-01-20 07:00 | 2.5 | 0.3755 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.5 | 5.3 | 6.9 | 6 | 0.68981
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-10 | 50-PL-20033-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2274 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 6.45 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-16 11:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.4 | 5.9 | 6.3 | 6.2 | 0.65574
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-10 | 80-PW-44016-01C02-P CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 22912 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.2 | CML-10 | CML: Elbow | 3 | 2023-02-17 | 2024-04-06 | 2015-05-02 07:00 | 2.5 | 0.30751 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.17892 | 4.9 | 5.3 | 5.2 | 5.4 | 0.21602
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-7 | 50-PW-44012-01X01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2021 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 5.65 | CML-7 | CML: Elbow | 3 | 2019-01-29 | 2019-09-08 | 2014-03-27 09:30 | 2.5 | 0.53641 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.8 | 6 | 5.1 | 0.3873
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23037-25C02-A | CML-7 | 150-PG-23037-25C02-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13097 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 23.35 | CML-7 | CML: Elbow | 3 | 2018-05-13 | 2017-02-10 | 2014-01-10 09:00 | 15.88 | 1.2255 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.2 | 12 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.32 |  | 21.2 | 24.1 | 23.9 | 24.2 | 1.4387
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-3 | 200-PG-23505-09C02-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2684 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 20.425 | CML-3 | CML: Elbow | 3 | 2055-05-31 | 2049-05-31 | 2014-03-12 09:00 | 14.06 | 0 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 19.8 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.74 | 0 | 19.9 | 19.8 | 21 | 21 | 0.66521
FG02 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 25-FG-45455-01C02-E | CML-13 | 25-FG-45455-01C02-E CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8134 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.55 | CML-13 | CML: type TBC | 1 | 2303-03-05 | 2230-06-04 | 2015-01-23 07:30 | 2.5 | 0.01214 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.3 | 7.5 | 6.4 | 0.65574
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-8 | 250-PG-23003-06C02-PA CML-8 | Yes | FPSO 2014 | Pipe Wall Thickness | 24246 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.65 | CML-8 | CML: Pipe Length | 3 | 2118-06-20 | 2101-08-21 | 2014-09-24 07:00 | 7.9 | 0.0684 | A2: Right Quadrant |  | 12.09 | 7.9 | 9.0519 | 15 | 3 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 15.3 | 15 | 15.8 | 16.5 | 0.65574
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-10 | 300-FL-43080-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2389 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 10.75 | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.9 | 12 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 10.6 | 11.1 | 11.4 | 0.65574
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23072-03C03 | CML-4 | 100-PG-23072-03C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20608 | Rope Access. Line is FFS | 2014-05-25 10:30 | 2014-05-25 11:30 |  |  | Administrator | 2015-09-08 08:12 | [32 empty] | 11.65 | CML-4 | CML: type TBC | 6 | 2295-09-21 | 2252-09-15 | 2014-05-25 10:30 | 2.5 | 0.03055 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 11.1 | 3 O'Clock | 100 | 11.13 | 100-PG-23072-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.5 | 11.1 | 12.6 | 11.4 | 0.65574
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-5 | 100-WC-40516-1CG CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8678 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:54 | [32 empty] | 9.225 | CML-5 | CML: Elbow | 3 | 2074-01-04 | 2058-09-17 | 2015-02-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.56 | 2.5 | 4.03 | 8.6 | 3 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.9 | 8.6 | 9.7 | 9.7 | 0.56199
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-37 | 150-PG-23506-25C02 CML-37 |  | FPSO 2014 | Pipe Wall Thickness | 2811 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.325 | CML-37 | CML: Pipe Length | 3 | 2108-12-07 | 2084-10-10 | 2014-03-15 09:00 | 15.88 | 0.06351 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.9 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.02 |  | 22 | 23.3 | 21.9 | 22.1 | 0.65511
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45044-03C02 | CML-16 | 50-FG-45044-03C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 7804 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:00 | [32 empty] | 9.425 | CML-16 | CML: Elbow | 6 | 2085-07-27 | 2084-03-07 | 2015-01-13 07:00 | 2.5 | 0.08642 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 10 | 9.9 | 9.2 | 8.6 | 0.65511
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57051-01C02 | CML-6 | 50-DC-57051-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1399 | Rope access | 2014-04-05 14:00 | 2014-04-05 15:00 | [36 empty] | 6.025 | CML-6 | CML: type TBC | 3 | 2024-02-12 | 2025-04-07 | 2014-04-05 14:00 | 2.5 | 0.28388 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DC-57051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.2 | 7 | 5.6 | 5.3 | 0.75
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57051-01C02 | CML-3 | 50-DC-57051-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1396 | Rope access | 2014-04-05 14:00 | 2014-04-05 15:00 | [36 empty] | 5.575 | CML-3 | CML: type TBC | 3 | 2024-02-12 | 2025-04-07 | 2014-04-05 14:00 | 2.5 | 0.28388 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DC-57051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.7 | 5.7 | 5.3 | 0.1893
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-9 | 50-DC-57451-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1380 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 5.75 | CML-9 | CML: type TBC | 3 | 2024-02-10 | 2025-04-05 | 2014-04-05 10:30 | 2.5 | 0.28401 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.1 | 5.9 | 5.7 | 5.3 | 0.34157
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2421 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 1.149mm/ yr | [35 empty] | 5.475 | CML-2 | CML: type TBC | 3 | 2016-06-23 | 2016-07-30 | 2014-03-20 07:00 | 2.5 | 1.1488 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 6 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.9 | 5.1 | 5.3 | 0.35
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56130-01C02 | CML-9 | 50-DH-56130-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21061 | Rope Access | 2014-05-15 13:00 | 2014-05-15 14:00 | [36 empty] | 5.775 | CML-9 | CML: type TBC | 3 | 2017-05-02 | 2017-10-03 | 2014-05-15 13:00 | 2.5 | 0.77494 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56130-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6.2 | 6 | 4.8 | 6.1 | 0.65511
WC01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-WC-40006-01C02 | CML-9 | 150-WC-40006-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12995 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 6.225 | CML-9 | CML: type TBC | 3 | 2021-07-04 | 2022-05-17 | 2014-01-20 07:00 | 2.5 | 0.3755 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.3 | 6.9 | 6.4 | 0.6702
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-37 | 300-PF-20001-03C03-P CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 23485 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 14.025 | CML-37 | CML: Fitting | 6 | 2043-07-10 | 2038-02-08 | 2015-07-27 07:00 | 4.9 | 0.31102 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 | -0.9708 | 13.6 | 13.7 | 13.8 | 15 | 0.65511
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57068-01C02 | CML-8 | 50-DC-57068-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1336 | Rope access | 2014-04-04 07:00 | 2014-04-04 08:00 | [36 empty] | 5.625 | CML-8 | CML: type TBC | 3 | 2024-01-27 | 2025-03-20 | 2014-04-04 07:00 | 2.5 | 0.28507 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DC-57068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.3 | 5.7 | 5.9 | 0.25
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57068-01C02 | CML-7 | 50-DC-57068-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1335 | Rope access | 2014-04-04 07:00 | 2014-04-04 08:00 | [36 empty] | 5.6 | CML-7 | CML: type TBC | 3 | 2024-01-27 | 2025-03-20 | 2014-04-04 07:00 | 2.5 | 0.28507 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DC-57068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 5.9 | 5.9 | 0.34641
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-12 | 50-DN-56101-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 852 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.625 | CML-12 | CML: Elbow | 3 | 2024-01-05 | 2025-02-24 | 2014-04-02 14:00 | 2.5 | 0.28666 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 6.2 | 5.3 | 5.4 | 0.40311
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-6 | 80-PL-44008-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5743 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 6.475 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.3 | 7.2 | 6.5 | 0.54391
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-16 | 250-PG-23003-06C02-PA CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21005 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.975 | CML-16 | CML: Reducing Tee | 3 | 2034-08-31 | 2036-12-11 | 2014-05-24 10:30 | 2.5 | 0.14296 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 6.8 | 6.2 | 5.4 | 0.65511
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-11 | 200-FH-43025-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2484 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 10.5 | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.7 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 10.5 | 11.3 | 10.5 | 0.6532
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56133-01C02 | CML-3 | 50-DN-56133-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1320 |  | 2014-03-31 10:15 | 2014-03-31 10:30 | [36 empty] | 5.375 | CML-3 | CML: type TBC | 3 | 2023-12-09 | 2025-01-24 | 2014-03-31 10:15 | 2.5 | 0.2887 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DN-56133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.5 | 5.4 | 5.3 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-46 | 50-DH-56062-01C02 CML-46 |  | FPSO 2015 | Pipe Wall Thickness | 9133 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 6.4 | CML-46 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.4 | 6.4 | 7.2 | 5.6 | 0.6532
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-21 | 300-PG-20005-03C03-P CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 22783 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.1 | CML-21 | CML: Reducing Tee | 6 | 2031-11-09 | 2028-07-16 | 2015-04-29 07:00 | 4.9 | 0.50775 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | 0.50004 | 14.9 | 14.1 | 13.3 | 14.1 | 0.6532
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-3 | 250-PL-20006-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13173 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.6 | CML-3 | CML: Elbow | 3 | 2018-11-28 | 2018-11-13 | 2014-01-21 13:00 | 2.5 | 0.7003 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 6 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.5 | 7 | 5.9 | 7 | 0.52281
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-21 | 50-FG-45023-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 1169 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 9.0667 | CML-21 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.7 | 9.1 |  | 8.4 | 0.65064
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-3 | 50-CG-38452-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12966 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 9.9333 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 3 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  |  | 9.3 | 10.6 | 9.9 | 0.65064
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-6 | 50-DC-57043-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2151 | Rope Access | 2014-03-29 13:00 | 2014-03-29 15:00 | [36 empty] | 5.75 | CML-6 | CML: Pipe Length | 3 | 2023-11-15 | 2024-12-29 | 2014-03-29 13:00 | 2.5 | 0.29051 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.4 | 5.9 | 5.3 | 5.4 | 0.50662
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-5 | 50-DC-57044-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2143 | Rope Access | 2014-03-29 10:30 | 2014-03-29 12:00 | [36 empty] | 5.825 | CML-5 | CML: Elbow | 3 | 2023-11-14 | 2024-12-27 | 2014-03-29 10:30 | 2.5 | 0.29061 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.3 | 5.8 | 5.3 | 5.9 | 0.4113
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-4 | 50-DC-57044-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2142 | Rope Access | 2014-03-29 10:30 | 2014-03-29 12:00 | [36 empty] | 5.45 | CML-4 | CML: Pipe Length | 3 | 2023-11-14 | 2024-12-27 | 2014-03-29 10:30 | 2.5 | 0.29061 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.6 | 5.5 | 5.3 | 0.1291
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57044-01C02 | CML-3 | 50-DC-57044-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2141 | Rope Access | 2014-03-29 10:30 | 2014-03-29 12:00 | [36 empty] | 5.475 | CML-3 | CML: Elbow | 3 | 2023-11-14 | 2024-12-27 | 2014-03-29 10:30 | 2.5 | 0.29061 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.7 | 5.5 | 5.4 | 0.17078
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-4 | 300-PL-20011-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 23789 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.3 | CML-4 | CML: Pipe Length | 3 | 2024-09-08 | 2024-08-09 | 2014-09-25 07:00 | 2.5 | 0.34127 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 3 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7 | 5.9 | 6.3 | 6 | 0.49666
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-29 | 300-PF-20501-03C03-P CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 21705 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.475 | CML-29 | CML: type TBC | 6 | 2046-12-29 | 2040-12-14 | 2014-09-28 07:00 | 4.9 | 0.27886 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.2 | 14.4 | 15.4 | 13.9 | 0.65
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-40 | 200-PL-20019-01C02 CML-40 |  | FPSO 2014 | Pipe Wall Thickness | 21291 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.425 | CML-40 | CML: Fitting | 3 | 2024-10-21 | 2024-09-21 | 2014-09-30 07:00 | 2.5 | 0.33776 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.3 | 6.7 | 6.8 | 5.9 | 0.4113
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2102 | Rope Access | 2014-03-28 13:00 | 2014-03-28 14:00 | [36 empty] | 5.75 | CML-7 | CML: type TBC | 3 | 2023-11-02 | 2024-12-15 | 2014-03-28 13:00 | 2.5 | 0.29147 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-WC-40021-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.5 | 6.5 | 5.3 | 0.52599
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-11 | 150-FH-43518-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5525 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 7.175 | CML-11 | CML: Elbow | 3 | 2019-11-17 | 2018-10-13 | 2014-06-01 07:00 | 1.23 | 0.90927 | A1: Outside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.2 | 12 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.97 | 0 | 6.2 | 7.5 | 7.5 | 7.5 | 0.65
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-19 | 250-PW-20022-01C03-P CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 23117 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 9.025 | CML-19 | CML: Fitting | 6 | 2048-11-23 | 2046-11-17 | 2015-05-10 07:00 | 2.5 | 0.19067 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.9 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | 0.89461 | 9 | 9 | 9.2 | 8.9 | 0.12583
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-9 | 200-PG-23006-09C02-PA CML-9 | Yes | FPSO 2014 | Pipe Wall Thickness | 23842 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 17.925 | CML-9 | CML: Fitting | 3 | 2025-09-18 | 2021-08-16 | 2014-09-25 07:00 | 9.3 | 0.72804 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 17.3 | 12 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 17.3 | 17.6 | 18.8 | 18 | 0.65
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45018-03C02 | CML-6 | 50-FG-45018-03C02 CML-6 | yes | FPSO 2013 | Pipe Wall Thickness | 10505 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.775 | CML-6 | CML: type TBC | 3 | 2014-06-14 | 2014-06-12 | 2013-11-15 | 2.5 | 2.9287 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45018-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.7 | 5.7 | 4.5 | 4.2 | 0.65
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-12 | 80-DH-56074-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20957 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 5.9 | CML-12 | CML: Elbow | 3 | 2019-05-21 | 2020-01-30 | 2014-05-24 07:00 | 2.5 | 0.50057 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.5 | 6.2 | 5.9 | 5 | 0.64807
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-19 | 200-PL-20008-01C02-H CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8816 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.125 | CML-19 | CML: Pipe Length | 3 | 2025-06-30 | 2025-05-28 | 2015-02-21 07:00 | 2.5 | 0.3185 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 6 | 6.4 | 5.8 | 0.27538
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-5 | 50-PW-44040-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23240 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.025 | CML-5 | CML: Elbow | 3 | 2022-08-22 | 2023-08-18 | 2015-05-11 07:00 | 2.5 | 0.32934 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 0.089024 | 5.1 | 4.9 | 5.2 | 4.9 | 0.15
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-27 | 200-PL-20010-01C02-P CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 23827 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.325 | CML-27 | CML: Pipe Length | 3 | 2024-09-08 | 2024-08-09 | 2014-09-25 07:00 | 2.5 | 0.34127 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 6.3 | 6.4 | 5.9 | 0.3304
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-12 | 200-PG-24001-09C02 CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10268 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 18.1 | CML-12 | CML: Pipe Length | 3 | 2017-03-08 | 2015-12-03 | 2013-11-09 | 9.2 | 2.4031 | A2: Right Quadrant |  | 15.26 | 9.2 | 12.23 | 17.2 | 3 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 18.4 | 17.2 | 18.7 | 18.1 | 0.64807
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-15 | 300-PG-23001-03C03 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 10965 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.1 | CML-15 | CML: Elbow | 6 | 2019-02-01 | 2018-02-17 | 2014-01-09 | 5.22 | 1.5948 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 13.3 | 6 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.08 |  | 13.9 | 14.4 | 13.3 | 14.8 | 0.64807
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20044-03C03-P | CML-8 | 80-PG-20044-03C03-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23336 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-19 07:00 | 2015-07-19 15:00 | [36 empty] | 11.7 | CML-8 | CML: Elbow | 6 | 2093-05-14 | 2081-03-09 | 2015-07-19 07:00 | 2.5 | 0.10786 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 3 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | 0.18966 | 11.5 | 10.9 | 12 | 12.4 | 0.64807
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-4 | 300-PF-20001-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21142 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 14.2 | CML-4 | CML: Pipe Length | 6 | 2024-04-07 | 2022-04-25 | 2014-07-16 07:30 | 4.9 | 0.86288 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 3 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 14.8 | 13.3 | 14.5 | 14.2 | 0.64807
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-6 | 150-PG-20054-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21517 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 12.6 | CML-6 | CML: Elbow | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.9 | 6 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 13.4 | 12.8 | 11.9 | 12.3 | 0.64807
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-19 | 80-CG-38459-09C02-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21428 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 16.7 | CML-19 | CML: Equal Tee | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A3: Inside Quadrant |  | 6.7 | 4.1 | 5.4 | 16 | 6 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 |  | 17.3 | 16.3 | 16 | 17.2 | 0.64807
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-12 | 50-CG-38470-01C02-P CML-12 | Yes | FPSO 2015 | Pipe Wall Thickness | 23618 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 3.5 | CML-12 | CML: Elbow | 3 | 2015-11-27 | 2016-03-03 | 2015-10-28 07:00 | 2.5 | 1.2204 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 2.6 | 3 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.1 |  | 3.5 | 2.6 | 4.1 | 3.8 | 0.64807
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-7 | 50-DH-56062-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 9094 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.3 | CML-7 | CML: type TBC | 3 | 2019-01-28 | 2019-09-07 | 2015-03-02 07:00 | 2.5 | 0.53669 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.5 | 5 | 6.1 | 4.6 | 0.64807
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-4 | 80-PW-44016-01C02-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 21936 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.775 | CML-4 | CML: Elbow | 3 | 2021-09-15 | 2022-09-02 | 2014-10-10 07:00 | 2.5 | 0.36037 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 6.1 | 6.2 | 5.8 | 0.54391
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-7 | 25-FG-45455-01C02-E CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1554 | Rope Access | 2014-04-09 08:00 | 2014-04-09 09:00 | [36 empty] | 6.85 | CML-7 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-09 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-WC-40014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.4 | 7.3 | 6.7 | 6 | 0.6455
PG05 | Montara_Topside | Yes | Diesel Oil (62) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2991 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.25 | CML-6 | CML: Elbow | 1 | 2033-04-19 | 2028-11-21 | 2014-05-01 10:30 | 2.5 | 0.15279 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 5.4 | 6.7 | 6.8 | 0.6455
PG05 | Montara_Topside | Yes | Diesel Oil (62) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22270 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.25 | CML-6 | CML: Elbow | 1 | 2033-04-19 | 2028-11-21 | 2014-05-01 10:30 | 2.5 | 0.15279 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 5.4 | 6.7 | 6.8 | 0.6455
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-6 | 50-PF-20301-03C03-P CML-6 | yes | FPSO 2014 | Pipe Wall Thickness | 3004 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.85 | CML-6 | CML: Elbow | 6 | 2028-05-09 | 2030-09-09 | 2014-05-01 07:00 | 3.61 | 0.30572 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 7.9 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.29 | 0 | 9.2 | 7.9 | 9 | 9.3 | 0.6455
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-6 | 50-PF-20301-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22283 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.85 | CML-6 | CML: Elbow | 6 | 2028-05-09 | 2030-09-09 | 2014-05-01 07:00 | 3.61 | 0.30572 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 7.9 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.29 |  | 9.2 | 7.9 | 9 | 9.3 | 0.6455
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-15 | 200-PW-44018-01X01 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1990 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.475 | CML-15 | CML: Pipe Length | 3 | 2019-01-28 | 2019-09-07 | 2014-03-27 07:00 | 2.5 | 0.5366 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.9 | 5.5 | 5.1 | 5.4 | 0.3304
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-2 | 80-PW-44035-01C02-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 21925 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 5.6 | CML-2 | CML: Elbow | 3 | 2021-09-09 | 2022-08-27 | 2014-10-09 07:00 | 2.5 | 0.3611 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 3 O'Clock | 20 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5 | 5.7 | 6.2 | 0.49666
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-22 | 200-PL-20010-01C02-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 23822 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.225 | CML-22 | CML: Reducing Tee | 3 | 2024-09-08 | 2024-08-09 | 2014-09-25 07:00 | 2.5 | 0.34127 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 3 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 5.9 | 6.1 | 6.5 | 0.27538
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-18 | 250-PG-23004-06C03-A CML-18 |  | FPSO 2016 | Pipe Wall Thickness | 24456 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | [36 empty] | 18.175 | CML-18 | CML: Pipe Length | 6 | 2048-05-09 | 2041-09-05 | 2016-07-05 07:00 | 8.55 | 0.27772 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 17.4 | 9 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.85 | -0.20857 | 18.8 | 18.6 | 17.9 | 17.4 | 0.64485
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-22 | 200-PG-24001-09C02 CML-22 |  | FPSO 2013 | Pipe Wall Thickness | 10278 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 18.375 | CML-22 | CML: Elbow | 3 | 2022-02-05 | 2019-03-12 | 2013-11-09 | 9.2 | 1.0429 | A4: Left Quadrant |  | 15.26 | 9.2 | 12.23 | 17.8 | 9 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 18.2 | 18.2 | 19.3 | 17.8 | 0.64485
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20302-03C03-P | CML-5 | 200-PG-20302-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5858 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 12.725 | CML-5 | CML: Pipe Length | 6 | 2024-07-20 | 2022-07-15 | 2014-06-25 10:30 | 3.3 | 0.84352 | A3: Inside Quadrant |  | 6.7 | 3.3 | 5 | 11.8 | 6 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 13.3 | 12.9 | 11.8 | 12.9 | 0.64485
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-10 | 50-DH-56109-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20999 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.625 | CML-10 | CML: Elbow | 3 | 2016-12-15 | 2017-05-03 | 2014-05-24 10:30 | 2.5 | 0.85777 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.8 | 5.8 | 6.2 | 4.7 | 0.64485
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-30 | 300-PG-20004-03C03-P CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 6153 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.425 | CML-30 | CML: Pipe Length | 6 | 2035-07-16 | 2031-07-24 | 2014-07-11 07:30 | 4.9 | 0.42325 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 15.2 | 14 | 14.7 | 13.8 | 0.64485
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38486-09C02-P | CML-32 | 80-CG-38486-09C02-P CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 5473 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 6.102mm/ yr | [34 empty] | Low alarm breach | 16.325 | CML-32 | CML: Elbow | 3 | 2016-07-07 | 2015-03-19 | 2014-05-28 07:00 | 2.5 | 6.102 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 15.4 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.9 |  | 16.5 | 16.5 | 16.9 | 15.4 | 0.64485
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-13 | 200-PL-20010-01C02-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23526 | Re-check on line as Per RBI 2014 Report | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 6.175 | CML-13 | CML: Fitting | 3 | 2031-11-09 | 2031-09-21 | 2015-07-28 07:00 | 2.5 | 0.20863 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | -0.11928 | 5.9 | 6 | 6.5 | 6.3 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-7 | 50-FH-43137-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12859 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 7.9667 | CML-7 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-01-23 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 6 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.7 | 8.7 | 7.5 |  | 0.64291
PG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45306-03C03-P | CML-1 | 80-FG-45306-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22085 | Protective mesh removed | 2014-07-02 11:00 | 2014-07-02 12:00 | [36 empty] | 10.75 | CML-1 | CML: Pipe Length | 6 | 2022-07-05 | 2021-02-14 | 2014-07-02 11:00 | 2.5 | 0.94827 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.1 | 6 O'Clock | 80 | 11.13 | 80-FG-45306-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 11.3 | 11.3 | 10.1 | 10.3 | 0.64031
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2112 |  | 2014-03-29 07:00 | 2014-03-29 08:00 | Check Corrosion Rate of 0.533mm/ yr | [35 empty] | 5.525 | CML-1 | CML: Reducing Tee | 3 | 2019-02-11 | 2019-09-23 | 2014-03-29 07:00 | 2.5 | 0.53304 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.8 | 5.7 | 5.5 | 5.1 | 0.30957
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-2 | 80-PG-23025-06C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20541 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 11.525 | CML-2 | CML: Pipe Length | 6 | 2076-08-18 | 2067-10-15 | 2014-05-27 08:00 | 2.8 | 0.13168 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 11 | 6 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 | -0.33525 | 11 | 11.8 | 11 | 12.3 | 0.63966
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-22 | 300-PG-20004-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 6145 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.225 | CML-22 | CML: Fitting | 6 | 2031-08-28 | 2028-05-17 | 2014-07-11 07:30 | 4.9 | 0.51331 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 14.5 | 13.7 | 15 | 13.7 | 0.63966
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-12 | 50-CG-38466-01C02 CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 2526 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.525 | CML-12 | CML: type TBC | 3 | 2018-02-15 | 2018-08-18 | 2014-04-02 13:00 | 2.5 | 0.64508 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 5 | 6.4 | 5.1 | 5 | 5.6 | 0.63966
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-8 | 300-FH-43001-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12520 |  | 2014-01-24 13:00 | 2014-01-24 15:00 | [36 empty] | 7.425 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-24 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 9 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7 | 7.5 | 8.3 | 6.9 | 0.63966
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-4 | 250-PG-23015-06C03-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13036 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 14.375 | CML-4 | CML: Elbow | 6 | 2014-10-14 | 2014-07-10 | 2014-01-11 13:00 | 8.55 | 7.0873 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 13.9 | 6 O'Clock | 100 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.35 |  | 14 | 14.3 | 13.9 | 15.3 | 0.63966
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43103-01C02 | CML-1 | 300-FH-43103-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20421 | Protective mesh removed | 2014-07-02 14:00 | 2014-07-02 15:00 | [36 empty] | 10.575 | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-07-02 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.1 | 12 O'Clock | 300 | 6.35 | 300-FH-43103-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.1 | 10.2 | 11.5 | 10.5 | 0.63966
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-2 | 80-DH-56140-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21074 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 11.075 | CML-2 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 10.2 | 6 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 11.6 | 11 | 10.2 | 11.5 | 0.63966
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-19 | 300-PF-20501-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21695 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.025 | CML-19 | CML: Pipe Length | 6 | 2029-07-20 | 2026-08-25 | 2014-09-28 07:00 | 4.9 | 0.58033 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 14.1 | 14.9 | 13.5 | 13.6 | 0.63966
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-17 | 100-PW-20021-01C02-P CML-17 | yes | FPSO 2014 | Pipe Wall Thickness | 21820 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.625 | CML-17 | CML: Elbow | 3 | 2018-02-11 | 2018-04-08 | 2014-10-11 07:00 | 2.5 | 0.74866 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 6 | 5.6 | 5.9 | 0.45
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56126-01C02 | CML-2 | 80-DH-56126-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21047 | Rope Access | 2014-05-17 07:00 | 2014-05-17 08:00 | [36 empty] | 5.675 | CML-2 | CML: type TBC | 3 | 2017-07-27 | 2018-01-20 | 2014-05-17 07:00 | 2.5 | 0.71897 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 9 O'Clock | 80 | 5.49 | 80-DH-56126-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.6 | 6.1 | 6.2 | 4.8 | 0.63966
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-17 | 50-FG-45019-03C02 CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10499 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 8.325 | CML-17 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2013-11-15 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 7.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8.6 | 9 | 8.2 | 0.63966
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56065-01C02 | CML-3 | 50-DH-56065-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3411 | Rope Access | 2014-05-11 09:30 | 2014-05-11 11:00 | [36 empty] | 8.475 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-11 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.8 | 3 O'Clock | 50 | 5.54 | 50-DH-56065-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.8 | 7.8 | 9.2 | 8.1 | 0.63966
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-18 | 50-CG-38452-09C02-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23758 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.375 | CML-18 | CML: Elbow | 3 | 2389-10-29 | 2292-02-08 | 2015-10-30 07:00 | 2.5 | 0.01657 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.1 | 8.7 | 9.5 | 10.2 | 0.63966
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-1 | 50-CG-38487-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20840 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.225 | CML-1 | CML: Elbow | 3 | 2221-12-21 | 2167-10-29 | 2014-10-02 07:00 | 2.5 | 0.0299 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 | -0.48132 | 10.1 | 8.7 | 8.8 | 9.3 | 0.63966
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2098 | Rope Access | 2014-03-28 13:00 | 2014-03-28 14:00 | [36 empty] | 5.775 | CML-3 | CML: type TBC | 3 | 2023-11-02 | 2024-12-15 | 2014-03-28 13:00 | 2.5 | 0.29147 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-WC-40021-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.8 | 5.3 | 6.3 | 0.4113
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56122-01C02 | CML-5 | 50-DH-56122-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1825 |  | 2014-04-29 14:00 | 2014-04-29 14:30 | [36 empty] | 6.375 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-29 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 7.3 | 6.3 | 0.63966
FG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-FG-45455-01C02-E | CML-17 | 25-FG-45455-01C02-E CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20880 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 6.525 | CML-17 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-04 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 80 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.8 | 7.3 | 0.63966
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-23 | 50-PF-20300-03C03-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21589 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.275 | CML-23 | CML: type TBC | 6 | 2031-06-22 | 2031-02-16 | 2014-05-26 09:30 | 2.5 | 0.3453 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.8 | 9.7 | 9.2 | 8.4 | 0.63966
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-5 | 250-PW-44509-01C03-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22990 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 10.05 | CML-5 | CML: Elbow | 6 | 2061-09-11 | 2058-12-13 | 2015-05-05 07:00 | 2.5 | 0.14013 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | 0.37056 | 11.3 | 10.1 | 9 | 9.8 | 0.95394
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23505-09C02-A | CML-3 | 200-PG-23505-09C02-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 373 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 20.425 | CML-3 | CML: Elbow | 3 | 2055-05-31 | 2049-05-31 | 2014-03-12 | 14.06 | 0 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 19.8 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.74 |  | 19.9 | 19.8 | 21 | 21 | 0.66521
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-18 | 50-PL-23300-09C03 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 13134 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 11.475 | CML-18 | CML: type TBC | 6 | 2034-03-18 | 2031-05-14 | 2014-02-04 07:00 | 2.81 | 0.39691 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.8 | 12 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.99 |  | 10.8 | 11.1 | 12.2 | 11.8 | 0.63966
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-57066-01C03 | CML-5 | 50-PL-57066-01C03 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13037 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 15.825 | CML-5 | CML: Pipe Length | 6 | 2015-06-07 | 2015-01-17 | 2014-01-11 13:00 | 8.55 | 4.8116 | A4: Left Quadrant |  | 12.26 | 8.55 | 10.405 | 15.3 | 9 O'Clock | 100 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.75 |  | 15.9 | 15.4 | 16.7 | 15.3 | 0.63966
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-1 | 200-PG-23065-09C02-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20083 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 17.75 | CML-1 | CML: Pipe Length | 3 | 2016-12-18 | 2015-11-06 | 2014-05-29 07:00 | 10.17 | 2.2769 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 16 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.83 | 0.46845 | 17.7 | 16 | 19.1 | 18.2 | 1.3026
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-10 | 150-WC-40006-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1244 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 19.35 | CML-10 | CML: type TBC | 3 | 2023-08-31 | 2024-10-06 | 2014-03-23 13:00 | 2.5 | 0.2964 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.2 | 6 | 5.9 | 0.3873
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 24239 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.3 | CML-1 | CML: Reducer | 3 | 2037-08-28 | 2033-10-10 | 2014-09-24 07:00 | 7.9 | 0.29638 | A1: Outside Quadrant |  | 12.09 | 7.9 | 9.0519 | 14.7 | 12 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 14.7 | 15.8 | 14.8 | 15.9 | 0.6377
WC01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-WC-40006-01C02 | CML-6 | 150-WC-40006-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12992 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 5.6 | CML-6 | CML: type TBC | 3 | 2021-07-04 | 2022-05-17 | 2014-01-20 07:00 | 2.5 | 0.3755 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6 | 5.8 | 5.3 | 5.3 | 0.3559
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43144-01C02 | CML-1 | 100-FH-43144-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10524 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 8.4 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-15 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.9 | 3 O'Clock | 100 | 6.02 | 100-FH-43144-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.4 | 7.9 | 9.3 | 8 | 0.6377
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56061-01C02 | CML-4 | 50-DH-56061-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3368 | Rope Access | 2014-05-10 08:00 | 2014-05-10 09:00 | [36 empty] | 5.5 | CML-4 | CML: type TBC | 3 | 2016-06-15 | 2016-10-12 | 2014-05-10 08:00 | 2.5 | 0.99932 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56061-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.7 | 4.6 | 5.6 | 6.1 | 0.6377
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-23 | 50-DH-56070-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 3239 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.8 | CML-23 | CML: type TBC | 3 | 2021-10-17 | 2022-09-10 | 2014-05-09 07:00 | 2.5 | 0.36256 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 6.3 | 6.4 | 5.2 | 0.6377
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-18 | 200-FH-43025-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2491 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 7.2 | CML-18 | CML: type TBC | 3 | 2075-11-17 | 2075-06-03 | 2014-03-24 07:00 | 2.5 | 0.06159 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 3 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.2 | 6.3 | 7.7 | 7.6 | 0.6377
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-16 | 200-PW-44018-01X01 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2458 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.549mm/ yr | [35 empty] | 5.35 | CML-16 | CML: type TBC | 3 | 2018-12-12 | 2019-07-16 | 2014-03-20 09:30 | 2.5 | 0.54926 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.7 | 5.5 | 5.1 | 0.3
WC01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2115 |  | 2014-03-29 07:00 | 2014-03-29 08:00 | [36 empty] | 5.625 | CML-4 | CML: Reducing Tee | 3 | 2023-11-12 | 2024-12-25 | 2014-03-29 07:00 | 2.5 | 0.29075 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.4 | 5.3 | 5.9 | 0.32016
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3047 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 6.3 | CML-4 | CML: type TBC | 3 | 2033-05-29 | 2035-07-22 | 2014-05-03 07:00 | 2.5 | 0.15195 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.7 | 6.8 | 6.3 | 0.6377
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-10 | 200-PW-44018-01X01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1985 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.425 | CML-10 | CML: Fitting | 3 | 2019-01-28 | 2019-09-07 | 2014-03-27 07:00 | 2.5 | 0.5366 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 5.7 | 5.6 | 0.27538
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-26 | 200-FH-43025-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 2499 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 10.55 | CML-26 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.6 | 3 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.8 | 9.6 | 10.9 | 10.9 | 0.63509
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40047-01C02 | CML-6 | 50-WC-40047-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1706 | Rope Access | 2014-04-13 10:15 | 2014-04-13 11:15 | [36 empty] | 5.525 | CML-6 | CML: Elbow | 3 | 2024-05-22 | 2025-07-26 | 2014-04-13 10:15 | 2.5 | 0.27684 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-WC-40047-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 6 | 5.4 | 0.32016
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23048-09C02 | CML-6 | 50-PG-23048-09C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20588 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.55 | CML-6 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.9 | 3 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10.4 | 8.9 | 9.3 | 9.6 | 0.63509
WC01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-WC-40006-01C02 | CML-10 | 150-WC-40006-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12996 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 5.5 | CML-10 | CML: type TBC | 3 | 2021-07-04 | 2022-05-17 | 2014-01-20 07:00 | 2.5 | 0.3755 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.5 | 5.3 | 5.3 | 0.28284
PG05 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 250-PG-23003-06C02-PA | CML-8 | 250-PG-23003-06C02-PA CML-8 | yes | FPSO 2014 | Pipe Wall Thickness | 2522 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 5.7667 | CML-8 | CML: type TBC | 3 | 2031-07-31 | 2033-07-12 | 2014-04-02 13:00 | 2.5 | 0.16724 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 5.4 |  | 5.4 | 6.5 | 5.4 | 0.63509
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-6 | 150-WC-40006-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1941 | Rope Access. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Mar. 2020). RBI to be updated | 2014-03-26 09:30 | 2014-03-26 10:30 |  |  | Administrator | 2015-09-08 12:56 | [32 empty] | 5.5 | CML-6 | CML: Pipe Length | 3 | 2023-10-06 | 2024-11-15 | 2014-03-26 09:30 | 2.5 | 0.29357 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.4 | 5.9 | 0.2708
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-11 | 80-CG-38459-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 13082 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 15.7667 | CML-11 | CML: Tee | 6 | 2096-09-16 | 2085-01-22 | 2014-02-07 11:00 | 2.8 | 0 | A2: Right Quadrant |  | 5.13 | 2.8 | 3.965 | 15.4 | 9 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.6 |  |  | 15.4 | 16.5 | 15.4 | 0.63509
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-4 | 50-CG-38001-09C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10917 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 12.5333 | CML-4 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0 | A1: Outside Quadrant |  | 5.74 |  |  | 11.8 | 12 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 11.8 | 11.8 | 12.9 |  | 12.9 | 0.63509
WC01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-WC-40006-01C02 | CML-19 | 150-WC-40006-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2461 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 5.65 | CML-19 | CML: type TBC | 3 | 2023-07-22 | 2024-08-23 | 2014-03-20 09:30 | 2.5 | 0.29959 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.8 | 5.3 | 5.9 | 5.6 | 0.26458
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-1 | 200-PG-23065-09C02-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 415 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 17.775 | CML-1 | CML: Pipe Length | 3 | 2016-05-01 | 2015-06-01 | 2014-03-12 09:00 | 10.17 | 2.7724 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 16.1 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.93 |  | 17.7 | 16.1 | 19.1 | 18.2 | 1.258
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-22 | 350-FL-43511-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 2303 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 12.775 | CML-22 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 12 | 6 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 13 | 12.6 | 12 | 13.5 | 0.63443
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-20 | 100-WC-40516-1CG CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 8693 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:57 | [32 empty] | 9.125 | CML-20 | CML: Elbow | 3 | 2074-01-04 | 2058-09-17 | 2015-02-13 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.56 | 2.5 | 4.03 | 8.8 | 3 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.3 | 8.8 | 9.3 | 9.1 | 0.23629
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-10 | 80-CG-38459-09C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23707 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 6.2 | CML-10 | CML: Elbow | 3 | 2093-07-29 | 2102-11-29 | 2015-10-30 07:00 | 2.5 | 0.03727 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 40 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.4 | 6.6 | 6.8 | 0.63246
FL01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 150-FL-43174-01C02 | CML-6 | 150-FL-43174-01C02 CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 23697 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.125 | CML-6 | CML: Elbow | 3 | 2017-01-04 | 2017-05-25 | 2015-10-30 07:00 | 2.5 | 0.8449 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.5 | 3 O'Clock | 50 | 5.54 | 50-CG-38456-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4 | 3.5 | 4 | 5 | 0.62915
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-40 | 50-DH-56062-01C02 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 9127 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 6.175 | CML-40 | CML: type TBC | 3 | 2035-08-02 | 2037-12-18 | 2015-03-02 07:00 | 2.5 | 0.13703 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.8 | 6.3 | 6.3 | 5.3 | 0.62915
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-12 | 250-PG-23003-06C02-PA CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5509 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 17.875 | CML-12 | CML: Pipe Length | 3 | 2016-09-27 | 2016-04-06 | 2014-05-31 07:00 | 14.06 | 1.2625 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 17 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.94 | 0 | 18 | 17 | 18 | 18.5 | 0.62915
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-12 | 250-PG-23003-06C02-PA CML-12 | no | FPSO 2014 | Pipe Wall Thickness | 20657 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 17.875 | CML-12 | CML: Pipe Length | 3 | 2016-09-27 | 2016-04-06 | 2014-05-31 07:00 | 14.06 | 1.2625 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 17 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.94 | 0.91345 | 18 | 17 | 18 | 18.5 | 0.62915
WC01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2271 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 5.525 | CML-7 | CML: Fitting | 3 | 2023-06-03 | 2024-06-29 | 2014-03-16 11:30 | 2.5 | 0.30366 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.7 | 5.3 | 5.8 | 0.263
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-2 | 100-PW-20021-01C02-P CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 21805 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.375 | CML-2 | CML: Elbow | 3 | 2018-02-11 | 2018-04-08 | 2014-10-11 07:00 | 2.5 | 0.74866 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 6 | 5.3 | 0.43493
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-17 | 50-FG-45301-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 5803 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.125 | CML-17 | CML: Elbow | 3 | 2022-11-26 | 2023-12-02 | 2014-06-23 13:00 | 2.5 | 0.32022 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.4 | 6.6 | 6.3 | 5.2 | 0.62915
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-12 | 200-PW-44018-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2454 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.549mm/ yr | [35 empty] | 5.5 | CML-12 | CML: type TBC | 3 | 2018-12-12 | 2019-07-16 | 2014-03-20 09:30 | 2.5 | 0.54926 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.7 | 5.1 | 5.6 | 0.2708
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-41 | 300-PF-20003-03C03-P CML-41 |  | FPSO 2014 | Pipe Wall Thickness | 21779 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 16.925 | CML-41 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-10-01 07:00 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 16 | 6 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 17.4 | 17.1 | 16 | 17.2 | 0.62915
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43115-01C02 | CML-2 | 80-FH-43115-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12822 |  | 2014-01-20 09:00 | 2014-01-20 10:00 | [36 empty] | 6 | CML-2 | CML: type TBC | 3 | 2020-01-02 | 2020-10-08 | 2014-01-20 09:00 | 2.5 | 0.45356 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-FH-43115-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.7 | 5.9 | 5.2 | 6.2 | 0.62716
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24405 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.3 | CML-4 | CML: Pipe Length | 1 | 2043-01-05 | 2033-03-19 | 2016-06-08 07:00 | 2.53 | 0 | A2: Right Quadrant |  | 4.49 | 2.53 | 3.51 | 5.5 | 3 O'Clock | 50 | 5.49 | 80-FG-45045-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.97 |  | 6.1 | 5.5 | 6.8 | 6.8 | 0.62716
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-2 | 300-PW-44003-01C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21844 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 9.85 | CML-2 | CML: Reducing Tee | 6 | 2021-08-30 | 2020-09-15 | 2014-10-19 07:00 | 2.5 | 0.94629 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.2 | 10.8 | 10.4 | 9 | 0.88506
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-20 | 300-PF-20001-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21158 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.774mm/ yr | 40 | Kirstie Albone | 2017-03-23 13:53 | [32 empty] | 14.1 | CML-20 | CML: Fitting | 6 | 2025-07-07 | 2023-05-04 | 2014-07-16 07:30 | 4.9 | 0.77392 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 13.4 | 14.9 | 14.2 | 13.9 | 0.62716
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-13 | 50-CG-38470-01C02-P CML-13 | Yes | FPSO 2015 | Pipe Wall Thickness | 23619 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 3.75 | CML-13 | CML: Pipe Length | 3 | 2016-05-31 | 2016-09-26 | 2015-10-28 07:00 | 2.5 | 1.0129 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.1 | 12 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.6 |  | 3.1 | 3.6 | 3.7 | 4.6 | 0.6245
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-10 | 80-FH-43158-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12891 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 6.45 | CML-10 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-22 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 9 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 7.2 | 6.1 | 6.7 | 5.8 | 0.6245
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-15 | 200-PG-23008-15S01-A CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 9102 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.75 | CML-15 | CML: type TBC | 3 | 2025-07-04 | 2026-10-21 | 2015-03-02 07:00 | 2.5 | 0.25122 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.5 | 6 | 5.1 | 5.4 | 0.6245
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-4 | 100-WC-40516-1CG CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8677 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:54 | [32 empty] | 9.25 | CML-4 | CML: Elbow | 3 | 2074-01-04 | 2058-09-17 | 2015-02-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.56 | 2.5 | 4.03 | 8.9 | 6 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.4 | 9.5 | 8.9 | 9.2 | 0.26458
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56068-01C02 | CML-3 | 50-DH-56068-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3353 | Rope Access | 2014-05-08 14:00 | 2014-05-08 14:30 | [36 empty] | 5.75 | CML-3 | CML: type TBC | 3 | 2018-09-05 | 2019-03-31 | 2014-05-08 14:00 | 2.5 | 0.57702 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DH-56068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.5 | 5.9 | 5.6 | 5 | 0.6245
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23037-25C02-A | CML-11 | 150-PG-23037-25C02-A CML-11 | yes | FPSO 2014 | Pipe Wall Thickness | 13101 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 23.975 | CML-11 | CML: Elbow | 3 | 2074-02-10 | 2058-10-06 | 2014-01-10 09:00 | 15.88 | 0 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 22.1 | 9 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.22 |  | 24.4 | 26.4 | 23 | 22.1 | 1.8733
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-10 | 200-PG-23065-09C02-A CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 20084 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 19.125 | CML-10 | CML: Elbow | 3 | 2020-12-26 | 2018-08-09 | 2014-05-29 07:00 | 10.17 | 1.0679 | A3: Inside Quadrant |  | 15.26 | 10.17 | 12.715 | 17.2 | 6 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.03 | 0.9369 | 21.1 | 19.8 | 17.2 | 18.4 | 1.6919
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-8 | 150-FL-43174-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12906 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.95 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 3 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8 | 7.1 | 8.1 | 8.6 | 0.6245
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-14 | 50-CG-38487-09C02-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23583 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 9.15 | CML-14 | CML: Elbow | 3 | 2072-08-03 | 2057-03-24 | 2015-09-10 07:00 | 2.5 | 0.10538 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 | 0.53207 | 9.1 | 8.5 | 9 | 10 | 0.6245
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-7 | 50-CG-38452-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2506 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.45 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.2 | 8.1 | 7.8 | 6.7 | 0.6245
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56558-01C02 | CML-3 | 50-DH-56558-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21134 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-21 08:56 | [32 empty] | 7.1 | CML-3 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-08 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56558-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.6 |  | 6.4 | 7.3 | 0.6245
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38459-09C02-P | CML-13 | 80-CG-38459-09C02-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23441 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 15.275 | CML-13 | CML: Elbow | 3 | 2019-05-07 | 2016-11-06 | 2015-07-23 07:00 | 2.5 | 3.1914 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 14.6 | 6 O'Clock | 250 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.1 | 3.0362 | 15.3 | 15.1 | 14.6 | 16.1 | 0.62383
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-1 | 200-PG-20300-03C03-P CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24481 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.74mm/ yr |  | Kirstie Albone | 2017-03-23 10:08 | Loss within CA no further action required, include in next inspection | [31 empty] | 10.975 | CML-1 | CML: Elbow | 6 | 2026-02-08 | 2023-10-24 | 2016-07-09 07:00 | 3.3 | 0.74011 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 10.4 | 12 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 | -0.10282 | 10.4 | 10.6 | 11.1 | 11.8 | 0.62383
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-51 | 300-PF-20003-03C03-P CML-51 |  | FPSO 2014 | Pipe Wall Thickness | 21789 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 12.925 | CML-51 | CML: Elbow | 6 | 2019-09-01 | 2018-05-21 | 2014-10-01 07:00 | 4.1 | 1.6254 | A4: Left Quadrant |  | 8.27 | 4.1 | 6.185 | 12.1 | 9 O'Clock | 250 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 13.3 | 13.5 | 12.8 | 12.1 | 0.62383
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-17 | 300-PG-20004-03C03-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 6140 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.025 | CML-17 | CML: Fitting | 6 | 2022-04-20 | 2020-09-14 | 2014-07-11 07:30 | 4.9 | 1.0536 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.1 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 13.1 | 14.4 | 14.2 | 14.4 | 0.62383
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-9 | 100-DH-56082-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 3377 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 5.475 | CML-9 | CML: type TBC | 3 | 2016-02-16 | 2016-03-20 | 2014-05-10 09:30 | 2.5 | 1.2968 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 6 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6.1 | 5.9 | 4.8 | 5.1 | 0.62383
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-1 | 50-DH-56070-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3217 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.075 | CML-1 | CML: type TBC | 3 | 2084-08-21 | 2092-04-12 | 2014-05-09 07:00 | 2.5 | 0.04265 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 6.9 | 5.5 | 6.2 | 0.62383
WC01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2266 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 5.575 | CML-2 | CML: Elbow | 3 | 2023-06-03 | 2024-06-29 | 2014-03-16 11:30 | 2.5 | 0.30366 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.9 | 5.3 | 5.6 | 0.25
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-2 | 50-PL-20033-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21831 |  | 2014-10-12 07:00 | 2014-10-12 12:00 | [36 empty] | 6.25 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | -1.0438 | 5.9 | 6.4 | 6.3 | 6.4 | 0.23805
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-26 | 100-PW-20021-01C02-P CML-26 | yes | FPSO 2015 | Pipe Wall Thickness | 22844 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.4 | CML-26 | CML: Elbow | 3 | 2020-01-05 | 2020-03-25 | 2015-04-30 07:00 | 2.5 | 0.53316 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.72637 | 5.6 | 5.1 | 5.9 | 5 | 0.42426
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-3 | 50-CG-38467-01C02 CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 22274 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.675 | CML-3 | CML: Equal Tee | 3 | 2025-01-05 | 2026-04-05 | 2014-05-01 11:00 | 2.5 | 0.26192 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0 | 5.3 | 5.3 | 6.6 | 5.5 | 0.62383
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-3 | 50-CG-38467-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2995 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.675 | CML-3 | CML: Equal Tee | 3 | 2025-01-05 | 2026-04-05 | 2014-05-01 11:00 | 2.5 | 0.26192 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 6.6 | 5.5 | 0.62383
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-9 | 200-PW-44018-01X01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2451 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.549mm/ yr | [35 empty] | 5.5 | CML-9 | CML: type TBC | 3 | 2018-12-12 | 2019-07-16 | 2014-03-20 09:30 | 2.5 | 0.54926 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.7 | 5.1 | 5.6 | 0.2708
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-18 | 100-DH-56086-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 20977 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 7.375 | CML-18 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.7 | 12 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 8 | 7.8 | 7 | 0.62383
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-5 | 200-PG-20300-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5870 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | [36 empty] | 12.775 | CML-5 | CML: Elbow | 6 | 2046-10-27 | 2040-10-11 | 2014-06-25 09:30 | 3.3 | 0.2812 | A2: Right Quadrant |  | 6.7 | 3.3 | 5 | 12.4 | 9 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 12.6 | 12.4 | 13.7 | 12.4 | 0.62383
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-7 | 250-PW-20022-01C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2050 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 9.75 | CML-7 | CML: Elbow | 6 | 2034-01-11 | 2032-11-09 | 2014-03-28 07:00 | 2.5 | 0.32818 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 9 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.8 | 10.4 | 9.8 | 9 | 0.57446
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-10 | 200-PG-23065-09C02-A CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 424 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.175 | CML-10 | CML: Elbow | 3 | 2020-09-27 | 2018-06-08 | 2014-03-12 09:00 | 10.17 | 1.1038 | A3: Inside Quadrant |  | 15.26 | 10.17 | 12.715 | 17.4 | 6 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.23 |  | 21.1 | 19.8 | 17.4 | 18.4 | 1.6174
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-13 | 50-PF-20300-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21579 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.5 | CML-13 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 10.4 | 9.4 | 9.2 | 9 | 0.62183
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21021 | Rope Access | 2014-05-19 11:00 | 2014-05-19 12:00 | [36 empty] | 5.6 | CML-2 | CML: type TBC | 3 | 2020-01-31 | 2020-10-18 | 2014-05-19 11:00 | 2.5 | 0.45566 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.5 | 6.5 | 5.1 | 0.62183
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-9 | 150-FH-43136-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2770 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.2 | CML-9 | CML: Elbow | 3 | 2019-04-13 | 2018-03-23 | 2014-03-13 09:00 | 1.03 | 1.036 | A4: Left Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.3 | 9 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.27 |  | 7.3 | 7.7 | 7.5 | 6.3 | 0.62183
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-11 | 200-PL-20035-03C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21334 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.575 | CML-11 | CML: Elbow | 3 | 2017-12-13 | 2017-03-04 | 2014-06-27 13:00 | 3.61 | 1.0068 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.1 | 6 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.49 |  | 7.9 | 8 | 7.1 | 7.3 | 0.44253
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-1 | 50-PL-23514-01C03 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8634 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:17 | [32 empty] | 8.7 | CML-1 | CML: Elbow | 6 | 2024-09-03 | 2024-06-16 | 2015-02-10 11:30 | 2.5 | 0.55385 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.8 | 6 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 9.2 | 8.8 | 7.8 | 9 | 0.62183
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-6 | 100-DH-56561-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7938 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 9.7 | CML-6 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-17 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9 | 12 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.4 | 10 | 10.4 | 0.62183
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-3 | 100-DH-56561-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7935 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 10.4 | CML-3 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-17 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.7 | 12 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 11.1 | 10.7 | 10.1 | 0.62183
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43126-01C02 | CML-3 | 100-FH-43126-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2512 | Rope Access | 2014-03-24 14:30 | 2014-03-24 15:00 | [36 empty] | 10.8 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-24 14:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.9 | 12 O'Clock | 100 | 6.02 | 100-FH-43126-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 11.1 | 10.9 | 11.3 | 0.62183
PL03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PL-57066-01C03 | CML-8 | 50-PL-57066-01C03 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22873 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.2 | CML-8 | CML: Reducing Tee | 6 | 2028-03-21 | 2026-07-03 | 2015-05-01 07:00 | 2.5 | 0.52718 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.3 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | 0.37629 | 10.3 | 10.7 | 10.5 | 9.3 | 0.62183
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23029-25C02-P | CML-8 | 80-PG-23029-25C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20566 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [36 empty] | 23.1 | CML-8 | CML: Fitting | 3 | 2024-10-24 | 2043-08-22 | 2014-07-02 07:00 | 14.1 | 0 | A4: Left Quadrant |  | 12.24 | 14.1 | 12.2175 | 22.6 | 9 O'Clock | 150 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 22.8 | 24 | 23 | 22.6 | 0.62183
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-19 | 200-PG-24001-09C02 CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10275 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 18.3 | CML-19 | CML: Elbow | 3 | 2022-02-05 | 2019-03-12 | 2013-11-09 | 9.2 | 1.0429 | A3: Inside Quadrant |  | 15.26 | 9.2 | 12.23 | 17.8 | 6 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 19.2 | 18.2 | 17.8 | 18 | 0.62183
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-8 | 250-PG-20036-01C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21366 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.45 | CML-8 | CML: Elbow | 6 | 2018-12-09 | 2018-08-16 | 2014-07-14 07:30 | 2.5 | 1.2247 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.9 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9.3 | 8.5 | 7.9 | 8.1 | 0.61914
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23023-03C03 | CML-11 | 50-PL-23023-03C03 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10211 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.55 | CML-11 | CML: type TBC | 6 | 2017-02-09 | 2017-01-14 | 2013-11-08 | 2.5 | 1.6881 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8 | 3 O'Clock | 50 | 8.74 | 50-PL-23023-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 9.4 | 8 | 8.6 | 8.2 | 0.61914
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-8 | 350-FL-43511-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2289 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 10.25 | CML-8 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 9.4 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.2 | 10.8 | 10.6 | 9.4 | 0.61914
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-5 | 50-PW-44040-01C02 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 1980 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.3 | CML-5 | CML: Elbow | 3 | 2018-01-10 | 2018-07-10 | 2014-03-27 07:00 | 2.5 | 0.65855 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.9 | 5.1 | 5 | 5.2 | 0.40825
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-7 | 100-PG-23028-25C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 446 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 17.325 | CML-7 | CML: Pipe Length | 3 | 2021-10-06 | 2019-03-19 | 2014-03-12 09:00 | 9.4 | 0.92413 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 16.4 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 17.6 | 16.4 | 17.6 | 17.7 | 0.61847
FG01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-FG-45024-01C02 | CML-1 | 50-FG-45024-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1362 | Rope access | 2014-04-04 13:00 | 2014-04-04 15:00 | [36 empty] | 9.875 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-04 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 10.4 | 9.5 | 10.4 | 0.61847
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-11 | 150-WC-40006-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1986 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.625 | CML-11 | CML: Pipe Length | 3 | 2023-10-18 | 2024-11-27 | 2014-03-27 07:00 | 2.5 | 0.29269 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.8 | 5.8 | 5.3 | 0.23629
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-19 | 100-PW-20021-01C02-P CML-19 | yes | FPSO 2015 | Pipe Wall Thickness | 22837 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.4 | CML-19 | CML: Elbow | 3 | 2020-01-05 | 2020-03-25 | 2015-04-30 07:00 | 2.5 | 0.53316 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 3 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.36318 | 5.7 | 5 | 5.7 | 5.2 | 0.3559
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-9 | 200-PL-20035-03C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21344 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.55 | CML-9 | CML: Reducer | 3 | 2017-12-13 | 2017-03-04 | 2014-06-27 13:00 | 3.61 | 1.0068 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 7.1 | 9 O'Clock | 150 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.49 |  | 7.6 | 7.5 | 8 | 7.1 | 0.36968
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-4 | 80-CG-38459-09C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23701 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 15.275 | CML-4 | CML: Reducing Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 14.8 | 3 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.3 |  | 14.8 | 14.8 | 16.1 | 15.4 | 0.61847
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56127-01C02 | CML-1 | 80-DH-56127-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21049 | Rope Access | 2014-05-22 14:00 | 2014-05-22 15:00 | [36 empty] | 5.675 | CML-1 | CML: Elbow | 3 | 2017-08-19 | 2018-02-15 | 2014-05-22 14:00 | 2.5 | 0.70827 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 9 O'Clock | 80 | 5.49 | 80-DH-56127-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6.2 | 5.7 | 6 | 4.8 | 0.61847
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-10 | 50-DH-56137-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 5451 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 3.576mm/ yr | [34 empty] | Low alarm breach | 18.725 | CML-10 | CML: Elbow | 3 | 2018-09-16 | 2016-06-24 | 2014-05-28 07:00 | 2.5 | 3.5763 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 17.9 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 |  | 18.8 | 18.8 | 19.4 | 17.9 | 0.61847
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-2 | 100-WC-40027-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 834 |  | 2014-04-02 09:00 | 2014-04-02 10:00 | Check Corrosion Rate of 0.861mm/ yr |  | Nestor | 2016-04-01 | [32 empty] | 5.525 | CML-2 | CML: Elbow | 3 | 2017-07-02 | 2017-08-21 | 2014-04-02 09:00 | 2.5 | 0.86058 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 6 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.7 | 5.3 | 5.6 | 0.17078
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40062-01C02 | CML-3 | 100-WC-40062-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 827 |  | 2014-04-02 08:00 | 2014-04-02 09:00 | Check Corrosion Rate of 0.861mm/ yr | [35 empty] | 5.425 | CML-3 | CML: Elbow | 3 | 2017-07-02 | 2017-08-21 | 2014-04-02 08:00 | 2.5 | 0.8607 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 9 O'Clock | 100 | 6.02 | 100-WC-40062-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 5.6 | 5.3 | 0.15
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38482-01C02 | CML-2 | 25-CG-38482-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10377 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.475 | CML-2 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 12 O'Clock | 25 | 6.35 | 25-CG-38482-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.6 | 6.5 | 6.8 | 7 | 0.61847
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56087-01C02 | CML-9 | 100-DH-56087-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8039 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:32 | [32 empty] | 7.025 | CML-9 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2015-01-20 14:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.3 | 3 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.8 | 6.3 | 7.1 | 6.9 | 0.61847
CG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2874 | Rope Access | 2014-04-24 13:00 | 2014-04-24 14:00 | Check Corrosion Rate of 0.602mm/ yr | [35 empty] | 5.825 | CML-2 | CML: type TBC | 3 | 2021-12-31 | 2020-10-09 | 2014-04-24 13:00 | 0.37 | 0.60176 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 5 | 12 O'Clock | 50 | 5.54 | 50-DC-57024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.63 |  | 5 | 5.9 | 6.5 | 5.9 | 0.61847
WC01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12987 |  | 2014-01-20 07:00 | 2014-01-20 09:00 | [36 empty] | 5.5 | CML-1 | CML: type TBC | 3 | 2021-07-04 | 2022-05-17 | 2014-01-20 07:00 | 2.5 | 0.3755 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 5.6 | 5.6 | 0.14142
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-4 | 50-FG-45024-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23503 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 8.375 | CML-4 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2015-07-28 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.6 | 12 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.57 | 0.26449 | 7.6 | 8.3 | 8.5 | 9.1 | 0.61847
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38460-01C02-P | CML-7 | 80-CG-38460-01C02-P CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 20888 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 8.575 | CML-7 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.7 | 6 O'Clock | 50 | 5.49 | 80-CG-38460-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9.1 | 8.6 | 7.7 | 8.9 | 0.61847
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40510-1CG | CML-2 | 100-WC-40510-1CG CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8662 | Material Class Not Selectable | 2015-02-12 11:00 | 2015-02-12 12:00 |  |  | Administrator | 2015-09-08 12:16 | [32 empty] | 9.5 | CML-2 | CML: Elbow | 3 | 2074-01-04 | 2058-09-17 | 2015-02-12 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.56 | 2.5 | 4.03 | 9 | 9 O'Clock | 100 | 8.56 | 100-WC-40510-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.6 | 9.7 | 9.7 | 9 | 0.33665
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-6 | 50-DH-56109-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20995 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 6.775 | CML-6 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-05-24 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.8 | 7.1 | 7.3 | 0.61847
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38008-01C02 | CML-2 | 50-CG-38008-01C02 CML-2 | Yes | FPSO 2015 | Pipe Wall Thickness | 8430 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 8.175 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 3 O'Clock | 15 | 5.54 | 50-CG-38008-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.7 | 7.5 | 7.8 | 8.7 | 0.61847
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38491-09C02 | CML-2 | 50-CG-38491-09C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2541 |  | 2014-04-03 10:00 | 2014-04-03 11:00 | [36 empty] | 9.175 | CML-2 | CML: type TBC | 3 | 2025-04-24 | 2022-03-23 | 2014-04-03 10:00 | 2.5 | 0.52412 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 12 O'Clock | 50 | 8.74 | 50-CG-38491-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.5 | 9.2 | 9.7 | 0.61847
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20045-03C03-P | CML-1 | 80-PG-20045-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21457 | Protective mesh removed | 2014-06-29 11:00 | 2014-06-29 12:00 | [36 empty] | 11.375 | CML-1 | CML: Elbow | 6 | 2053-11-01 | 2047-09-04 | 2014-06-29 11:00 | 2.5 | 0.21336 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 9 O'Clock | 80 | 11.13 | 80-PG-20045-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 12.2 | 10.9 | 11.5 | 10.9 | 0.61847
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-3 | 80-FH-43005-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12553 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 5.8 | CML-3 | CML: type TBC | 3 | 2023-06-22 | 2024-08-22 | 2014-01-20 10:00 | 2.5 | 0.29711 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 12 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.7 | 5.6 | 5.6 | 0.61644
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1412 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.729mm/ yr | [35 empty] | 6.1 | CML-6 | CML: type TBC | 3 | 2018-03-28 | 2018-05-25 | 2014-04-07 07:00 | 2.5 | 0.72931 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.1 | 6.9 | 6 | 0.61644
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38493-01C02 | CML-5 | 25-CG-38493-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10374 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.4 | CML-5 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 12 O'Clock | 25 | 6.35 | 25-CG-38493-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.6 | 6.5 | 6.4 | 7.1 | 0.61644
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-2 | 50-PF-20301-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3000 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.3 | CML-2 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 8.6 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.99 | 0 | 9.2 | 8.6 | 9.3 | 10.1 | 0.61644
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-2 | 50-PF-20301-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22279 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.3 | CML-2 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 8.6 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.99 |  | 9.2 | 8.6 | 9.3 | 10.1 | 0.61644
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-24 | 50-PW-44040-01C02 CML-24 | yes | FPSO 2014 | Pipe Wall Thickness | 1999 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.3 | CML-24 | CML: Elbow | 3 | 2018-01-10 | 2018-07-10 | 2014-03-27 07:00 | 2.5 | 0.65855 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.6 | 5 | 5 | 5.6 | 0.34641
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-18 | 100-PW-20021-01C02-P CML-18 | yes | FPSO 2015 | Pipe Wall Thickness | 22836 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.35 | CML-18 | CML: Elbow | 3 | 2020-01-05 | 2020-03-25 | 2015-04-30 07:00 | 2.5 | 0.53316 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.36318 | 5 | 5.3 | 5.3 | 5.8 | 0.33166
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-22 | 150-WC-40006-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 1997 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.45 | CML-22 | CML: Pipe Length | 3 | 2023-10-18 | 2024-11-27 | 2014-03-27 07:00 | 2.5 | 0.29269 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.4 | 5.3 | 5.5 | 0.1291
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-1 | 250-PW-44509-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22036 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.55 | CML-1 | CML: Pipe Length | 6 | 2048-03-03 | 2046-03-12 | 2014-10-20 07:00 | 2.5 | 0.19465 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.9 | 9.5 | 9 | 9.8 | 0.40415
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-19 | 80-PW-44016-01C02-P CML-19 | yes | FPSO 2014 | Pipe Wall Thickness | 21951 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.425 | CML-19 | CML: Equal Tee | 3 | 2021-09-15 | 2022-09-02 | 2014-10-10 07:00 | 2.5 | 0.36037 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.4 | 5.8 | 5 | 0.3304
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-26 | 250-PL-20006-01C02-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 13196 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 7.4 | CML-26 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A3: Inside Quadrant |  | 3.35 | 3.61 | 3.0831 | 7.1 | 6 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.49 |  | 7.5 | 7.4 | 7.1 | 7.6 | 0.21602
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 200-WC-40400-01C02 | CML-3 | 200-WC-40400-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20404 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.95 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 6 O'Clock | 200 | 6.35 | 200-WC-40400-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.1 | 6.9 | 6.7 | 7.1 | 0.19149
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-10 | 50-CG-38452-09C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23750 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.65 | CML-10 | CML: Elbow | 3 | 2031-05-04 | 2026-09-08 | 2015-10-30 07:00 | 2.5 | 0.3479 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 7.9 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.7 | 7.9 | 8.6 | 9.4 | 0.61373
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-12 | 80-PL-44008-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23780 | Reject Oil Line Re-Inspection | 2015-04-18 07:00 | 2015-04-18 15:00 | [36 empty] | 6.7 | CML-12 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-04-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 12 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 2.3139 | 6 | 7.1 | 7.4 | 6.3 | 0.65828
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-13 | 50-PW-44013-01X01 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10327 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.375 | CML-13 | CML: Reducer | 3 | 2016-06-24 | 2016-10-22 | 2013-11-10 | 2.5 | 0.99136 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.4 | 5.1 | 5.7 | 0.25
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-10 | 200-PL-20018-01C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23476 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 6.425 | CML-10 | CML: Fitting | 3 | 2037-01-02 | 2036-10-31 | 2015-07-24 07:00 | 2.5 | 0.16309 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 40 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 0.48505 | 6 | 6.8 | 6.3 | 6.6 | 0.35
FH01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-FH-43507-01C02 | CML-6 | 100-FH-43507-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21603 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 10.35 | CML-6 | CML: Equal Tee | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 9.8 | 9 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.19 |  | 11.1 | 10.6 | 9.9 | 9.8 | 0.61373
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-21 | 100-FG-45001-09C02 CML-21 | Yes | FPSO 2015 | Pipe Wall Thickness | 23326 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.85 | CML-21 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 11.3 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | -0.78392 | 12.6 | 11.3 | 11.4 | 12.1 | 0.61373
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-21 | 50-PF-20300-03C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21587 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.375 | CML-21 | CML: type TBC | 6 | 2038-12-31 | 2038-07-04 | 2014-05-26 09:30 | 2.5 | 0.24374 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.8 | 9.8 | 9.4 | 8.5 | 0.61305
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-6 | 50-DC-57450-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20322 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.75 | CML-6 | CML: Elbow | 3 | 2042-08-16 | 2045-10-03 | 2014-10-05 07:00 | 2.5 | 0.10401 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.8 | 6.1 | 5.4 | 0.28868
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 200-WC-40400-01C02 | CML-4 | 200-WC-40400-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20405 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.925 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 6 O'Clock | 200 | 6.35 | 200-WC-40400-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.1 | 6.9 | 6.7 | 7 | 0.17078
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 200-WC-40400-01C02 | CML-1 | 200-WC-40400-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20402 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 8.325 | CML-1 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2014-10-18 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 12 O'Clock | 200 | 6.35 | 200-WC-40400-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.8 | 8.3 | 8.2 | 0.34034
DH01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-DH-56137-01C02 | CML-5 | 50-DH-56137-01C02 CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24305 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 17.125 | CML-5 | CML: Reducing Tee | 3 | 2054-10-24 | 2049-02-10 | 2016-05-27 07:00 | 1.88 | 0 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 16.5 | 12 O'Clock | 40 | 6.02 | 100-FG-45008-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.62 |  | 16.5 | 17.7 | 17.6 | 16.7 | 0.61305
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-8 | 50-CG-38465-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20871 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 5.675 | CML-8 | CML: Reducer | 3 | 2042-07-25 | 2045-09-09 | 2014-10-04 07:00 | 2.5 | 0.10422 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 80 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.8 | 5.9 | 5.4 | 0.22174
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38462-01C02 | CML-2 | 50-CG-38462-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20830 | Reviewed on 20/11/14. FFS. This line has not been RBI assessed. CML to be rechecked Oct. 18 based on other line on this circuit which are a 48m interval | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 15:39 | [32 empty] | 5.575 | CML-2 | CML: Reducing Tee | 3 | 2042-07-25 | 2045-09-09 | 2014-10-04 07:00 | 2.5 | 0.10422 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-CG-38462-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 5.4 | 5.4 | 5.4 | 0.35
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38464-01C02 | CML-5 | 50-CG-38464-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20839 | Reviewed on 20/11/14. FFS. This line has not been RBI assessed. CML to be rechecked Oct. 18 based on other line on this circuit which are a 48m interval | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 16:18 | [32 empty] | 6.075 | CML-5 | CML: Elbow | 3 | 2042-07-25 | 2045-09-09 | 2014-10-04 07:00 | 2.5 | 0.10422 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-CG-38464-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 7.8 | 5.5 | 5.4 | 1.1529
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FH-43309-01C02 | CML-4 | 50-FH-43309-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20446 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.4 | CML-4 | CML: Pipe Length | 3 | 2038-05-27 | 2041-01-30 | 2014-07-26 07:00 | 2.5 | 0.12158 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43309-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FH-43309-01C02 | CML-2 | 50-FH-43309-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20444 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.425 | CML-2 | CML: Elbow | 3 | 2038-05-27 | 2041-01-30 | 2014-07-26 07:00 | 2.5 | 0.12158 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43309-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 5.4 | 5.4 | 0.05
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FH-43308-01C02 | CML-4 | 50-FH-43308-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20441 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.4 | CML-4 | CML: Pipe Length | 3 | 2038-05-27 | 2041-01-30 | 2014-07-26 07:00 | 2.5 | 0.12158 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43308-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
RP01 | Montara_Topside | No | Flare (43) | Pipework | 50-FH-43308-01C02 | CML-1 | 50-FH-43308-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20438 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 17.55 | CML-1 | CML: Pipe Length | 3 | 2038-05-27 | 2041-01-30 | 2014-07-26 07:00 | 2.5 | 0.12158 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-FH-43308-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 54 | 24.3
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 200-WC-40400-01C02 | CML-2 | 200-WC-40400-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20403 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 9.675 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-10-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.5 | 9 O'Clock | 200 | 6.35 | 200-WC-40400-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 10.2 | 10.2 | 9.8 | 8.5 | 0.80571
DH01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-DH-56137-01C02 | CML-5 | 50-DH-56137-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22061 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 18.575 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2014-05-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 17.7 | 6 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.2 |  | 19 | 19 | 17.7 | 18.6 | 0.61305
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-2 | 200-PL-20018-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23475 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 6.325 | CML-2 | CML: Fitting | 3 | 2037-01-02 | 2036-10-31 | 2015-07-24 07:00 | 2.5 | 0.16309 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 40 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 0 | 6.3 | 6.3 | 6.7 | 6 | 0.28723
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-4 | 300-PF-20001-03C03-P CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24484 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.441mm/ yr | 40 | Kirstie Albone | 2017-03-23 16:01 | [32 empty] | 13.675 | CML-4 | CML: Pipe Length | 6 | 2034-08-27 | 2030-11-01 | 2016-07-09 07:00 | 4.9 | 0.44085 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.9 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | 0 | 12.9 | 14.3 | 14 | 13.5 | 0.61305
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-17 | 200-FH-43025-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2490 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 8.275 | CML-17 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.7 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 8.9 | 8.7 | 0.61305
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-8 | 80-PG-20046-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21467 | Protective mesh removed | 2014-06-28 08:00 | 2014-06-28 09:00 | [36 empty] | 10.875 | CML-8 | CML: Elbow | 6 | 2022-06-01 | 2021-01-16 | 2014-06-28 08:00 | 2.5 | 0.95824 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 10.1 | 3 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.9 | 10.1 | 10.9 | 11.6 | 0.61305
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-33 | 300-PF-20001-03C03-P CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 21171 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 14.575 | CML-33 | CML: Fitting | 6 | 2052-05-26 | 2045-05-22 | 2014-07-16 07:30 | 4.9 | 0.24018 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 14 | 14.1 | 15.2 | 15 | 0.61305
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-6 | 100-PG-23028-25C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 445 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 17.075 | CML-6 | CML: Pipe Length | 3 | 2020-09-29 | 2018-07-03 | 2014-03-12 09:00 | 9.4 | 1.0525 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 16.3 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 17.7 | 16.3 | 16.9 | 17.4 | 0.61305
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-20 | 300-PG-20005-03C03-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 22782 | 6 O Clock position no reading due to pipe support | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.9333 | CML-20 | CML: Reducing Tee | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.4 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 | -0.87506 | 15.6 | 14.8 |  | 14.4 | 0.61101
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-17 | 150-WC-40006-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1992 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.375 | CML-17 | CML: Pipe Length | 3 | 2023-10-18 | 2024-11-27 | 2014-03-27 07:00 | 2.5 | 0.29269 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.5 | 5.3 | 0.095743
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-7 | 100-WC-40027-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 839 |  | 2014-04-02 09:00 | 2014-04-02 10:00 | Check Corrosion Rate of 0.861mm/ yr |  | Nestor | 2016-04-01 | [32 empty] | 5.425 | CML-7 | CML: Elbow | 3 | 2017-07-02 | 2017-08-21 | 2014-04-02 09:00 | 2.5 | 0.86058 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 12 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.5 | 5.4 | 5.5 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-6 | 200-FH-43037-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12675 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 9 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 6 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  |  | 9.4 | 8.3 | 9.3 | 0.60828
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1977 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.425 | CML-2 | CML: Pipe Length | 3 | 2023-10-18 | 2024-11-27 | 2014-03-27 07:00 | 2.5 | 0.29269 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.5 | 5.3 | 5.5 | 5.4 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56058-01C02 | CML-2 | 50-DH-56058-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3174 | Rope Access | 2014-05-07 09:30 | 2014-05-07 10:30 | [36 empty] | 6.375 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56058-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.9 | 6.9 | 5.8 | 5.9 | 0.60759
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-2 | 50-DH-56056-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20126 | Rope Access | 2014-05-07 09:30 | 2014-05-07 10:30 | [36 empty] | 6.375 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 7008 | 6.9 | 6.9 | 5.8 | 5.9 | 0.60759
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-27 | 25-FG-45455-01C02-E CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 21278 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.675 | CML-27 | CML: Fitting | 3 | 2028-01-23 | 2027-12-15 | 2014-09-30 07:00 | 2.5 | 0.2627 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 7.4 | 6.4 | 6.9 | 0.60759
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-23 | 200-PL-20008-01C02-H CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 8820 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.025 | CML-23 | CML: Elbow | 3 | 2025-06-30 | 2025-05-28 | 2015-02-21 07:00 | 2.5 | 0.3185 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 6.1 | 5.8 | 6.2 | 0.17078
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-3 | 200-PL-20034-03C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23464 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 7.875 | CML-3 | CML: Elbow | 3 | 2023-06-01 | 2021-09-12 | 2015-07-24 07:00 | 3.61 | 0.45666 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 7.2 | 9 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.59 | 0.28023 | 7.7 | 7.8 | 8.8 | 7.2 | 0.6702
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-3 | 200-FH-43131-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2824 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 8.025 | CML-3 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.5 | 12 O'Clock | 200 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.16 |  | 7.5 | 7.9 | 7.8 | 8.9 | 0.60759
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-6 | 50-PW-44012-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2020 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 5.425 | CML-6 | CML: Pipe Length | 3 | 2019-01-29 | 2019-09-08 | 2014-03-27 09:30 | 2.5 | 0.53641 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.1 | 5.4 | 5.6 | 0.23629
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2443 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | Check Corrosion Rate of 0.549mm/ yr | [35 empty] | 5.425 | CML-1 | CML: type TBC | 3 | 2018-12-12 | 2019-07-16 | 2014-03-20 09:30 | 2.5 | 0.54926 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.5 | 5.1 | 5.5 | 5.6 | 0.22174
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23034-01C03 | CML-6 | 50-PL-23034-01C03 CML-6 | no | FPSO 2014 | Pipe Wall Thickness | 20574 | Reviewed on 26/11/14.FFS. Repeat Oct.19 | 2014-10-12 07:00 | 2014-10-12 12:00 |  |  | Nestor | 2014-11-26 16:19 | [32 empty] | 8.925 | CML-6 | CML: Elbow | 6 | 2029-03-07 | 2028-11-16 | 2014-10-12 07:00 | 2.5 | 0.39555 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 12 O'Clock | 50 | 8.74 | 50-PL-23034-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 9.2 | 9.6 | 8.7 | 0.60759
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-1 | 50-CG-24002-09C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2547 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 11.275 | CML-1 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 10.4 | 3 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 11.5 | 10.4 | 11.8 | 11.4 | 0.60759
WC01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13166 |  | 2014-01-18 15:00 | 2014-01-18 17:00 | This is branc line from main line | [34 empty] | Low alarm breach | 5.35 | CML-7 | CML: type TBC | 3 | 2014-07-26 | 2014-04-08 | 2014-01-18 15:00 | 2.5 | 5.4208 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 5.3 | 6 O'Clock | 50 | 8.74 | 50-PL-24036-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.4 | 5.3 | 5.3 | 5.4 | 0.057735
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38495-01C02 | CML-5 | 25-CG-38495-01C02 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10402 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.775 | CML-5 | CML: type TBC | 3 | 2017-04-04 | 2017-03-24 | 2013-11-12 | 2.5 | 1.0015 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 25 | 6.35 | 25-CG-38495-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 5.9 | 5.9 | 7 | 6.9 | 7.3 | 0.60759
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 519 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 8.9667 | CML-2 | CML: Equal Tee | 6 | 2015-03-20 | 2015-05-18 | 2014-03-13 09:00 | 5.22 | 2.8266 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 8.1 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.88 |  | 8.1 | 9.7 |  | 9.1 | 0.80829
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-32 | 350-FL-43512-01C02 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 6546 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.825 | CML-32 | CML: Elbow | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 9.3 | 9 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 |  | 9.6 | 9.7 | 10.7 | 9.3 | 0.60759
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-8 | 50-DH-56137-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5449 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 4.89mm/ yr | [34 empty] | Low alarm breach | 17.325 | CML-8 | CML: Straight | 3 | 2017-04-14 | 2015-08-28 | 2014-05-28 07:00 | 2.5 | 4.8897 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 16.6 | 12 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.1 |  | 16.6 | 17.6 | 17.1 | 18 | 0.60759
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-26 | 200-PW-44018-01X01 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 2001 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.3 | CML-26 | CML: Pipe Length | 3 | 2019-01-28 | 2019-09-07 | 2014-03-27 07:00 | 2.5 | 0.5366 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.6 | 5.2 | 5.3 | 0.21602
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-3 | 300-FH-43001-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12515 |  | 2014-01-24 13:00 | 2014-01-24 15:00 | [36 empty] | 9.9 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-24 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 3 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.6 | 9.2 | 10.5 | 10.3 | 0.60553
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56130-01C02 | CML-3 | 50-DH-56130-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21055 | Rope Access | 2014-05-15 13:00 | 2014-05-15 14:00 | [36 empty] | 6.5 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-15 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-DH-56130-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 7.4 | 6.3 | 0.60553
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-2 | 200-PL-20034-03C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21599 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 7.825 | CML-2 | CML: Elbow | 3 | 2018-06-05 | 2017-07-26 | 2014-06-28 13:00 | 3.61 | 0.91124 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.2 | 6 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.59 |  | 8.2 | 7.8 | 7.2 | 8.1 | 0.45
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-12 | 300-PF-20001-03C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21150 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.507mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:54 | [32 empty] | 14.3 | CML-12 | CML: Fitting | 6 | 2031-11-18 | 2028-07-24 | 2014-07-16 07:30 | 4.9 | 0.50705 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 13.7 | 14 | 14.4 | 15.1 | 0.60553
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56043-01C02 | CML-2 | 80-DH-56043-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20930 | Rope Access | 2014-05-16 07:00 | 2014-05-16 08:00 | [36 empty] | 5.3 | CML-2 | CML: type TBC | 3 | 2018-04-06 | 2018-10-29 | 2014-05-16 07:00 | 2.5 | 0.61653 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-DH-56043-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 6.2 | 4.9 | 5 | 5.1 | 0.60553
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23017-03C03-A | CML-2 | 250-PG-23017-03C03-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10976 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 12.4 | CML-2 | CML: Elbow | 6 | 2017-08-14 | 2017-01-13 | 2014-01-09 | 4.4 | 1.973 | A1: Outside Quadrant |  | 6.7 | 4.4 | 5.55 | 11.5 | 12 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 11.5 | 12.6 | 12.8 | 12.7 | 0.60553
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-37 | 300-PF-20001-03C03-P CML-37 |  | FPSO 2016 | Pipe Wall Thickness | 24485 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 14.1 | CML-37 | CML: Fitting | 6 | 2064-06-19 | 2055-04-15 | 2016-07-09 07:00 | 4.9 | 0.18342 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | -0.10489 | 13.7 | 13.8 | 15 | 13.9 | 0.60553
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-32 | 50-FG-45023-01C02 CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 1180 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.6 | CML-32 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.5 | 6.4 | 6.2 | 6.3 | 0.60553
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-5 | 50-DH-56070-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3221 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.4 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.8 | 6.7 | 7.1 | 0.60553
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20013-01C02-P | CML-3 | 200-PL-20013-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21213 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 6.9 | CML-3 | CML: Fitting | 3 | 2030-08-19 | 2030-07-04 | 2014-07-14 07:30 | 2.5 | 0.22348 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 6 O'Clock | 200 | 6.35 | 200-PL-20013-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.9 | 7.3 | 6.1 | 7.3 | 0.56569
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-6 | 150-PG-20507-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2850 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 12 | CML-6 | CML: type TBC | 6 | 2098-02-09 | 2085-10-05 | 2014-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 11.4 | 9 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.6 | 12.7 | 12.3 | 11.4 | 0.60553
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-6 | 50-PL-20033-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21835 |  | 2014-10-12 07:00 | 2014-10-12 12:00 | [36 empty] | 6.375 | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 | -0.69586 | 6.2 | 7 | 6.2 | 6.1 | 0.41932
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56128-01C02 | CML-2 | 80-DH-56128-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21052 | Rope Access | 2014-05-22 13:00 | 2014-05-22 14:00 | [36 empty] | 5.2 | CML-2 | CML: Elbow | 3 | 2016-09-07 | 2017-01-24 | 2014-05-22 13:00 | 2.5 | 0.91368 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 9 O'Clock | 80 | 5.49 | 80-DH-56128-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 6 | 5.3 | 4.9 | 4.6 | 0.60553
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-29 | 300-PW-44003-01C03 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 22894 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.4 | CML-29 | CML: Elbow | 6 | 2024-10-30 | 2023-07-04 | 2015-05-01 07:00 | 2.5 | 0.68376 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | 5.6443 | 9.8 | 9.4 | 9 | 9.4 | 0.3266
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-1 | 50-PL-23022-03C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1857 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.55 | CML-1 | CML: type TBC | 6 | 2140-06-02 | 2137-12-23 | 2014-03-25 08:30 | 2.5 | 0.0491 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.7 | 12 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 9.6 | 10.1 | 9.8 | 0.60277
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43170-01C02 | CML-4 | 250-FL-43170-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 23071 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.35 | CML-4 | CML: Elbow | 3 | 2022-02-28 | 2022-02-05 | 2015-05-07 07:00 | 2.5 | 0.43989 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 9 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 0.19363 | 6.6 | 6.9 | 6.4 | 5.5 | 0.60277
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-22 | 25-FG-45455-01C02-E CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 2464 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 6.55 | CML-22 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.5 | 7.4 | 6.3 | 0.60277
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-7 | 400-FH-43508-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 6556 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.35 | CML-7 | CML: Pipe Length | 3 | 2062-08-12 | 2057-12-18 | 2015-03-30 07:00 | 3 | 0 | A1: Outside Quadrant |  | 4.92 | 3 | 3.465 | 8.5 | 12 O'Clock | 500 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.5 | 9.6 | 9.9 | 9.4 | 0.60277
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23034-01C03 | CML-8 | 50-PL-23034-01C03 CML-8 | no | FPSO 2014 | Pipe Wall Thickness | 20576 | Reviewed on 26/11/14.FFS. Repeat Oct.19 | 2014-10-12 07:00 | 2014-10-12 12:00 |  |  | Nestor | 2014-11-26 16:20 | [32 empty] | 9.25 | CML-8 | CML: Elbow | 6 | 2038-06-15 | 2037-12-21 | 2014-10-12 07:00 | 2.5 | 0.24905 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-PL-23034-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.5 | 8.4 | 9.3 | 9.8 | 0.60277
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-7 | 50-PW-44040-01C02 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 1982 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.275 | CML-7 | CML: Elbow | 3 | 2018-01-10 | 2018-07-10 | 2014-03-27 07:00 | 2.5 | 0.65855 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.7 | 5.1 | 5.3 | 0.30957
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-31 | 300-PF-20003-03C03-P CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 21769 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.35 | CML-31 | CML: Reducing Tee | 6 | 2035-05-07 | 2031-05-27 | 2014-10-01 07:00 | 4.9 | 0.42695 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 15 | 14.7 | 14 | 13.7 | 0.60277
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-13 | 50-FG-45302-01C02 CML-13 | Yes | FPSO 2014 | Pipe Wall Thickness | 5781 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 7.25 | CML-13 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 12 O'Clock | 25 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.3 | 7.8 | 7.5 | 0.60277
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-15 | 200-PG-24001-09C02 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10271 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 17.75 | CML-15 | CML: Pipe Length | 3 | 2016-11-09 | 2015-09-15 | 2013-11-09 | 9.2 | 2.6298 | A2: Right Quadrant |  | 15.26 | 9.2 | 12.23 | 17.1 | 3 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 17.4 | 17.1 | 18.1 | 18.4 | 0.60277
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1981 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.35 | CML-6 | CML: Fitting | 3 | 2019-01-28 | 2019-09-07 | 2014-03-27 07:00 | 2.5 | 0.5366 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 5.4 | 5.1 | 5.3 | 0.20817
FL02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-FL-43454-01C02-P | CML-18 | 50-FL-43454-01C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2437 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | [36 empty] | 9.675 | CML-18 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.1 | 6 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.7 | 9.4 | 9.1 | 10.5 | 0.60208
WC01 | Montara_Topside | Yes | Chemical Injection (42) | Pipework | 150-WC-40006-01C02 | CML-11 | 150-WC-40006-01C02 CML-11 | Yes | FPSO 2015 | Pipe Wall Thickness | 8422 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 7 | CML-11 | CML: type TBC | 1 | 2049-08-24 | 2041-08-13 | 2015-01-31 10:00 | 2.5 | 0.08385 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 7.8 | 5.4 | 8.4 | 6.4 | 1.3565
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-11 | 50-FG-45302-01C02 CML-11 | Yes | FPSO 2014 | Pipe Wall Thickness | 5779 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 6.325 | CML-11 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 25 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 5.8 | 7.1 | 5.9 | 0.60208
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-2 | 250-PW-44509-01C03-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22987 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.3 | CML-2 | CML: Elbow | 6 | 2061-09-11 | 2058-12-13 | 2015-05-05 07:00 | 2.5 | 0.14013 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 9 | 9 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | -0.18528 | 9.5 | 9.5 | 9.2 | 9 | 0.24495
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-10 | 80-CG-38459-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10984 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 17.625 | CML-10 | CML: type TBC | 6 | 2096-05-30 | 2084-11-28 | 2014-01-09 | 4.4 | 0 | A1: Outside Quadrant |  | 6.7 | 4.4 | 5.55 | 16.8 | 12 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.4 |  | 16.8 | 17.6 | 18.2 | 17.9 | 0.60208
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2605 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 5.275 | CML-6 | CML: type TBC | 3 | 2019-08-24 | 2019-08-09 | 2014-04-26 09:30 | 2.5 | 0.48756 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | -0.45512 | 5.5 | 5.1 | 5.4 | 5.1 | 0.20616
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43302-01C02 | CML-7 | 250-FH-43302-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12923 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.4 | CML-7 | CML: type TBC | 3 | 2016-05-19 | 2016-05-11 | 2014-01-26 07:00 | 2.5 | 1.2965 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 12 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.7 | 6.7 | 6.7 | 0.6
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-15 | 250-PG-23005-06C03 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10061 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 17.5 | CML-15 | CML: Pipe Length | 6 | 2016-04-11 | 2015-09-26 | 2013-11-06 | 8.6 | 3.3728 | A1: Outside Quadrant |  | 12.26 | 8.6 | 10.43 | 16.8 | 12 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 16.8 | 18 | 18 | 17.2 | 0.6
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-18 | 50-DH-56137-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 5686 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 0.454mm/ yr | [34 empty] | Low alarm breach | 17.7 | CML-18 | CML: Elbow | 3 | 2017-12-01 | 2016-01-09 | 2014-06-21 14:00 | 2.5 | 4.203 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 17 | 3 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.5 |  | 18.2 | 17 | 17.4 | 18.2 | 0.6
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-4 | 50-PW-44014-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2006 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 5.325 | CML-4 | CML: Pipe Length | 3 | 2019-01-29 | 2019-09-08 | 2014-03-27 10:00 | 2.5 | 0.53638 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.1 | 5.6 | 5.3 | 0.20616
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24302 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.35 | CML-2 | CML: Equal Tee | 3 | 2054-10-24 | 2049-02-10 | 2016-05-27 07:00 | 1.88 | 0 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 6.5 | 12 O'Clock | 100 | 6.02 | 100-FG-45008-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 |  | 6.5 | 7.9 | 7.5 | 7.5 | 0.59722
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8065 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 6.675 | CML-5 | CML: type TBC | 3 | 2049-02-07 | 2052-12-07 | 2015-01-22 07:30 | 2.5 | 0.08512 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-VA-23056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.7 | 5.4 | 7.2 | 7.4 | 0.89954
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-5 | 250-PW-44509-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22040 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 10.1 | CML-5 | CML: Elbow | 6 | 2147-06-24 | 2139-11-09 | 2014-10-20 07:00 | 2.5 | 0.05046 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.2 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 11.3 | 10.2 | 9.2 | 9.7 | 0.89815
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-3 | 50-CG-38476-01C02-H CML-3 | Yes | FPSO 2015 | Pipe Wall Thickness | 23635 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 12.05 | CML-3 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 11.2 | 9 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 12.2 | 12.6 | 12.2 | 11.2 | 0.59722
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43074-01C02 | CML-4 | 50-FL-43074-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1789 | Rope access | 2014-04-28 09:30 | 2014-04-28 10:30 | [36 empty] | 5.75 | CML-4 | CML: Equal Tee | 3 | 2021-07-12 | 2022-05-26 | 2014-04-28 09:30 | 2.5 | 0.37448 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-FL-43074-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.6 | 6.6 | 5.6 | 0.59722
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20052-01C02-P | CML-1 | 200-PL-20052-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 23872 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.575 | CML-1 | CML: Pipe Length | 3 | 2033-10-01 | 2033-08-08 | 2014-09-26 07:00 | 2.5 | 0.1892 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 200 | 6.35 | 200-PL-20052-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.6 | 6.5 | 7.1 | 0.4113
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45051-03C02 | CML-1 | 150-FG-45051-03C02 CML-1 | yes | FPSO 2016 | Pipe Wall Thickness | 24375 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.35 | CML-1 | CML: Elbow | 3 | 2058-04-03 | 2050-06-04 | 2016-06-06 07:00 | 2.5 | 0.10274 | A4: Left Quadrant |  | 4.11 | 2.5 | 3.305 | 6.8 | 9 O'Clock | 150 | 7.11 | 150-FG-45051-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.2 | 8.2 | 7.2 | 6.8 | 0.59722
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-6 | 100-PG-23028-25C02-P CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 20553 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 17.05 | CML-6 | CML: Pipe Length | 3 | 2022-10-13 | 2019-12-02 | 2014-05-30 09:30 | 9.4 | 0.82362 | A2: Right Quadrant |  | 14.12 | 9.4 | 11.76 | 16.3 | 3 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 | 0 | 17.7 | 16.3 | 16.9 | 17.3 | 0.59722
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-37 | 250-PW-44006-01X01 CML-37 |  | FPSO 2014 | Pipe Wall Thickness | 1934 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 5.3 | CML-37 | CML: Elbow | 3 | 2015-12-06 | 2015-11-30 | 2014-03-26 07:00 | 2.5 | 1.5295 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.1 | 12 O'Clock | 50 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.5 | 5.3 | 5.3 | 0.1633
FH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FH-43141-01C02 | CML-2 | 150-FH-43141-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 6251 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.95 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.4 | 6 O'Clock | 50 | 2.5 | 50-WF-71329-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.8 | 3.8 | 3.4 | 4.8 | 0.59722
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-5 | 50-CG-38474-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23629 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 4.55 | CML-5 | CML: Elbow | 3 | 2017-05-23 | 2017-10-26 | 2015-10-28 07:00 | 2.5 | 0.7638 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 4.7 | 3.7 | 4.7 | 5.1 | 0.59722
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-51 | 300-PF-20001-03C03-P CML-51 |  | FPSO 2015 | Pipe Wall Thickness | 23487 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 11.575 | CML-51 | CML: Elbow | 6 | 2019-07-19 | 2018-04-16 | 2015-07-27 07:00 | 4.1 | 1.6572 | A4: Left Quadrant |  | 8.27 | 4.1 | 6.185 | 10.7 | 9 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | 0.19416 | 11.7 | 11.9 | 12 | 10.7 | 0.59652
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-11 | 300-PW-44003-01C03 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21853 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 9.825 | CML-11 | CML: Elbow | 6 | 2023-02-24 | 2022-01-08 | 2014-10-19 07:00 | 2.5 | 0.80181 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.2 | 10.6 | 9.3 | 9.2 | 0.68496
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-18 | 200-PW-44018-01X01 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1993 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.275 | CML-18 | CML: Pipe Length | 3 | 2019-01-28 | 2019-09-07 | 2014-03-27 07:00 | 2.5 | 0.5366 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.2 | 5.4 | 5.1 | 0.15
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-20 | 25-FG-45455-01C02-E CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 1955 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 6.425 | CML-20 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.3 | 6.3 | 6 | 6.1 | 0.59652
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-9 | 50-DH-56137-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21093 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.425 | CML-9 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6 | 6 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.3 | 6.3 | 6 | 6.1 | 0.59652
PW03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10142 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 0.998mm/ yr | [35 empty] | 5.275 | CML-2 | CML: Elbow | 3 | 2016-06-17 | 2016-10-14 | 2013-11-09 | 2.5 | 0.99752 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.4 | 5.2 | 5.1 | 0.15
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-6 | 50-DH-56116-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5216 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.225 | CML-6 | CML: Elbow | 3 | 2017-05-22 | 2017-10-25 | 2014-05-20 09:30 | 2.5 | 0.7643 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.1 | 6.1 | 4.9 | 0.59652
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-10 | 50-CG-38452-09C02-P CML-10 | Yes | FPSO 2015 | Pipe Wall Thickness | 7858 | Line is FFS. Current RBI frequency is 48m. Action: CML’s to Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-08 13:38 | [32 empty] | 6.775 | CML-10 | CML: Elbow | 3 | 2027-04-16 | 2027-03-10 | 2015-01-14 07:00 | 2.5 | 0.27731 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.2 | 6.9 | 7.1 | 5.9 | 0.59652
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43120-01C02 | CML-8 | 200-FH-43120-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12842 |  | 2014-02-06 07:00 | 2014-02-06 09:00 | [36 empty] | 9.275 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.4 | 12 O'Clock | 200 | 6.35 | 200-FH-43120-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.4 | 9.7 | 9.6 | 0.59652
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20031-01C03-P | CML-5 | 150-PG-20031-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 23867 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 11.825 | CML-5 | CML: Equal Tee | 6 | 2098-02-09 | 2085-10-05 | 2014-09-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 11.4 | 9 O'Clock | 150 | 10.97 | 150-PG-20031-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.5 | 12.7 | 11.7 | 11.4 | 0.59652
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-5 | 50-FG-45021-03C02 CML-5 | yes | FPSO 2013 | Pipe Wall Thickness | 10533 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5 | CML-5 | CML: type TBC | 3 | 2014-06-17 | 2014-06-14 | 2013-11-16 | 2.5 | 2.9113 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.2 | 3 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 5.5 | 4.2 | 4.9 | 5.4 | 0.59442
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-12 | 300-PG-20049-03C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21498 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | Check Corrosion Rate of 0.623mm/ yr | 39 | Kirstie Albone | 2017-03-23 13:11 | [32 empty] | 14.1 | CML-12 | CML: Fitting | 6 | 2028-06-10 | 2025-09-27 | 2014-06-28 10:45 | 4.9 | 0.62314 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 12 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 13.6 | 14.9 | 13.7 | 14.2 | 0.59442
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-11 | 50-DH-56062-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 9098 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.5 | CML-11 | CML: type TBC | 3 | 2020-08-09 | 2021-05-18 | 2015-03-02 07:00 | 2.5 | 0.4225 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6.2 | 5.7 | 5.3 | 4.8 | 0.59442
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-21 | 100-FG-45001-09C02 CML-21 |  | FPSO 2013 | Pipe Wall Thickness | 10436 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.7 | CML-21 | CML: type TBC | 3 | 2015-12-26 | 2015-04-20 | 2013-11-13 | 4.7 | 2.4997 | A3: Inside Quadrant |  | 8.13 | 4.7 | 6.415 | 10 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 11.4 | 10.9 | 10 | 10.5 | 0.59442
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-4 | 50-PW-44014-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23149 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.2 | CML-4 | CML: Pipe Length | 3 | 2026-10-24 | 2028-04-01 | 2015-05-10 07:00 | 2.5 | 0.22674 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0 | 5.1 | 5.1 | 5.2 | 5.4 | 0.14142
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23025-06C03 | CML-18 | 80-PG-23025-06C03 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 13089 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 8.9 | CML-18 | CML: Elbow | 6 | 2015-07-08 | 2015-03-22 | 2014-02-07 11:00 | 2.8 | 3.9627 | A1: Outside Quadrant |  | 5.13 | 2.8 | 3.965 | 8.4 | 12 O'Clock | 25 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.4 | 9.7 | 9 | 8.5 | 0.59442
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-21 | 300-PG-20005-03C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 6177 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.35 | CML-21 | CML: Reducing Tee | 6 | 2031-08-28 | 2028-05-17 | 2014-07-11 07:30 | 4.9 | 0.51331 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 14.9 | 14 | 13.7 | 14.8 | 0.59161
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-14 | 50-CG-38487-09C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20853 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.45 | CML-14 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-10-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 9 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | -1.444 | 9.4 | 9 | 9.1 | 10.3 | 0.59161
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56092-01C02 | CML-1 | 80-DH-56092-01C02 CML-1 | yes | FPSO 2014 | Pipe Wall Thickness | 20984 | Rope Access | 2014-05-17 13:00 | 2014-05-17 15:00 | [36 empty] | 5.15 | CML-1 | CML: type TBC | 3 | 2015-10-29 | 2016-02-09 | 2014-05-17 13:00 | 2.5 | 1.2391 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.3 | 12 O'Clock | 80 | 5.49 | 80-DH-56092-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 5.5 | 5.2 | 5.6 | 0.59161
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-12 | 250-PG-23003-06C02-PA CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 7691 | Re-check.Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-13 13:50 | [32 empty] | 5.15 | CML-12 | CML: Elbow | 3 | 2017-05-08 | 2017-10-10 | 2015-01-08 13:00 | 2.5 | 0.77164 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 0.26225 | 4.3 | 5.5 | 5.2 | 5.6 | 0.59161
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21028 | Rope Access | 2014-05-19 09:30 | 2014-05-19 11:00 | [36 empty] | 5.65 | CML-2 | CML: type TBC | 3 | 2020-01-30 | 2020-10-18 | 2014-05-19 09:30 | 2.5 | 0.45574 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56119-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.2 | 6.3 | 6 | 5.1 | 0.59161
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-7 | 200-PL-20010-01C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23524 | Re-check on line as Per RBI 2014 Report | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 6.375 | CML-7 | CML: Fitting | 3 | 2046-08-11 | 2046-05-14 | 2015-07-28 07:00 | 2.5 | 0.1159 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 40 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 | 0.35784 | 6.4 | 6.1 | 6.8 | 6.2 | 0.30957
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-17 | 50-CG-38487-09C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20817 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 10.15 | CML-17 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.5 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.6 | 9.8 | 9.5 | 10.7 | 0.59161
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-26 | 250-PG-23004-06C03-A CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 13026 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 18.625 | CML-26 | CML: Elbow | 6 | 2112-12-10 | 2093-12-05 | 2014-01-11 15:00 | 8.55 | 0.0975 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.2 | 12 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.65 |  | 18.2 | 18.4 | 19.5 | 18.4 | 0.5909
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-7 | 25-VA-23054-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5860 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 14.575 | CML-7 | CML: Equal Tee | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 10:30 | 3.3 | 0 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 13.7 | 9 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 14.8 | 14.8 | 15 | 13.7 | 0.5909
PG06 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PG-23008-15S01-A | CML-1 | 200-PG-23008-15S01-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5661 | Rope access | 2014-06-21 13:00 | 2014-06-21 14:00 | Check Corrosion Rate of 0.417mm/ yr | [35 empty] | 5.975 | CML-1 | CML: Elbow | 3 | 2020-09-15 | 2021-06-28 | 2014-06-21 13:00 | 2.5 | 0.41656 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.2 | 6.4 | 6.2 | 5.1 | 0.5909
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-9 | 50-CG-38452-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 3432 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 7.925 | CML-9 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.1 | 12 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.9 | 8.4 | 8.3 | 0.5909
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-8 | 25-FG-45455-01C02-E CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 22064 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.625 | CML-8 | CML: type TBC | 3 | 2186-01-24 | 2173-04-24 | 2014-05-25 07:00 | 2.5 | 0.02037 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 6 | 6 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 7.4 | 6 | 6.7 | 0.5909
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-36 | 50-DH-56062-01C02 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 9123 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 6.925 | CML-36 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 7.7 | 6.3 | 7 | 0.5909
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-10 | 50-PL-23515-01C03 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8659 | Line is FFS despite the High CR on CML-1 to 6. They are all in the same spool. Current RBI frequency is 48m. Action: to recheck CML-1 to 6 in a year to confirm CR. RBI frequency to stay at 48m | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:52 | [32 empty] | 8.775 | CML-10 | CML: Elbow | 6 | 2033-01-26 | 2032-09-10 | 2015-02-12 07:00 | 2.5 | 0.31724 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 6 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 9.6 | 8.7 | 8.2 | 8.6 | 0.5909
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-57066-01C03 | CML-17 | 50-PL-57066-01C03 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 13133 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 10.325 | CML-17 | CML: type TBC | 6 | 2017-03-27 | 2016-09-17 | 2014-02-04 07:00 | 2.81 | 2.161 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 9.6 | 12 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.79 |  | 9.6 | 10.1 | 10.7 | 10.9 | 0.5909
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20301-03C03-P | CML-1 | 200-PG-20301-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5880 |  | 2014-06-25 14:00 | 2014-06-25 15:00 | [36 empty] | 12.525 | CML-1 | CML: Pipe Length | 6 | 2023-06-11 | 2021-08-17 | 2014-06-25 14:00 | 3.3 | 0.9369 | A3: Inside Quadrant |  | 6.7 | 3.3 | 5 | 11.7 | 6 O'Clock | 200 | 12.7 | 200-PG-20301-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 12.7 | 12.6 | 11.7 | 13.1 | 0.5909
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-22 | 300-PF-20501-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 21698 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.875 | CML-22 | CML: Pipe Length | 6 | 2086-07-01 | 2073-05-09 | 2014-09-28 07:00 | 4.9 | 0.12813 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 15.5 | 15.1 | 14.8 | 14.1 | 0.5909
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44025-01X01 | CML-2 | 50-PW-44025-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5577 |  | 2014-06-19 08:00 | 2014-06-19 08:30 | [36 empty] | 5.2 | CML-2 | CML: Reducer | 3 | 2020-08-31 | 2021-06-11 | 2014-06-19 08:00 | 2.5 | 0.41896 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-PW-44025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.1 | 5.3 | 5.3 | 0.11547
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-23 | 150-PG-23506-25C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 2797 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.975 | CML-23 | CML: Pipe Length | 3 | 2024-01-11 | 2021-05-06 | 2014-03-15 09:00 | 15.88 | 0.57155 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.5 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.62 |  | 21.5 | 22 | 21.6 | 22.8 | 0.5909
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-14 | 200-PG-23065-09C02-A CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20085 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 18.55 | CML-14 | CML: Pipe Length | 3 | 2023-12-22 | 2020-08-26 | 2014-05-29 07:00 | 10.17 | 0.76568 | A1: Outside Quadrant |  | 15.26 | 10.17 | 12.715 | 17.5 | 12 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.33 | 0.9369 | 17.5 | 19 | 18.6 | 19.1 | 0.73258
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44025-01X01 | CML-2 | 50-PW-44025-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21902 |  | 2014-06-19 08:00 | 2014-06-19 08:30 | [36 empty] | 5.2 | CML-2 | CML: Reducer | 3 | 2020-08-31 | 2021-06-11 | 2014-06-19 08:00 | 2.5 | 0.41896 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-PW-44025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 5.9637 | 5.1 | 5.1 | 5.3 | 5.3 | 0.11547
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56114-01C02 | CML-1 | 50-DH-56114-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5226 | Rope Access | 2014-05-20 11:00 | 2014-05-20 12:00 | [36 empty] | 5.275 | CML-1 | CML: Elbow | 3 | 2017-05-23 | 2017-10-25 | 2014-05-20 11:00 | 2.5 | 0.76416 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56114-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.3 | 6.1 | 4.9 | 0.5909
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-7 | 100-DH-56088-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5200 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 7.475 | CML-7 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-05-20 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.7 | 6 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.7 | 8.1 | 6.7 | 7.4 | 0.5909
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-6 | 350-FL-43511-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2287 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 8.125 | CML-6 | CML: type TBC | 3 | 2032-12-06 | 2030-05-10 | 2014-03-17 08:00 | 2.5 | 0.27753 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.7 | 6 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9 | 7.9 | 7.7 | 7.9 | 0.5909
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-6 | 50-FL-43454-01C02-P CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 20509 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 9.375 | CML-6 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.9 | 12 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9 | 9.4 | 10.2 | 0.5909
DH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-DH-56137-01C02 | CML-20 | 50-DH-56137-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 2301 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 17.075 | CML-20 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 16.3 | 12 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.8 |  | 16.3 | 17 | 17.7 | 17.3 | 0.5909
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-6 | 300-PF-20003-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21744 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 9.125 | CML-6 | CML: Elbow | 6 | 2016-01-17 | 2015-05-27 | 2014-10-01 07:00 | 2.5 | 4.4718 | A1: Outside Quadrant |  | 8.27 | 2.5 | 5.385 | 8.3 | 12 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.2 | 9.3 | 9.7 | 0.5909
FH01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-FH-43141-01C02 | CML-9 | 150-FH-43141-01C02 CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 5065 |  | 2015-03-06 07:00 | 2015-03-06 15:00 | Minimum WT reading has exceeded Low Alarm | [34 empty] | Low alarm breach | 3.775 | CML-9 | CML: type TBC | 0 | 2036-10-14 | 2030-08-10 | 2015-03-06 07:00 | 2.5 | 0.037 | A4: Left Quadrant |  | 3.38 | 2.5 | 2.7287 | 3.3 | 9 O'Clock | 25 | 3.38 | 0100-DC-57L9001-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 4.6 | 3.8 | 3.3 | 0.5909
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23302-01C02 | CML-6 | 80-VA-23302-01C02 CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 22522 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.6 | CML-6 | CML: Elbow | 3 | 2015-09-05 | 2015-12-10 | 2015-04-20 07:00 | 2.5 | 1.3204 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 3 | 6 O'Clock | 50 | 5.49 | 80-VA-23302-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.5 |  | 4 | 3.2 | 3 | 4.2 | 0.58878
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38495-01C02 | CML-4 | 25-CG-38495-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10401 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.4 | CML-4 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 12 O'Clock | 25 | 6.35 | 25-CG-38495-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.6 | 6.6 | 6.4 | 7 | 0.58878
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23030-09C02-P | CML-3 | 50-PG-23030-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20746 | Protective mesh removed/Rope access | 2014-07-02 09:30 | 2014-07-02 11:00 | [36 empty] | 9.3 | CML-3 | CML: type TBC | 3 | 2182-09-20 | 2138-10-07 | 2014-07-02 09:30 | 2.5 | 0.03683 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 12 O'Clock | 50 | 8.74 | 50-PG-23030-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 8.9 | 9.9 | 9.7 | 0.58878
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-3 | 300-PW-44003-01C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21845 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 10.075 | CML-3 | CML: Elbow | 6 | 2023-02-24 | 2022-01-08 | 2014-10-19 07:00 | 2.5 | 0.80181 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.2 | 9.2 | 10.4 | 10.5 | 0.59652
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-1 | 300-PG-20005-03C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22763 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14 | CML-1 | CML: Reducing Tee | 6 | 2033-12-22 | 2030-04-12 | 2015-04-29 07:00 | 4.9 | 0.4554 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 | 1.3751 | 14.8 | 13.8 | 14 | 13.4 | 0.58878
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-9 | 50-PF-20300-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21575 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.5 | CML-9 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.1 | 9.9 | 10.1 | 8.9 | 0.58878
PG05 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1938 | Rope Access.Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Mar. 2020). RBI to be updated | 2014-03-26 09:30 | 2014-03-26 10:30 |  |  | Administrator | 2015-09-08 12:56 | [32 empty] | 6.2 | CML-3 | CML: Elbow | 3 | 2031-02-26 | 2033-01-21 | 2014-03-26 09:30 | 2.5 | 0.17125 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.8 | 6.4 | 5.4 | 6.2 | 0.58878
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22963 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 6.375 | CML-5 | CML: Elbow | 3 | 2077-04-17 | 2084-09-24 | 2015-05-04 07:00 | 2.5 | 0.04678 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.35437 | 7.3 | 6.4 | 5.4 | 6.4 | 0.77621
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8326 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.475 | CML-7 | CML: type TBC | 3 | 2049-06-17 | 2053-04-30 | 2015-01-28 07:30 | 2.5 | 0.08428 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.8 | 6.8 | 6.9 | 0.71822
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-4 | 150-PG-20009-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2698 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 11.1 | CML-4 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-12 09:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 10.5 | 6 O'Clock | 100 | 8.56 | 100-PG-20009-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11.7 | 11.5 | 10.5 | 10.7 | 0.58878
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-4 | 150-PG-20009-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 669 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 11.1 | CML-4 | CML: Pipe Length | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 09:00 | 2.03 | 0 | A3: Inside Quadrant |  | 1.11 | 2.03 | 1.57 | 10.5 | 6 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.47 | 0 | 11.7 | 11.5 | 10.5 | 10.7 | 0.58878
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-4 | 150-PG-20009-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 387 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 11.1 | CML-4 | CML: Pipe Length | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 | 2.03 | 0 | A3: Inside Quadrant |  | 1.11 | 2.03 | 1.57 | 10.5 | 6 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.47 |  | 11.7 | 11.5 | 10.5 | 10.7 | 0.58878
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8064 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 6.375 | CML-4 | CML: type TBC | 3 | 2049-02-07 | 2052-12-07 | 2015-01-22 07:30 | 2.5 | 0.08512 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-VA-23056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.4 | 7.1 | 6.6 | 0.71356
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-11 | 250-FH-43303-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12949 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 11.6667 | CML-11 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 11 | 12 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11 | 12.1 | 11.9 |  | 0.58595
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22254 | Deck Level | 2014-05-01 13:00 | 2014-05-01 14:00 | [36 empty] | 5.5 | CML-2 | CML: Elbow | 3 | 2019-10-14 | 2020-06-11 | 2014-05-01 13:00 | 2.48 | 0.48006 | A4: Left Quadrant |  | 2.54 | 2.48 | 2.1637 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FL-43072-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.62 |  | 5.8 | 5.5 | 5.6 | 5.1 | 0.29439
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20508-03C03-P | CML-1 | 300-PF-20508-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6510 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 | [36 empty] | 16.875 | CML-1 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-24 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 16.2 | 6 O'Clock | 300 | 14.27 | 300-PF-20508-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 16.7 | 17 | 16.2 | 17.6 | 0.58523
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-15 | 250-PW-44509-01C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 22050 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.775 | CML-15 | CML: Pipe Length | 6 | 2147-06-24 | 2139-11-09 | 2014-10-20 07:00 | 2.5 | 0.05046 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.2 | 3 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.7 | 9.2 | 10.4 | 9.8 | 0.49244
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-5 | 200-PG-23008-15S01-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3471 | Rope Access | 2014-05-13 10:30 | 2014-05-13 12:00 | [36 empty] | 5.725 | CML-5 | CML: type TBC | 3 | 2020-09-08 | 2021-07-14 | 2014-05-13 10:30 | 2.5 | 0.4109 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 9 O'Clock | 80 | 5.49 | 80-DH-56012-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6 | 6.4 | 5.4 | 5.1 | 0.58523
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-25 | 50-PF-20301-03C03-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 3023 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.125 | CML-25 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.4 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.79 | 0 | 9.8 | 9 | 8.4 | 9.3 | 0.58523
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-25 | 50-PF-20301-03C03-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 22302 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.125 | CML-25 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.4 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.79 |  | 9.8 | 9 | 8.4 | 9.3 | 0.58523
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-21 | 200-FH-43025-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 2494 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 8.675 | CML-21 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8 | 6 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8.8 | 8.5 | 8 | 9.4 | 0.58523
WC01 | Montara_Topside | Yes | Potable Water (53) | Pipework | 150-WC-40006-01C02 | CML-8 | 150-WC-40006-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8234 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.875 | CML-8 | CML: type TBC | 3 | 2049-04-13 | 2053-02-17 | 2015-01-25 07:30 | 2.5 | 0.0847 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.8 | 5.5 | 5.8 | 5.4 | 0.63966
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45044-03C02 | CML-2 | 50-FG-45044-03C02 CML-2 | no | FPSO 2014 | Pipe Wall Thickness | 20570 | Reviewed on 26/11/14.FFS. Repeat Oct.19 | 2014-10-12 07:00 | 2014-10-12 12:00 |  |  | Nestor | 2014-11-26 16:19 | [32 empty] | 9.325 | CML-2 | CML: Elbow | 6 | 2074-03-22 | 2073-01-19 | 2014-10-12 07:00 | 2.5 | 0.10255 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 3 O'Clock | 50 | 8.74 | 50-PL-23034-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.2 | 8.6 | 9.5 | 10 | 0.58523
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-5 | 50-CG-38452-09C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2504 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.775 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 8.5 | 8 | 7.3 | 0.58523
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-7 | 50-CG-38474-01C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23631 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.075 | CML-7 | CML: Elbow | 3 | 2018-11-16 | 2019-06-18 | 2015-10-28 07:00 | 2.5 | 0.55624 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 3 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 5.3 | 4.2 | 5.4 | 5.4 | 0.58523
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56012-01C02 | CML-2 | 80-DH-56012-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3468 | Rope Access | 2014-05-13 10:30 | 2014-05-13 12:00 | [36 empty] | 5.925 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-13 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-DH-56012-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 5.6 | 6.8 | 0.58523
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-3 | 50-PW-44040-01C02 CML-3 | yes | FPSO 2014 | Pipe Wall Thickness | 1978 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.275 | CML-3 | CML: Elbow | 3 | 2018-01-10 | 2018-07-10 | 2014-03-27 07:00 | 2.5 | 0.65855 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5 | 5.2 | 5.7 | 0.29861
WC01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23049 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 6 | CML-5 | CML: Elbow | 6 | 2016-04-26 | 2015-11-17 | 2015-05-06 07:00 | 2.5 | 2.9696 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 5.4 | 12 O'Clock | 40 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.6 | 5.5 | 6.5 | 0.6377
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2975 | Deck Level | 2014-05-01 13:00 | 2014-05-01 14:00 | [36 empty] | 5.5 | CML-2 | CML: Elbow | 3 | 2019-10-14 | 2020-06-11 | 2014-05-01 13:00 | 2.48 | 0.48006 | A4: Left Quadrant |  | 2.54 | 2.48 | 2.1637 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-FL-43072-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.62 |  | 5.8 | 5.5 | 5.6 | 5.1 | 0.29439
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24301 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 | Wet CO2 Gas Corrosion, downstream of super heaters and approaching dew point temperature (36 Deg C) |  | Nestor | 2016-11-08 | Reviewed. Line FFS. No internal damage in RBI | [31 empty] | 4.85 | CML-1 | CML: Elbow | 3 | 2021-07-21 | 2020-06-07 | 2016-05-27 07:00 | 1.88 | 0.50839 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 4.5 | 3 O'Clock | 100 | 6.02 | 100-FG-45008-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.62 |  | 4.9 | 4.5 | 5 | 5 | 0.23805
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22959 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 6.35 | CML-1 | CML: Elbow | 3 | 2077-04-17 | 2084-09-24 | 2015-05-04 07:00 | 2.5 | 0.04678 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 1.5947 | 6.6 | 6.7 | 6.7 | 5.4 | 0.63509
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8444 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.925 | CML-2 | CML: type TBC | 3 | 2049-09-12 | 2053-08-04 | 2015-02-01 07:30 | 2.5 | 0.08373 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AU-63021-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.4 | 6.5 | 5.4 | 0.60759
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-1 | 50-PW-44040-01C02 CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 23236 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.275 | CML-1 | CML: Elbow | 3 | 2024-05-07 | 2025-07-09 | 2015-05-11 07:00 | 2.5 | 0.27788 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.26707 | 5 | 5.1 | 5.4 | 5.6 | 0.27538
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57008-01C02 | CML-6 | 80-DC-57008-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23278 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 6.5 | CML-6 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 7.3 | 5.5 | 7.3 | 0.93808
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57008-01C02 | CML-3 | 80-DC-57008-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23275 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.775 | CML-3 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.9 | 6 | 5.7 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57008-01C02 | CML-10 | 80-DC-57008-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23282 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.8 | CML-10 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 5.6 | 5.5 | 6.3 | 0.3559
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-43 | 200-PL-20019-01C02 CML-43 |  | FPSO 2014 | Pipe Wall Thickness | 21294 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.275 | CML-43 | CML: Pipe Length | 3 | 2033-12-01 | 2033-10-08 | 2014-09-30 07:00 | 2.5 | 0.18764 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.7 | 6.1 | 6.2 | 0.28723
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-18 | 300-PW-44003-01C03 CML-18 | Yes | FPSO 2014 | Pipe Wall Thickness | 21860 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 16:26 | [32 empty] | 9.575 | CML-18 | CML: Elbow | 6 | 2023-02-24 | 2022-01-08 | 2014-10-19 07:00 | 2.5 | 0.80181 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.4 | 9.8 | 9.2 | 9.9 | 0.3304
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56019-01C02 | CML-3 | 80-DH-56019-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3463 | Rope Access | 2014-05-13 09:30 | 2014-05-13 10:30 | [36 empty] | 9.875 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-13 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 9 | 9 O'Clock | 80 | 5.49 | 80-DH-56019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 10.2 | 10.2 | 10.1 | 9 | 0.58523
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-20 | 50-DH-56137-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23448 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 18.025 | CML-20 | CML: Pipe Length | 3 | 2023-03-19 | 2019-02-02 | 2015-07-23 07:00 | 2.5 | 1.9316 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.3 | 6 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 | -0.82806 | 18.5 | 17.8 | 17.3 | 18.5 | 0.58523
PL03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-PL-57066-01C03 | CML-7 | 50-PL-57066-01C03 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23093 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 10.025 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.3 | 6 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.8 | 0.8774 | 10.7 | 9.9 | 9.3 | 10.2 | 0.58523
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-4 | 50-DC-57043-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23129 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.55 | CML-4 | CML: Pipe Length | 3 | 2160-10-18 | 2176-08-12 | 2015-05-10 07:00 | 2.5 | 0.02061 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -0.53841 | 5.5 | 5.6 | 5.5 | 5.6 | 0.057735
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-4 | 200-PG-23006-09C02-PA CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 23837 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 19.5 | CML-4 | CML: Fitting | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A3: Inside Quadrant |  | 15.26 | 9.3 | 12.28 | 18.7 | 6 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 19.6 | 20.1 | 18.7 | 19.6 | 0.5831
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-8 | 50-PG-23074-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20630 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.6 | CML-8 | CML: Elbow | 3 | 2019-11-23 | 2020-08-03 | 2014-07-26 07:00 | 2.5 | 0.46896 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 6.4 | 5.5 | 5 | 0.5831
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-10 | 400-FH-43508-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6559 | Rope Access.Line is FFS. Action: to recheck in a year (Mar. 2016) to confirm CR. | 2015-03-30 07:00 | 2015-03-30 15:00 |  |  | Administrator | 2015-09-07 16:09 | [32 empty] | 8.9 | CML-10 | CML: Pipe Length | 3 | 2062-08-12 | 2057-12-18 | 2015-03-30 07:00 | 3 | 0 | A2: Right Quadrant |  | 4.92 | 3 | 3.465 | 8.1 | 3 O'Clock | 500 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 9 | 8.1 | 9 | 9.5 | 0.5831
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-26 | 200-PL-20019-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 21277 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.425 | CML-26 | CML: Fitting | 3 | 2033-12-01 | 2033-10-08 | 2014-09-30 07:00 | 2.5 | 0.18764 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.6 | 6.3 | 6.7 | 0.27538
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-33 | 150-WC-40006-01C02 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 8957 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 6.225 | CML-33 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.2 | 6.5 | 6.8 | 5.4 | 0.60208
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-6 | 250-PW-44509-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22041 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 9.475 | CML-6 | CML: Reducing Tee | 6 | 2147-06-24 | 2139-11-09 | 2014-10-20 07:00 | 2.5 | 0.05046 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.2 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.6 | 9.5 | 9.2 | 9.6 | 0.1893
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-6 | 50-DC-57025-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22940 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.925 | CML-6 | CML: Elbow | 3 | 2159-02-18 | 2174-10-08 | 2015-05-02 07:00 | 2.5 | 0.02085 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -0.091479 | 6.3 | 6.1 | 5.5 | 5.8 | 0.35
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56006-01C02 | CML-1 | 80-DH-56006-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3444 | Rope Access | 2014-05-12 10:30 | 2014-05-12 11:30 | [36 empty] | 6.05 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-12 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-DH-56006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 5.8 | 5.6 | 6.9 | 0.58023
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20070-01C02-P | CML-5 | 100-PL-20070-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21565 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.175 | CML-5 | CML: Fitting | 3 | 2048-08-12 | 2049-10-10 | 2014-07-17 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 6 O'Clock | 100 | 6.02 | 100-PL-20070-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.2 | 6.1 | 6.2 | 0.05
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22340 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.85 | CML-4 |  | 3 | 2434-05-27 | 2401-06-21 | 2014-04-30 13:00 | 2.5 | 0.01094 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.1 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.8 | 8 | 7.1 | 8.5 | 0.58023
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-17 | 50-PL-23516-03C03 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 7805 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:00 | [32 empty] | 9.05 | CML-17 | CML: Elbow | 6 | 2043-02-15 | 2042-07-22 | 2015-01-13 07:00 | 2.5 | 0.20988 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.9 | 9.8 | 9.1 | 8.4 | 0.58023
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-17 | 400-FH-43500-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 5653 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 10.05 | CML-17 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 9.4 | 9 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 9.9 | 10.1 | 10.8 | 9.4 | 0.58023
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71335-01K01 | CML-4 | 150-WF-71335-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 6402 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 5.775 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 5.5 | 6 O'Clock | 150 | 3 | 150-WF-71335-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 5.9 | 5.5 | 5.9 | 0.1893
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-9 | 50-GN-67002-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 9068 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.875 | CML-9 | CML: type TBC | 3 | 2146-04-03 | 2160-07-04 | 2015-03-01 09:30 | 2.5 | 0.02287 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.4 | 5.8 | 5.5 | 5.8 | 0.37749
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-8 | 50-GN-67002-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 9067 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.65 | CML-8 | CML: type TBC | 3 | 2146-04-03 | 2160-07-04 | 2015-03-01 09:30 | 2.5 | 0.02287 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.9 | 5.5 | 5.7 | 0.19149
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-13 | 50-AU-63015-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 9044 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.7 | CML-13 | CML: type TBC | 3 | 2146-03-26 | 2160-06-26 | 2015-03-01 07:00 | 2.5 | 0.02287 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.9 | 5.9 | 5.5 | 0.23094
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-18 | 50-AI-63004-01E01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 9009 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.875 | CML-18 | CML: type TBC | 3 | 2146-01-09 | 2160-04-03 | 2015-02-28 07:00 | 2.5 | 0.02291 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 6.1 | 6.2 | 5.5 | 0.3304
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-12 | 50-AI-63007-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8936 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.875 | CML-12 | CML: type TBC | 3 | 2145-08-16 | 2159-10-24 | 2015-02-26 09:00 | 2.5 | 0.02298 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 6.2 | 6.2 | 0.37749
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-27 | 50-AU-63018-01E01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 8923 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.55 | CML-27 | CML: type TBC | 3 | 2145-06-14 | 2159-08-15 | 2015-02-25 13:00 | 2.5 | 0.02301 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.5 | 5.5 | 5.7 | 0.1
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-17 | 50-AU-63018-01E01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8913 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.7 | CML-17 | CML: type TBC | 3 | 2145-06-14 | 2159-08-15 | 2015-02-25 13:00 | 2.5 | 0.02301 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 5.8 | 5.5 | 5.7 | 0.14142
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-10 | 50-AU-63018-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8906 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.85 | CML-10 | CML: type TBC | 3 | 2145-06-14 | 2159-08-15 | 2015-02-25 13:00 | 2.5 | 0.02301 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.2 | 6.2 | 5.5 | 0.40415
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-8 | 50-AU-63018-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8904 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 6.05 | CML-8 | CML: type TBC | 3 | 2145-06-14 | 2159-08-15 | 2015-02-25 13:00 | 2.5 | 0.02301 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6 | 5.5 | 6 | 6.7 | 0.49329
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63019-01E01 | CML-6 | 50-AU-63019-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8874 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 08:00 | 2015-02-25 09:00 | [36 empty] | 5.95 | CML-6 | CML: type TBC | 3 | 2145-05-29 | 2159-07-29 | 2015-02-25 08:00 | 2.5 | 0.02302 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-AU-63019-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.1 | 6.2 | 5.5 | 6 | 0.31091
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63010-01E01 | CML-3 | 50-AI-63010-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8773 |  | 2015-02-15 13:00 | 2015-02-15 14:00 | [36 empty] | 5.825 | CML-3 | CML: type TBC | 3 | 2143-05-16 | 2157-04-26 | 2015-02-15 13:00 | 2.5 | 0.02338 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-AI-63010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 6.1 | 6.1 | 0.32016
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63010-01E01 | CML-6 | 50-AI-63010-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8776 |  | 2015-02-15 13:00 | 2015-02-15 14:00 | [36 empty] | 5.7 | CML-6 | CML: type TBC | 3 | 2143-05-16 | 2157-04-26 | 2015-02-15 13:00 | 2.5 | 0.02338 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-AI-63010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.1 | 5.5 | 5.7 | 0.28284
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67009-01E01 | CML-9 | 50-GN-67009-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8787 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.95 | CML-9 | CML: type TBC | 3 | 2143-04-27 | 2157-04-05 | 2015-02-15 07:00 | 2.5 | 0.02339 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.1 | 6 | 6.2 | 0.31091
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-12 | 50-GN-67006-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8757 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.7 | CML-12 | CML: type TBC | 3 | 2143-04-27 | 2157-04-05 | 2015-02-15 07:00 | 2.5 | 0.02339 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 5.5 | 5.5 | 5.5 | 0.4
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-9 | 50-GN-67006-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8754 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.9 | CML-9 | CML: type TBC | 3 | 2143-04-27 | 2157-04-05 | 2015-02-15 07:00 | 2.5 | 0.02339 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 5.5 | 6.3 | 5.5 | 0.46188
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-5 | 50-GN-67006-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8750 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.9 | CML-5 | CML: type TBC | 3 | 2143-04-27 | 2157-04-05 | 2015-02-15 07:00 | 2.5 | 0.02339 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6 | 5.5 | 6.1 | 6 | 0.2708
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-2 | 50-GN-67006-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8747 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.575 | CML-2 | CML: type TBC | 3 | 2143-04-27 | 2157-04-05 | 2015-02-15 07:00 | 2.5 | 0.02339 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.5 | 5.6 | 5.6 | 0.05
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-12 | 50-GN-67004-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8617 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.575 | CML-12 | CML: type TBC | 3 | 2142-01-27 | 2155-11-18 | 2015-02-09 07:30 | 2.5 | 0.02361 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 5.6 | 5.6 | 0.05
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-11 | 50-GN-67004-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8616 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6 | CML-11 | CML: type TBC | 3 | 2142-01-27 | 2155-11-18 | 2015-02-09 07:30 | 2.5 | 0.02361 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 6.3 | 6.6 | 0.53541
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-10 | 50-GN-67004-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8615 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.9 | CML-10 | CML: type TBC | 3 | 2142-01-27 | 2155-11-18 | 2015-02-09 07:30 | 2.5 | 0.02361 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.2 | 6 | 5.9 | 0.29439
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-8 | 50-GN-67004-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8613 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6 | CML-8 | CML: type TBC | 3 | 2142-01-27 | 2155-11-18 | 2015-02-09 07:30 | 2.5 | 0.02361 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 7 | 5.9 | 5.6 | 5.5 | 0.68799
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63035-01E01 | CML-2 | 50-AI-63035-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8583 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-07 14:00 | 2015-02-07 16:00 | [36 empty] | 5.975 | CML-2 | CML: type TBC | 3 | 2141-09-18 | 2155-06-26 | 2015-02-07 14:00 | 2.5 | 0.02368 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-AI-63035-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.2 | 5.5 | 6.1 | 6.1 | 0.32016
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63034-01E01 | CML-5 | 50-AI-63034-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8577 |  | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.825 | CML-5 | CML: type TBC | 3 | 2141-01-12 | 2154-09-24 | 2015-02-04 07:30 | 2.5 | 0.02381 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-AI-63034-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.2 | 5.5 | 6.1 | 0.37749
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67001-01E01 | CML-11 | 50-GN-67001-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8556 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.725 | CML-11 | CML: type TBC | 3 | 2141-01-12 | 2154-09-24 | 2015-02-04 07:30 | 2.5 | 0.02381 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 6.3 | 5.5 | 5.5 | 0.38622
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67001-01E01 | CML-10 | 50-GN-67001-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8555 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.7 | CML-10 | CML: type TBC | 3 | 2141-01-12 | 2154-09-24 | 2015-02-04 07:30 | 2.5 | 0.02381 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.3 | 5.5 | 5.5 | 0.4
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67001-01E01 | CML-5 | 50-GN-67001-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8550 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.7 | CML-5 | CML: type TBC | 3 | 2141-01-12 | 2154-09-24 | 2015-02-04 07:30 | 2.5 | 0.02381 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.2 | 5.5 | 5.6 | 5.5 | 0.33665
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67001-01E01 | CML-3 | 50-GN-67001-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8548 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.875 | CML-3 | CML: type TBC | 3 | 2141-01-12 | 2154-09-24 | 2015-02-04 07:30 | 2.5 | 0.02381 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 5.9 | 6.2 | 5.5 | 0.28723
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67001-01E01 | CML-2 | 50-GN-67001-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8547 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.8 | CML-2 | CML: type TBC | 3 | 2141-01-12 | 2154-09-24 | 2015-02-04 07:30 | 2.5 | 0.02381 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 6.3 | 5.6 | 5.5 | 0.3559
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-3 | 50-AI-63009-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8525 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 5.6 | CML-3 | CML: type TBC | 3 | 2140-10-28 | 2154-07-01 | 2015-02-03 07:30 | 2.5 | 0.02384 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.7 | 5.7 | 5.5 | 0.11547
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-2 | 50-AI-63009-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8524 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.175 | CML-2 | CML: type TBC | 3 | 2140-10-28 | 2154-07-01 | 2015-02-03 07:30 | 2.5 | 0.02384 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.2 | 6.5 | 6.5 | 0.4717
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-1 | 50-AI-63009-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8523 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 5.875 | CML-1 | CML: type TBC | 3 | 2140-10-28 | 2154-07-01 | 2015-02-03 07:30 | 2.5 | 0.02384 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 6.3 | 5.8 | 5.5 | 0.3304
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40510-1CG | CML-3 | 100-WC-40510-1CG CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8663 | Material Class Not Selectable | 2015-02-12 11:00 | 2015-02-12 12:00 |  |  | Administrator | 2015-09-08 12:16 | [32 empty] | 9.75 | CML-3 | CML: Elbow | 3 | 2074-01-04 | 2058-09-17 | 2015-02-12 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.56 | 2.5 | 4.03 | 9.2 | 9 O'Clock | 100 | 8.56 | 100-WC-40510-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10 | 10 | 9.8 | 9.2 | 0.37859
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63020-01E01 | CML-5 | 50-AU-63020-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8485 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.075 | CML-5 | CML: type TBC | 3 | 2140-08-13 | 2154-04-08 | 2015-02-02 07:30 | 2.5 | 0.02388 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-AU-63020-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 6.2 | 5.5 | 6.3 | 0.38622
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67007-01E01 | CML-5 | 50-GN-67007-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8476 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 5.575 | CML-5 | CML: type TBC | 3 | 2140-08-13 | 2154-04-08 | 2015-02-02 07:30 | 2.5 | 0.02388 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.5 | 5.7 | 5.5 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-3 | 50-AI-63012-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8453 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.925 | CML-3 | CML: type TBC | 3 | 2140-05-29 | 2154-01-14 | 2015-02-01 07:30 | 2.5 | 0.02392 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 5.8 | 5.5 | 6.5 | 0.41932
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-2 | 50-AI-63012-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8452 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.85 | CML-2 | CML: type TBC | 3 | 2140-05-29 | 2154-01-14 | 2015-02-01 07:30 | 2.5 | 0.02392 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 6.4 | 5.7 | 5.5 | 0.3873
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42314-01S01 | CML-5 | 50-CI-42314-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8427 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 6.7 | CML-5 | CML: type TBC | 1 | 2140-03-22 | 2112-02-13 | 2015-01-31 10:00 | 2.5 | 0.02396 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-CI-42314-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 7.1 | 5.5 | 7.5 | 6.7 | 0.8641
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63037-01E01 | CML-1 | 50-AI-63037-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8397 | All fittings CAST. Readings taken on piping directly adjacent to fitting. Reducing tee no reducer as shown on ISO | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.025 | CML-1 | CML: type TBC | 3 | 2139-12-29 | 2153-07-30 | 2015-01-30 07:30 | 2.5 | 0.024 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-AI-63037-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.4 | 6.4 | 5.8 | 0.45
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63001-01E01 | CML-2 | 50-AI-63001-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8309 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 5.6 | CML-2 | CML: type TBC | 3 | 2139-05-22 | 2152-11-27 | 2015-01-27 09:45 | 2.5 | 0.02412 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-AI-63001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.7 | 5.6 | 5.5 | 0.08165
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-1 | 50-WD-53011-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8277 | Reducing Hose Coupling | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.325 | CML-1 | CML: type TBC | 3 | 2139-02-28 | 2152-08-27 | 2015-01-26 07:30 | 2.5 | 0.02416 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.2 | 5.5 | 6.8 | 6.8 | 0.61847
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-25 | 50-WD-53010-01E01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 8268 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.6 | CML-25 | CML: type TBC | 3 | 2139-02-28 | 2152-08-27 | 2015-01-26 07:30 | 2.5 | 0.02416 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.6 | 5.5 | 5.7 | 0.08165
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-19 | 50-WD-53010-01E01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8262 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6 | CML-19 | CML: type TBC | 3 | 2139-02-28 | 2152-08-27 | 2015-01-26 07:30 | 2.5 | 0.02416 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.9 | 5.5 | 6.1 | 5.5 | 0.66332
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69006-01S01 | CML-6 | 50-OL-69006-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8195 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.975 | CML-6 | CML: type TBC | 1 | 2138-09-29 | 2110-12-20 | 2015-01-24 07:30 | 2.5 | 0.02424 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.2 | 6 | 6.2 | 0.3304
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-20 | 50-WD-53007-01E01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 8159 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.975 | CML-20 | CML: type TBC | 3 | 2138-09-29 | 2152-03-12 | 2015-01-24 07:30 | 2.5 | 0.02424 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 6.3 | 5.5 | 6.5 | 0.49917
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-1 | 100-OL-69001-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8103 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.45 | CML-1 | CML: type TBC | 1 | 2024-07-23 | 2021-10-05 | 2015-01-23 07:30 | 2.5 | 0.31564 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.5 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.8 | 7.2 | 6.3 | 0.73258
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69004-01S01 | CML-8 | 80-OL-69004-01S01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8099 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 5.6 | CML-8 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.49 | 2.5 | 3.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.6 | 5.5 | 5.7 | 0.08165
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-29 | 250-PG-23003-06C02-PA CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 3245 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.95 | CML-29 | CML: type TBC | 3 | 2033-10-06 | 2035-12-13 | 2014-05-09 07:00 | 2.5 | 0.14929 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 6.4 | 6.5 | 5.4 | 0.58023
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2016 | Pipe Wall Thickness | 24307 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 | Wet CO2 Gas Corrosion, downstream of super heaters and approaching dew point temperature (36 Deg C) |  | Nestor | 2016-11-08 | Reviewed. Line FFS. No internal damage in RBI | [31 empty] | 4.8 | CML-7 | CML: Elbow | 3 | 2021-07-21 | 2020-06-07 | 2016-05-27 07:00 | 1.88 | 0.50839 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 4.5 | 3 O'Clock | 100 | 6.02 | 100-FG-45008-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.62 |  | 4.9 | 4.5 | 4.8 | 5 | 0.21602
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-7 | 300-FL-43080-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2386 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 6.65 | CML-7 | CML: type TBC | 3 | 2025-09-11 | 2025-08-10 | 2014-03-19 07:00 | 2.5 | 0.31326 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 7.1 | 6.2 | 7.2 | 0.58023
FG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-FG-45024-01C02 | CML-6 | 50-FG-45024-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2552 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 9.65 | CML-6 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 9 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.5 | 9.4 | 10.5 | 9.2 | 0.58023
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-2 | 50-DC-57013-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7671 | New Isometric drawing | 2015-01-08 09:30 | 2015-01-08 12:00 |  |  | Administrator | 2015-09-08 12:38 | [32 empty] | 5.7 | CML-2 | CML: Elbow | 3 | 2135-06-08 | 2148-07-11 | 2015-01-08 09:30 | 2.5 | 0.0249 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.7 | 6.1 | 5.5 | 0.28284
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-1 | 50-DC-57013-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7670 | New Isometric drawing | 2015-01-08 09:30 | 2015-01-08 12:00 |  |  | Administrator | 2015-09-08 12:38 | [32 empty] | 5.55 | CML-1 | CML: Elbow | 3 | 2135-06-08 | 2148-07-11 | 2015-01-08 09:30 | 2.5 | 0.0249 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.6 | 5.5 | 5.5 | 0.057735
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-4 | 50-DC-57013-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7669 | Re-check | 2015-01-08 09:30 | 2015-01-08 12:00 |  |  | Administrator | 2015-09-08 12:38 | [32 empty] | 5.7 | CML-4 | CML: Elbow | 3 | 2135-06-08 | 2148-07-11 | 2015-01-08 09:30 | 2.5 | 0.0249 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -1.7809 | 5.5 | 5.7 | 6.1 | 5.5 | 0.28284
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-2 | 50-DC-57013-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7667 | Re-check | 2015-01-08 09:30 | 2015-01-08 12:00 |  |  | Administrator | 2015-09-08 12:38 | [32 empty] | 5.55 | CML-2 | CML: Elbow | 3 | 2135-06-08 | 2148-07-11 | 2015-01-08 09:30 | 2.5 | 0.0249 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -1.7809 | 5.6 | 5.6 | 5.5 | 5.5 | 0.057735
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-1 | 50-DC-57013-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7666 | Re-check | 2015-01-08 09:30 | 2015-01-08 12:00 |  |  | Administrator | 2015-09-08 12:38 | [32 empty] | 5.75 | CML-1 | CML: Elbow | 3 | 2135-06-08 | 2148-07-11 | 2015-01-08 09:30 | 2.5 | 0.0249 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | -1.7809 | 5.6 | 6.1 | 5.5 | 5.8 | 0.26458
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57048-03C02 | CML-3 | 50-DC-57048-03C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7615 |  | 2015-01-07 07:00 | 2015-01-07 08:00 | [36 empty] | 5.925 | CML-3 | CML: Elbow | 3 | 2135-03-16 | 2134-05-27 | 2015-01-07 07:00 | 2.5 | 0.02494 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57048-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.1 | 6.2 | 5.9 | 5.5 | 0.30957
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-14 | 150-WC-40006-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 9073 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 6.125 | CML-14 | CML: type TBC | 3 | 2051-05-15 | 2055-06-11 | 2015-03-01 09:30 | 2.5 | 0.08004 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.8 | 5.4 | 6 | 6.3 | 0.58523
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-8 | 200-PL-20035-03C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21343 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.7 | CML-8 | CML: Fitting | 3 | 2018-12-25 | 2018-01-10 | 2014-06-27 13:00 | 3.61 | 0.82035 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 7.3 | 9 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.69 |  | 8 | 7.5 | 8 | 7.3 | 0.3559
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38472-01C02 | CML-9 | 50-CG-38472-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23664 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 7.35 | CML-9 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 3 O'Clock | 40 | 5.54 | 50-CG-38472-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.5 | 6.8 | 7 | 8.1 | 0.58023
WC01 | Montara_Topside | Yes | Diesel Oil (62) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8050 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.9 | CML-2 | CML: type TBC | 3 | 2049-01-16 | 2052-11-13 | 2015-01-21 07:30 | 2.5 | 0.08526 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DO-62003-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.4 | 5.4 | 5.4 | 6.4 | 0.57735
WC01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-WC-40006-01C02 | CML-6 | 150-WC-40006-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23479 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 6.15 | CML-6 | CML: Fitting | 3 | 2022-02-08 | 2022-01-16 | 2015-07-24 07:00 | 2.5 | 0.44268 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 6 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.98317 | 6.2 | 6.6 | 5.4 | 6.4 | 0.52599
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22253 | Deck Level | 2014-05-01 13:00 | 2014-05-01 14:00 | [36 empty] | 5.35 | CML-1 | CML: Elbow | 3 | 2019-10-14 | 2020-06-11 | 2014-05-01 13:00 | 2.48 | 0.48006 | A2: Right Quadrant |  | 2.54 | 2.48 | 2.1637 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-FL-43072-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.62 |  | 5.6 | 5.1 | 5.4 | 5.3 | 0.20817
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43091-01C02 | CML-7 | 80-FL-43091-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5832 | Rope access | 2014-06-24 10:30 | 2014-06-24 12:00 | [36 empty] | 6.35 | CML-7 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-24 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 3 O'Clock | 80 | 5.49 | 80-FL-43091-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.4 | 5.7 | 6.2 | 7.1 | 0.58023
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56143-01C02 | CML2 | 25-DH-56143-01C02 CML2 |  | FPSO 2015 | Pipe Wall Thickness | 7531 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 |  |  | Nestor | 2014-11-24 10:32 | [32 empty] | 6.25 | CML2 |  | 3 | 2026-06-22 | 2026-05-18 | 2015-04-13 07:00 | 2.5 | 0.29466 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 25 | 6.35 | 25-DH-56143-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 7.1 | 6.1 | 5.8 | 6 | 0.58023
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38477-01C02-P | CML-4 | 50-CG-38477-01C02-P CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10373 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.25 | CML-4 | CML: type TBC | 3 | 2016-07-23 | 2016-07-14 | 2013-11-12 | 2.5 | 1.2241 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 25 | 6.35 | 25-CG-38493-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 5.8 | 5.8 | 6.1 | 6 | 7.1 | 0.58023
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-29 | 200-PG-23007-09C03-PA CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 20716 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 20.35 | CML-29 | CML: Fitting | 6 | 2027-02-11 | 2024-03-20 | 2014-06-30 13:00 | 10.22 | 0.7586 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 19.8 | 9 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.58 |  | 19.9 | 20.9 | 20.8 | 19.8 | 0.58023
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23063-09C02 | CML-10 | 50-PG-23063-09C02 CML-10 | Yes | FPSO 2013 | Pipe Wall Thickness | 10736 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 9.15 | CML-10 | CML: type TBC | 3 | 2020-01-21 | 2018-05-01 | 2013-11-19 | 2.5 | 0.93918 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 12 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.4 | 9.6 | 9.3 | 0.58023
PG02 | Montara_Topside | No | Separation (20) | Pipework | 250-PG-20042-01D01-P | CML-12 | 250-PG-20042-01D01-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21445 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 5.925 | CML-12 | CML: Fitting | 1 | 2018-06-19 | 2016-08-06 | 2014-07-13 07:30 | 2.5 | 0.7617 | A1: Outside Quadrant |  | 5.35 | 2.5 | 3.925 | 5.5 | 12 O'Clock | 250 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6 | 6 | 6.2 | 0.29861
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-10 | 50-DH-56137-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20549 | Rope Access | 2014-05-27 08:00 | 2014-05-27 09:00 | [36 empty] | 18.15 | CML-10 | CML: Pipe Length | 6 | 2096-09-16 | 2085-01-22 | 2014-05-27 08:00 | 2.8 | 0 | A3: Inside Quadrant |  | 5.13 | 2.8 | 3.965 | 17.5 | 6 O'Clock | 80 | 11.13 | 80-PG-23025-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.7 | -22.1263 | 18.2 | 18.9 | 17.5 | 18 | 0.58023
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-14 | 300-PF-20501-03C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21690 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 17.95 | CML-14 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 17.1 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.2 |  | 18.1 | 17.1 | 18.2 | 18.4 | 0.58023
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-9 | 50-PL-23515-01C03 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8658 | Line is FFS despite the High CR . Current RBI frequency is 48m.RBI frequency to stay at 48m. Action: to recheck CML-1 to 6 in a year to confirm CR. RBI frequency to stay at 48m | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:51 | [32 empty] | 8.675 | CML-9 | CML: Elbow | 6 | 2026-01-19 | 2025-10-22 | 2015-02-12 07:00 | 2.5 | 0.49349 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 9 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.7 | 9.3 | 8.8 | 7.9 | 0.57951
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-8 | 80-PW-44016-01C02-P CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 22910 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.4 | CML-8 | CML: Elbow | 3 | 2025-02-11 | 2026-06-23 | 2015-05-02 07:00 | 2.5 | 0.25539 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.17892 | 5 | 5.6 | 5.5 | 5.5 | 0.2708
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-35 | 300-PF-20500-03C03-P CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 21655 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.625 | CML-35 | CML: Pipe Length | 6 | 2059-05-03 | 2051-01-28 | 2014-09-27 07:00 | 4.9 | 0.20391 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 14.5 | 15.4 | 14.6 | 14 | 0.57951
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2974 | Deck Level | 2014-05-01 13:00 | 2014-05-01 14:00 | [36 empty] | 5.35 | CML-1 | CML: Elbow | 3 | 2019-10-14 | 2020-06-11 | 2014-05-01 13:00 | 2.48 | 0.48006 | A2: Right Quadrant |  | 2.54 | 2.48 | 2.1637 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-FL-43072-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.62 |  | 5.6 | 5.1 | 5.4 | 5.3 | 0.20817
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24383 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.875 | CML-1 | CML: Elbow | 1 | 2035-06-01 | 2029-05-31 | 2016-06-07 07:00 | 1.71 | 0 | A1: Outside Quadrant |  | 2.91 | 1.71 | 2.31 | 4.4 | 12 O'Clock | 50 | 3.91 | 50-FG-45054-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.69 |  | 4.4 | 5 | 4.6 | 5.5 | 0.48563
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-5 | 80-DC-57005-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20251 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 5.75 | CML-5 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-06-02 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 9 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6 | 5.7 | 5.8 | 5.5 | 0.20817
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-3 | 80-DC-57005-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20249 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 5.75 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-06-02 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 6 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 5.8 | 5.5 | 5.9 | 0.17321
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-1 | 80-DC-57005-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20247 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 5.7 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-06-02 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.7 | 5.7 | 5.9 | 0.1633
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57007-01C02 | CML-1 | 80-DC-57007-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20265 | Rope access | 2014-06-02 11:00 | 2014-06-02 12:00 | [36 empty] | 5.925 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-06-02 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-DC-57007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.8 | 6.2 | 6.2 | 0.34034
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-4 | 50-PW-44040-01C02 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 1979 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.225 | CML-4 | CML: Elbow | 3 | 2018-01-10 | 2018-07-10 | 2014-03-27 07:00 | 2.5 | 0.65855 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.2 | 5 | 5.6 | 0.263
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38493-01C02 | CML-2 | 25-CG-38493-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10371 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.475 | CML-2 | CML: type TBC | 3 | 2016-01-28 | 2016-01-21 | 2013-11-12 | 2.5 | 1.4466 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 12 O'Clock | 25 | 6.35 | 25-CG-38493-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | 5.7 | 5.7 | 6.6 | 6.5 | 7.1 | 0.57951
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-9 | 50-PL-23020-01C03 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10123 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.575 | CML-9 | CML: type TBC | 6 | 2016-04-28 | 2016-04-07 | 2013-11-08 | 2.5 | 2.1444 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.8 | 12 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 7.8 | 8.7 | 9.2 | 8.6 | 0.57951
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-20 | 250-PG-23004-06C03-A CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 13020 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 19.275 | CML-20 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.5 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.95 |  | 19.3 | 19.4 | 18.5 | 19.9 | 0.57951
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-8 | 80-CG-38459-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 6131 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 17.425 | CML-8 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 16.8 | 3 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 |  | 17.4 | 16.8 | 18.2 | 17.3 | 0.57951
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-23 | 80-CG-38459-09C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 10973 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 17.875 | CML-23 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 17.1 | 12 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.88 |  | 17.1 | 18.5 | 18 | 17.9 | 0.57951
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2447 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 6.7 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.6 | 6 | 7.4 | 6.8 | 0.57735
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24389 | Lagging removed | 2016-06-07 07:00 | 2016-06-07 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 4.7 | CML-1 | CML: Elbow | 1 | 2035-06-01 | 2029-05-31 | 2016-06-07 07:00 | 1.71 | 0 | A4: Left Quadrant |  | 2.91 | 1.71 | 2.31 | 4.4 | 9 O'Clock | 50 | 3.91 | 50-FG-45049-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.69 |  | 4.6 | 5.2 | 4.6 | 4.4 | 0.34641
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-3 | 150-FL-43453-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2247 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 8.4333 | CML-3 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 8.1 | 9 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  |  | 9.1 | 8.1 | 8.1 | 0.57735
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-14 | 150-WC-40006-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8890 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.85 | CML-14 | CML: type TBC | 3 | 2051-02-17 | 2055-03-06 | 2015-02-25 09:30 | 2.5 | 0.08055 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 6.3 | 6.2 | 0.46547
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45024-01C02 | CML-3 | 50-FG-45024-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23592 | Re-check of line as requested by ops supervisor | 2015-09-15 15:30 | 2015-09-15 16:30 | [36 empty] | 9.55 | CML-3 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2015-09-15 15:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 3 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 0.086047 | 9.2 | 9.2 | 9.4 | 10.4 | 0.57446
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-1 | 250-PW-20039-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5833 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 9.875 | CML-1 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.4 | 6 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.3 | 10 | 9.4 | 9.8 | 0.37749
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 | yes | FPSO 2016 | Pipe Wall Thickness | 23763 | re-check line | 2016-02-13 07:00 | 2016-02-13 15:00 | [35 empty] | Low alarm breach | 8.075 | CML-1 | CML: Elbow | 3 | 2018-06-11 | 2017-09-06 | 2016-02-13 07:00 | 4.7 | 1.2459 | A1: Outside Quadrant |  | 7.97 | 4.7 | 5.6494 | 7.6 | 12 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0 | 7.6 | 8.7 | 7.9 | 8.1 | 0.46458
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56028-01C02 | CML-8 | 80-DH-56028-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20905 | Rope Access | 2014-05-22 07:00 | 2014-05-22 08:00 | [36 empty] | 6.35 | CML-8 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-05-22 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 9 O'Clock | 80 | 5.49 | 80-DH-56028-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.5 | 6.7 | 6.7 | 5.5 | 0.57446
FG02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-FG-45455-01C02-E | CML-1 | 25-FG-45455-01C02-E CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20987 | Rope Access | 2014-05-24 09:30 | 2014-05-24 10:30 | [36 empty] | 6.35 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-24 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-DH-56108-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.2 | 6 | 6.2 | 6 | 0.57446
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-15 | 25-FG-45455-01C02-E CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2394 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 6.85 | CML-15 | CML: type TBC | 3 | 2022-03-10 | 2022-02-14 | 2014-03-19 07:00 | 2.5 | 0.43856 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 7 | 7.2 | 7.2 | 0.57446
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56091-01C02 | CML-1 | 80-DH-56091-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20982 | Rope Access | 2014-05-17 11:00 | 2014-05-17 12:00 | [36 empty] | 5.55 | CML-1 | CML: type TBC | 3 | 2018-04-12 | 2018-11-04 | 2014-05-17 11:00 | 2.5 | 0.61448 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 9 O'Clock | 80 | 5.49 | 80-DH-56091-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 6.3 | 5.5 | 5.5 | 4.9 | 0.57446
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45024-01C02 | CML-5 | 50-FG-45024-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 23857 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.25 | CML-5 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A1: Outside Quadrant |  |  | 2.7 |  | 9.4 | 12 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.4 | 10.6 | 10.4 | 10.6 | 0.57446
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-6 | 250-PW-20022-01C03-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23104 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 10.375 | CML-6 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2015-05-10 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 9.5 | 9 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 1.163 | 11.4 | 10.9 | 9.7 | 9.5 | 0.9215
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-16 | 200-PG-23007-09C03-PA CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23405 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 19.85 | CML-16 | CML: Fitting | 6 | 2027-02-23 | 2024-03-29 | 2015-07-22 07:00 | 10.22 | 0.75682 | A3: Inside Quadrant |  | 14.62 | 10.22 | 12.42 | 19 | 6 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.78 | -0.094376 | 20.2 | 20.2 | 19 | 20 | 0.57446
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-VA-23302-01C02 | CML-2 | 80-VA-23302-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 22518 | Possible incorrect schedule pipe. | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 3.35 | CML-2 | CML: Elbow | 3 | 2015-08-04 | 2015-11-05 | 2015-04-20 07:00 | 2.5 | 1.3735 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 2.9 | 6 O'Clock | 50 | 5.49 | 80-VA-23302-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.4 |  | 4.1 | 2.9 | 2.9 | 3.5 | 0.57446
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-11 | 200-PL-20035-03C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23472 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 24.675 | CML-11 | CML: Elbow | 3 | 2024-07-20 | 2022-08-22 | 2015-07-24 07:00 | 3.61 | 0.41006 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.3 | 6 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.69 | -0.18634 | 7.8 | 7.6 | 7.3 | 7.6 | 0.20616
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-3 | 250-PG-23005-06C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10049 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 16.525 | CML-3 | CML: Elbow | 6 | 2015-01-18 | 2014-09-27 | 2013-11-06 | 8.6 | 5.9139 | A1: Outside Quadrant |  | 12.26 | 8.6 | 10.43 | 15.7 | 12 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 15.7 | 16.8 | 17 | 16.6 | 0.57373
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56059-01C02 | CML-1 | 50-DH-56059-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3339 | Rope Access | 2014-05-08 11:00 | 2014-05-08 12:00 | [36 empty] | 8.125 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-08 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.6 | 12 O'Clock | 50 | 5.54 | 50-DH-56059-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 7.7 | 8.8 | 8.4 | 0.57373
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-2 | 50-DH-56137-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21086 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.375 | CML-2 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.6 | 12 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.7 | 6.9 | 6.3 | 0.57373
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-6 | 250-PG-23005-06C03 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10052 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 17.325 | CML-6 | CML: Elbow | 6 | 2016-04-11 | 2015-09-26 | 2013-11-06 | 8.6 | 3.3728 | A4: Left Quadrant |  | 12.26 | 8.6 | 10.43 | 16.8 | 9 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 18.1 | 17.4 | 17 | 16.8 | 0.57373
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-33 | 50-DH-56062-01C02 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 9120 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.725 | CML-33 | CML: type TBC | 3 | 2029-01-24 | 2030-09-29 | 2015-03-02 07:00 | 2.5 | 0.19412 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6 | 5.3 | 6.4 | 5.2 | 0.57373
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-25 | 50-PW-44040-01C02 CML-25 | yes | FPSO 2015 | Pipe Wall Thickness | 23260 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.3 | CML-25 | CML: Pipe Length | 3 | 2024-05-07 | 2025-07-09 | 2015-05-11 07:00 | 2.5 | 0.27788 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.17805 | 5.6 | 5.4 | 5 | 5.2 | 0.2582
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-12 | 400-FH-43508-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6561 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.275 | CML-12 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 8.6 | 12 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.3 | 10 | 9.2 | 0.57373
PW03 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PW-44018-01X01 | CML-17 | 200-PW-44018-01X01 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 13187 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.525 | CML-17 | CML: Tee | 3 | 2048-08-08 | 2055-05-16 | 2014-01-21 13:00 | 3.61 | 0.07781 | A4: Left Quadrant |  | 3.35 | 3.61 | 3.0831 | 6.3 | 9 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.69 |  | 6.4 | 6.7 | 6.7 | 6.3 | 0.20616
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-11 | 50-CG-38458-01C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23739 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.225 | CML-11 | CML: Elbow | 3 | 2020-06-20 | 2021-03-23 | 2015-10-30 07:00 | 2.5 | 0.43073 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.2 | 4.5 | 5.3 | 5.9 | 0.57373
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56141-01C02 | CML-1 | 50-DH-56141-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21068 | Rope Access | 2014-05-15 08:00 | 2014-05-15 09:00 | [36 empty] | 5.475 | CML-1 | CML: type TBC | 3 |  |  | 2014-05-15 08:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 4.8 | 9 O'Clock | 80 |  | 80-DH-56141-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.2 | 6 | 5.9 | 4.8 | 0.57373
PG05 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21563 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 5.925 | CML-3 | CML: Elbow | 3 | 2019-10-23 | 2020-01-08 | 2014-07-17 07:30 | 2.5 | 0.55019 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 9 O'Clock | 100 | 6.02 | 100-PL-20070-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 6 | 6.7 | 5.4 | 0.57373
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-62 | 350-FL-43512-01C02 CML-62 |  | FPSO 2015 | Pipe Wall Thickness | 6549 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 8.575 | CML-62 | CML: type TBC | 3 | 222262 | 2443-03-19 | 2015-03-30 07:00 | 2.5 | 0.01094 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 6 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.6 | 9.3 | 7.9 | 8.5 | 0.57373
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-17 | 50-DH-56070-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 3233 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.875 | CML-17 | CML: type TBC | 3 | 2021-10-17 | 2022-09-10 | 2014-05-09 07:00 | 2.5 | 0.36256 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.3 | 6.4 | 5.6 | 5.2 | 0.57373
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24403 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.275 | CML-2 | CML: Elbow | 1 | 2043-01-05 | 2033-03-19 | 2016-06-08 07:00 | 2.53 | 0 | A4: Left Quadrant |  | 4.49 | 2.53 | 3.51 | 5.5 | 9 O'Clock | 80 | 5.49 | 80-FG-45045-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.97 |  | 6.2 | 6.8 | 6.6 | 5.5 | 0.57373
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-9 | 100-DH-56088-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 5202 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 6.325 | CML-9 | CML: Reducing Tee | 3 | 2028-11-21 | 2029-05-27 | 2014-05-20 07:00 | 2.5 | 0.22729 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 3 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 7 | 5.8 | 5.9 | 6.6 | 0.57373
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 | yes | FPSO 2016 | Pipe Wall Thickness | 24413 | Re-check as requested by N.Sequera | 2016-07-06 07:00 | 2016-07-06 15:00 | Check Corrosion Rate of 0.668mm/ yr | 41 | Kirstie Albone | 2017-03-23 14:58 | [32 empty] | 7.975 | CML-8 | CML: Elbow | 6 | 2023-07-18 | 2022-12-20 | 2016-07-06 07:00 | 2.5 | 0.66786 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.2 | 12 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 | 0.20798 | 7.2 | 7.9 | 8.5 | 8.3 | 0.57373
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-17 | 100-DC-57036-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1423 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.612mm/ yr | [35 empty] | 5.625 | CML-17 | CML: type TBC | 3 | 2019-03-02 | 2019-05-10 | 2014-04-07 07:00 | 2.5 | 0.61168 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.6 | 5.8 | 5.5 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-8 | 100-DC-57036-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1414 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.612mm/ yr | [35 empty] | 5.675 | CML-8 | CML: type TBC | 3 | 2019-03-02 | 2019-05-10 | 2014-04-07 07:00 | 2.5 | 0.61168 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 5.7 | 5.9 | 0.17078
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57063-01C02 | CML-3 | 50-DC-57063-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1388 | Rope access | 2014-04-05 13:00 | 2014-04-05 14:00 | [36 empty] | 5.5 | CML-3 | CML: type TBC | 3 | 2077-08-13 | 2084-07-03 | 2014-04-05 13:00 | 2.5 | 0.04732 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.5 | 5.5 | 5.5 | 0
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57063-01C02 | CML-2 | 50-DC-57063-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1387 | Rope access | 2014-04-05 13:00 | 2014-04-05 14:00 | [36 empty] | 5.8 | CML-2 | CML: type TBC | 3 | 2077-08-13 | 2084-07-03 | 2014-04-05 13:00 | 2.5 | 0.04732 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6 | 5.7 | 5.5 | 6 | 0.24495
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-10 | 50-DC-57451-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1381 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 5.7 | CML-10 | CML: type TBC | 3 | 2077-08-05 | 2084-06-24 | 2014-04-05 10:30 | 2.5 | 0.04734 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 5.6 | 6.1 | 0.2708
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-10 | 250-PG-23003-06C02-PA CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2036 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 6.225 | CML-10 | CML: type TBC | 3 | 2040-08-31 | 2043-11-03 | 2014-03-27 14:30 | 2.5 | 0.10964 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 12 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.7 | 6.3 | 6.5 | 0.57373
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 | yes | FPSO 2016 | Pipe Wall Thickness | 24152 | re-check line | 2016-02-13 | 2016-02-13 | [35 empty] | Low alarm breach | 8.075 | CML-1 | CML: Elbow | 3 | 2018-06-11 | 2017-09-06 | 2016-02-13 | 4.7 | 1.2463 | A1: Outside Quadrant |  | 7.97 | 4.7 | 5.6494 | 7.6 | 12 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 1.971 | 7.6 | 8.7 | 7.9 | 8.1 | 0.46458
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1696 | Rope Access | 2014-04-13 09:15 | 2014-04-13 10:15 | [36 empty] | 7.875 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 09:15 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 3 O'Clock | 50 | 5.54 | 50-WC-40018-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.8 | 7.2 | 8.6 | 7.9 | 0.57373
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57068-01C02 | CML-1 | 50-DC-57068-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1329 | Rope access | 2014-04-04 07:00 | 2014-04-04 08:00 | [36 empty] | 5.925 | CML-1 | CML: type TBC | 3 | 2077-05-10 | 2084-03-20 | 2014-04-04 07:00 | 2.5 | 0.04751 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-DC-57068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.5 | 6.1 | 6.5 | 0.46458
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-16 | 250-PG-23003-06C02-PA CML-16 | Yes | FPSO 2014 | Pipe Wall Thickness | 24254 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 16.075 | CML-16 | CML: Elbow | 3 | 2085-04-24 | 2073-10-17 | 2014-09-24 07:00 | 7.9 | 0 | A3: Inside Quadrant |  | 12.09 | 7.9 | 9.0519 | 15.3 | 6 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 16.6 | 16 | 15.3 | 16.4 | 0.57373
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-12 | 100-PG-23503-03C03-A CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2728 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10.925 | CML-12 | CML: Pipe Length | 6 | 2019-04-09 | 2019-07-21 | 2014-03-13 09:00 | 5.66 | 0.93368 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.4 | 12 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.74 |  | 10.4 | 10.5 | 11.6 | 11.2 | 0.57373
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-8 | 300-PW-44003-01C03 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21850 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 10.6 | CML-8 | CML: Reducing Tee | 6 | 2026-10-03 | 2025-03-17 | 2014-10-19 07:00 | 2.5 | 0.58511 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 11.3 | 10.9 | 10.7 | 9.5 | 0.7746
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-10 | 300-PW-44003-01C03 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22875 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.125 | CML-10 | CML: Reducing Tee | 6 | 2031-11-16 | 2029-09-26 | 2015-05-01 07:00 | 2.5 | 0.42278 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 12 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 1.5052 | 9.5 | 10.7 | 10.7 | 9.6 | 0.66521
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56096-01C02 | CML-3 | 50-DN-56096-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1312 |  | 2014-03-31 09:30 | 2014-03-31 10:00 | [36 empty] | 5.55 | CML-3 | CML: type TBC | 3 | 2076-07-18 | 2083-04-27 | 2014-03-31 09:30 | 2.5 | 0.04812 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DN-56096-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.5 | 5.5 | 5.6 | 0.057735
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56094-01C02 | CML-3 | 50-DN-56094-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1306 |  | 2014-03-31 07:00 | 2014-03-31 08:00 | [36 empty] | 5.75 | CML-3 | CML: type TBC | 3 | 2076-07-10 | 2083-04-18 | 2014-03-31 07:00 | 2.5 | 0.04814 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DN-56094-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.7 | 5.7 | 6.1 | 0.25166
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-17 | 50-FG-45024-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1200 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 8.375 | CML-17 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 3 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.3 | 7.9 | 9.2 | 8.1 | 0.57373
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-9 | 300-PW-44003-01C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21851 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 10.425 | CML-9 | CML: Reducing Tee | 6 | 2026-10-03 | 2025-03-17 | 2014-10-19 07:00 | 2.5 | 0.58511 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.5 | 11 | 10.7 | 9.5 | 0.65
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-1 | 150-PG-20009-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2695 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 11 | CML-1 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-12 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 10.2 | 9 O'Clock | 100 | 8.56 | 100-PG-20009-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 11 | 11.5 | 11.3 | 10.2 | 0.57155
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-1 | 150-PG-20009-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 666 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 11 | CML-1 | CML: Pipe Length | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 09:00 | 2.03 | 0 | A4: Left Quadrant |  | 1.11 | 2.03 | 1.57 | 10.2 | 9 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.17 | 0 | 11 | 11.5 | 11.3 | 10.2 | 0.57155
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-3 | 50-DC-57025-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2114 |  | 2014-03-29 07:00 | 2014-03-29 08:00 | [36 empty] | 6.05 | CML-3 | CML: Elbow | 3 | 2076-02-09 | 2082-11-01 | 2014-03-29 07:00 | 2.5 | 0.04846 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 7 | 5.8 | 5.5 | 5.9 | 0.65574
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-2 | 50-DC-57025-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2113 |  | 2014-03-29 07:00 | 2014-03-29 08:00 | [36 empty] | 5.85 | CML-2 | CML: Elbow | 3 | 2076-02-09 | 2082-11-01 | 2014-03-29 07:00 | 2.5 | 0.04846 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 6.1 | 6.1 | 5.5 | 0.3
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-1 | 150-PG-20009-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 384 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 11 | CML-1 | CML: Pipe Length | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 | 2.03 | 0 | A4: Left Quadrant |  | 1.11 | 2.03 | 1.57 | 10.2 | 9 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.17 |  | 11 | 11.5 | 11.3 | 10.2 | 0.57155
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-2 | 300-PF-20500-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21622 | Protective mesh removed | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.9 | CML-2 | CML: Reducing Tee | 6 | 2086-05-06 | 2073-03-25 | 2014-09-27 07:00 | 4.9 | 0.12839 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 3 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 15.2 | 14.1 | 15.4 | 14.9 | 0.57155
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-9 | 25-FG-45455-01C02-E CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12628 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.6 | CML-9 | CML: type TBC | 3 | 2017-01-21 | 2017-06-13 | 2014-01-23 10:00 | 2.5 | 0.8337 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 6.3 | 5 | 5.3 | 0.57155
PG05 | Montara_Topside | Yes | Diesel Oil (62) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2989 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.1 | CML-4 | CML: Elbow | 1 | 2033-04-19 | 2028-11-21 | 2014-05-01 10:30 | 2.5 | 0.15279 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.4 | 6.7 | 6.4 | 0.57155
PG05 | Montara_Topside | Yes | Diesel Oil (62) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22268 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.1 | CML-4 | CML: Elbow | 1 | 2033-04-19 | 2028-11-21 | 2014-05-01 10:30 | 2.5 | 0.15279 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.4 | 6.7 | 6.4 | 0.57155
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8610 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.925 | CML-5 | CML: type TBC | 3 | 2050-03-05 | 2054-02-13 | 2015-02-09 07:30 | 2.5 | 0.08264 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 6.2 | 6.4 | 0.45735
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-16 | 50-WC-40071-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1951 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 5.725 | CML-16 | CML: Pipe Length | 3 | 2075-07-04 | 2082-03-02 | 2014-03-26 09:30 | 2.5 | 0.04893 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.9 | 5.5 | 5.9 | 5.6 | 0.20616
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-10 | 50-WC-40071-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1945 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 6.475 | CML-10 | CML: Elbow | 3 | 2075-07-04 | 2082-03-02 | 2014-03-26 09:30 | 2.5 | 0.04893 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 7.2 | 7.3 | 5.9 | 0.91059
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-4 | 50-WC-40071-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1939 | Rope Access. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Mar. 2020). RBI to be updated | 2014-03-26 09:30 | 2014-03-26 10:30 |  |  | Administrator | 2015-09-08 12:56 | [32 empty] | 5.575 | CML-4 | CML: Pipe Length | 3 | 2075-07-04 | 2082-03-02 | 2014-03-26 09:30 | 2.5 | 0.04893 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 5.6 | 5.5 | 5.5 | 0.095743
PW03 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PW-44018-01X01 | CML-19 | 200-PW-44018-01X01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 13189 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.475 | CML-19 | CML: Tee | 3 | 2048-08-08 | 2055-05-16 | 2014-01-21 13:00 | 3.61 | 0.07781 | A2: Right Quadrant |  | 3.35 | 3.61 | 3.0831 | 6.3 | 3 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.69 |  | 6.7 | 6.3 | 6.4 | 6.5 | 0.17078
PW03 | Montara_Topside | Yes | Chemical Injection (42) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8419 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 6.725 | CML-8 | CML: type TBC | 1 | 2028-05-01 | 2025-01-10 | 2015-01-31 10:00 | 2.5 | 0.20364 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 7.5 | 5.2 | 7.4 | 6.8 | 1.0626
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-7 | 50-PG-23024-03C03 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10039 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 8 | CML-7 | CML: Elbow | 6 | 2015-10-01 | 2015-06-26 | 2013-11-06 | 0.97 | 3.3266 | A1: Outside Quadrant |  | 2.74 | 0.97 | 1.855 | 7.3 | 12 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.33 |  | 7.3 | 8.7 | 8 | 8 | 0.57155
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38489-01C02-P | CML-2 | 50-CG-38489-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20859 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 26.95 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 9 O'Clock | 50 | 5.54 | 50-CG-38489-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9.2 | 8.2 | 8.7 | 7.9 | 0.57155
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-23 | 50-DC-57020-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 2465 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 5.725 | CML-23 | CML: type TBC | 3 | 2074-04-04 | 2080-10-13 | 2014-03-20 09:30 | 2.5 | 0.04993 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 5.6 | 6 | 5.5 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-14 | 50-DC-57020-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2456 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 5.925 | CML-14 | CML: type TBC | 3 | 2074-04-04 | 2080-10-13 | 2014-03-20 09:30 | 2.5 | 0.04993 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.9 | 6.7 | 5.6 | 0.54391
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-7 | 50-DC-57020-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2449 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 5.7 | CML-7 | CML: type TBC | 3 | 2074-04-04 | 2080-10-13 | 2014-03-20 09:30 | 2.5 | 0.04993 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.9 | 5.7 | 5.7 | 0.1633
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-15 | 100-DC-57075-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2434 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.649mm/ yr | [35 empty] | 5.725 | CML-15 | CML: type TBC | 3 | 2018-10-31 | 2019-01-04 | 2014-03-20 07:00 | 2.5 | 0.64935 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 6 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 5.5 | 5.5 | 6.2 | 0.3304
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-2 | 100-DC-57038-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2365 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | Check Corrosion Rate of 0.653mm/ yr | [35 empty] | 5.8 | CML-2 | CML: type TBC | 3 | 2018-10-20 | 2018-12-23 | 2014-03-18 14:00 | 2.5 | 0.65317 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 12 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.8 | 6.3 | 5.6 | 0.3559
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23216 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.15 | CML-7 | CML: Elbow | 3 | 2033-06-09 | 2035-10-08 | 2015-05-11 07:00 | 2.5 | 0.14923 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 2.7943 | 6.2 | 5.2 | 6 | 7.2 | 0.8226
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-7 | 300-PF-20003-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21745 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 8.9 | CML-7 | CML: Elbow | 6 | 2016-02-03 | 2015-06-08 | 2014-10-01 07:00 | 2.5 | 4.3968 | A1: Outside Quadrant |  | 8.27 | 2.5 | 5.385 | 8.4 | 12 O'Clock | 50 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.7 | 8.6 | 8.9 | 0.57155
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-3 | 200-PW-44018-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8580 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-07 14:00 | 2015-02-07 16:00 | Check Corrosion Rate of 0.681mm/ yr | [35 empty] | 6.275 | CML-3 | CML: type TBC | 3 | 2019-01-25 | 2019-01-10 | 2015-02-07 14:00 | 2.5 | 0.68077 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 9 O'Clock | 25 | 6.35 | 25-AI-63006-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.5 | 7.1 | 6.3 | 5.2 | 0.7932
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-9 | 300-PG-20005-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 6165 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 13.9 | CML-9 | CML: Pipe Length | 6 | 2025-05-14 | 2023-03-21 | 2014-07-11 07:30 | 4.9 | 0.78347 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 13.4 | 14.7 | 13.6 | 13.9 | 0.57155
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-20 | 80-CG-38459-09C02-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23717 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 11.5 | CML-20 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 10.8 | 3 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.5 | 10.8 | 11.5 | 12.2 | 0.57155
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-10 | 50-FG-45020-03C02 CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 2609 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 4.85 | CML-10 | CML: type TBC | 3 | 2015-03-13 | 2015-03-08 | 2014-04-26 09:30 | 2.5 | 1.7065 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 1.8205 | 5.1 | 5.2 | 4 | 5.1 | 0.56862
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-27 | 50-DH-56137-01C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 6150 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 20.55 | CML-27 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 19.7 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 |  | 19.7 | 20.8 | 20.8 | 20.9 | 0.56862
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-23 | 200-PW-44018-01X01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 23232 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.3 | CML-23 | CML: Elbow | 3 | 2033-06-09 | 2035-10-08 | 2015-05-11 07:00 | 2.5 | 0.14923 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 2.445 | 5.2 | 6.5 | 7 | 6.5 | 0.77028
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-12 | 250-PG-20036-01C03-P CML-12 | Yes | FPSO 2014 | Pipe Wall Thickness | 21370 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.55 | CML-12 | CML: Elbow | 6 | 2018-12-09 | 2018-08-16 | 2014-07-14 07:30 | 2.5 | 1.2247 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.9 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.8 | 9.2 | 7.9 | 8.3 | 0.56862
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-14 | 50-CG-38466-01C02 CML-14 | yes | FPSO 2014 | Pipe Wall Thickness | 2528 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 8.4667 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-02 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8 | 9 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 | 8 |  | 8.3 | 9.1 | 8 | 0.56862
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-23 | 50-FG-45023-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 1171 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 8.9667 | CML-23 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.5 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  |  | 8.8 | 9.6 | 8.5 | 0.56862
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-9 | 25-PG-23300-25C02 CML-9 | Yes | FPSO 2014 | Pipe Wall Thickness | 20676 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 9.975 | CML-9 | CML: Pipe Length | 3 | 2060-04-24 | 2051-11-12 | 2014-05-27 09:30 | 4.4 | 0 | A3: Inside Quadrant |  | 6.09 | 4.4 | 5.245 | 9.6 | 9 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 9.9 | 10.8 | 9.6 | 9.6 | 0.56789
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-2 | 80-PG-20046-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21461 | Protective mesh removed | 2014-06-28 08:00 | 2014-06-28 09:00 | [36 empty] | 11.425 | CML-2 | CML: Elbow | 6 | 2030-11-27 | 2028-03-28 | 2014-06-28 08:00 | 2.5 | 0.49308 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.6 | 12 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.6 | 11.8 | 11.8 | 11.5 | 0.56789
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-18 | 300-PF-20001-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21156 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.475 | CML-18 | CML: Elbow | 6 | 2015-10-16 | 2015-03-17 | 2014-07-16 07:30 | 2.5 | 4.9549 | A2: Right Quadrant |  | 8.27 | 2.5 | 5.385 | 8.7 | 3 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.9 | 8.7 | 9.4 | 9.9 | 0.56789
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-10 | 200-PG-23065-09C02-A CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23401 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 18.7 | CML-10 | CML: Elbow | 3 | 2044-04-25 | 2034-08-06 | 2015-07-22 07:00 | 10.17 | 0.26162 | A3: Inside Quadrant |  | 15.26 | 10.17 | 12.715 | 17.7 | 6 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.53 | -0.43556 | 19.5 | 19.4 | 17.7 | 18.2 | 0.89069
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-14 | 200-PG-23065-09C02-A CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 428 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.6 | CML-14 | CML: Pipe Length | 3 | 2024-08-30 | 2021-02-14 | 2014-03-12 09:00 | 10.17 | 0.71877 | A1: Outside Quadrant |  | 15.26 | 10.17 | 12.715 | 17.7 | 12 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.53 |  | 17.7 | 19 | 18.6 | 19.1 | 0.6377
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-18 | 250-PG-23003-06C02-PA CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 24256 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 13.775 | CML-18 | CML: Elbow | 3 | 2018-06-02 | 2017-08-13 | 2014-09-24 07:00 | 7.9 | 1.4363 | A1: Outside Quadrant |  | 12.09 | 7.9 | 9.0519 | 13.2 | 12 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 13.2 | 14.4 | 14.1 | 13.4 | 0.56789
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-43 | 300-PF-20001-03C03-P CML-43 |  | FPSO 2014 | Pipe Wall Thickness | 21181 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.507mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:55 | [32 empty] | 14.325 | CML-43 | CML: Fitting | 6 | 2031-11-18 | 2028-07-24 | 2014-07-16 07:30 | 4.9 | 0.50705 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 13.7 | 14.9 | 14.7 | 14 | 0.56789
FL02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-FL-43454-01C02-P | CML-7 | 50-FL-43454-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13146 |  | 2014-01-18 13:00 | 2014-01-18 15:00 | [36 empty] | 9.575 | CML-7 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-01-18 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 9.1 | 6 O'Clock | 50 | 8.74 | 50-PL-24003-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.4 | 9.4 | 9.1 | 10.4 | 0.56789
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40509-1CG | CML-3 | 150-WC-40509-1CG CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8701 | Material Class Not Selectable.Line is FFS. Action: to recheck in two year(Feb. 2017) to confirm CR | 2015-02-13 14:00 | 2015-02-13 15:00 | Check Corrosion Rate of 0.803mm/ yr | 36 | Administrator | 2015-09-08 11:51 | [32 empty] | 10.575 | CML-3 | CML: Elbow | 3 | 2023-12-15 | 2020-07-20 | 2015-02-13 14:00 | 2.5 | 0.80319 | A2: Right Quadrant |  | 7.97 | 2.5 | 5.235 | 9.6 | 3 O'Clock | 150 | 10.97 | 150-WC-40509-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 11.1 | 9.6 | 11.1 | 10.5 | 0.70887
PG02 | Montara_Topside | No | Separation (20) | Pipework | 300-PG-20028-03D01-P | CML-3 | 300-PG-20028-03D01-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21330 | Protective mesh removed | 2014-06-27 08:00 | 2014-06-27 09:00 | [36 empty] | 7.05 | CML-3 | CML: Elbow | 1 | 2038-04-25 | 2030-11-12 | 2014-06-27 08:00 | 3.86 | 0 | A3: Inside Quadrant |  | 5.35 | 3.86 | 4.605 | 6.9 | 6 O'Clock | 300 | 6.35 | 300-PG-20028-03D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.04 |  | 7.1 | 7.2 | 6.9 | 7 | 0.1291
PW03 | Montara_Topside | Yes | Steam (55) | Pipework | 200-PW-44018-01X01 | CML-17 | 200-PW-44018-01X01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8847 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 5.8 | CML-17 | CML: type TBC | 3 | 2031-04-17 | 2033-05-16 | 2015-02-24 07:00 | 2.5 | 0.16714 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 6 | 6.8 | 0.76594
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-5 | 80-FH-43005-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12555 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 5.975 | CML-5 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-20 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 9 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.8 | 5.9 | 5.6 | 5.6 | 0.56789
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-28 | 250-PW-44006-01X01 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 1925 | Rope Access | 2014-03-26 07:00 | 2014-03-26 09:00 | [36 empty] | 6.175 | CML-28 | CML: Fitting | 3 | 2016-02-24 | 2016-02-17 | 2014-03-26 07:00 | 2.5 | 1.4072 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 7 | 6.3 | 5.2 | 6.2 | 0.74106
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56066-01C02 | CML-1 | 50-DH-56066-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3278 | Rope Access | 2014-05-09 14:00 | 2014-05-09 15:00 | [36 empty] | 6.875 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56066-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.2 | 6.3 | 6.5 | 7.5 | 0.56789
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-12 | 25-FG-45455-01C02-E CML-12 |  | FPSO 2016 | Pipe Wall Thickness | 24357 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.625 | CML-12 | CML: Equal Tee | 3 | 2034-07-10 | 2034-05-14 | 2016-06-06 07:00 | 2.5 | 0.18229 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.8 | 6.8 | 7.1 | 0.56789
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56024-01C02 | CML-3 | 80-DH-56024-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3490 | Rope Access | 2014-05-14 13:00 | 2014-05-14 14:00 | [36 empty] | 6.975 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-14 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.5 | 6 O'Clock | 80 | 5.49 | 80-DH-56024-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.8 | 6.8 | 6.5 | 6.8 | 0.56789
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-9 | 300-PW-44003-01C03 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22874 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.175 | CML-9 | CML: Reducing Tee | 6 | 2031-11-16 | 2029-09-26 | 2015-05-01 07:00 | 2.5 | 0.42278 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 0 | 10 | 10.7 | 10.5 | 9.5 | 0.53774
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38492-01C02 | CML-5 | 50-CG-38492-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2539 |  | 2014-04-03 08:00 | 2014-04-03 09:00 | [36 empty] | 8.125 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-03 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 6 O'Clock | 50 | 5.54 | 50-CG-38492-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.7 | 7.8 | 7.5 | 8.5 | 0.56789
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-2 | 50-PL-23514-01C03 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8635 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:18 | [32 empty] | 9.225 | CML-2 | CML: Elbow | 6 | 2044-07-17 | 2043-12-11 | 2015-02-10 11:30 | 2.5 | 0.20033 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.6 | 9.3 | 9.6 | 0.56789
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-28 | 250-PL-20006-01C02-P CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 13198 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 7.4 | CML-28 | CML: Reducer | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A3: Inside Quadrant |  | 3.35 | 3.61 | 3.0831 | 7.3 | 6 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.69 |  | 7.4 | 7.4 | 7.3 | 7.5 | 0.08165
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-20 | 200-PG-24001-09C02 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10276 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 18.075 | CML-20 | CML: Pipe Length | 3 | 2018-09-02 | 2016-11-29 | 2013-11-09 | 9.2 | 1.723 | A3: Inside Quadrant |  | 15.26 | 9.2 | 12.23 | 17.5 | 6 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 18.4 | 18.7 | 17.5 | 17.7 | 0.56789
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-9 | 200-PG-23065-09C02-A CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 423 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.95 | CML-9 | CML: Pipe Length | 3 | 2027-02-09 | 2022-10-19 | 2014-03-12 09:00 | 10.17 | 0.59042 | A4: Left Quadrant |  | 15.26 | 10.17 | 12.715 | 17.8 | 9 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.63 |  | 19.1 | 19.7 | 19.2 | 17.8 | 0.81035
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-22 | 200-PL-20019-01C02 CML-22 | yes | FPSO 2014 | Pipe Wall Thickness | 21273 | Reviewed on 27/11/14. FFS. recheck on Sep.15 | 2014-09-30 07:00 | 2014-09-30 15:00 |  |  | Nestor | 2014-11-27 15:58 | [32 empty] | 7.7 | CML-22 | CML: Elbow | 3 | 2047-08-03 | 2047-05-04 | 2014-09-30 07:00 | 2.5 | 0.11259 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.2 | 6.2 | 7.5 | 9.9 | 1.5684
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-9 | 150-WC-40006-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8905 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 6.075 | CML-9 | CML: type TBC | 3 | 2051-02-20 | 2055-03-10 | 2015-02-25 13:00 | 2.5 | 0.08053 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.4 | 6.3 | 6.2 | 0.45735
WC01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-WC-40006-01C02 | CML-10 | 150-WC-40006-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8394 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.075 | CML-10 | CML: type TBC | 3 | 2049-07-31 | 2049-05-05 | 2015-01-30 07:30 | 2.5 | 0.084 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.4 | 6.3 | 5.4 | 6.2 | 0.45735
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-2 | 200-PG-23065-09C02-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 416 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.175 | CML-2 | CML: Pipe Length | 3 | 2030-11-29 | 2025-05-29 | 2014-03-12 09:00 | 10.17 | 0.46207 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 17.9 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.73 |  | 19.7 | 17.9 | 19.1 | 20 | 0.92871
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-17 | 250-PG-23004-06C03-A CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23384 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 17.975 | CML-17 | CML: Pipe Length | 6 | 2037-07-15 | 2032-12-04 | 2015-07-21 07:00 | 8.55 | 0.40229 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 17.4 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.85 | 0.087552 | 18.1 | 17.7 | 17.4 | 18.7 | 0.56199
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-7 | 300-PW-44003-01C03 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22872 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.175 | CML-7 | CML: Reducing Tee | 6 | 2031-11-16 | 2029-09-26 | 2015-05-01 07:00 | 2.5 | 0.42278 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 1.8814 | 10.5 | 10.7 | 10 | 9.5 | 0.53774
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-54 | 300-PF-20001-03C03-P CML-54 |  | FPSO 2014 | Pipe Wall Thickness | 21192 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.445mm/ yr | 40 | Kirstie Albone | 2017-03-23 15:59 | [32 empty] | 12.925 | CML-54 | CML: Elbow | 6 | 2018-12-07 | 2017-10-20 | 2014-07-16 07:30 | 4.1 | 1.8414 | A4: Left Quadrant |  | 8.27 | 4.1 | 6.185 | 12.2 | 9 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 12.8 | 13.5 | 13.2 | 12.2 | 0.56199
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-8 | 200-PG-20300-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5873 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | [36 empty] | 13.925 | CML-8 | CML: Cap End | 6 | 2107-05-31 | 2090-05-30 | 2014-06-25 09:30 | 3.3 | 0 | A3: Inside Quadrant |  | 6.7 | 3.3 | 5 | 13.2 | 6 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 14.2 | 13.8 | 13.2 | 14.5 | 0.56199
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-29 | 300-PG-20005-03C03-P CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 22791 | New location | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.425 | CML-29 | CML: Reducing Tee | 6 | 2051-06-23 | 2044-08-18 | 2015-04-29 07:00 | 4.9 | 0.24602 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 3 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14.9 | 13.8 | 14.9 | 14.1 | 0.56199
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-24 | 50-CG-38001-09C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 10938 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 10.525 | CML-24 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0 | A3: Inside Quadrant |  | 5.74 |  |  | 9.9 | 6 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 9.9 | 11 | 10.2 | 9.9 | 11 | 0.56199
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45042-03C02-E | CML-1 | 50-FG-45042-03C02-E CML-1 | yes | FPSO 2016 | Pipe Wall Thickness | 24315 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.725 | CML-1 | CML: Elbow | 3 | 2030-04-24 | 2030-03-15 | 2016-06-01 07:00 | 2.5 | 0.17979 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 12 O'Clock | 50 | 5.54 | 50-FG-45042-03C02-E | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.6 | 6.3 | 6 | 0.56199
FG02 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8095 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.575 | CML-4 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 6 | 12 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.7 | 7.3 | 6.3 | 0.56199
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-8 | 25-FG-45455-01C02-E CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1688 | Rope Access | 2014-04-13 07:30 | 2014-04-13 08:30 | [36 empty] | 6.575 | CML-8 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-WC-40028-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 7.3 | 6.3 | 6.7 | 0.56199
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-22 | 200-PL-20019-01C02 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 23482 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 7.25 | CML-22 | CML: Elbow | 3 | 2068-06-16 | 2068-01-21 | 2015-07-24 07:00 | 2.5 | 0.0699 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | 0 | 6.2 | 7.3 | 8 | 7.5 | 0.75939
PW03 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8085 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 5.725 | CML-7 | CML: type TBC | 1 | 2030-05-22 | 2026-09-09 | 2015-01-23 07:30 | 2.5 | 0.17603 | A2: Right Quadrant |  | 4.49 | 2.5 | 3.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.2 | 6.7 | 5.7 | 0.68496
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67301-01E01 | CML-2 | 25-GN-67301-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22496 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.825 | CML-2 | CML: Pipe Length | 3 | 2023-02-02 | 2023-01-07 | 2015-04-20 07:00 | 2.5 | 0.39772 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.8 | 5.6 | 6.1 | 0.20616
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67300-01E01 | CML-7 | 25-GN-67300-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22491 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 6.625 | CML-7 | CML: Reducer | 3 | 2023-02-02 | 2023-01-07 | 2015-04-20 07:00 | 2.5 | 0.39772 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 3 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.3 | 5.6 | 6.8 | 7.8 | 0.92511
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22845 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 6.2 | CML-1 | CML: Elbow | 3 | 2033-02-15 | 2035-06-03 | 2015-04-30 07:00 | 2.5 | 0.15158 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-DC-57006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.18159 | 6.5 | 6.6 | 5.2 | 6.5 | 0.66833
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-8 | 50-PW-44012-01X01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2022 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 6 | CML-8 | CML: Elbow | 3 | 2020-09-28 | 2021-07-13 | 2014-03-27 09:30 | 2.5 | 0.4145 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.2 | 6.6 | 6.5 | 0.66833
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71315-01K01 | CML-6 | 150-WF-71315-01K01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5135 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 5.75 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 5.6 | 3 O'Clock | 150 | 3 | 150-WF-71315-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 5.6 | 5.7 | 5.8 | 0.1291
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71315-01K01 | CML-4 | 150-WF-71315-01K01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 5133 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 5.825 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 5.6 | 12 O'Clock | 150 | 3 | 150-WF-71315-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.1 | 5.8 | 5.8 | 0.20616
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-29 | 150-WC-40006-01C02 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 9020 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6 | CML-29 | CML: type TBC | 3 | 2051-04-21 | 2055-05-15 | 2015-02-28 07:00 | 2.5 | 0.08018 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.1 | 6 | 6.5 | 0.45461
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-27 | 50-GN-67002-01E01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 9086 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.675 | CML-27 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 5.6 | 5.9 | 0.15
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-7 | 50-GN-67002-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 9066 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.9 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6 | 6 | 6 | 0.2
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-14 | 50-AU-63015-01E01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 9045 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.95 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 6.1 | 5.6 | 6.1 | 0.23805
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-3 | 50-AU-63015-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 9034 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.875 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 5.6 | 5.9 | 6 | 0.1893
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-2 | 50-AU-63015-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 9033 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.9 | 5.7 | 6.8 | 0.54772
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-16 | 50-AI-63004-01E01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 9007 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.775 | CML-16 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.8 | 5.9 | 5.6 | 0.12583
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-21 | 50-AI-63007-01E01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 8945 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.95 | CML-21 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-26 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 6.1 | 6.1 | 5.6 | 0.23805
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-2 | 50-AU-63018-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8898 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.95 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 5.6 | 6 | 6 | 0.25166
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63023-01E01 | CML-6 | 50-AU-63023-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8867 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 07:00 | 2015-02-25 08:00 | [36 empty] | 5.725 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-AU-63023-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 5.8 | 5.8 | 0.095743
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40509-1CG | CML-5 | 150-WC-40509-1CG CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8703 | Material Class Not Selectable.Line is FFS. Action: to recheck in two year(Feb. 2017) to confirm CR | 2015-02-13 14:00 | 2015-02-13 15:00 | Check Corrosion Rate of 0.745mm/ yr | 36 | Administrator | 2015-09-08 11:50 | [32 empty] | 10.975 | CML-5 | CML: Elbow | 3 | 2024-10-13 | 2021-02-10 | 2015-02-13 14:00 | 2.5 | 0.74456 | A1: Outside Quadrant |  | 7.97 | 2.5 | 5.235 | 9.7 | 12 O'Clock | 150 | 10.97 | 150-WC-40509-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 11.6 | 11.3 | 11.3 | 0.86168
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67011-01E01 | CML-2 | 50-GN-67011-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8760 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.95 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 6.3 | 5.7 | 5.6 | 0.35119
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-8 | 50-GN-67006-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8753 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 6 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.1 | 6.1 | 6.2 | 0.2708
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-4 | 50-GN-67006-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8749 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.9 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 6.2 | 5.6 | 5.6 | 0.34641
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-17 | 50-GN-67004-01E01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8622 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.6 | CML-17 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-09 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 5.6 | 5.6 | 0
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-14 | 50-GN-67004-01E01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8619 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6.1 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-09 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.1 | 5.6 | 6.3 | 6.4 | 0.3559
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-6 | 50-GN-67004-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8611 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6.05 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-09 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 6.2 | 5.6 | 6.2 | 0.3
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63034-01E01 | CML-4 | 50-AI-63034-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8576 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.075 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-AI-63034-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.3 | 6.2 | 6.2 | 0.32016
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63034-01E01 | CML-3 | 50-AI-63034-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8575 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.925 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-AI-63034-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 6.2 | 6.3 | 0.37749
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67001-01E01 | CML-9 | 50-GN-67001-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8554 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.6 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 5.6 | 5.6 | 0
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-4 | 200-FH-43131-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2825 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.975 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-15 09:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 3 O'Clock | 200 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.1 | 7.4 | 7.7 | 8.7 | 0.56199
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63020-01E01 | CML-8 | 50-AU-63020-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8488 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 5.65 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-AU-63020-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 5.6 | 5.7 | 0.057735
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67007-01E01 | CML-6 | 50-GN-67007-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8477 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 5.875 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-GN-67007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.8 | 5.6 | 6.4 | 0.3594
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67008-01E01 | CML-9 | 50-GN-67008-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8471 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.05 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-GN-67008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.6 | 6.3 | 5.7 | 0.47958
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67008-01E01 | CML-8 | 50-GN-67008-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8470 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.025 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-GN-67008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.6 | 6.3 | 5.6 | 5.6 | 0.5058
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67008-01E01 | CML-3 | 50-GN-67008-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8465 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.05 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-GN-67008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.5 | 6.5 | 5.6 | 5.6 | 0.51962
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-11 | 50-AI-63012-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8461 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.95 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.7 | 6.7 | 5.6 | 0.50662
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-7 | 50-AI-63012-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8457 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.875 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 6.4 | 5.8 | 0.3594
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-6 | 50-AI-63012-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8456 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.675 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.7 | 5.6 | 5.7 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63021-01E01 | CML-1 | 50-AU-63021-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8443 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.05 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-AU-63021-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.7 | 6.2 | 5.7 | 5.6 | 0.50662
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42315-01S01 | CML-5 | 50-CI-42315-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8416 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 7.2 | CML-5 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 8.3 | 6.6 | 8.3 | 1.3342
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63037-01E01 | CML-3 | 50-AI-63037-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8399 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 5.675 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-AI-63037-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 5.7 | 5.7 | 0.05
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23408-01C02-P | CML-4 | 50-PG-23408-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8382 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 6.325 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-PG-23408-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.3 | 6.7 | 6.7 | 0.51881
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-13 | 50-AI-63450-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8332 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.875 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 5.8 | 6.4 | 0.3594
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-5 | 50-AI-63450-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8324 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.85 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 5.8 | 6.3 | 0.31091
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63044-01E01 | CML-3 | 50-AI-63044-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8306 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 5.775 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-AI-63044-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 5.7 | 6.1 | 0.22174
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63013-01E01 | CML-4 | 50-AI-63013-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8303 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.15 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-AI-63013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 6.5 | 6.7 | 5.6 | 0.53229
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53003-01E01 | CML-9 | 50-WD-53003-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8299 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.025 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-WD-53003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.7 | 6 | 5.6 | 5.8 | 0.47871
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-9 | 50-WD-53011-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8285 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.975 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.2 | 6.1 | 6 | 0.263
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-4 | 50-WD-53011-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8280 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.625 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 5.6 | 5.6 | 0.05
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-31 | 50-WD-53010-01E01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 8274 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.025 | CML-31 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 6.6 | 5.6 | 6.1 | 0.43493
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-26 | 50-WD-53010-01E01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 8269 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.7 | CML-26 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 5.8 | 5.7 | 0.08165
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-24 | 50-WD-53010-01E01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 8267 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.7 | CML-24 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.8 | 5.7 | 5.6 | 0.08165
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-5 | 50-WD-53010-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8248 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.8 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 5.7 | 6.2 | 0.2708
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53015-01E01 | CML-9 | 50-WD-53015-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8235 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.825 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.8 | 6 | 5.9 | 0.17078
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53015-01E01 | CML-4 | 50-WD-53015-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8230 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.925 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.3 | 5.6 | 5.6 | 6.2 | 0.37749
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-10 | 50-WD-53014-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8225 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.4 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.9 | 6.6 | 5.6 | 6.5 | 0.55976
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-4 | 50-WD-53014-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8219 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.375 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.6 | 6.4 | 5.6 | 6.9 | 0.55603
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53012-01E01 | CML-4 | 50-WD-53012-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8212 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.1 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-WD-53012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.4 | 5.6 | 6.3 | 6.1 | 0.3559
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53012-01E01 | CML-2 | 50-WD-53012-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8210 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.25 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-WD-53012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.5 | 6.3 | 5.6 | 6.6 | 0.45092
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53012-01E01 | CML-1 | 50-WD-53012-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8209 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.875 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-WD-53012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.8 | 6.3 | 5.6 | 0.29861
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53016-01E01 | CML-7 | 50-WD-53016-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8208 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.525 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-WD-53016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 7.7 | 7 | 5.8 | 5.6 | 0.99791
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-9 | 50-WD-53007-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8148 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.625 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 5.6 | 5.6 | 0.05
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69003-01S01 | CML-6 | 80-OL-69003-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8084 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6 | CML-6 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 5.6 | 12 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6 | 6.5 | 5.9 | 0.37417
DO01 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62001-01C02 | CML-6 | 50-DO-62001-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8046 |  | 2015-01-21 07:30 | 2015-01-21 15:00 | [36 empty] | 5.8 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-21 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-DO-62001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.8 | 5.9 | 5.9 | 0.14142
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-11 | 50-PW-44040-01C02 CML-11 | yes | FPSO 2015 | Pipe Wall Thickness | 23246 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.3 | CML-11 | CML: Pipe Length | 3 | 2024-05-07 | 2025-07-09 | 2015-05-11 07:00 | 2.5 | 0.27788 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.26707 | 5.4 | 5.6 | 5.2 | 5 | 0.2582
PW03 | Montara_Topside | Yes | Steam (55) | Pipework | 200-PW-44018-01X01 | CML-15 | 200-PW-44018-01X01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8845 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 5.95 | CML-15 | CML: type TBC | 3 | 2031-04-17 | 2033-05-16 | 2015-02-24 07:00 | 2.5 | 0.16714 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.8 | 6 | 6.8 | 0.66081
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-11 | 200-PW-44018-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23283 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 6.15 | CML-11 | CML: Elbow | 3 | 2033-06-19 | 2035-10-20 | 2015-05-12 07:00 | 2.5 | 0.14902 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6.4 | 6.6 | 6.4 | 0.64031
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-14 | 50-PF-20301-03C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 3012 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.2 | CML-14 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.7 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 | 0 | 9.4 | 8.8 | 8.7 | 9.9 | 0.55976
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-14 | 50-PF-20301-03C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 22291 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.2 | CML-14 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.7 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 |  | 9.4 | 8.8 | 8.7 | 9.9 | 0.55976
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-14 | 50-PF-20300-03C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21580 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.3 | CML-14 | CML: type TBC | 6 | 2038-12-31 | 2038-07-04 | 2014-05-26 09:30 | 2.5 | 0.24374 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.8 | 9.5 | 9.4 | 8.5 | 0.55976
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56028-01C02 | CML-3 | 80-DH-56028-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20900 | Rope Access | 2014-05-22 07:00 | 2014-05-22 08:00 | [36 empty] | 5.5 | CML-3 | CML: Elbow | 3 | 2019-05-09 | 2020-01-16 | 2014-05-22 07:00 | 2.5 | 0.50339 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 3 O'Clock | 80 | 5.49 | 80-DH-56028-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5 | 6.3 | 5.3 | 0.55976
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-12 | 50-FG-45302-01C02 CML-12 | Yes | FPSO 2014 | Pipe Wall Thickness | 5780 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 6.1 | CML-12 | CML: Elbow | 3 | 2026-11-07 | 2028-04-17 | 2014-06-23 11:00 | 2.5 | 0.22609 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 25 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.6 | 5.3 | 6.3 | 6.2 | 0.55976
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-2 | 50-DH-56056-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20119 | Rope Access | 2014-05-07 07:00 | 2014-05-07 08:00 | [36 empty] | 6.2 | CML-2 | CML: type TBC | 3 | 2084-03-22 | 2091-10-27 | 2014-05-07 07:00 | 2.5 | 0.0429 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.6 | 6.7 | 6 | 5.5 | 0.55976
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-2 | 50-DH-56056-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3167 | Rope Access | 2014-05-07 07:00 | 2014-05-07 08:00 | [36 empty] | 6.2 | CML-2 | CML: type TBC | 3 | 2084-03-22 | 2091-10-27 | 2014-05-07 07:00 | 2.5 | 0.0429 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.6 | 6.7 | 6 | 5.5 | 0.55976
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-2 | 50-DH-56013-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1851 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 6.2 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 7 | 6.1 | 6 | 5.7 | 0.55976
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-2 | 50-DH-56013-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22331 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 6.2 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 7 | 6.1 | 6 | 5.7 | 0.55976
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38477-01C02-P | CML-5 | 50-CG-38477-01C02-P CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10388 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.3 | CML-5 | CML: type TBC | 3 | 2016-07-23 | 2016-07-14 | 2013-11-12 | 2.5 | 1.2241 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 25 | 6.35 | 25-CG-38494-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 5.8 | 5.8 | 6.5 | 5.9 | 7 | 0.55976
PW03 | Montara_Topside | Yes | Chemical Injection (42) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7481 | No pipe schedule on drawing | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 5.9 | CML-8 | CML: type TBC | 1 | 2030-02-03 | 2026-05-25 | 2015-04-13 07:00 | 2.5 | 0.18215 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-CI-42043-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.4 | 6.4 | 5.6 | 5.2 | 0.6
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56138-01C02 | CML-1 | 50-DH-56138-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22309 | Rope Access | 2014-05-06 14:00 | 2014-05-06 15:00 | [36 empty] | 8 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.7 | 7.6 | 7.5 | 8.2 | 0.55976
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-12 | 50-CG-38465-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20875 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 6.925 | CML-12 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 7 | 7.8 | 5.6 | 7.3 | 0.94296
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-2 | 250-PW-20039-01C03-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22966 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 10.2 | CML-2 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2015-05-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.5 | 6 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 0 | 10.5 | 10.6 | 9.5 | 10.2 | 0.49666
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-48 | 150-FL-43174-01C02 CML-48 |  | FPSO 2015 | Pipe Wall Thickness | 5533 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 4.25 | CML-48 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 6 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4.5 | 4.8 | 3.5 | 4.2 | 0.55678
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-10 | 150-WC-40006-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 9069 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.95 | CML-10 | CML: type TBC | 3 | 2051-05-15 | 2055-06-10 | 2015-03-01 09:30 | 2.5 | 0.08004 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.5 | 5.9 | 6 | 5.4 | 0.45092
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23746 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 17.75 | CML-6 | CML: Reducer | 3 | 2075-10-24 | 2059-08-12 | 2015-10-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 17.2 | 6 O'Clock | 100 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.7 |  | 18.5 | 17.8 | 17.2 | 17.5 | 0.55678
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-3 | 25-PW-44028-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22952 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 6.55 | CML-3 | CML: Elbow | 3 | 2034-07-04 | 2034-05-08 | 2015-05-02 07:00 | 2.5 | 0.18242 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 25 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | 0 | 6 | 6.3 | 7.3 | 6.6 | 0.55678
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-9 | 150-FL-43514-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20502 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.55 | CML-9 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.8 | 9 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.5 | 8.1 | 7.8 | 6.8 | 0.55678
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57301-01C02 | CML-2 | 50-DC-57301-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5662 | Rope access | 2014-06-21 13:00 | 2014-06-21 14:00 | [36 empty] | 6 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-21 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-DC-57301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 6.3 | 6.2 | 5.6 | 0.31623
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-13 | 400-FH-43508-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6562 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.35 | CML-13 | CML: Elbow | 3 | 2022-04-04 | 2021-02-02 | 2015-03-30 07:00 | 2.5 | 0.61263 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 6.8 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.1 | 6.8 | 8.1 | 7.4 | 0.55678
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-12 | 200-PW-44018-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23284 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 6.075 | CML-12 | CML: Elbow | 3 | 2033-06-19 | 2035-10-20 | 2015-05-12 07:00 | 2.5 | 0.14902 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.4 | 5.2 | 6.5 | 6.2 | 0.59652
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-11 | 80-DC-57005-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20257 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 5.775 | CML-11 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-06-02 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 9 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.8 | 6 | 5.6 | 0.17078
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38477-01C02-P | CML-7 | 50-CG-38477-01C02-P CML-7 | no | FPSO 2015 | Pipe Wall Thickness | 23410 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 18.225 | CML-7 | CML: Pipe Length | 3 | 2023-11-11 | 2022-05-15 | 2015-07-22 07:00 | 14.06 | 0.40177 | A1: Outside Quadrant |  | 15.26 | 14.06 | 14.66 | 17.4 | 12 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.34 | -0.17506 | 17.4 | 18.4 | 18.5 | 18.6 | 0.55603
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-18 | 100-FG-45304-03C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 22074 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.225 | CML-18 | CML: type TBC | 3 | 2021-08-20 | 2021-01-11 | 2014-05-25 07:00 | 2.5 | 0.42786 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.76 | 5.6 | 3 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 5.6 | 7.2 | 6.2 | 0.69462
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-13 | 100-FG-45304-03C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 22069 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 5.7 | CML-13 | CML: type TBC | 3 | 2021-08-20 | 2021-01-11 | 2014-05-25 07:00 | 2.5 | 0.42786 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.6 | 12 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.8 | 5.7 | 5.7 | 0.08165
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-10 | 300-PG-20506-03C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 13224 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 16.425 | CML-10 | CML: type TBC | 6 | 2107-02-11 | 2090-04-05 | 2014-02-04 15:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 15.6 | 9 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 16.8 | 16.7 | 16.6 | 15.6 | 0.55603
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-11 | 200-PG-23008-15S01-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 3227 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.775 | CML-11 | CML: type TBC | 3 | 2019-11-21 | 2020-08-01 | 2014-05-09 07:00 | 2.5 | 0.46919 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.6 | 6.4 | 6 | 5.1 | 0.55603
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-28 | 50-PF-20300-03C03-P CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 21594 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.375 | CML-28 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.9 | 9.6 | 9.4 | 8.6 | 0.55603
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-20 | 300-PG-20005-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 6176 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.375 | CML-20 | CML: Reducing Tee | 6 | 2031-08-28 | 2028-05-17 | 2014-07-11 07:30 | 4.9 | 0.51331 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 13.7 | 15 | 14.6 | 14.2 | 0.55603
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-20 | 80-PW-44016-01C02-P CML-20 | yes | FPSO 2014 | Pipe Wall Thickness | 21952 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.375 | CML-20 | CML: Elbow | 3 | 2021-09-15 | 2022-09-02 | 2014-10-10 07:00 | 2.5 | 0.36037 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.5 | 5.5 | 5.5 | 0.25
FG01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-FG-45024-01C02 | CML-1 | 50-FG-45024-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1277 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 9.575 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 9 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.3 | 10.4 | 9.4 | 9.2 | 0.55603
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-8 | 50-FG-45024-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23507 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 8.975 | CML-8 | CML: Tee | 3 | 2074-03-18 | 2063-04-04 | 2015-07-28 07:00 | 1.03 | 0 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 8.2 | 12 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.17 | 0.46286 | 8.2 | 9.5 | 9.2 | 9 | 0.55603
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-47 | 150-WC-40006-01C02 CML-47 |  | FPSO 2015 | Pipe Wall Thickness | 8971 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.9 | CML-47 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 6.2 | 6.3 | 5.4 | 0.42426
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-2 | 50-PL-23300-09C03 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13118 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 11.425 | CML-2 | CML: type TBC | 6 | 2046-06-12 | 2041-12-04 | 2014-02-04 07:00 | 2.81 | 0.24991 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.9 | 12 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.09 |  | 10.9 | 12 | 11 | 11.8 | 0.55603
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-11 | 300-PG-23002-03C03-A CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10107 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 16.975 | CML-11 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2013-11-07 | 5.22 | 0 | A4: Left Quadrant |  | 8.27 | 5.22 | 6.745 | 16.6 | 9 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.38 |  | 16.8 | 16.7 | 17.8 | 16.6 | 0.55603
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-19 | 50-DH-56137-01C02 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 23447 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 18.025 | CML-19 | CML: Pipe Length | 3 | 2022-12-25 | 2018-12-15 | 2015-07-23 07:00 | 2.5 | 1.9783 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 17.2 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.7 | -0.18401 | 18.3 | 18.4 | 18.2 | 17.2 | 0.55603
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38455-01C02-H | CML-3 | 50-CG-38455-01C02-H CML-3 | High Priority | FPSO 2015 | Pipe Wall Thickness | 23687 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.475 | CML-3 | CML: Elbow | 3 | 2023-04-30 | 2024-05-22 | 2015-10-30 07:00 | 2.5 | 0.30648 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 3 O'Clock | 50 | 5.54 | 50-CG-38455-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6.1 | 4.8 | 5.7 | 5.3 | 0.55603
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43171-01C02 | CML-4 | 80-FL-43171-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20526 |  | 2014-10-06 07:00 | 2014-10-06 15:00 | [36 empty] | 6.325 | CML-4 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 9 O'Clock | 80 | 5.49 | 80-FL-43171-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 7 | 6.1 | 5.7 | 0.55603
FG02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-FG-45455-01C02-E | CML-8 | 25-FG-45455-01C02-E CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5201 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 6.775 | CML-8 | CML: Reducing Tee | 3 | 2183-08-28 | 2189-04-11 | 2014-05-20 07:00 | 2.5 | 0.02066 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 6 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7 | 6.8 | 6 | 7.3 | 0.55603
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-10 | 80-FH-43151-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2244 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 7.325 | CML-10 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.7 | 3 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.1 | 6.7 | 7.5 | 8 | 0.55603
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-11 | 50-PW-44014-01X01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2013 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 6 | CML-11 | CML: Pipe Length | 3 | 2020-09-29 | 2021-07-13 | 2014-03-27 10:00 | 2.5 | 0.41447 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.9 | 6.5 | 5.2 | 6.4 | 0.59442
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-7 | 25-PG-23300-25C02 CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 20674 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 8.675 | CML-7 | CML: Elbow | 3 | 2019-04-10 | 2018-03-21 | 2014-05-27 09:30 | 4.4 | 0.80009 | A4: Left Quadrant |  | 6.09 | 4.4 | 5.245 | 8.3 | 9 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 8.4 | 9.5 | 8.5 | 8.3 | 0.55603
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-32 | 250-PW-44006-01X01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 8024 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 6.025 | CML-32 | CML: Pipe Length | 3 | 2018-11-25 | 2018-11-10 | 2015-01-20 08:30 | 2.5 | 0.70151 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.12164 | 6.4 | 6 | 5.2 | 6.5 | 0.5909
FL02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FL-43454-01C02-P | CML-6 | 50-FL-43454-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 23858 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.125 | CML-6 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A1: Outside Quadrant |  |  | 2.7 |  | 9.3 | 12 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.3 | 10.4 | 10.3 | 10.5 | 0.55603
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56561-01C02 | CML-10 | 100-DH-56561-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 7942 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 10.325 | CML-10 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-17 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 9.5 | 12 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.5 | 10.7 | 10.6 | 10.5 | 0.55603
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-7 | 200-PL-20018-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 23879 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 7.125 | CML-7 | CML: Elbow | 3 | 2047-04-22 | 2047-01-22 | 2014-09-26 07:00 | 2.5 | 0.11352 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.7 | 7.2 | 6.2 | 7.4 | 0.65
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-1 | 80-DH-56140-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21073 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 11.025 | CML-1 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 10.4 | 6 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.8 | 11.2 | 10.4 | 11.7 | 0.55603
PW03 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8086 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.05 | CML-8 | CML: type TBC | 1 | 2030-05-22 | 2026-09-09 | 2015-01-23 07:30 | 2.5 | 0.17603 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6.3 | 6.5 | 6.2 | 0.58023
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-18 | 200-PL-20008-01C02-H CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8815 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.25 | CML-18 | CML: Elbow | 3 | 2028-03-06 | 2028-01-27 | 2015-02-21 07:00 | 2.5 | 0.26059 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.1 | 6.8 | 5.9 | 0.3873
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23079 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.975 | CML-2 | CML: Elbow | 3 | 2077-07-26 | 2085-01-13 | 2015-05-07 07:00 | 2.5 | 0.04658 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 20 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 3.0268 | 6.1 | 5.4 | 6 | 6.4 | 0.41932
DH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-DH-56137-01C02 | CML-9 | 50-DH-56137-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12736 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 5.45 | CML-9 | CML: Elbow | 3 | 2015-04-16 | 2015-05-09 | 2014-01-24 09:00 | 2.5 | 1.8759 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 4.8 | 9 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.8 | 6 | 5.2 | 4.8 | 0.55076
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-5 | 50-DO-62002-01S01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2990 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.325 | CML-5 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.9 | 7.7 | 6.1 | 0.93941
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-5 | 50-DO-62002-01S01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22269 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.325 | CML-5 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.9 | 7.7 | 6.1 | 0.93941
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56033-01C02 | CML-1 | 80-DH-56033-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20914 | Rope Access | 2014-05-21 09:30 | 2014-05-21 11:00 | [36 empty] | 5.55 | CML-1 | CML: Elbow | 3 | 2019-05-03 | 2020-01-10 | 2014-05-21 09:30 | 2.5 | 0.50466 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-DH-56033-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.2 | 5.8 | 6.2 | 5 | 0.55076
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-6 | 150-FH-43157-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10662 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.9333 | CML-6 | CML: type TBC | 3 | 2016-06-08 | 2016-03-14 | 2013-11-18 | 2.5 | 1.5244 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.4 | 3 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  |  | 6.4 | 7.5 | 6.9 | 0.55076
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-8 | 50-FH-43016-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12607 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 7.0667 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-01-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 12 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7.1 | 7.6 |  | 0.55076
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-27 | 100-DC-57036-01C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 1433 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.494mm/ yr | [35 empty] | 6.15 | CML-27 | CML: type TBC | 3 | 2020-07-14 | 2020-10-08 | 2014-04-07 07:00 | 2.5 | 0.49405 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.7 | 5.8 | 6.5 | 0.53229
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-19 | 100-DC-57036-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1425 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.494mm/ yr | [35 empty] | 5.775 | CML-19 | CML: type TBC | 3 | 2020-07-14 | 2020-10-08 | 2014-04-07 07:00 | 2.5 | 0.49405 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.9 | 5.8 | 5.6 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-11 | 50-DC-57451-01C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1382 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 6 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 6.7 | 6 | 0.49666
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57067-01C02 | CML-3 | 50-DC-57067-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1340 | Rope access | 2014-04-04 08:00 | 2014-04-04 09:00 | [36 empty] | 5.825 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-04 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-DC-57067-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 6 | 6 | 0.20616
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57068-01C02 | CML-6 | 50-DC-57068-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1334 | Rope access | 2014-04-04 07:00 | 2014-04-04 08:00 | [36 empty] | 5.775 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-DC-57068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.1 | 5.6 | 5.7 | 5.7 | 0.22174
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-25 | 150-WC-40006-01C02 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 9016 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.8 | CML-25 | CML: type TBC | 3 | 2051-04-21 | 2055-05-15 | 2015-02-28 07:00 | 2.5 | 0.08018 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 6.2 | 5.4 | 5.5 | 0.40825
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56097-01C02 | CML-2 | 50-DN-56097-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1324 |  | 2014-04-01 07:00 | 2014-04-01 08:00 | [36 empty] | 5.675 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-DN-56097-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 5.7 | 5.7 | 0.05
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-7 | 200-PG-24001-09C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10263 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 17.825 | CML-7 | CML: Pipe Length | 3 | 2016-08-01 | 2015-07-11 | 2013-11-09 | 9.2 | 2.8565 | A4: Left Quadrant |  | 15.26 | 9.2 | 12.23 | 17 | 9 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 18.1 | 18.1 | 18.1 | 17 | 0.55
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-8 | 300-PF-20500-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21628 | Protective mesh removed | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.425 | CML-8 | CML: Fitting | 6 | 2035-03-02 | 2031-04-03 | 2014-09-27 07:00 | 4.9 | 0.43049 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 14.3 | 14.8 | 13.7 | 14.9 | 0.55
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23026-09C02-P | CML-3 | 150-PG-23026-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 24262 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 21.025 | CML-3 | CML: Equal Tee | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A2: Right Quadrant |  | 11.27 | 7 | 9.135 | 20.5 | 3 O'Clock | 150 | 14.27 | 150-PG-23026-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.5 |  | 20.9 | 20.5 | 20.9 | 21.8 | 0.55
PW03 | Montara_Topside | Yes | Potable Water (53) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8205 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.825 | CML-4 | CML: type TBC | 3 | 2028-03-08 | 2029-10-08 | 2015-01-25 07:30 | 2.5 | 0.2057 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-WD-53016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6.3 | 5.5 | 6.3 | 0.56199
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-8 | 50-DC-57025-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2119 |  | 2014-03-29 07:00 | 2014-03-29 08:00 | [36 empty] | 6.1 | CML-8 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-29 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.5 | 6.5 | 5.8 | 0.46904
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-4 | 150-PG-23043-06C02-P CML-4 | yes | FPSO 2016 | Pipe Wall Thickness | 23766 | re-check line | 2016-02-13 07:00 | 2016-02-13 15:00 | [35 empty] | Low alarm breach | 8.075 | CML-4 | CML: Elbow | 3 | 2018-10-05 | 2017-12-14 | 2016-02-13 07:00 | 4.7 | 1.1719 | A1: Outside Quadrant |  | 7.97 | 4.7 | 5.6494 | 7.8 | 6 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 0 | 7.8 | 7.8 | 7.8 | 8.9 | 0.55
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-4 | 150-PG-23043-06C02-P CML-4 | yes | FPSO 2016 | Pipe Wall Thickness | 24155 | re-check line | 2016-02-13 | 2016-02-13 | [35 empty] | Low alarm breach | 8.075 | CML-4 | CML: Elbow | 3 | 2018-10-05 | 2017-12-13 | 2016-02-13 | 4.7 | 1.1723 | A1: Outside Quadrant |  | 7.97 | 4.7 | 5.6494 | 7.8 | 6 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 1.7918 | 7.8 | 7.8 | 7.8 | 8.9 | 0.55
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-22 | 50-WC-40071-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 1957 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 5.65 | CML-22 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.8 | 5.6 | 5.6 | 0.1
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-19 | 50-WC-40071-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1954 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 5.75 | CML-19 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.9 | 5.6 | 5.7 | 0.1291
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-18 | 50-WC-40071-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1953 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 6.25 | CML-18 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.5 | 5.6 | 6.5 | 6.4 | 0.43589
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-11 | 50-WC-40071-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1946 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 5.7 | CML-11 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 5.7 | 5.6 | 5.6 | 0.14142
FL02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-FL-43454-01C02-P | CML-2 | 50-FL-43454-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23159 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 9.675 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 3 O'Clock | 250 | 6.35 | 250-DC-57065-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 1.7464 | 9.3 | 9.2 | 10.4 | 9.8 | 0.55
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-9 | 300-PG-20037-03C03-PA CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21384 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | Check Corrosion Rate of 0.529mm/ yr | [35 empty] | 14.475 | CML-9 | CML: Fitting | 6 | 2030-04-25 | 2027-07-15 | 2014-06-29 13:00 | 5.33 | 0.52866 | A3: Inside Quadrant |  | 8.27 | 5.33 | 6.8 | 13.7 | 6 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.37 |  | 14.6 | 15 | 13.7 | 14.6 | 0.55
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-25 | 300-PG-20005-03C03-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 6181 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.325 | CML-25 | CML: Elbow | 6 | 2028-12-07 | 2026-02-21 | 2014-07-11 07:30 | 4.9 | 0.60336 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14.7 | 14.8 | 13.6 | 14.2 | 0.55
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43074-01C02 | CML-5 | 50-FL-43074-01C02 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 1790 | Rope access | 2014-04-28 09:30 | 2014-04-28 10:30 | [36 empty] | 5.175 | CML-5 | CML: Elbow | 3 | 2016-09-12 | 2017-01-19 | 2014-04-28 09:30 | 2.5 | 0.92518 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-FL-43074-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 4.8 | 5.3 | 5.9 | 0.55
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23028-25C02-P | CML-2 | 100-PG-23028-25C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 441 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 17.275 | CML-2 | CML: Elbow | 3 | 2023-02-09 | 2020-02-23 | 2014-03-12 09:00 | 9.4 | 0.79578 | A3: Inside Quadrant |  | 14.12 | 9.4 | 11.76 | 16.5 | 6 O'Clock | 100 | 17.12 | 100-PG-23028-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 17.8 | 17.4 | 16.5 | 17.4 | 0.55
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-6 | 50-DC-57020-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2448 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 5.875 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 6.3 | 6 | 0.34034
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-21 | 100-DC-57075-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 2440 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.524mm/ yr | [35 empty] | 5.775 | CML-21 | CML: type TBC | 3 | 2020-02-14 | 2020-05-05 | 2014-03-20 07:00 | 2.5 | 0.52448 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 12 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.7 | 6.1 | 5.7 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-14 | 100-DC-57075-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2433 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.524mm/ yr | [35 empty] | 5.875 | CML-14 | CML: type TBC | 3 | 2020-02-14 | 2020-05-05 | 2014-03-20 07:00 | 2.5 | 0.52448 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 3 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6 | 5.6 | 5.9 | 6 | 0.1893
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-13 | 100-DC-57075-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2432 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.524mm/ yr | [35 empty] | 5.875 | CML-13 | CML: type TBC | 3 | 2020-02-14 | 2020-05-05 | 2014-03-20 07:00 | 2.5 | 0.52448 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 9 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 6.5 | 5.7 | 5.6 | 0.41932
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-7 | 100-DC-57075-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2426 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.524mm/ yr | [35 empty] | 5.75 | CML-7 | CML: type TBC | 3 | 2020-02-14 | 2020-05-05 | 2014-03-20 07:00 | 2.5 | 0.52448 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.6 | 6 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 5.8 | 5.6 | 5.8 | 0.1
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-9 | 300-PG-20037-03C03-PA CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23343 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.175 | CML-9 | CML: Fitting | 6 | 2046-11-17 | 2041-05-17 | 2015-07-20 07:00 | 5.33 | 0.26697 | A1: Outside Quadrant |  | 8.27 | 5.33 | 6.8 | 13.7 | 6 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.37 | 0 | 13.7 | 14.7 | 13.7 | 14.6 | 0.55
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-17 | 50-DH-56137-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 5685 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | [35 empty] | Low alarm breach | 18.075 | CML-17 | CML: Elbow | 3 | 2018-08-15 | 2016-06-06 | 2014-06-21 14:00 | 2.5 | 3.635 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 17.6 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.1 |  | 18.8 | 17.7 | 18.2 | 17.6 | 0.55
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-11 | 200-PW-44018-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8907 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.675 | CML-11 | CML: type TBC | 3 | 2028-12-12 | 2030-08-13 | 2015-02-25 13:00 | 2.5 | 0.19557 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6.2 | 6.1 | 5.2 | 0.55
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-9 | 150-FH-43026-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23508 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 6.975 | CML-9 | CML: Pipe Length | 3 | 2027-10-26 | 2025-03-22 | 2015-07-28 07:00 | 1.03 | 0.42189 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.2 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.17 | 0.59511 | 7.5 | 7.1 | 6.2 | 7.1 | 0.55
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20015-01C02-P | CML-3 | 200-PL-20015-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21228 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 6.925 | CML-3 | CML: Fitting | 3 | 2042-02-09 | 2041-11-24 | 2014-07-14 07:30 | 2.5 | 0.13409 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 40 | 6.35 | 200-PL-20015-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.2 | 7.5 | 6.2 | 6.8 | 0.56199
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23033-03C03 | CML-4 | 50-PL-23033-03C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1876 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.725 | CML-4 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 6 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10 | 10 | 8.9 | 10 | 0.55
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-19 | 50-PF-20301-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 3017 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.175 | CML-19 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8.4 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.79 | 0 | 9.7 | 9.3 | 9.3 | 8.4 | 0.55
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-19 | 50-PF-20301-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 22296 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.175 | CML-19 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8.4 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.79 |  | 9.7 | 9.3 | 9.3 | 8.4 | 0.55
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-8 | 150-WC-40006-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8553 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.8 | CML-8 | CML: type TBC | 3 | 2049-11-16 | 2053-10-15 | 2015-02-04 07:30 | 2.5 | 0.08332 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.6 | 6.3 | 5.9 | 0.39158
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-26 | 300-PW-44003-01C03 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 22891 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.075 | CML-26 | CML: Pipe Length | 6 | 2031-11-16 | 2029-09-26 | 2015-05-01 07:00 | 2.5 | 0.42278 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 0.18814 | 10.2 | 9.5 | 10.2 | 10.4 | 0.39476
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-9 | 200-FH-43114-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12817 |  | 2014-02-01 12:00 | 2014-02-01 14:00 | [36 empty] | 9.725 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 12:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9 | 9 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 10.2 | 10.1 | 9.6 | 9 | 0.55
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45030-03C03 | CML-3 | 50-PL-45030-03C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10466 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.675 | CML-3 | CML: type TBC | 6 | 2017-08-01 | 2017-02-10 | 2013-11-13 | 0.99 | 1.8582 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.9 | 12 O'Clock | 50 | 8.74 | 50-PL-45030-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.91 |  | 7.9 | 8.8 | 8.8 | 9.2 | 0.55
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-17 | 250-PG-23003-06C02-PA CML-17 | Yes | FPSO 2014 | Pipe Wall Thickness | 24255 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.475 | CML-17 | CML: Elbow | 3 | 2118-06-20 | 2101-08-21 | 2014-09-24 07:00 | 7.9 | 0.0684 | A4: Left Quadrant |  | 12.09 | 7.9 | 9.0519 | 15 | 9 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 16.2 | 15.6 | 15.1 | 15 | 0.55
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-1 | 50-FG-45021-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2613 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 9.7 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-04-26 10:45 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 9 | 3 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | -0.90432 | 10.3 | 9 | 9.9 | 9.6 | 0.54772
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-18 | 300-PG-20506-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 13232 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.3 | CML-18 | CML: type TBC | 6 | 2024-08-09 | 2022-08-05 | 2014-02-04 15:00 | 4.9 | 0.8368 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 6 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 15 | 14.1 | 13.7 | 14.4 | 0.54772
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56025-01C02 | CML-3 | 80-DH-56025-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3487 | Rope Access | 2014-05-14 11:00 | 2014-05-14 12:00 | [36 empty] | 5.6 | CML-3 | CML: type TBC | 3 | 2017-07-15 | 2018-01-06 | 2014-05-14 11:00 | 2.5 | 0.72484 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 12 O'Clock | 80 | 5.49 | 80-DH-56025-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 6 | 5.7 | 5.9 | 0.54772
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8994 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.625 | CML-3 | CML: type TBC | 3 | 2051-04-21 | 2055-05-15 | 2015-02-28 07:00 | 2.5 | 0.08018 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 6.2 | 5.4 | 0.38622
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40509-1CG | CML-2 | 150-WC-40509-1CG CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8700 | Material Class Not Selectable.Line is FFS. Action: to recheck in two year(Feb. 2017) to confirm CR | 2015-02-13 14:00 | 2015-02-13 15:00 | Check Corrosion Rate of 0.745mm/ yr | 36 | Administrator | 2015-09-08 11:51 | [32 empty] | 10.2 | CML-2 | CML: Elbow | 3 | 2024-10-13 | 2021-02-10 | 2015-02-13 14:00 | 2.5 | 0.74456 | A1: Outside Quadrant |  | 7.97 | 2.5 | 5.235 | 9.7 | 12 O'Clock | 150 | 10.97 | 150-WC-40509-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 9.9 | 10.8 | 10.4 | 0.49666
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1852 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 6 | CML-3 | CML: type TBC | 3 | 2033-08-03 | 2035-10-03 | 2014-05-06 08:00 | 2.5 | 0.15059 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.7 | 5.8 | 5.4 | 6.1 | 0.54772
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-17 | 50-DH-56137-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21101 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6 | CML-17 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5.6 | 3 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.8 | 5.6 | 5.9 | 5.7 | 0.54772
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-9 | 25-FG-45455-01C02-E CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21260 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.6 | CML-9 | CML: Fitting | 3 | 2028-01-23 | 2027-12-15 | 2014-09-30 07:00 | 2.5 | 0.2627 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 7.3 | 6 | 6.7 | 0.54772
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-14 | 200-FH-43025-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2487 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 7.2 | CML-14 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7.8 | 7.4 | 7.1 | 0.54772
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43035-01C02 | CML-1 | 100-FH-43035-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12660 |  | 2014-01-22 10:00 | 2014-01-22 11:00 | [36 empty] | 5.9 | CML-1 | CML: type TBC | 3 | 2016-03-07 | 2016-04-09 | 2014-01-22 10:00 | 2.5 | 1.2714 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 6 O'Clock | 100 | 6.02 | 100-FH-43035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.5 | 5.8 | 5.2 | 6.1 | 0.54772
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-1 | 80-PW-44016-01C02-P CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 22903 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.325 | CML-1 | CML: Elbow | 3 | 2025-02-11 | 2026-06-23 | 2015-05-02 07:00 | 2.5 | 0.25539 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.17892 | 5.4 | 5.5 | 5 | 5.4 | 0.22174
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2971 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 6 | CML-6 | CML: Elbow | 3 | 2029-01-18 | 2027-01-20 | 2014-05-01 14:00 | 0.54 | 0.31636 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 | 0 | 6.3 | 5.2 | 6.1 | 6.4 | 0.54772
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22250 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 6 | CML-6 | CML: Elbow | 3 | 2029-01-18 | 2027-01-20 | 2014-05-01 14:00 | 0.54 | 0.31636 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 6.3 | 5.2 | 6.1 | 6.4 | 0.54772
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-1 | 400-FH-43508-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6550 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.2 | CML-1 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 8.4 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.6 | 8.4 | 9.3 | 9.5 | 0.54772
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-5 | 50-CG-38487-09C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20844 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.8 | CML-5 | CML: Elbow | 3 | 2037-12-13 | 2031-08-01 | 2014-10-02 07:00 | 2.5 | 0.25415 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 1.444 | 9.6 | 8.5 | 8.4 | 8.7 | 0.54772
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-29 | 300-FL-43070-01C02 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 12722 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 9.6 | CML-29 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9 | 9 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.3 | 10.2 | 9.9 | 9 | 0.54772
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20302-03C03-P | CML-3 | 200-PG-20302-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5856 | Rope Access | 2014-06-25 10:30 | 2014-06-25 12:00 | [36 empty] | 12.4 | CML-3 | CML: Elbow | 6 | 2024-07-20 | 2022-07-15 | 2014-06-25 10:30 | 3.3 | 0.84352 | A2: Right Quadrant |  | 6.7 | 3.3 | 5 | 11.8 | 3 O'Clock | 200 | 12.7 | 200-PG-20302-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 12.5 | 11.8 | 12.2 | 13.1 | 0.54772
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-24 | 300-PW-44003-01C03 CML-24 | yes | FPSO 2014 | Pipe Wall Thickness | 21866 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 17:08 | [32 empty] | 10 | CML-24 | CML: Elbow | 6 | 2026-10-03 | 2025-03-17 | 2014-10-19 07:00 | 2.5 | 0.58511 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.4 | 9.5 | 10.1 | 10 | 0.37417
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20026-03C03-P | CML-2 | 80-PG-20026-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21666 | Protective mesh removed | 2014-06-26 08:00 | 2014-06-26 09:00 | [36 empty] | 11.5 | CML-2 | CML: Elbow | 6 | 2041-05-12 | 2037-02-07 | 2014-06-26 08:00 | 2.5 | 0.30858 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.8 | 12 O'Clock | 80 | 11.13 | 80-PG-20026-03C03-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 11.4 | 11.7 | 12.1 | 0.54772
DH01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-DH-56137-01C02 | CML-16 | 50-DH-56137-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23060 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 18.4 | CML-16 | CML: Reducing Tee | 6 | 2099-09-17 | 2086-07-24 | 2015-05-06 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 17.6 | 9 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.1 |  | 18.7 | 18.8 | 18.5 | 17.6 | 0.54772
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-7 | 80-PW-44035-01C02-P CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 21930 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 5.25 | CML-7 | CML: Elbow | 3 | 2021-09-09 | 2022-08-27 | 2014-10-09 07:00 | 2.5 | 0.3611 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5.3 | 5.2 | 5 | 0.20817
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-1 | 50-PF-20301-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2999 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.35 | CML-1 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.7 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 | 0 | 8.7 | 9.5 | 10 | 9.2 | 0.54467
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-1 | 50-PF-20301-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22278 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.35 | CML-1 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.7 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 |  | 8.7 | 9.5 | 10 | 9.2 | 0.54467
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20068-01C02-P | CML-1 | 100-PL-20068-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21549 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.55 | CML-1 | CML: Fitting | 3 | 2048-08-12 | 2049-10-10 | 2014-07-17 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 6 O'Clock | 100 | 6.02 | 100-PL-20068-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.9 | 6.2 | 6.8 | 0.35119
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38457-01C02-P | CML-6 | 50-CG-38457-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23724 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.85 | CML-6 | CML: Equal Tee | 3 | 2030-01-31 | 2031-11-16 | 2015-10-30 07:00 | 2.5 | 0.18223 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-CG-38457-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.8 | 6.3 | 5.1 | 6.2 | 0.54467
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56030-01C02 | CML-2 | 80-DH-56030-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20911 | Rope Access | 2014-05-22 08:00 | 2014-05-22 09:00 | [36 empty] | 5.95 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-22 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 3 O'Clock | 80 | 5.49 | 80-DH-56030-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.7 | 5.5 | 5.6 | 6 | 0.54467
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20017-01C02-P | CML-3 | 200-PL-20017-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21242 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 6.65 | CML-3 | CML: Fitting | 3 | 2042-02-09 | 2041-11-24 | 2014-07-14 07:30 | 2.5 | 0.13409 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-PL-20017-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7 | 6.8 | 6.2 | 6.6 | 0.34157
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44007-01X01 | CML-1 | 250-PW-44007-01X01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1958 | Rope Access | 2014-03-26 11:30 | 2014-03-26 10:30 | [36 empty] | 6 | CML-1 | CML: Pipe Length | 3 | 2016-02-25 | 2016-02-17 | 2014-03-26 11:30 | 2.5 | 1.4063 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 9 O'Clock | 250 | 6.35 | 250-PW-44007-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.2 | 6.4 | 6.2 | 5.2 | 0.5416
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8607 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.825 | CML-2 | CML: type TBC | 3 | 2050-03-05 | 2054-02-13 | 2015-02-09 07:30 | 2.5 | 0.08264 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 6.2 | 5.6 | 5.4 | 0.38622
PG02 | Montara_Topside | No | Separation (20) | Pipework | 300-PG-20025-03D01-P | CML-3 | 300-PG-20025-03D01-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22798 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 7.1 | CML-3 | CML: Elbow | 1 | 2038-04-25 | 2030-11-12 | 2015-04-29 07:00 | 3.86 | 0 | A4: Left Quadrant |  | 5.35 | 3.86 | 4.605 | 7 | 9 O'Clock | 300 | 6.35 | 300-PG-20025-03D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 | -0.23856 | 7.1 | 7.1 | 7.2 | 7 | 0.08165
PG02 | Montara_Topside | No | Separation (20) | Pipework | 300-PG-20025-03D01-P | CML-1 | 300-PG-20025-03D01-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21321 | Protective mesh removed | 2014-06-27 07:00 | 2014-06-27 08:00 | [36 empty] | 7.275 | CML-1 | CML: Reducer | 1 | 2038-04-25 | 2030-11-12 | 2014-06-27 07:00 | 3.86 | 0 | A4: Left Quadrant |  | 5.35 | 3.86 | 4.605 | 7 | 9 O'Clock | 300 | 6.35 | 300-PG-20025-03D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.14 |  | 7.2 | 7.8 | 7.1 | 7 | 0.3594
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-3 | 80-CG-38459-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 24259 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 19.75 | CML-3 | CML: Reducer | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A3: Inside Quadrant |  | 11.27 | 7 | 9.135 | 19 | 6 O'Clock | 150 | 14.27 | 150-PG-23047-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12 |  | 19.7 | 20.1 | 19 | 20.2 | 0.54467
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43036-01C02 | CML-2 | 100-FH-43036-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12666 |  | 2014-01-26 10:00 | 2014-01-26 11:00 | [36 empty] | 5.75 | CML-2 | CML: type TBC | 3 | 2016-08-14 | 2016-09-22 | 2014-01-26 10:00 | 2.5 | 1.0977 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 3 O'Clock | 100 | 6.02 | 100-FH-43036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.5 | 5.3 | 5.8 | 5.4 | 0.54467
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-8 | 150-WC-40006-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8766 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.925 | CML-8 | CML: type TBC | 3 | 2050-07-15 | 2054-07-09 | 2015-02-15 09:30 | 2.5 | 0.08184 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 6.3 | 5.9 | 5.4 | 0.38622
FG02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5624 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 6.75 | CML-5 | CML: Elbow | 3 | 2024-12-29 | 2024-11-29 | 2014-06-20 13:00 | 2.5 | 0.33221 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.8 | 7.3 | 6 | 6.9 | 0.54467
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-5 | 50-FL-43454-01C02-P CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 20508 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 6.55 | CML-5 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.3 | 6.4 | 6 | 6.5 | 0.54467
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1824 |  | 2014-04-29 14:00 | 2014-04-29 14:30 | [36 empty] | 7.85 | CML-4 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-04-29 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 12 O'Clock | 50 | 5.54 | 50-DH-56122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.7 | 8.5 | 8 | 0.54467
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56068-01C02 | CML-1 | 50-DH-56068-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3351 | Rope Access | 2014-05-08 14:00 | 2014-05-08 14:30 | [36 empty] | 5.45 | CML-1 | CML: type TBC | 3 | 2018-09-05 | 2019-03-31 | 2014-05-08 14:00 | 2.5 | 0.57702 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DH-56068-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.7 | 6.1 | 5 | 0.54467
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56106-01C02 | CML-1 | 80-DH-56106-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2027 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 7.95 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-27 14:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.5 | 12 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8 | 7.6 | 8.7 | 0.54467
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-22 | 100-FG-45001-09C02 CML-22 | Yes | FPSO 2015 | Pipe Wall Thickness | 23327 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.25 | CML-22 | CML: type TBC | 3 | 2034-12-09 | 2029-03-13 | 2015-07-11 07:00 | 4.7 | 0.29852 | A3: Inside Quadrant |  | 8.13 | 4.7 | 6.415 | 10.5 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | -0.42211 | 11.7 | 11.2 | 10.5 | 11.6 | 0.54467
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-11 | 100-PG-23503-03C03-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5513 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 11.15 | CML-11 | CML: Pipe Length | 6 | 2020-11-28 | 2021-04-09 | 2014-06-01 07:00 | 5.66 | 0.72942 | A3: Inside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.4 | 6 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.74 | 0.45673 | 11.2 | 11.3 | 10.4 | 11.7 | 0.54467
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-36 | 300-PF-20001-03C03-P CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 21174 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.418mm/ yr | 40 | Kirstie Albone | 2017-03-23 16:07 | [32 empty] | 14.35 | CML-36 | CML: Fitting | 6 | 2035-10-24 | 2031-10-14 | 2014-07-16 07:30 | 4.9 | 0.4181 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 13.8 | 14.3 | 15.1 | 14.2 | 0.54467
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20015-01C02-P | CML-2 | 200-PL-20015-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21227 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 6.625 | CML-2 | CML: Fitting | 3 | 2042-02-09 | 2041-11-24 | 2014-07-14 07:30 | 2.5 | 0.13409 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 200 | 6.35 | 200-PL-20015-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.9 | 6.9 | 6.2 | 0.34034
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-28 | 300-PG-20005-03C03-P CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 22790 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 8.95 | CML-28 | CML: Elbow | 6 | 2017-03-06 | 2016-04-03 | 2015-04-29 07:00 | 2.5 | 3.125 | A2: Right Quadrant |  | 8.27 | 2.5 | 5.385 | 8.3 | 3 O'Clock | 50 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | 0.37503 | 9.1 | 8.3 | 8.8 | 9.6 | 0.54467
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23034-01C03 | CML-4 | 50-PL-23034-01C03 CML-4 | no | FPSO 2014 | Pipe Wall Thickness | 20572 | Reviewed on 26/11/14.FFS. Repeat Oct.19 | 2014-10-12 07:00 | 2014-10-12 12:00 |  |  | Nestor | 2014-11-26 16:19 | [32 empty] | 9.05 | CML-4 | CML: Elbow | 6 | 2032-10-05 | 2032-05-22 | 2014-10-12 07:00 | 2.5 | 0.3223 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 6 O'Clock | 50 | 8.74 | 50-PL-23034-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.1 | 9.6 | 8.3 | 9.2 | 0.54467
FG03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 80-FG-45045-06S01-E | CML-5 | 80-FG-45045-06S01-E CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24406 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.975 | CML-5 | CML: Elbow | 1 | 2043-01-05 | 2033-03-19 | 2016-06-08 07:00 | 2.53 | 0 | A1: Outside Quadrant |  | 4.49 | 2.53 | 3.51 | 5.7 | 12 O'Clock | 80 | 5.49 | 80-FG-45045-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.17 |  | 5.7 | 6.1 | 6.3 | 5.8 | 0.27538
FG03 | Montara_Topside | No | Fuel Gas (45) | Pipework | 80-FG-45045-06S01-E | CML-1 | 80-FG-45045-06S01-E CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24402 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.95 | CML-1 | CML: Elbow | 1 | 2043-01-05 | 2033-03-19 | 2016-06-08 07:00 | 2.53 | 0 | A2: Right Quadrant |  | 4.49 | 2.53 | 3.51 | 5.7 | 3 O'Clock | 80 | 5.49 | 80-FG-45045-06S01-E | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.17 |  | 6.2 | 5.7 | 5.9 | 6 | 0.20817
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-1 | 300-PW-44003-01C03 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22866 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.8 | CML-1 | CML: Elbow | 6 | 2031-11-16 | 2029-09-26 | 2015-05-01 07:00 | 2.5 | 0.42278 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | -0.37629 | 9.5 | 10 | 9.5 | 10.2 | 0.3559
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-27 | 300-PG-20005-03C03-P CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 6183 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 9.55 | CML-27 | CML: Elbow | 6 | 2015-11-06 | 2015-04-02 | 2014-07-11 07:30 | 2.5 | 4.8359 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.9 | 9 O'Clock | 50 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10.2 | 9.7 | 9.4 | 8.9 | 0.54467
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-4 | 50-DH-56137-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5482 | Rope Access | 2014-05-28 11:30 | 2014-05-28 14:00 | [36 empty] | 17.95 | CML-4 | CML: Fitting | 3 | 2163-03-18 |  | 2014-05-28 11:30 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 17.5 | 3 O'Clock | 300 | 17.48 | 300-WC-40513-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15 |  | 18.7 | 17.5 | 18 | 17.6 | 0.54467
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-1 | 80-CG-38459-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21385 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 17.675 | CML-1 | CML: Reducer | 6 | 2091-05-30 | 2082-05-30 | 2014-07-12 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 6.7 | 4.9 | 5.8 | 16.9 | 6 O'Clock | 300 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12 |  | 18.1 | 18 | 16.9 | 17.7 | 0.54391
FL02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-FL-43454-01C02-P | CML-2 | 50-FL-43454-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21128 | Reviewed on 20/11/14. FFS. Recheck in Oct. 19. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-20 17:39 | [32 empty] | 9.525 | CML-2 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-08 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56556-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.5 | 9.2 | 10.3 | 9.1 | 0.54391
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40500-1CG | CML-23 | 400-WC-40500-1CG CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 5691 | Material class 1CG | 2014-06-21 14:00 | 2014-06-21 16:00 | Check Corrosion Rate of 7.175mm/ yr | [34 empty] | Medium alarm breach | 11.075 | CML-23 | CML: Pipe Length | 3 | 2015-02-23 | 2014-06-02 | 2014-06-21 14:00 | 2.5 | 10.924 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 9.9 | 9 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 11.1 | 12 | 11.3 | 9.9 | 0.87321
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-3 | 100-PG-23071-01C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2401 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 12.275 | CML-3 | CML: type TBC | 6 | 2098-02-09 | 2085-10-05 | 2014-03-19 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.7 | 12 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 11.7 | 12.1 | 13 | 12.3 | 0.54391
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-24 | 150-PG-23506-25C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 2798 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.525 | CML-24 | CML: Pipe Length | 3 | 2045-04-03 | 2037-03-15 | 2014-03-15 09:00 | 15.88 | 0.19052 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.8 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.92 |  | 22.5 | 23.1 | 21.8 | 22.7 | 0.54391
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20002-03C03-P | CML-7 | 300-PF-20002-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 6519 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:11 | [32 empty] | 17.725 | CML-7 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-24 07:30 | 4.9 | 0 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 17 | 3 O'Clock | 300 | 14.27 | 300-PF-20002-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.1 |  | 18.3 | 17 | 17.7 | 17.9 | 0.54391
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-3 | 50-CG-38454-01C02-H CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 23667 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.475 | CML-3 | CML: Equal Tee | 3 | 2024-11-16 | 2026-02-08 | 2015-10-30 07:00 | 2.5 | 0.26507 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 6.2 | 5.3 | 5.5 | 0.54391
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-12 | 80-PW-44016-01C02-P CML-12 | yes | FPSO 2014 | Pipe Wall Thickness | 21944 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.275 | CML-12 | CML: Elbow | 3 | 2021-09-15 | 2022-09-02 | 2014-10-10 07:00 | 2.5 | 0.36037 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.3 | 5.4 | 0.1893
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-5 | 50-DC-57025-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22939 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 6.15 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | -0.54887 | 5.7 | 6.2 | 6.6 | 6.1 | 0.36968
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-1 | 50-DC-57025-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22935 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 18.075 | CML-1 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | -0.54887 | 5.7 | 55 | 5.9 | 5.7 | 24.6168
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-2 | 50-DC-57013-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22926 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.9 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-02 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | -0.64094 | 5.8 | 5.7 | 6.1 | 6 | 0.18257
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-44 | 200-PL-20019-01C02 CML-44 |  | FPSO 2014 | Pipe Wall Thickness | 21295 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.425 | CML-44 | CML: Pipe Length | 3 | 2047-08-03 | 2047-05-04 | 2014-09-30 07:00 | 2.5 | 0.11259 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.9 | 6.2 | 6.2 | 6.4 | 0.3304
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2117 |  | 2014-03-29 07:00 | 2014-03-29 08:00 | [36 empty] | 5.975 | CML-6 | CML: Elbow | 3 | 2031-04-30 | 2033-04-01 | 2014-03-29 07:00 | 2.5 | 0.1696 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.7 | 6 | 5.4 | 5.8 | 0.54391
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-17 | 200-PL-20019-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21268 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.575 | CML-17 | CML: Pipe Length | 3 | 2047-08-03 | 2047-05-04 | 2014-09-30 07:00 | 2.5 | 0.11259 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 7 | 6.2 | 6.5 | 0.3304
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-4 | 300-FL-43080-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2383 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 6.975 | CML-4 | CML: type TBC | 3 | 2033-11-19 | 2033-09-25 | 2014-03-19 07:00 | 2.5 | 0.18796 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.4 | 7 | 6.2 | 7.3 | 0.54391
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67300-01E01 | CML-1 | 25-GN-67300-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22485 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.8 | CML-1 | CML: Elbow | 3 | 2024-07-29 | 2024-06-30 | 2015-04-20 07:00 | 2.5 | 0.34469 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 3 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.7 | 5.9 | 5.8 | 0.08165
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-9 | 150-WC-40006-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8767 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.725 | CML-9 | CML: type TBC | 3 | 2050-07-15 | 2054-07-09 | 2015-02-15 09:30 | 2.5 | 0.08184 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.1 | 6 | 5.4 | 0.37749
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 200-WF-71306-01K01 | CML-1 | 200-WF-71306-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5187 | Pipe Schedule Estimated. Rope Access | 2015-03-12 07:00 | 2015-03-12 15:00 | [36 empty] | 6.45 | CML-1 | CML: type TBC | 0.5 | 2025-05-31 | 2021-11-30 | 2015-03-12 07:00 | 2.8 | 0 | A4: Left Quadrant |  | 3.5 | 2.8 | 3.15 | 6 | 9 O'Clock | 200 | 4 | 200-WF-71306-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.3 | 6.8 | 6.7 | 6 | 0.36968
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71315-01K01 | CML-3 | 150-WF-71315-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5132 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 5.75 | CML-3 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 5.7 | 9 O'Clock | 150 | 3 | 150-WF-71315-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 5.8 | 5.7 | 0.057735
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-4 | 50-AU-63015-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 9035 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.9 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 5.7 | 5.9 | 6 | 0.14142
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-24 | 50-AU-63018-01E01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 8920 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.975 | CML-24 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.2 | 6.1 | 5.9 | 5.7 | 0.22174
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-16 | 50-AU-63018-01E01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8912 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.75 | CML-16 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 5.7 | 5.8 | 0.057735
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-18 | 50-PF-20301-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 3016 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.325 | CML-18 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.9 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.29 | 0 | 10.1 | 9.3 | 8.9 | 9 | 0.54391
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-18 | 50-PF-20301-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 22295 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.325 | CML-18 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.9 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.29 |  | 10.1 | 9.3 | 8.9 | 9 | 0.54391
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-4 | 300-PW-44003-01C03 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22869 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 9.8 | CML-4 | CML: Elbow | 6 | 2031-11-16 | 2029-09-26 | 2015-05-01 07:00 | 2.5 | 0.42278 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.5 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 0.37629 | 10.1 | 9.5 | 9.9 | 9.7 | 0.2582
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-11 | 50-GN-67006-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8756 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 6.025 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.1 | 6.2 | 6.1 | 5.7 | 0.22174
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67001-01E01 | CML-4 | 50-GN-67001-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8549 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.1 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.2 | 5.7 | 6.3 | 6.2 | 0.2708
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67001-01E01 | CML-1 | 50-GN-67001-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8546 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.1 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.5 | 6.4 | 5.8 | 0.40825
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63020-01E01 | CML-1 | 50-AU-63020-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8481 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.125 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-AU-63020-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.4 | 5.7 | 6.1 | 6.3 | 0.30957
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-12 | 50-AI-63012-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8462 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.8 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.9 | 5.7 | 5.8 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-10 | 50-AI-63012-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8460 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.9 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 6.1 | 5.7 | 5.8 | 0.18257
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-1 | 50-AI-63012-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8451 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.825 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.9 | 5.9 | 5.7 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63021-01E01 | CML-4 | 50-AU-63021-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8446 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.775 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-AU-63021-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.7 | 5.8 | 5.9 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40406-01C02 | CML-5 | 50-WC-40406-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8437 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 5.975 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-WC-40406-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.9 | 6.5 | 5.8 | 0.3594
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63016-01E01 | CML-3 | 50-AU-63016-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8407 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.025 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-AU-63016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.4 | 5.7 | 6.3 | 5.7 | 0.37749
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23411-03C02-P | CML-7 | 50-PG-23411-03C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8391 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.075 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2015-01-30 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.8 | 5.7 | 7 | 0.61847
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23411-03C02-P | CML-4 | 50-PG-23411-03C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8388 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.075 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 5.9 | 6.4 | 0.3304
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23408-01C02-P | CML-3 | 50-PG-23408-01C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8381 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 6.025 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-PG-23408-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6 | 6.2 | 6.2 | 0.23629
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23408-01C02-P | CML-2 | 50-PG-23408-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8380 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 6.025 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-PG-23408-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 5.9 | 6.2 | 0.27538
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63030-01E01 | CML-9 | 50-AI-63030-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8350 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.925 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-AI-63030-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 5.7 | 6.5 | 0.38622
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63030-01E01 | CML-7 | 50-AI-63030-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8348 |  | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.775 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-AI-63030-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.9 | 5.7 | 5.7 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63011-01E01 | CML-4 | 50-AI-63011-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8341 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.3 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-AI-63011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.6 | 6.4 | 5.7 | 6.5 | 0.40825
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-14 | 50-AI-63450-01E01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8333 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.775 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.8 | 5.8 | 5.7 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-10 | 50-AI-63450-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8329 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.125 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.4 | 5.7 | 6.4 | 6 | 0.34034
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-9 | 50-AI-63450-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8328 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.95 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.4 | 5.8 | 5.9 | 0.31091
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-6 | 50-AI-63450-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8325 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.025 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 6.8 | 5.7 | 5.7 | 0.5252
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63001-01E01 | CML-6 | 50-AI-63001-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8313 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.475 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-AI-63001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.8 | 6.9 | 6.5 | 5.7 | 0.54391
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63013-01E01 | CML-2 | 50-AI-63013-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8301 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.3 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-AI-63013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6 | 6.8 | 6.7 | 0.53541
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53003-01E01 | CML-5 | 50-WD-53003-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8295 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.3 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-WD-53003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.4 | 6.4 | 6.7 | 5.7 | 0.42426
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-3 | 50-WD-53011-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8279 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.125 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.7 | 6.6 | 6.5 | 0.49244
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-30 | 50-WD-53010-01E01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 8273 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.95 | CML-30 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.6 | 5.8 | 5.7 | 0.43589
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-17 | 50-WD-53010-01E01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8260 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6 | CML-17 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 6 | 6 | 0.24495
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-6 | 50-WD-53010-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8249 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.95 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.7 | 6 | 6.4 | 0.33166
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-3 | 50-WD-53010-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8246 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.3 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 7.3 | 6.4 | 5.7 | 0.73485
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53015-01E01 | CML-10 | 50-WD-53015-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8236 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.3 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.7 | 6.5 | 6.3 | 0.43205
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-9 | 50-WD-53014-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8224 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.85 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 5.8 | 5.7 | 6 | 0.1291
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-6 | 50-WD-53014-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8221 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.825 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 5.7 | 5.8 | 5.9 | 0.095743
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53016-01E01 | CML-6 | 50-WD-53016-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8207 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.1 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-WD-53016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 6.6 | 5.7 | 6.3 | 0.42426
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53016-01E01 | CML-3 | 50-WD-53016-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8204 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.9 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-WD-53016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.1 | 5.9 | 5.7 | 5.9 | 0.1633
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69006-01S01 | CML-7 | 50-OL-69006-01S01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8196 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.225 | CML-7 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6 | 6.8 | 6.4 | 0.47871
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-2 | 300-PG-23002-03C03-A CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10098 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 17.2 | CML-2 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2013-11-07 | 5.22 | 0 | A2: Right Quadrant |  | 8.27 | 5.22 | 6.745 | 16.4 | 3 O'Clock | 40 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.18 |  | 17.4 | 16.4 | 17.6 | 17.4 | 0.5416
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53008-01E01 | CML-7 | 50-WD-53008-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8172 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.875 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-WD-53008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.2 | 5.8 | 5.8 | 0.22174
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53008-01E01 | CML-5 | 50-WD-53008-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8170 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.9 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-WD-53008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.7 | 5.8 | 6.4 | 0.33665
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53008-01E01 | CML-4 | 50-WD-53008-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8169 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.3 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-WD-53008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 6.6 | 6.4 | 5.7 | 0.40825
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-19 | 50-WD-53007-01E01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8158 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.875 | CML-19 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 5.7 | 5.8 | 0.28723
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-12 | 50-WD-53007-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8151 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.9 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.7 | 5.9 | 6.3 | 0.28284
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-1 | 50-WD-53007-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8140 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.1 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 5.7 | 6.4 | 6.4 | 0.3559
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-14 | 100-OL-69002-01S01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8135 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.425 | CML-14 | CML: type TBC | 1 | 2031-07-11 | 2026-12-23 | 2015-01-23 07:30 | 2.5 | 0.19424 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.6 | 7.2 | 6.2 | 0.63443
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-8 | 100-OL-69002-01S01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8129 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.35 | CML-8 | CML: type TBC | 1 | 2031-07-11 | 2026-12-23 | 2015-01-23 07:30 | 2.5 | 0.19424 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6 | 7.3 | 6.4 | 0.69522
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-4 | 100-OL-69002-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8125 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.35 | CML-4 | CML: type TBC | 1 | 2031-07-11 | 2026-12-23 | 2015-01-23 07:30 | 2.5 | 0.19424 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 6.8 | 6.6 | 0.47958
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-18 | 100-OL-69001-01S01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8120 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.45 | CML-18 | CML: type TBC | 1 | 2031-07-11 | 2026-12-23 | 2015-01-23 07:30 | 2.5 | 0.19424 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.9 | 6.6 | 6.6 | 0.51962
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-5 | 100-OL-69001-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8107 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.275 | CML-5 | CML: type TBC | 1 | 2031-07-11 | 2026-12-23 | 2015-01-23 07:30 | 2.5 | 0.19424 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.5 | 6.8 | 6.1 | 0.47871
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-13 | 200-PW-44018-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23285 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.95 | CML-13 | CML: Elbow | 3 | 2033-06-19 | 2035-10-20 | 2015-05-12 07:00 | 2.5 | 0.14902 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.4 | 5.2 | 6 | 6.2 | 0.52599
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-7 | 150-FH-43026-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23506 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 6.9 | CML-7 | CML: Pipe Length | 3 | 2026-05-23 | 2024-01-20 | 2015-07-28 07:00 | 1.03 | 0.46825 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.1 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.07 | 0.59511 | 7.3 | 6.1 | 7.1 | 7.1 | 0.5416
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-38 | 150-PG-23506-25C02 CML-38 |  | FPSO 2014 | Pipe Wall Thickness | 20091 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.2 | CML-38 | CML: Pipe Length | 3 | 2018-08-26 | 2017-04-29 | 2014-05-29 07:00 | 15.88 | 1.1586 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.8 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.92 | 73.0003 | 22 | 20.8 | 21 | 21 | 0.5416
PW03 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 200-PW-44018-01X01 | CML-20 | 200-PW-44018-01X01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 9079 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.65 | CML-20 | CML: type TBC | 3 | 2029-01-16 | 2030-09-20 | 2015-03-01 09:30 | 2.5 | 0.19439 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 6.1 | 6.1 | 0.51962
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23300-09C03 | CML-7 | 50-PL-23300-09C03 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13123 |  | 2014-02-04 07:00 | 2014-02-04 11:00 | [36 empty] | 11.8 | CML-7 | CML: type TBC | 6 | 2093-08-18 | 2082-08-28 | 2014-02-04 07:00 | 2.81 | 0.1029 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 11 | 3 O'Clock | 50 | 11.07 | 50-PL-23300-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.19 |  | 12 | 11 | 12 | 12.2 | 0.5416
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44023-01C03-P | CML-2 | 250-PW-44023-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21917 | Protective mesh removed | 2014-06-24 08:00 | 2014-06-24 09:00 | [36 empty] | 12.9 | CML-2 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 12.5 | 3 O'Clock | 250 | 9.27 | 250-PW-44023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 13.7 | 12.5 | 12.7 | 12.7 | 0.5416
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44023-01C03-P | CML-2 | 250-PW-44023-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5819 | Protective mesh removed | 2014-06-24 08:00 | 2014-06-24 09:00 | [36 empty] | 12.9 | CML-2 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 12.5 | 3 O'Clock | 250 | 9.27 | 250-PW-44023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 13.7 | 12.5 | 12.7 | 12.7 | 0.5416
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-4 | 150-PG-23043-06C02-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 24273 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 9.375 | CML-4 | CML: Elbow | 3 | 2017-01-17 | 2016-06-30 | 2014-09-24 07:00 | 4.7 | 1.7251 | A3: Inside Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.7 | 6 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 9.3 | 10 | 8.7 | 9.5 | 0.53774
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40516-1CG | CML-25 | 100-WC-40516-1CG CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 8698 | Material Class Not Selectable | 2015-02-13 07:00 | 2015-02-13 14:00 |  |  | Administrator | 2015-09-08 11:58 | [32 empty] | 10.45 | CML-25 | CML: Elbow | 3 | 2074-01-04 | 2058-09-17 | 2015-02-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.56 | 2.5 | 4.03 | 10.3 | 12 O'Clock | 100 | 8.56 | 100-WC-40516-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 10.5 | 10.5 | 10.5 | 0.1
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38482-01C02 | CML-6 | 25-CG-38482-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10381 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.125 | CML-6 | CML: type TBC | 3 | 2015-09-20 | 2015-09-14 | 2013-11-12 | 2.5 | 1.6692 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 12 O'Clock | 25 | 6.35 | 25-CG-38482-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 | 5.6 | 5.6 | 6.3 | 5.8 | 6.8 | 0.53774
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-8 | 50-DH-56116-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5218 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.425 | CML-8 | CML: Elbow | 3 | 2017-05-22 | 2017-10-25 | 2014-05-20 09:30 | 2.5 | 0.7643 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 6.1 | 5.5 | 4.8 | 0.53774
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20068-01C02-P | CML-5 | 100-PL-20068-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21553 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.525 | CML-5 | CML: Fitting | 3 | 2048-08-12 | 2049-10-10 | 2014-07-17 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 12 O'Clock | 100 | 6.02 | 100-PL-20068-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.8 | 6.3 | 6.8 | 0.32016
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-8 | 250-DC-57064-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20288 | Reviewed on 18/11/14. FFS. Repeat in Oct. 19. | 2014-10-11 07:00 | 2014-10-11 15:00 | Check Corrosion Rate of 0.477mm/ yr |  | Nestor | 2014-11-24 09:03 | [32 empty] | 6.1 | CML-8 | CML: Pipe Length | 3 | 2021-06-24 | 2021-06-02 | 2014-10-11 07:00 | 2.5 | 0.47708 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 12 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.3 | 6.1 | 6.3 | 0.28284
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23280 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.725 | CML-8 | CML: Equal Tee | 3 | 2033-06-19 | 2035-10-20 | 2015-05-12 07:00 | 2.5 | 0.14902 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.4 | 5.8 | 5.2 | 5.5 | 0.51235
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-15 | 50-DH-56070-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 3231 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.575 | CML-15 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.9 | 6.4 | 5.9 | 7.1 | 0.53774
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44037-01C03 | CML-1 | 300-PW-44037-01C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21911 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 10.675 | CML-1 | CML: Reducing Tee | 6 | 2111-01-21 | 2099-09-28 | 2014-10-16 07:00 | 2.5 | 0.07993 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 10.2 | 9 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 11.3 | 10.5 | 10.7 | 10.2 | 0.46458
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-2 | 250-PW-20039-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5834 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 9.6 | CML-2 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.5 | 9 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.7 | 9.5 | 9.7 | 9.5 | 0.11547
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-7 | 50-DC-57450-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20323 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.975 | CML-7 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 5.9 | 6.3 | 5.7 | 0.25
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-18 | 250-PW-20022-01C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2061 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.75 | CML-18 | CML: Fitting | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.6 | 12 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 9.6 | 11.9 | 10.4 | 11.1 | 0.9815
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-10 | 300-PG-20004-03C03-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23364 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14 | CML-10 | CML: Pipe Length | 6 | 2048-06-27 | 2042-03-07 | 2015-07-20 07:00 | 4.9 | 0.26697 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | -0.488 | 13.7 | 13.8 | 14.8 | 13.7 | 0.53541
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-5 | 200-PW-44018-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8901 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.775 | CML-5 | CML: type TBC | 3 | 2028-12-12 | 2030-08-13 | 2015-02-25 13:00 | 2.5 | 0.19557 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6.2 | 5.5 | 6.2 | 0.5058
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-9 | 300-PG-23002-03C03-A CML-9 | Yes | FPSO 2013 | Pipe Wall Thickness | 10105 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 13.2 | CML-9 | CML: Elbow | 6 | 2015-10-10 | 2015-05-18 | 2013-11-07 | 5.22 | 3.8337 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 12.6 | 12 O'Clock | 40 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.38 |  | 12.6 | 13.9 | 13.1 | 13.2 | 0.53541
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-26 | 300-PG-20004-03C03-P CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 23368 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 13.7 | CML-26 | CML: Elbow | 6 | 2032-02-06 | 2028-09-27 | 2015-07-20 07:00 | 4.9 | 0.50116 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 | -0.97599 | 13.3 | 14 | 14.3 | 13.2 | 0.53541
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-13 | 300-PG-20004-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 6136 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 12.3 | CML-13 | CML: Pipe Length | 6 | 2017-12-22 | 2016-12-10 | 2014-07-11 07:30 | 3.3 | 2.4044 | A1: Outside Quadrant |  | 8.27 | 3.3 | 5.785 | 11.6 | 12 O'Clock | 200 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.6 | 12.3 | 12.9 | 12.4 | 0.53541
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56555-01C02 | CML-3 | 50-DH-56555-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21125 | Reviewed 20/11/14. FFS. Re check Oct.18. Review RBI to include this line. CML-2 avg. WT is 5.0 mm. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. Based on CML’s checked Line is FFS. Action: Update RBI study to include this line. While RBI is updated rest of CMLs to be inspected in 48m. | 2014-10-08 07:00 | 2014-10-08 15:00 | [36 empty] | 6.1 | CML-3 | CML: Elbow | 3 | 2030-07-23 | 2032-05-24 | 2014-10-08 07:00 | 2.5 | 0.17722 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56555-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.3 | 5.3 | 6.4 | 6.4 | 0.53541
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-10 | 80-PW-44016-01C02-P CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 21942 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.275 | CML-10 | CML: Elbow | 3 | 2021-09-15 | 2022-09-02 | 2014-10-10 07:00 | 2.5 | 0.36037 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.4 | 5.3 | 5.4 | 0.1893
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56032-01C02 | CML-1 | 80-DH-56032-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20912 | Rope Access | 2014-05-21 13:00 | 2014-05-21 14:00 | [36 empty] | 5.3 | CML-1 | CML: Elbow | 3 | 2017-02-01 | 2017-07-08 | 2014-05-21 13:00 | 2.5 | 0.8133 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 3 O'Clock | 80 | 5.49 | 80-DH-56032-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.7 | 4.7 | 5.8 | 5 | 0.53541
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-4 | 50-DH-56013-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1853 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 6 | CML-4 | CML: type TBC | 3 | 2084-01-09 | 2091-08-08 | 2014-05-06 08:00 | 2.5 | 0.04303 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 6.6 | 6.3 | 0.53541
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-4 | 50-DH-56013-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22333 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 6 | CML-4 | CML: type TBC | 3 | 2084-01-09 | 2091-08-08 | 2014-05-06 08:00 | 2.5 | 0.04303 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.6 | 6.6 | 6.3 | 0.53541
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45005-03C02-E | CML-1 | 150-FG-45005-03C02-E CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24319 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.1 | CML-1 | CML: Equal Tee | 3 | 2034-10-08 | 2031-06-22 | 2016-06-01 07:00 | 2.77 | 0.20309 | A2: Right Quadrant |  | 4.11 | 2.77 | 3.44 | 6.5 | 3 O'Clock | 150 | 7.11 | 150-FG-45005-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.73 |  | 7 | 6.5 | 7.1 | 7.8 | 0.53541
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8761 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.65 | CML-3 | CML: type TBC | 3 | 2050-07-15 | 2054-07-09 | 2015-02-15 09:30 | 2.5 | 0.08184 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.2 | 5.5 | 5.5 | 0.36968
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-2 | 80-DC-57005-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20248 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 6 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-06-02 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 6 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.2 | 6.2 | 5.7 | 5.9 | 0.24495
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57005-01C02 | CML-13 | 80-DC-57005-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20259 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 5.825 | CML-13 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-06-02 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 9 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 5.8 | 5.8 | 5.7 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-5 | 300-PL-20011-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 23790 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.65 | CML-5 | CML: Fitting | 3 | 2047-03-28 | 2046-12-27 | 2014-09-25 07:00 | 2.5 | 0.11376 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 40 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.8 | 6.2 | 6.8 | 6.8 | 0.3
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-28 | 300-PW-44003-01C03 CML-28 | yes | FPSO 2014 | Pipe Wall Thickness | 21870 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 17:10 | [32 empty] | 10.525 | CML-28 | CML: Pipe Length | 6 | 2028-08-19 | 2026-11-14 | 2014-10-19 07:00 | 2.5 | 0.51287 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.6 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.5 | 11.5 | 10.5 | 9.6 | 0.77621
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45305-03C02 | CML-5 | 100-FG-45305-03C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22081 | Rope Access | 2014-05-25 09:30 | 2014-05-25 10:30 | [36 empty] | 5.8 | CML-5 | CML: type TBC | 3 | 2024-03-17 | 2023-05-31 | 2014-05-25 09:30 | 2.5 | 0.3259 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.76 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-FG-45305-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.8 | 5.9 | 5.7 | 0.08165
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45305-03C02 | CML-1 | 100-FG-45305-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22077 | Rope Access | 2014-05-25 09:30 | 2014-05-25 10:30 | [36 empty] | 6 | CML-1 | CML: type TBC | 3 | 2024-03-17 | 2023-05-31 | 2014-05-25 09:30 | 2.5 | 0.3259 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.76 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-FG-45305-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.2 | 6 | 6.1 | 5.7 | 0.21602
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-26 | 300-PW-44003-01C03 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 21868 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 17:09 | [32 empty] | 10.625 | CML-26 | CML: Pipe Length | 6 | 2028-08-19 | 2026-11-14 | 2014-10-19 07:00 | 2.5 | 0.51287 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.6 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 11.1 | 9.6 | 10.8 | 11 | 0.69462
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-15 | 400-FH-43508-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6564 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 7.7 | CML-15 | CML: Elbow | 3 | 2025-06-28 | 2023-11-24 | 2015-03-30 07:00 | 2.5 | 0.44853 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.1 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8.2 | 7.1 | 7.4 | 8.1 | 0.53541
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-14 | 300-FL-43080-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2393 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 11 | CML-14 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.3 | 3 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 11.1 | 10.3 | 11.6 | 11 | 0.53541
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-6 | 50-DH-56137-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21090 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.25 | CML-6 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.6 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.9 | 6.3 | 6.2 | 5.6 | 0.53229
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23033-03C03 | CML-6 | 50-PL-23033-03C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1878 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.35 | CML-6 | CML: type TBC | 6 | 2140-05-23 | 2137-12-13 | 2014-03-25 07:00 | 2.5 | 0.04911 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.7 | 12 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 8.7 | 9.4 | 10 | 9.3 | 0.53229
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23009-09C02 | CML-1 | 200-PG-23009-09C02 CML-1 | Yes | FPSO 2014 | Pipe Wall Thickness | 10911 | Deck Level | 2014-01-06 | 2014-01-06 | [36 empty] | 18.15 | CML-1 | CML: type TBC | 3 | 2020-06-25 | 2018-02-18 | 2014-01-06 | 9.3 | 1.2667 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 17.5 | 12 O'Clock | 200 | 18.26 | 200-PG-23009-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 17.5 | 18.2 | 18.8 | 18.1 | 0.53229
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20057-01C02-P | CML-1 | 100-PW-20057-01C02-P CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 22814 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.225 | CML-1 | CML: Elbow | 3 | 2020-01-05 | 2020-03-25 | 2015-04-30 07:00 | 2.5 | 0.53316 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 2.9495 | 5 | 5.2 | 5.3 | 5.4 | 0.17078
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-21 | 300-PG-20004-03C03-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 6144 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.15 | CML-21 | CML: Fitting | 6 | 2028-12-07 | 2026-02-21 | 2014-07-11 07:30 | 4.9 | 0.60336 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 13.6 | 14.5 | 13.8 | 14.7 | 0.53229
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-2 | 300-PW-44003-01C03 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22867 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.075 | CML-2 | CML: Reducing Tee | 6 | 2034-06-23 | 2032-01-13 | 2015-05-01 07:00 | 2.5 | 0.37059 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.6 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 | -1.1289 | 9.6 | 9.6 | 10.3 | 10.8 | 0.58523
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56143-01C02 | CML1 | 25-DH-56143-01C02 CML1 |  | FPSO 2015 | Pipe Wall Thickness | 7530 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 6.225 | CML1 |  | 3 | 2026-06-22 | 2026-05-18 | 2015-04-13 07:00 | 2.5 | 0.29466 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 25 | 6.35 | 25-DH-56143-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.9 | 5.8 | 5.8 | 6.4 | 0.53151
FG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FG-45044-03C02 | CML-4 | 50-FG-45044-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21995 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 9.025 | CML-4 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.6 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.8 | 9.8 | 8.9 | 8.6 | 0.53151
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-3 | 200-PL-20019-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23478 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 6.55 | CML-3 | CML: Fitting | 3 | 2068-06-16 | 2068-01-21 | 2015-07-24 07:00 | 2.5 | 0.0699 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | -2.7037 | 6.5 | 6.2 | 6.8 | 6.7 | 0.26458
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-18 | 50-PW-44040-01C02 CML-18 | yes | FPSO 2015 | Pipe Wall Thickness | 23253 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.15 | CML-18 | CML: Pipe Length | 3 | 2024-05-07 | 2025-07-09 | 2015-05-11 07:00 | 2.5 | 0.27788 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.089024 | 5.1 | 5 | 5.3 | 5.2 | 0.1291
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-6 | 200-PL-20019-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21257 | Reviewed on 27/11/14. FFS. recheck on Sep.15 | 2014-09-30 07:00 | 2014-09-30 15:00 |  |  | Nestor | 2014-11-27 15:57 | [32 empty] | 6.525 | CML-6 | CML: Fitting | 3 | 2047-08-03 | 2047-05-04 | 2014-09-30 07:00 | 2.5 | 0.11259 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.7 | 6.5 | 6.7 | 0.23629
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43302-01C02 | CML-1 | 250-FH-43302-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12917 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.575 | CML-1 | CML: type TBC | 3 | 2018-01-01 | 2017-12-19 | 2014-01-26 07:00 | 2.5 | 0.83893 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 3 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.8 | 5.8 | 6.7 | 7 | 0.53151
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-15 | 80-FH-43009-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12593 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.775 | CML-15 | CML: Pipe Length | 3 | 2025-01-24 | 2023-07-31 | 2014-02-05 08:00 | 0.54 | 0.42453 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 9 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 5.5 | 6 | 6.4 | 5.2 | 0.53151
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56115-01C02 | CML-4 | 50-DH-56115-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5235 | Rope Access | 2014-05-20 13:00 | 2014-05-20 14:00 | [36 empty] | 5.475 | CML-4 | CML: Elbow | 3 | 2016-12-01 | 2017-04-17 | 2014-05-20 13:00 | 2.5 | 0.86722 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56115-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.9 | 5.7 | 5.6 | 4.7 | 0.53151
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38009-01C02 | CML-6 | 50-CG-38009-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7864 |  | 2015-01-14 08:00 | 2015-01-14 09:00 | [36 empty] | 5.375 | CML-6 | CML: Elbow | 3 | 2019-04-14 | 2019-11-30 | 2015-01-14 08:00 | 2.5 | 0.51761 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 15 | 5.54 | 50-CG-38009-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.4 | 4.7 | 6 | 5.4 | 0.53151
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-24 | 50-DH-56070-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 3240 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.325 | CML-24 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.3 | 7 | 6.3 | 5.7 | 0.53151
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-3 | 50-DH-56137-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21087 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 7.025 | CML-3 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.4 | 12 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7 | 7 | 7.7 | 0.53151
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56087-01C02 | CML-6 | 100-DH-56087-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8036 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:32 | [32 empty] | 7.925 | CML-6 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-20 14:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.5 | 9 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.6 | 7.5 | 8.1 | 7.5 | 0.53151
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8765 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.85 | CML-7 | CML: type TBC | 3 | 2050-07-15 | 2054-07-09 | 2015-02-15 09:30 | 2.5 | 0.08184 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 6.1 | 6.2 | 0.36968
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23034-01C03 | CML-5 | 50-PL-23034-01C03 CML-5 | no | FPSO 2014 | Pipe Wall Thickness | 20573 | Reviewed on 26/11/14.FFS. Repeat Oct.19 | 2014-10-12 07:00 | 2014-10-12 12:00 |  |  | Nestor | 2014-11-26 16:19 | [32 empty] | 9.325 | CML-5 | CML: Elbow | 6 | 2075-10-24 | 2074-08-12 | 2014-10-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 3 O'Clock | 50 | 8.74 | 50-PL-23034-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.1 | 8.9 | 9.2 | 10.1 | 0.53151
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8339 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.95 | CML-2 | CML: type TBC | 3 | 2049-06-17 | 2053-04-30 | 2015-01-28 07:30 | 2.5 | 0.08428 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-AI-63011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 5.4 | 6.2 | 6.1 | 0.36968
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-3 | 80-CG-38459-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21533 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 15.075 | CML-3 | CML: Reducer | 6 | 2074-01-04 | 2073-09-17 | 2014-07-17 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 14.4 | 12 O'Clock | 100 | 8.56 | 100-PG-20056-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.9 |  | 14.4 | 14.9 | 15.5 | 15.5 | 0.53151
PW03 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 200-PW-44018-01X01 | CML-11 | 200-PW-44018-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8769 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.7 | CML-11 | CML: type TBC | 3 | 2028-09-12 | 2030-05-04 | 2015-02-15 09:30 | 2.5 | 0.19875 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.9 | 5.4 | 5.2 | 6.3 | 0.49666
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-22 | 100-DC-57036-01C02 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 1428 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.376mm/ yr | [35 empty] | 5.775 | CML-22 | CML: type TBC | 3 | 2022-10-05 | 2023-01-25 | 2014-04-07 07:00 | 2.5 | 0.37642 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 5.8 | 5.8 | 5.7 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-15 | 100-DC-57036-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1421 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | Check Corrosion Rate of 0.376mm/ yr | [35 empty] | 5.925 | CML-15 | CML: type TBC | 3 | 2022-10-05 | 2023-01-25 | 2014-04-07 07:00 | 2.5 | 0.37642 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 6.1 | 6.1 | 0.20616
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57063-01C02 | CML-5 | 50-DC-57063-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1390 | Rope access | 2014-04-05 13:00 | 2014-04-05 14:00 | [36 empty] | 6.925 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 7.5 | 7 | 7.5 | 0.85
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57063-01C02 | CML-1 | 50-DC-57063-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1386 | Rope access | 2014-04-05 13:00 | 2014-04-05 14:00 | [36 empty] | 21.075 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DC-57063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 66 | 6.1 | 5.7 | 29.9518
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-13 | 50-DC-57451-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1384 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 6.525 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.5 | 6.6 | 7.3 | 0.65511
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20044-03C03-P | CML-5 | 80-PG-20044-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21453 | Protective mesh removed | 2014-06-29 09:30 | 2014-06-29 11:00 | [36 empty] | 11.075 | CML-5 | CML: Fitting | 6 | 2028-03-02 | 2025-12-02 | 2014-06-29 09:30 | 2.5 | 0.58453 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.5 | 6 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11.7 | 10.8 | 10.5 | 11.3 | 0.53151
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23006-09C02-PA | CML-16 | 200-PG-23006-09C02-PA CML-16 | Yes | FPSO 2014 | Pipe Wall Thickness | 23849 | Protective mesh removed/Rope Access | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 20.125 | CML-16 | CML: Reducer | 3 | 2103-01-05 | 2073-03-18 | 2014-09-25 07:00 | 9.3 | 0 | A1: Outside Quadrant |  | 15.26 | 9.3 | 12.28 | 19.5 | 12 O'Clock | 200 | 18.26 | 200-PG-23006-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 19.5 | 20.4 | 19.9 | 20.7 | 0.53151
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-12 | 50-DH-56137-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5453 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 4.182mm/ yr | [34 empty] | Low alarm breach | 18.075 | CML-12 | CML: Straight | 3 | 2017-12-09 | 2016-01-14 | 2014-05-28 07:00 | 2.5 | 4.1825 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 17.3 | 3 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 |  | 18.5 | 17.3 | 18.3 | 18.2 | 0.53151
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-6 | 150-FL-43174-01C02 CML-6 | yes | FPSO 2015 | Pipe Wall Thickness | 8540 | Estimated Pipe Schedule | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 4.1 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-02-04 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 6 O'Clock | 100 | 3 | 100-WF-71321-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 4.6 | 4.4 | 3.4 | 4 | 0.52915
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-17 | 50-WC-40071-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1952 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 5.975 | CML-17 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.8 | 6.1 | 5.7 | 6.3 | 0.27538
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-13 | 50-WC-40071-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1948 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 5.9 | CML-13 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.2 | 5.7 | 5.9 | 5.8 | 0.21602
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-7 | 50-WC-40071-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1942 | Rope Access. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Mar. 2020). RBI to be updated | 2014-03-26 09:30 | 2014-03-26 10:30 |  |  | Administrator | 2015-09-08 12:56 | [32 empty] | 6 | CML-7 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 3 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.1 | 5.7 | 6.1 | 6.1 | 0.2
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-1 | 50-WC-40071-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1936 | Rope Access. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Mar. 2020). RBI to be updated | 2014-03-26 09:30 | 2014-03-26 10:30 |  |  | Administrator | 2015-09-08 12:55 | [32 empty] | 5.875 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 5.9 | 5.7 | 6 | 0.12583
PW03 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8551 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.575 | CML-6 | CML: type TBC | 3 | 2028-06-05 | 2030-01-15 | 2015-02-04 07:30 | 2.5 | 0.20234 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.3 | 5.4 | 5.4 | 5.2 | 0.49244
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-8 | 250-PG-23003-06C02-PA CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 20027 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.8 | CML-8 | CML: type TBC | 3 | 2023-06-18 | 2024-07-16 | 2013-11-17 | 2.5 | 0.30237 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 |  | 6.4 | 5.4 | 0.52915
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43081-01C02 | CML-2 | 80-FH-43081-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12724 |  | 2014-01-27 08:00 | 2014-01-27 09:00 |  |  | Nestor | 2014-11-19 17:17 | [32 empty] | 6.3 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-01-27 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 6 O'Clock | 80 | 5.49 | 80-FH-43081-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 7 | 6.4 | 5.8 | 6 | 0.52915
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-1 | 25-PW-44028-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5694 |  | 2014-06-22 07:00 | 2014-06-22 08:00 | [36 empty] | 6.7 | CML-1 | CML: Elbow | 3 | 2040-07-23 | 2040-05-12 | 2014-06-22 07:00 | 2.5 | 0.14173 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 25 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | -0.81367 | 6.2 | 6.4 | 7.4 | 6.8 | 0.52915
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-10 | 50-DC-57056-03C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1142 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 5.85 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 5.9 | 6 | 0.1291
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-11 | 50-DC-57020-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2453 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 5.925 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 6.3 | 5.9 | 0.263
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-3 | 50-DC-57020-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2445 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 5.925 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 5.7 | 5.8 | 5.7 | 0.38622
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-2 | 50-DC-57020-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2444 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 6.275 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.9 | 6.7 | 5.8 | 5.7 | 0.61305
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-19 | 100-DC-57075-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2438 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.4mm/ yr | [35 empty] | 5.85 | CML-19 | CML: type TBC | 3 | 2022-03-21 | 2022-07-05 | 2014-03-20 07:00 | 2.5 | 0.3996 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.7 | 6.3 | 5.7 | 0.3
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-17 | 100-DC-57075-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2436 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.4mm/ yr | [35 empty] | 5.825 | CML-17 | CML: type TBC | 3 | 2022-03-21 | 2022-07-05 | 2014-03-20 07:00 | 2.5 | 0.3996 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 5.7 | 5.9 | 5.7 | 0.15
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-12 | 100-DC-57075-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2431 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.4mm/ yr | [35 empty] | 5.725 | CML-12 | CML: type TBC | 3 | 2022-03-21 | 2022-07-05 | 2014-03-20 07:00 | 2.5 | 0.3996 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 5.8 | 5.7 | 5.7 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-9 | 100-DC-57075-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2428 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.4mm/ yr | [35 empty] | 6.1 | CML-9 | CML: type TBC | 3 | 2022-03-21 | 2022-07-05 | 2014-03-20 07:00 | 2.5 | 0.3996 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 6 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 7.2 | 5.7 | 5.8 | 0.73485
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-6 | 100-DC-57075-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2425 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.4mm/ yr | [35 empty] | 6.15 | CML-6 | CML: type TBC | 3 | 2022-03-21 | 2022-07-05 | 2014-03-20 07:00 | 2.5 | 0.3996 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 6 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.9 | 6.3 | 5.7 | 6.7 | 0.44347
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57019-01C02 | CML-3 | 50-DC-57019-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2411 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 6.1 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 6.4 | 6.3 | 5.7 | 0.31623
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-4 | 200-FH-43131-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20465 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 7.9 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-05-30 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 3 O'Clock | 200 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 | -1.9205 | 8 | 7.4 | 7.6 | 8.6 | 0.52915
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44028-01C02 | CML-2 | 25-PW-44028-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5695 |  | 2014-06-22 07:00 | 2014-06-22 08:00 | [36 empty] | 9.5 | CML-2 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-06-22 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.1 | 3 O'Clock | 20 | 6.35 | 25-PW-44028-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | -5.3702 |  | 9.1 | 10.1 | 9.3 | 0.52915
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3044 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 5.9 | CML-1 | CML: type TBC | 3 | 2033-05-29 | 2035-07-22 | 2014-05-03 07:00 | 2.5 | 0.15195 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.4 | 6.6 | 5.6 | 0.52915
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-18 | 150-PG-23506-25C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2792 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.8 | CML-18 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.4 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.52 |  | 22.4 | 22.6 |  | 23.4 | 0.52915
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-23 | 50-DH-56137-01C02 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 23451 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 17.65 | CML-23 | CML: Pipe Length | 3 | 2022-05-08 | 2018-08-04 | 2015-07-23 07:00 | 2.5 | 2.1183 | A2: Right Quadrant |  | 18.44 | 2.5 | 10.47 | 16.9 | 3 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.4 | -6.4405 | 17.7 | 16.9 | 17.9 | 18.1 | 0.52599
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-3 | 80-CG-38459-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21510 | Protective mesh removed | 2014-06-29 08:00 | 2014-06-29 09:00 | [36 empty] | 14.55 | CML-3 | CML: Equal Tee | 6 | 2099-09-17 | 2086-07-24 | 2014-06-29 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 14.1 | 9 O'Clock | 80 | 11.13 | 80-PG-20053-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.6 |  | 14.3 | 14.5 | 15.3 | 14.1 | 0.52599
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56003-01C02 | CML-1 | 80-DH-56003-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3423 | Rope Access | 2014-05-11 14:30 | 2014-05-11 15:00 | [36 empty] | 5.15 | CML-1 | CML: type TBC | 3 | 2016-12-26 | 2017-05-27 | 2014-05-11 14:30 | 2.5 | 0.83676 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 6 O'Clock | 80 | 5.49 | 80-DH-56003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 5.1 | 4.7 | 5.9 | 0.52599
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8900 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.7 | CML-4 | CML: type TBC | 3 | 2051-02-20 | 2055-03-10 | 2015-02-25 13:00 | 2.5 | 0.08053 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 6.2 | 5.7 | 0.3559
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-3 | 50-FL-43454-01C02-P CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 20506 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.25 | CML-3 | CML: Elbow | 3 | 2018-12-10 | 2019-07-14 | 2014-10-05 07:00 | 2.5 | 0.54978 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6 | 5 | 5.2 | 4.8 | 0.52599
PW03 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 200-PW-44018-01X01 | CML-15 | 200-PW-44018-01X01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8620 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.725 | CML-15 | CML: type TBC | 3 | 2028-07-20 | 2030-03-05 | 2015-02-09 07:30 | 2.5 | 0.20071 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.5 | 6.2 | 6 | 0.45735
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56129-01C02 | CML-1 | 50-DH-56129-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3284 | Rope Access | 2014-05-09 15:30 | 2014-05-09 16:00 | [36 empty] | 5.65 | CML-1 | CML: type TBC | 3 | 2021-10-20 | 2022-09-14 | 2014-05-09 15:30 | 2.5 | 0.36218 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DH-56129-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.2 | 5.2 | 5.2 | 6 | 0.52599
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8762 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.7 | CML-4 | CML: type TBC | 3 | 2050-07-15 | 2054-07-09 | 2015-02-15 09:30 | 2.5 | 0.08184 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 6.2 | 5.7 | 5.4 | 0.3559
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-12 | 100-DH-56009-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 3435 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 6.05 | CML-12 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.6 | 12 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6 | 6.8 | 5.8 | 0.52599
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-3 | 200-PW-44018-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8899 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.675 | CML-3 | CML: type TBC | 3 | 2028-12-12 | 2030-08-13 | 2015-02-25 13:00 | 2.5 | 0.19557 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6 | 6.1 | 5.4 | 5.2 | 0.44253
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56084-01C02 | CML-7 | 100-DH-56084-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3349 | Rope Access | 2014-05-08 13:00 | 2014-05-08 14:00 | [36 empty] | 7.45 | CML-7 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-08 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.7 | 9 O'Clock | 100 | 6.02 | 100-DH-56084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.5 | 7.9 | 7.7 | 6.7 | 0.52599
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38452-09C02-P | CML-16 | 50-CG-38452-09C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 22356 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.95 | CML-16 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8 | 8.2 | 7.2 | 8.4 | 0.52599
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56007-01C02 | CML-1 | 80-DH-56007-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3447 | Rope Access | 2014-05-12 14:00 | 2014-05-12 15:00 | [36 empty] | 5.65 | CML-1 | CML: type TBC | 3 | 2018-03-18 | 2018-10-08 | 2014-05-12 14:00 | 2.5 | 0.62315 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-DH-56007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.7 | 6.1 | 4.9 | 5.9 | 0.52599
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-10 | 150-WC-40006-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8788 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.7 | CML-10 | CML: type TBC | 3 | 2050-07-13 | 2054-07-06 | 2015-02-15 07:00 | 2.5 | 0.08185 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-GN-67009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 5.7 | 6.2 | 0.3559
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-5 | 50-PL-23021-03C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10237 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.25 | CML-5 | CML: type TBC | 6 | 2015-08-15 | 2015-07-30 | 2013-11-08 | 2.5 | 2.8287 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.5 | 12 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8.3 | 8.7 | 8.5 | 0.52599
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20069-01C02-P | CML-5 | 100-PL-20069-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21559 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.35 | CML-5 | CML: Fitting | 3 | 2048-08-12 | 2049-10-10 | 2014-07-17 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-PL-20069-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.4 | 6.2 | 6.2 | 0.19149
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-14 | 50-CG-38452-09C02-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23754 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.85 | CML-14 | CML: Elbow | 3 | 2057-09-12 | 2046-03-15 | 2015-10-30 07:00 | 2.5 | 0.14082 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.6 | 8.4 | 8.6 | 8.8 | 0.52599
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38494-01C02 | CML-6 | 25-CG-38494-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10389 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 9.75 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2013-11-12 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 9 | 12 O'Clock | 25 | 6.35 | 25-CG-38494-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | 9 | 9 | 10.2 | 10 | 9.8 | 0.52599
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-6 | 50-PL-23020-01C03 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10120 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.45 | CML-6 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2013-11-08 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 10 | 12 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 11.2 | 10.4 | 10.2 | 0.52599
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56139-01C02 | CML-4 | 50-DH-56139-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21067 | Rope Access | 2014-05-15 11:00 | 2014-05-15 12:00 | [36 empty] | 4.925 | CML-4 | CML: type TBC | 3 | 2016-07-01 | 2016-10-30 | 2014-05-15 11:00 | 2.5 | 0.98462 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56139-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 4.6 | 5.7 | 4.8 | 0.5252
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-12 | 150-FG-45505-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 22352 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.625 | CML-12 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.3 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.5 | 7.3 | 8.4 | 0.5252
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-7 | 100-DH-56009-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3430 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.275 | CML-7 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 4.8 | 6 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 6 | 5 | 4.8 | 5.3 | 0.5252
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-5 | 300-PG-23400-01C03-P CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24459 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | Check Corrosion Rate of 0.585mm/ yr |  | John Wilson | 2017-03-24 09:40 | Anomily to re visit 7/5/2018 | [31 empty] | 8.775 | CML-5 | CML: Elbow | 6 | 2022-02-12 | 2022-11-23 | 2016-07-05 07:00 | 5.22 | 0.5845 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 8.5 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.28 | 0.20917 | 8.5 | 8.8 | 8.8 | 9 | 0.20616
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43122-01C02 | CML-4 | 50-FH-43122-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1762 | Rope access | 2014-04-27 08:30 | 2014-04-27 09:00 | [36 empty] | 5.775 | CML-4 | CML: Equal Tee | 3 | 2024-11-14 | 2026-02-06 | 2014-04-27 08:30 | 2.5 | 0.26517 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FH-43122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.5 | 6.5 | 5.8 | 0.5252
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8996 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.75 | CML-5 | CML: type TBC | 3 | 2051-04-21 | 2055-05-15 | 2015-02-28 07:00 | 2.5 | 0.08018 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 5.4 | 6 | 5.5 | 0.35119
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43116-01C02 | CML-5 | 150-FH-43116-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1775 | Rope access | 2014-04-27 13:00 | 2014-04-27 14:00 | [36 empty] | 7.075 | CML-5 | CML: Pipe Length | 3 | 2021-08-05 | 2020-12-15 | 2014-04-27 13:00 | 2.5 | 0.56317 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-FH-43116-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 7.8 | 6.6 | 7.1 | 0.5252
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56063-01C02 | CML-1 | 50-DH-56063-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3361 | Rope Access | 2014-05-10 07:00 | 2014-05-10 08:00 | [36 empty] | 8.775 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-10 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8 | 12 O'Clock | 50 | 5.54 | 50-DH-56063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 8 | 8.9 | 9.1 | 9.1 | 0.5252
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-7 | 50-CG-38452-09C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23747 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.625 | CML-7 | CML: Elbow | 3 | 2047-08-20 | 2038-10-01 | 2015-10-30 07:00 | 2.5 | 0.18223 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.3 | 8.5 | 9.4 | 0.5252
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PL-20033-01C02 | CML-8 | 50-PL-20033-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2272 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 6.325 | CML-8 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-03-16 11:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.3 | 6.2 | 6.2 | 0.1893
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-8 | 50-PL-23516-03C03 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 7796 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:03 | [32 empty] | 11.175 | CML-8 | CML: Reducing Tee | 6 | 2075-10-24 | 2074-08-12 | 2015-01-13 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 10.4 | 12 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 10.4 | 11.5 | 11.3 | 11.5 | 0.5252
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56141-01C02 | CML-4 | 50-DH-56141-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21071 | Rope Access | 2014-05-15 08:00 | 2014-05-15 09:00 | [36 empty] | 5.125 | CML-4 | CML: type TBC | 3 |  |  | 2014-05-15 08:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 4.4 | 6 O'Clock | 80 |  | 80-DH-56141-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 5.6 | 5.1 | 4.4 | 5.4 | 0.5252
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45040-03C02 | CML-1 | 25-FG-45040-03C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10559 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.475 | CML-1 | CML: type TBC | 3 | 2014-06-28 | 2014-05-15 | 2013-11-16 | 2.5 | 3.5848 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.925 | 4.7 | 3 O'Clock | 25 | 6.35 | 25-FG-45040-03C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.6 | 4.7 | 5.8 | 5.8 | 0.5252
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8772 |  | 2015-02-15 13:00 | 2015-02-15 14:00 | [36 empty] | 5.75 | CML-2 | CML: type TBC | 3 | 2050-07-18 | 2054-07-12 | 2015-02-15 13:00 | 2.5 | 0.08182 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 5.5 | 6 | 5.4 | 0.35119
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57008-01C02 | CML-1 | 80-DC-57008-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23273 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 6.575 | CML-1 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 3 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.9 | 5.8 | 6.8 | 6.8 | 0.51881
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57008-01C02 | CML-2 | 80-DC-57008-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23274 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 6.125 | CML-2 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 9 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 6.4 | 6 | 5.8 | 0.27538
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-20 | 150-WC-40006-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 8944 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.9 | CML-20 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 6 | 6.2 | 5.4 | 0.34641
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-7 | 150-PG-20054-01C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21518 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 12.575 | CML-7 | CML: Elbow | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.8 | 12 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 11.8 | 12.7 | 12.9 | 12.9 | 0.5252
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43091-01C02 | CML-1 | 80-FL-43091-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5826 | Rope access | 2014-06-24 10:30 | 2014-06-24 12:00 | [36 empty] | 8.9 | CML-1 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-06-24 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.2 | 12 O'Clock | 50 | 5.49 | 80-FL-43091-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.2 | 9.3 | 8.8 | 9.3 | 0.52281
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-19 | 80-CG-38459-09C02-P CML-19 |  | FPSO 2013 | Pipe Wall Thickness | 10065 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 20.8 | CML-19 | CML: Elbow | 6 | 2110-01-05 | 2091-09-17 | 2013-11-06 | 8.6 | 0 | A3: Inside Quadrant |  | 12.26 | 8.6 | 10.43 | 20.4 | 9 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.8 |  | 20.9 | 21.5 | 20.4 | 20.4 | 0.52281
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-20 | 200-PG-23065-09C02-A CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 434 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.8 | CML-20 | CML: Pipe Length | 3 | 2030-11-29 | 2025-05-29 | 2014-03-12 09:00 | 10.17 | 0.46207 | A3: Inside Quadrant |  | 15.26 | 10.17 | 12.715 | 17.9 | 6 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.73 |  | 19.6 | 18.3 | 17.9 | 19.4 | 0.82865
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-12 | 200-PG-23065-09C02-A CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 426 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.575 | CML-12 | CML: Pipe Length | 3 | 2030-11-29 | 2025-05-29 | 2014-03-12 09:00 | 10.17 | 0.46207 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 17.9 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.73 |  | 18.8 | 17.9 | 18.8 | 18.8 | 0.45
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-3 | 100-PW-20021-01C02-P CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 22821 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.125 | CML-3 | CML: Elbow | 3 | 2020-01-05 | 2020-03-25 | 2015-04-30 07:00 | 2.5 | 0.53316 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | 0.18159 | 5.3 | 5.1 | 5.1 | 5 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-45 | 200-PL-20019-01C02 CML-45 |  | FPSO 2014 | Pipe Wall Thickness | 21296 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.35 | CML-45 | CML: Pipe Length | 3 | 2047-08-03 | 2047-05-04 | 2014-09-30 07:00 | 2.5 | 0.11259 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.2 | 6.3 | 6.3 | 0.17321
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-13 | 50-PL-23041-06C03 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10226 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.7 | CML-13 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 2.4409 | A2: Right Quadrant |  | 5.07 |  |  | 10 | 3 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.6 | 10 | 11.1 | 11.1 | 0.52281
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-9 | 50-DC-57025-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22943 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 6.15 | CML-9 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.091479 | 6.3 | 6.2 | 5.8 | 6.3 | 0.23805
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-8 | 50-DC-57025-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22942 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.85 | CML-8 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | -0.18296 | 5.8 | 5.8 | 6 | 5.8 | 0.1
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57013-01C02 | CML-1 | 50-DC-57013-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22925 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.925 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | -0.9614 | 5.8 | 5.8 | 5.9 | 6.2 | 0.1893
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57006-01C02 | CML-2 | 80-DC-57006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22846 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 6.4 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-04-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 12 O'Clock | 80 | 5.49 | 80-DC-57006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.54478 | 5.8 | 6.8 | 6.3 | 6.7 | 0.45461
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-22 | 200-PG-23065-09C02-A CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 436 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.75 | CML-22 | CML: Elbow | 3 | 2037-08-22 | 2030-01-07 | 2014-03-12 09:00 | 10.17 | 0.33371 | A1: Outside Quadrant |  | 15.26 | 10.17 | 12.715 | 18 | 12 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.83 |  | 18 | 19.9 | 18.9 | 18.2 | 0.85829
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-20 | 150-PG-23506-25C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 2794 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 23.05 | CML-20 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.4 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.52 |  | 23.3 | 23.6 | 22.4 | 22.9 | 0.51962
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-10 | 100-FG-45001-09C02 CML-10 | Yes | FPSO 2015 | Pipe Wall Thickness | 23315 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 10.65 | CML-10 | CML: type TBC | 3 | 2026-07-31 | 2023-01-26 | 2015-07-11 07:00 | 4.7 | 0.48806 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 10.1 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 | -0.060302 | 10.1 | 10.8 | 10.4 | 11.3 | 0.51962
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-22 | 200-PW-44018-01X01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 8918 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.525 | CML-22 | CML: type TBC | 3 | 2028-12-12 | 2030-08-13 | 2015-02-25 13:00 | 2.5 | 0.19557 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.6 | 6.1 | 0.4272
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-19 | 250-FH-43303-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 12957 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 7.05 | CML-19 | CML: type TBC | 3 | 2064-02-06 | 2063-09-23 | 2014-01-27 10:00 | 2.5 | 0.07591 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7.1 | 7.4 | 7.4 | 0.51962
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67300-01E01 | CML-4 | 25-GN-67300-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22488 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.825 | CML-4 | CML: Elbow | 3 | 2026-08-10 | 2026-07-05 | 2015-04-20 07:00 | 2.5 | 0.29166 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 5.8 | 5.8 | 0.05
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67300-01E01 | CML-3 | 25-GN-67300-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22487 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.8 | CML-3 | CML: Elbow | 3 | 2026-08-10 | 2026-07-05 | 2015-04-20 07:00 | 2.5 | 0.29166 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 5.8 | 5.8 | 0
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67300-01E01 | CML-2 | 25-GN-67300-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22486 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.875 | CML-2 | CML: Elbow | 3 | 2026-08-10 | 2026-07-05 | 2015-04-20 07:00 | 2.5 | 0.29166 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 5.9 | 5.9 | 0.05
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 150-WF-71347-01K01 | CML-1 | 150-WF-71347-01K01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 6664 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 12:54 | [32 empty] | 5.875 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 5.8 | 12 O'Clock | 150 | 3 | 150-WF-71347-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 5.9 | 5.9 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-12 | 0200-DC-57L9006-AC21-00 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 5052 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.361mm/ yr | [35 empty] | 5.9 | CML-12 | CML: type TBC | 3 | 2017-08-06 | 2016-10-22 | 2015-03-05 07:00 | 2.5 | 1.3613 | A1: Outside Quadrant |  | 5.74 | 2.5 | 3.5737 | 5.8 | 6 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.1 | 5.8 | 5.9 | 0.14142
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-28 | 50-GN-67002-01E01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 9087 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 6.1 | CML-28 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 5.8 | 6.1 | 6.3 | 0.21602
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-24 | 50-GN-67002-01E01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 9083 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.925 | CML-24 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6 | 6 | 5.9 | 0.095743
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-6 | 50-GN-67002-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 9065 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 6.25 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6.7 | 6.7 | 0.51962
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-5 | 50-GN-67002-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 9064 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.95 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6.1 | 6.1 | 0.17321
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-1 | 50-GN-67002-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 9060 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 6.1 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 5.8 | 6.2 | 6.2 | 0.2
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-26 | 50-AU-63015-01E01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 9057 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.95 | CML-26 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6 | 6 | 6 | 0.1
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-7 | 50-AU-63015-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 9038 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.875 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 5.9 | 5.9 | 5.8 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-6 | 50-AU-63015-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 9037 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.925 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6 | 6.1 | 0.15
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-36 | 50-AI-63004-01E01 CML-36 |  | FPSO 2015 | Pipe Wall Thickness | 9027 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.85 | CML-36 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 5.9 | 5.8 | 0.057735
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-23 | 50-AI-63004-01E01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 9014 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.025 | CML-23 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6 | 6.5 | 5.8 | 0.3304
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63007-01E01 | CML-22 | 50-AI-63007-01E01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 8946 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.9 | CML-22 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-26 09:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.9 | 5.8 | 5.9 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-20 | 50-AU-63018-01E01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 8916 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 6.575 | CML-20 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.9 | 6.8 | 6.8 | 0.51881
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63005-01E01 | CML-11 | 50-AI-63005-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8887 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 6.175 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 6.2 | 5.8 | 6.5 | 0.28723
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63023-01E01 | CML-7 | 50-AU-63023-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8868 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 07:00 | 2015-02-25 08:00 | [36 empty] | 6.05 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AU-63023-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 6.4 | 5.8 | 5.8 | 0.3
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-50 | 150-WC-40006-01C02 CML-50 |  | FPSO 2015 | Pipe Wall Thickness | 8974 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.6 | CML-50 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 6.1 | 5.4 | 0.33665
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-3 | 250-PG-23015-06C03-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13035 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 16.35 | CML-3 | CML: Pipe Length | 6 | 2015-12-11 | 2015-06-18 | 2014-01-11 13:00 | 8.55 | 3.8363 | A2: Right Quadrant |  | 12.26 | 8.55 | 10.405 | 15.9 | 6 O'Clock | 100 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.35 |  | 16.8 | 15.9 | 15.9 | 16.8 | 0.51962
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-10 | 50-GN-67006-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8755 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 6.025 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.6 | 5.8 | 5.8 | 5.9 | 0.38622
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67001-01E01 | CML-7 | 50-GN-67001-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8552 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.175 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-GN-67001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 6.7 | 6.3 | 0.4113
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67003-01E01 | CML-1 | 50-GN-67003-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8496 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.05 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-GN-67003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.8 | 5.8 | 6.6 | 0.37859
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63020-01E01 | CML-6 | 50-AU-63020-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8486 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 5.825 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AU-63020-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 5.8 | 5.8 | 5.8 | 0.05
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67008-01E01 | CML-5 | 50-GN-67008-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8467 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.35 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-GN-67008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.6 | 5.8 | 6.6 | 0.37859
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-9 | 50-AI-63012-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8459 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.1 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6.5 | 6.3 | 0.3559
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-8 | 50-AI-63012-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8458 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.25 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.7 | 5.8 | 5.8 | 6.7 | 0.51962
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-5 | 50-AI-63012-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8455 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.325 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 6.5 | 5.8 | 6.5 | 0.35
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63021-01E01 | CML-8 | 50-AU-63021-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8450 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.825 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AU-63021-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 5.8 | 5.8 | 5.8 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63021-01E01 | CML-5 | 50-AU-63021-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8447 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.2 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-AU-63021-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 6.2 | 5.8 | 6.3 | 0.29439
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40406-01C02 | CML-6 | 50-WC-40406-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8438 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 6.1 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40406-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6 | 6.4 | 6.2 | 0.2582
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40406-01C02 | CML-3 | 50-WC-40406-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8435 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 5.975 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-WC-40406-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 5.9 | 6.1 | 5.8 | 0.15
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23411-03C02-P | CML-8 | 50-PG-23411-03C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8392 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.15 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6.6 | 6.4 | 0.41231
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23411-03C02-P | CML-6 | 50-PG-23411-03C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8390 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 5.875 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2015-01-30 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 5.9 | 5.8 | 5.9 | 0.05
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23411-03C02-P | CML-5 | 50-PG-23411-03C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8389 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.1 | 5.9 | 6.2 | 0.18257
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23411-03C02-P | CML-1 | 50-PG-23411-03C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8385 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.025 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.1 | 5.9 | 6.3 | 0.22174
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63030-01E01 | CML-8 | 50-AI-63030-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8349 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63030-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 6.5 | 5.8 | 5.8 | 0.33665
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63030-01E01 | CML-4 | 50-AI-63030-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8345 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.15 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63030-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 6.4 | 6.5 | 5.8 | 0.35119
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63030-01E01 | CML-3 | 50-AI-63030-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8344 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.975 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63030-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 6.4 | 5.8 | 5.8 | 0.28723
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63030-01E01 | CML-1 | 50-AI-63030-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8342 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.95 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63030-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 5.8 | 6.4 | 0.3
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-11 | 50-AI-63450-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8330 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 5.9 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.9 | 5.8 | 5.9 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-8 | 50-AI-63450-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8327 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.125 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.4 | 5.9 | 5.8 | 0.32016
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-2 | 50-AI-63450-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8321 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.275 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 6.8 | 6.4 | 5.8 | 0.4272
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63044-01E01 | CML-2 | 50-AI-63044-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8305 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.4 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-AI-63044-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.8 | 6.2 | 6.8 | 0.4899
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63013-01E01 | CML-1 | 50-AI-63013-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8300 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 5.875 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 5.9 | 5.8 | 5.9 | 0.05
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53003-01E01 | CML-6 | 50-WD-53003-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8296 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.3 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-WD-53003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.8 | 6.4 | 5.8 | 6.2 | 0.41633
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53003-01E01 | CML-4 | 50-WD-53003-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8294 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.3 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-WD-53003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 6.5 | 6.6 | 5.8 | 0.3559
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53003-01E01 | CML-1 | 50-WD-53003-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8291 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.975 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-WD-53003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 5.8 | 6 | 5.9 | 0.17078
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-6 | 50-WD-53011-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8282 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.85 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 5.9 | 5.9 | 0.057735
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-2 | 50-WD-53011-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8278 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.875 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 5.9 | 5.9 | 0.05
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-29 | 50-WD-53010-01E01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 8272 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.15 | CML-29 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 6 | 6.3 | 5.8 | 0.31091
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-28 | 50-WD-53010-01E01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 8271 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.825 | CML-28 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 5.8 | 5.8 | 0.05
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-23 | 50-WD-53010-01E01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 8266 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.175 | CML-23 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 6.6 | 6.4 | 0.38622
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-16 | 50-WD-53010-01E01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8259 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.225 | CML-16 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.1 | 6.8 | 6.2 | 0.41932
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-8 | 50-WD-53010-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8251 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 18.7 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 56 | 5.8 | 6.3 | 6.7 | 24.8694
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-7 | 50-WD-53010-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8250 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.4 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.7 | 5.8 | 6.8 | 6.3 | 0.45461
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53015-01E01 | CML-3 | 50-WD-53015-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8229 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.2 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 6.4 | 5.8 | 6.3 | 0.2708
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-11 | 50-WD-53014-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8226 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.15 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 5.8 | 5.9 | 6.7 | 0.40415
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-2 | 50-WD-53014-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8217 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.925 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 6 | 5.9 | 5.8 | 0.095743
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53012-01E01 | CML-3 | 50-WD-53012-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8211 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.975 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-WD-53012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 6.2 | 5.8 | 5.8 | 0.20616
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53008-01E01 | CML-9 | 50-WD-53008-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8174 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.825 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-WD-53008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 5.8 | 5.8 | 5.8 | 0.05
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53008-01E01 | CML-6 | 50-WD-53008-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8171 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.325 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-WD-53008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.7 | 6.5 | 6.3 | 5.8 | 0.38622
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53008-01E01 | CML-3 | 50-WD-53008-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8168 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.175 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-WD-53008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.5 | 5.8 | 6.6 | 0.43493
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-17 | 100-OL-69002-01S01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8138 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.35 | CML-17 | CML: type TBC | 1 | 2039-10-04 | 2033-02-21 | 2015-01-23 07:30 | 2.5 | 0.13354 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.8 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.5 | 6.7 | 6.4 | 0.3873
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-6 | 100-OL-69002-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8127 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.75 | CML-6 | CML: type TBC | 1 | 2039-10-04 | 2033-02-21 | 2015-01-23 07:30 | 2.5 | 0.13354 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.8 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.7 | 7.7 | 6.8 | 0.77675
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69004-01S01 | CML-6 | 80-OL-69004-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8097 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.475 | CML-6 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 4.49 | 2.5 | 3.1519 | 5.8 | 3 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.3 | 5.8 | 6.4 | 7.4 | 0.6702
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69004-01S01 | CML-5 | 80-OL-69004-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8096 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.45 | CML-5 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 5.8 | 12 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.7 | 6.8 | 6.5 | 0.45092
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-11 | 200-PW-44018-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 9042 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.825 | CML-11 | CML: type TBC | 3 | 2029-01-15 | 2030-09-19 | 2015-03-01 07:00 | 2.5 | 0.19443 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6.1 | 6 | 6 | 0.41932
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56091-01C02 | CML-2 | 80-DH-56091-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20983 | Rope Access | 2014-05-17 11:00 | 2014-05-17 12:00 | [36 empty] | 5.05 | CML-2 | CML: type TBC | 3 | 2016-08-21 | 2017-01-05 | 2014-05-17 11:00 | 2.5 | 0.92693 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 9 O'Clock | 80 | 5.49 | 80-DH-56091-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.8 | 4.9 | 4.9 | 4.6 | 0.51962
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-9 | 80-PW-44001-01C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23218 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 6.275 | CML-9 | CML: Elbow | 3 | 2028-04-20 | 2030-01-14 | 2015-05-11 07:00 | 2.5 | 0.20069 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 3 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 1.9211 | 6.1 | 5.1 | 7.1 | 6.8 | 0.88835
PG05 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21554 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.15 | CML-6 | CML: Elbow | 3 | 2019-10-23 | 2020-01-08 | 2014-07-17 07:30 | 2.5 | 0.55019 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 9 O'Clock | 100 | 6.02 | 100-PL-20068-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.5 | 6.2 | 6.5 | 5.4 | 0.51962
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43170-01C02 | CML-4 | 250-FL-43170-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2889 | Rope Access | 2014-04-25 07:00 | 2014-04-25 08:00 | [36 empty] | 6.45 | CML-4 | CML: Elbow | 3 | 2018-09-27 | 2018-09-13 | 2014-04-25 07:00 | 2.5 | 0.72268 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 12 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.8 | 6.8 | 6.5 | 0.51962
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-9 | 50-PF-20301-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 3007 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.35 | CML-9 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 8.8 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.19 | 0 | 9.1 | 8.8 | 9.5 | 10 | 0.51962
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-9 | 50-PF-20301-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 22286 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.35 | CML-9 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 8.8 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.19 |  | 9.1 | 8.8 | 9.5 | 10 | 0.51962
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-29 | 400-FH-43508-01C02 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 6578 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 8.85 | CML-29 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 8.1 | 9 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.9 | 9.2 | 9.2 | 8.1 | 0.51962
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-18 | 150-WC-40006-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8914 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.75 | CML-18 | CML: type TBC | 3 | 2051-02-20 | 2055-03-10 | 2015-02-25 13:00 | 2.5 | 0.08053 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.2 | 5.7 | 5.7 | 0.33166
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-27 | 300-PW-44003-01C03 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 22892 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10 | CML-27 | CML: Pipe Length | 6 | 2034-06-23 | 2032-01-13 | 2015-05-01 07:00 | 2.5 | 0.37059 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.6 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 | 1.1289 | 9.7 | 9.6 | 10.7 | 10 | 0.49666
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8902 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.825 | CML-6 | CML: type TBC | 3 | 2028-12-12 | 2030-08-13 | 2015-02-25 13:00 | 2.5 | 0.19557 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6 | 5.2 | 6 | 6.1 | 0.41932
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45004-03C02 | CML-3 | 150-FG-45004-03C02 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24335 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.85 | CML-3 | CML: Elbow | 3 | 2032-12-28 | 2029-07-28 | 2016-06-06 07:00 | 2.5 | 0.23531 | A2: Right Quadrant |  | 4.11 | 2.5 | 3.305 | 6.4 | 3 O'Clock | 150 | 7.11 | 150-FG-45004-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.4 | 6.7 | 7.6 | 0.51962
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-6 | 150-FH-43027-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10568 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 7.5 | CML-6 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2013-11-16 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  |  | 7.2 | 8.1 | 7.2 | 0.51962
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-2 | 200-PL-20019-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21253 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.4 | CML-2 | CML: Fitting | 3 | 2047-08-03 | 2047-05-04 | 2014-09-30 07:00 | 2.5 | 0.11259 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.4 | 6.2 | 6.5 | 0.14142
DH01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-DH-56137-01C02 | CML-1 | 50-DH-56137-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10464 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 15.6 | CML-1 | CML: type TBC | 6 | 2090-11-29 | 2082-02-28 | 2013-11-13 | 0.99 | 0 | A2: Right Quadrant |  | 2.74 | 0.99 | 1.865 | 15.3 | 9 O'Clock | 50 | 8.74 | 50-PL-45030-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.31 |  | 16.2 | 15.3 |  | 15.3 | 0.51962
PW03 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22502 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.6 | CML-8 | CML: Pipe Length | 3 | 2019-09-22 | 2019-09-05 | 2015-04-20 07:00 | 2.5 | 0.60984 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 3 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.2 | 5.9 | 6 | 0.40825
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-8 | 80-DH-56074-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20953 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 6.425 | CML-8 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-05-24 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 9 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7.2 | 6.2 | 6.2 | 6.1 | 0.51881
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-7 | 50-DH-56137-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21091 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 7.825 | CML-7 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 7.2 | 3 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.6 | 7.2 | 8.2 | 8.3 | 0.51881
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-3 | 200-PW-44018-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23080 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.65 | CML-3 | CML: Elbow | 3 | 2033-04-28 | 2035-08-23 | 2015-05-07 07:00 | 2.5 | 0.15008 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 20 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 2.8488 | 5.8 | 5.2 | 5.5 | 6.1 | 0.3873
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23405-03C02-P | CML-10 | 100-PG-23405-03C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 23862 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.375 | CML-10 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A1: Outside Quadrant |  |  | 2.7 |  | 6 | 12 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 6.5 | 6.6 | 6.4 | 0.263
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-12 | 50-DH-56137-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21096 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 5.025 | CML-12 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 4.7 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.8 | 4.8 | 4.8 | 4.7 | 0.51881
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-41 | 50-DH-56070-01C02 CML-41 |  | FPSO 2014 | Pipe Wall Thickness | 3257 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.525 | CML-41 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7 | 6.9 | 6.3 | 5.9 | 0.51881
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8400 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 5.75 | CML-4 | CML: type TBC | 3 | 2049-07-31 | 2053-06-17 | 2015-01-30 07:30 | 2.5 | 0.084 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AI-63037-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.7 | 5.7 | 6.2 | 0.33166
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43307-01C02-E | CML-4 | 200-PL-43307-01C02-E CML-4 | Yes | FPSO 2015 | Pipe Wall Thickness | 8793 | LAGGING REMOVAL REQUIRED | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 6.425 | CML-4 | CML: type TBC | 3 | 2032-03-21 | 2032-01-31 | 2015-02-15 09:30 | 2.5 | 0.2046 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 200 | 6.35 | 200-PL-43307-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 6.4 | 6.4 | 6 | 0.36856
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 150-DH-56080-01C02 | CML-3 | 150-DH-56080-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3326 | Rope Access | 2014-05-08 07:00 | 2014-05-08 09:00 | [36 empty] | 8.375 | CML-3 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-05-08 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.6 | 12 O'Clock | 150 | 7.11 | 150-DH-56080-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 7.6 | 8.7 | 8.6 | 8.6 | 0.51881
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8862 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 07:00 | 2015-02-25 08:00 | [36 empty] | 5.65 | CML-1 | CML: type TBC | 3 | 2051-02-15 | 2055-03-04 | 2015-02-25 07:00 | 2.5 | 0.08056 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-AU-63023-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 5.6 | 6.1 | 0.31091
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-2 | 150-PG-20009-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2696 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 11.325 | CML-2 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-12 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 11 | 9 O'Clock | 100 | 8.56 | 100-PG-20009-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11.1 | 12.1 | 11.1 | 11 | 0.51881
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-2 | 150-PG-20009-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 667 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 11.325 | CML-2 | CML: Elbow | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 09:00 | 2.03 | 0 | A4: Left Quadrant |  | 1.11 | 2.03 | 1.57 | 11 | 9 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.97 | 0 | 11.1 | 12.1 | 11.1 | 11 | 0.51881
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-2 | 150-PG-20009-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 385 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 11.325 | CML-2 | CML: Elbow | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 | 2.03 | 0 | A4: Left Quadrant |  | 1.11 | 2.03 | 1.57 | 11 | 9 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.97 |  | 11.1 | 12.1 | 11.1 | 11 | 0.51881
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-4 | 150-FH-43136-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5517 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 6.775 | CML-4 | CML: Pipe Length | 3 | 2021-12-24 | 2020-06-08 | 2014-06-01 07:00 | 1.03 | 0.70943 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.4 | 3 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 | 0.45673 | 6.4 | 6.4 | 6.8 | 7.5 | 0.51881
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-4 | 250-PL-20006-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13174 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.375 | CML-4 | CML: Pipe Length | 3 | 2029-11-23 | 2029-10-10 | 2014-01-21 13:00 | 2.5 | 0.23343 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.4 | 6.5 | 6.4 | 0.12583
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23017-03C03-A | CML-6 | 250-PG-23017-03C03-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10980 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 12.275 | CML-6 | CML: Elbow | 6 | 2019-01-08 | 2018-03-30 | 2014-01-09 | 4.4 | 1.4797 | A3: Inside Quadrant |  | 6.7 | 4.4 | 5.55 | 11.8 | 6 O'Clock | 250 | 12.7 | 250-PG-23017-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 12.9 | 12.5 | 11.8 | 11.9 | 0.51881
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-15 | 50-PL-23041-06C03 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10228 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 10.525 | CML-15 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 2.8972 | A3: Inside Quadrant |  | 5.07 |  |  | 9.8 | 6 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 10.9 | 10.5 | 9.8 | 10.9 | 0.51881
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23016-06C03-A | CML-2 | 250-PG-23016-06C03-A CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23538 | Re-check | 2015-08-03 09:30 | 2015-08-03 12:00 | [36 empty] | 18.725 | CML-2 | CML: Pipe Length | 6 | 2145-03-30 | 2120-01-22 | 2015-08-03 09:30 | 8.55 | 0.07361 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.1 | 12 O'Clock | 250 | 18.26 | 250-PG-23016-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.55 |  | 18.1 | 19.2 | 19.1 | 18.5 | 0.51881
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56046-01C02 | CML-3 | 80-DH-56046-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20937 | Rope Access | 2014-05-17 09:30 | 2014-05-17 11:00 | [36 empty] | 5.6 | CML-3 | CML: type TBC | 3 | 2019-04-09 | 2019-12-14 | 2014-05-17 09:30 | 2.5 | 0.51042 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-DH-56046-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5.4 | 6.2 | 5 | 0.5164
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H |  | 50-CG-38454-01C02-H |  | FPSO 2015 | Pipe Wall Thickness | 23681 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9 | 50-CG-38454-01C02-H | Piping | 3 | 2043-10-24 |  | 2015-10-30 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 8.4 | 12 O'Clock | 50 | 5.54 | Pipework | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.2 | 8.8 | 9.6 | 0.5164
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-19 | 100-FG-45304-03C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 22075 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 5.8 | CML-19 | CML: type TBC | 3 | 2029-02-09 | 2027-12-14 | 2014-05-25 07:00 | 2.5 | 0.22412 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 5.8 | 5.8 | 0
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-12 | 100-FG-45304-03C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 22068 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.4 | CML-12 | CML: type TBC | 3 | 2029-02-09 | 2027-12-14 | 2014-05-25 07:00 | 2.5 | 0.22412 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.76 | 5.8 | 3 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 5.8 | 6.5 | 6.8 | 0.42426
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-6 | 100-FG-45304-03C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22062 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.225 | CML-6 | CML: type TBC | 3 | 2029-02-09 | 2027-12-14 | 2014-05-25 07:00 | 2.5 | 0.22412 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.8 | 6 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.2 | 5.8 | 6.5 | 0.30957
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-3 | 100-FG-45304-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22059 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 5.9 | CML-3 | CML: type TBC | 3 | 2029-02-09 | 2027-12-14 | 2014-05-25 07:00 | 2.5 | 0.22412 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.8 | 3 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.8 | 6 | 6 | 0.11547
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-2 | 100-FG-45304-03C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22058 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.1 | CML-2 | CML: type TBC | 3 | 2029-02-09 | 2027-12-14 | 2014-05-25 07:00 | 2.5 | 0.22412 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.76 | 5.8 | 3 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 5.8 | 6.2 | 6.4 | 0.2582
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-10 | 200-PW-44018-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8886 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.475 | CML-10 | CML: type TBC | 3 | 2028-12-11 | 2030-08-11 | 2015-02-25 09:30 | 2.5 | 0.19562 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 6 | 5.5 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-4 | 150-FH-43027-01C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10566 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 7.7667 | CML-4 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2013-11-16 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 9 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  |  | 8.2 | 7.9 | 7.2 | 0.51316
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PL-20070-01C02-P | CML-1 | 100-PL-20070-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21561 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 6.275 | CML-1 | CML: Fitting | 3 | 2048-08-12 | 2049-10-10 | 2014-07-17 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-PL-20070-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.4 | 6.3 | 6.2 | 0.095743
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-15 | 300-PF-20501-03C03-P CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23530 | Re-check | 2015-07-29 07:00 | 2015-07-29 12:00 | [36 empty] | 14.275 | CML-15 | CML: Pipe Length | 6 | 2048-11-22 | 2042-07-07 | 2015-07-29 07:00 | 4.9 | 0.26393 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 | -1.0806 | 14.8 | 14.6 | 13.7 | 14 | 0.51235
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8997 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.75 | CML-6 | CML: type TBC | 3 | 2029-01-06 | 2030-09-09 | 2015-02-28 07:00 | 2.5 | 0.19473 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.9 | 5.9 | 6 | 5.2 | 0.36968
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-27 | 50-DH-56062-01C02 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 9114 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.725 | CML-27 | CML: type TBC | 3 | 2023-04-08 | 2024-04-29 | 2015-03-02 07:00 | 2.5 | 0.30831 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.9 | 5.8 | 6.2 | 5 | 0.51235
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-17 | 150-FG-45505-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 22357 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.875 | CML-17 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.3 | 9 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.4 | 7.6 | 8.2 | 7.3 | 0.51235
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-3 | 50-PL-45016-03C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10443 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.525 | CML-3 | CML: type TBC | 6 | 2018-02-23 | 2017-08-11 | 2013-11-13 | 0.99 | 1.637 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 8 | 12 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.01 |  | 8 | 8.8 | 9.1 | 8.2 | 0.51235
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8932 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.55 | CML-8 | CML: type TBC | 3 | 2028-12-20 | 2030-08-21 | 2015-02-26 09:00 | 2.5 | 0.19532 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 6 | 5.3 | 5.2 | 0.36968
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56064-01C02 | CML-1 | 50-DH-56064-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3271 | Rope Access | 2014-05-09 13:00 | 2014-05-09 14:00 | [36 empty] | 5.725 | CML-1 | CML: type TBC | 3 | 2021-10-19 | 2022-09-13 | 2014-05-09 13:00 | 2.5 | 0.36229 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-DH-56064-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.4 | 5.8 | 5.2 | 5.5 | 0.51235
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2267 | Rope Access | 2014-03-16 11:30 | 2014-03-16 13:00 | [36 empty] | 6.475 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-16 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-PL-20033-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 7.2 | 6.4 | 6.3 | 0.51235
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38472-01C02 | CML-5 | 50-CG-38472-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23660 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 7.225 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 40 | 5.54 | 50-CG-38472-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.3 | 6.5 | 7.7 | 7.4 | 0.51235
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 150-DH-56080-01C02 | CML-4 | 150-DH-56080-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3327 | Rope Access | 2014-05-08 07:00 | 2014-05-08 09:00 | [36 empty] | 8.075 | CML-4 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-05-08 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.4 | 9 O'Clock | 150 | 7.11 | 150-DH-56080-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8 | 8.3 | 8.6 | 7.4 | 0.51235
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-22 | 100-FG-45001-09C02 CML-22 |  | FPSO 2013 | Pipe Wall Thickness | 10437 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.375 | CML-22 | CML: type TBC | 3 | 2015-08-07 | 2015-01-06 | 2013-11-13 | 4.7 | 2.9421 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 9.8 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 10.7 | 9.8 | 10.9 | 10.1 | 0.51235
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-7 | 100-FG-45001-09C02 CML-7 | Yes | FPSO 2015 | Pipe Wall Thickness | 23312 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.325 | CML-7 | CML: type TBC | 3 | 2054-07-05 | 2043-07-19 | 2015-07-11 07:00 | 4.7 | 0.15637 | A4: Left Quadrant |  | 8.13 | 4.7 | 6.415 | 10.8 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | -0.36181 | 11 | 11.6 | 11.9 | 10.8 | 0.51235
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-3 | 200-PL-20035-03C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23470 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 7.625 | CML-3 | CML: Elbow | 3 | 2025-12-24 | 2023-10-27 | 2015-07-24 07:00 | 3.61 | 0.36347 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 7.4 | 9 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.79 | 0.093172 | 7.8 | 7.4 | 7.9 | 7.4 | 0.263
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40504-1CG | CML-1 | 150-WC-40504-1CG CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8632 | Rope Access / Material Class Not Selectable.Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Feb.. 2020). RBI to be updated | 2015-02-10 10:30 | 2015-02-10 11:30 |  |  | Administrator | 2015-09-08 12:47 | [32 empty] | 11.15 | CML-1 | CML: Pipe Length | 3 | 2052-03-28 | 2039-09-14 | 2015-02-10 10:30 | 2.5 | 0.21802 | A1: Outside Quadrant |  | 7.97 | 2.5 | 5.235 | 10.6 | 12 O'Clock | 150 | 10.97 | 150-WC-40504-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.6 | 11.4 | 11.5 | 11.1 | 0.40415
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-30 | 50-CG-38001-09C02 CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 10945 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 9.075 | CML-30 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0.39638 | A1: Outside Quadrant |  | 5.74 |  |  | 8.5 | 12 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.5 | 8.5 | 9.4 | 9.6 | 8.8 | 0.51235
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-20 | 50-PF-20301-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 3018 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.4 | CML-20 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.7 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 | 0 | 9.9 | 9.4 | 8.7 | 9.6 | 0.5099
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-20 | 50-PF-20301-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 22297 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.4 | CML-20 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.7 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.09 |  | 9.9 | 9.4 | 8.7 | 9.6 | 0.5099
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-14 | 200-PL-20035-03C02-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23473 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 7.725 | CML-14 | CML: Elbow | 3 | 2025-12-24 | 2023-10-27 | 2015-07-24 07:00 | 3.61 | 0.36347 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.4 | 6 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.79 | 0.093172 | 7.8 | 7.9 | 7.4 | 7.8 | 0.22174
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-12 | 50-FG-45020-03C02 CML-12 | yes | FPSO 2013 | Pipe Wall Thickness | 10584 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5 | CML-12 | CML: type TBC | 3 | 2014-10-08 | 2014-10-04 | 2013-11-17 | 2.5 | 2.2462 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 4.5 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 5.7 | 5 | 4.8 | 4.5 | 0.5099
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44006-01X01 | CML-24 | 250-PW-44006-01X01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 8016 |  | 2015-01-20 08:30 | 2015-01-20 14:00 | [36 empty] | 5.6 | CML-24 | CML: Pipe Length | 3 | 2018-11-25 | 2018-11-10 | 2015-01-20 08:30 | 2.5 | 0.70151 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 6 O'Clock | 250 | 6.35 | 250-PW-44006-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.12164 | 6 | 5.8 | 5.2 | 5.4 | 0.36515
CG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-CG-38452-09C02-P | CML-21 | 50-CG-38452-09C02-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 22361 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.7 | CML-21 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8.4 | 7.5 | 7.2 | 7.7 | 0.5099
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-21 | 100-DH-56082-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 3389 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 5.7 | CML-21 | CML: type TBC | 3 | 2016-08-29 | 2016-10-07 | 2014-05-10 09:30 | 2.5 | 1.0842 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 6 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.2 | 5.7 | 5 | 5.9 | 0.5099
PW03 | Montara_Topside | Yes | Fire Water (71) | Pipework | 200-PW-44018-01X01 | CML-17 | 200-PW-44018-01X01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 6633 |  | 2015-03-31 07:00 | 2015-03-31 15:00 | [36 empty] | 5.725 | CML-17 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-31 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 5.2 | 12 O'Clock | 50 | 2.5 | 50-WF-71343-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6 | 5.9 | 5.8 | 0.3594
PW03 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 9063 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.725 | CML-4 | CML: type TBC | 3 | 2029-01-16 | 2030-09-20 | 2015-03-01 09:30 | 2.5 | 0.19439 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6 | 5.2 | 5.9 | 5.8 | 0.3594
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20023-01C03-P | CML-3 | 250-PW-20023-01C03-P CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 5600 |  | 2014-06-20 07:00 | 2014-06-20 08:00 | [36 empty] | 10.075 | CML-3 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-06-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 9.6 | 9 O'Clock | 250 | 9.27 | 250-PW-20023-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 |  | 10.4 | 10.4 | 9.9 | 9.6 | 0.39476
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-7 | 400-FH-43500-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5643 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 9.9 | CML-7 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 9.4 | 6 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.6 | 9.7 | 9.4 | 9.9 | 0.5099
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43137-01C02 | CML-4 | 50-FH-43137-01C02 CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 12856 |  | 2014-01-23 08:00 | 2014-01-23 10:00 | [36 empty] | 4.9 | CML-4 | CML: Elbow | 3 | 2015-02-21 | 2015-04-29 | 2014-01-23 08:00 | 2.5 | 1.7607 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43137-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.7 | 5.6 | 4.9 | 4.4 | 0.5099
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-4 | 50-DH-56070-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3220 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.4 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.4 | 7.1 | 6.2 | 0.5099
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-41 | 150-PG-23506-25C02 CML-41 |  | FPSO 2014 | Pipe Wall Thickness | 20094 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.35 | CML-41 | CML: Pipe Length | 3 | 2019-02-24 | 2017-09-12 | 2014-05-29 07:00 | 15.88 | 1.0578 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 20.9 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.02 | 36.5001 | 21.5 | 21 | 22 | 20.9 | 0.50662
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-1 | 250-PW-20039-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22965 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 10.025 | CML-1 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2015-05-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.6 | 3 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 | -0.23267 | 10 | 9.6 | 10.2 | 10.3 | 0.30957
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23748 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.95 | CML-8 | CML: Elbow | 3 | 2041-04-18 | 2034-01-21 | 2015-10-30 07:00 | 2.5 | 0.22365 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.2 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 9.1 | 8.2 | 9.2 | 9.3 | 0.50662
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-2 | 200-PL-20034-03C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23463 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 7.625 | CML-2 | CML: Elbow | 3 | 2025-12-24 | 2023-10-27 | 2015-07-24 07:00 | 3.61 | 0.36347 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.4 | 6 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.79 | -0.18682 | 7.5 | 7.8 | 7.4 | 7.8 | 0.20616
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-1 | 50-DO-62002-01S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2986 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.3 | CML-1 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.9 | 6.1 | 5.8 | 0.46904
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-1 | 50-DO-62002-01S01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22265 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.3 | CML-1 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.9 | 6.1 | 5.8 | 0.46904
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-2 | 200-PL-20035-03C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23469 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 7.5 | CML-2 | CML: Elbow | 3 | 2025-12-24 | 2023-10-27 | 2015-07-24 07:00 | 3.61 | 0.36347 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.4 | 6 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.79 | 0.093172 | 7.4 | 7.4 | 7.4 | 7.8 | 0.2
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-2 | 50-CG-38467-01C02 CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 22273 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.25 | CML-2 | CML: Elbow | 3 | 2017-03-05 | 2017-07-31 | 2014-05-01 11:00 | 2.5 | 0.80757 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0 | 4.9 | 5.9 | 4.8 | 5.4 | 0.50662
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38467-01C02 | CML-2 | 50-CG-38467-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2994 | Rope Access | 2014-05-01 11:00 | 2014-05-01 12:00 | [36 empty] | 5.25 | CML-2 | CML: Elbow | 3 | 2017-03-05 | 2017-07-31 | 2014-05-01 11:00 | 2.5 | 0.80757 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-CG-38467-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.9 | 5.9 | 4.8 | 5.4 | 0.50662
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56088-01C02 | CML-4 | 100-DH-56088-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5197 | Rope Access | 2014-05-20 07:00 | 2014-05-20 09:00 | [36 empty] | 5.65 | CML-4 | CML: Elbow | 3 | 2018-02-22 | 2018-04-20 | 2014-05-20 07:00 | 2.5 | 0.74386 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 12 O'Clock | 100 | 6.02 | 100-DH-56088-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.4 | 5.4 | 5.5 | 0.50662
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-31 | 100-DC-57036-01C02 CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 1437 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 6.2 | CML-31 | CML: type TBC | 3 | 2027-01-03 | 2027-06-16 | 2014-04-07 07:00 | 2.5 | 0.25879 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 6.3 | 6.8 | 0.45461
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38005-01C02 | CML-7 | 50-CG-38005-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3107 | Rope Access | 2014-05-04 10:00 | 2014-05-04 10:30 | [36 empty] | 5.55 | CML-7 | CML: Elbow | 3 | 2017-10-20 | 2018-04-10 | 2014-05-04 10:00 | 2.5 | 0.69232 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 15 | 5.54 | 50-CG-38005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5.9 | 6 | 0.50662
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2030 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 6.15 | CML-4 | CML: type TBC | 3 | 2040-08-31 | 2043-11-03 | 2014-03-27 14:30 | 2.5 | 0.10964 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.3 | 6.5 | 5.4 | 6.4 | 0.50662
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56010-01C02 | CML-1 | 50-DH-56010-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22318 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 5.85 | CML-1 | CML: type TBC | 3 | 2084-01-17 | 2091-08-16 | 2014-05-06 10:30 | 2.5 | 0.04301 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.6 | 5.6 | 5.5 | 5.7 | 0.50662
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56010-01C02 | CML-1 | 50-DH-56010-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1838 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 5.85 | CML-1 | CML: type TBC | 3 | 2084-01-17 | 2091-08-16 | 2014-05-06 10:30 | 2.5 | 0.04301 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.6 | 5.6 | 5.5 | 5.7 | 0.50662
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-15 | 50-WC-40071-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1950 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 6.325 | CML-15 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 5.9 | 7.2 | 6.4 | 0.63966
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-14 | 50-WC-40071-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1949 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 6.45 | CML-14 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.9 | 6.4 | 5.8 | 6.7 | 0.47958
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-5 | 50-WC-40071-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1940 | Rope Access. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Mar. 2020). RBI to be updated | 2014-03-26 09:30 | 2014-03-26 10:30 |  |  | Administrator | 2015-09-08 12:56 | [32 empty] | 6.325 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.2 | 6.6 | 6.7 | 0.4113
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-5 | 80-PW-44035-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23269 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.85 | CML-5 | CML: Elbow | 3 | 2028-04-28 | 2030-01-22 | 2015-05-12 07:00 | 2.5 | 0.20041 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.5093 | 6.4 | 5.5 | 5.1 | 6.4 | 0.65574
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-16 | 200-PG-24001-09C02 CML-16 | yes | FPSO 2013 | Pipe Wall Thickness | 10272 | Deck Level | 2013-11-09 | 2013-11-09 | High alarm WT breach | [35 empty] | 7.45 | CML-16 | CML: Elbow | 3 | 2018-06-26 | 2017-08-08 | 2013-11-09 | 2.5 | 0.90683 | A2: Right Quadrant |  | 4.1 | 2.5 | 3.3 | 6.7 | 3 O'Clock | 40 | 7.1 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.7 | 6.7 | 7.6 | 7.8 | 0.50662
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56004-01C02 | CML-5 | 80-DH-56004-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3408 | Rope Access | 2014-05-11 07:00 | 2014-05-11 09:00 | [36 empty] | 7.75 | CML-5 | CML: type TBC | 3 |  |  | 2014-05-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 7 | 9 O'Clock | 100 |  | 100-DH-56004-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.1 | 7.9 | 8 | 7 | 0.50662
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43120-01C02 | CML-6 | 200-FH-43120-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12840 |  | 2014-02-06 07:00 | 2014-02-06 09:00 | [36 empty] | 7.75 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 6 O'Clock | 200 | 6.35 | 200-FH-43120-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8.1 | 7.6 | 7.1 | 8.2 | 0.50662
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-23 | 150-WC-40006-01C02 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 9054 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.725 | CML-23 | CML: type TBC | 3 | 2051-05-13 | 2055-06-08 | 2015-03-01 07:00 | 2.5 | 0.08006 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 5.8 | 5.6 | 5.4 | 0.29861
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8571 |  | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.8 | CML-5 | CML: type TBC | 3 | 2049-11-16 | 2053-10-15 | 2015-02-04 07:30 | 2.5 | 0.08332 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AI-63038-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 5.9 | 6.1 | 0.29439
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-13 | 150-PG-20054-01C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21524 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 12.05 | CML-13 | CML: Elbow | 6 | 2098-02-09 | 2085-10-05 | 2014-06-26 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 11.3 | 6 O'Clock | 150 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 12.2 | 12.4 | 11.3 | 12.3 | 0.50662
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-4 | 250-PW-20039-01C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22968 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.675 | CML-4 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2015-05-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.6 | 9 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.1 | -0.349 | 9.8 | 9.6 | 9.7 | 9.6 | 0.095743
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-8 | 80-PG-20046-03C03-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23339 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-19 07:00 | 2015-07-19 15:00 | [36 empty] | 10.725 | CML-8 | CML: Elbow | 6 | 2031-04-09 | 2028-07-19 | 2015-07-19 07:00 | 2.5 | 0.48305 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 10.1 | 3 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 | 0 | 10.9 | 10.1 | 10.6 | 11.3 | 0.5058
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-8 | 50-DC-57056-03C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1140 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.3 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 5.8 | 3 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 5.8 | 6.4 | 6.6 | 0.34641
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-9 | 50-CG-38452-09C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20968 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 7.675 | CML-9 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 12 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.5 | 7.8 | 8.3 | 0.5058
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-2 | 100-DC-57307-01C03 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 2310 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 3.479mm/ yr | [35 empty] | 6.025 | CML-2 | CML: type TBC | 6 | 2015-02-26 | 2015-02-23 | 2014-03-17 13:00 | 2.5 | 3.4793 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 5.8 | 6 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 6.1 | 5.8 | 6.2 | 0.17078
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-9 | 100-VA-80006-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2178 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 5.775 | CML-9 | CML: type TBC | 3 | 2016-12-20 | 2017-02-01 | 2014-03-30 13:00 | 2.5 | 0.98929 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 3 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.9 | 5.2 | 6.4 | 5.6 | 0.5058
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-7 | 250-PG-20036-01C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21365 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.975 | CML-7 | CML: Elbow | 6 | 2022-02-11 | 2021-08-14 | 2014-07-14 07:30 | 2.5 | 0.77771 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 8.4 | 9 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.4 | 8.7 | 9.4 | 8.4 | 0.5058
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63017-01E01 | CML-1 | 50-AU-63017-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8490 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.825 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-02-02 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 6 O'Clock | 25 | 6.35 | 25-AU-63017-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.7 | 6.6 | 7.3 | 0.32016
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63017-01E01 | CML-3 | 50-AU-63017-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8492 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.725 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 25 | 6.35 | 25-AU-63017-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.8 | 6.7 | 6.7 | 6.7 | 0.05
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-4 | 50-AU-63017-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12874 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 6.05 | CML-4 | CML: type TBC | 3 | 2024-04-01 | 2024-08-10 | 2014-02-03 08:00 | 2.5 | 0.32466 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6 | 6.2 | 6.2 | 5.8 | 0.19149
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-2 | 50-AU-63017-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12872 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 6.325 | CML-2 | CML: type TBC | 3 | 2024-04-01 | 2024-08-10 | 2014-02-03 08:00 | 2.5 | 0.32466 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.1 | 6.9 | 6.5 | 5.8 | 0.47871
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-5 | 50-AU-63017-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12875 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 6.2 | CML-5 | CML: type TBC | 3 | 2024-04-01 | 2024-08-10 | 2014-02-03 08:00 | 2.5 | 0.32466 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 3 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 5.8 | 6 | 6.5 | 0.3559
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-28 | 50-AU-63017-01E01 CML-28 | no | FPSO 2014 | Pipe Wall Thickness | 12721 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.275 | CML-28 | CML: type TBC | 3 | 2018-02-12 | 2018-01-31 | 2014-02-01 09:00 | 2.5 | 0.81814 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.8 | 6.1 | 6.7 | 6.5 | 0.40311
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-20 | 50-AU-63017-01E01 CML-20 | yes | FPSO 2014 | Pipe Wall Thickness | 12713 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.45 | CML-20 | CML: type TBC | 3 | 2018-02-12 | 2018-01-31 | 2014-02-01 09:00 | 2.5 | 0.81814 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.7 | 6.6 | 5.8 | 6.7 | 0.43589
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-5 | 50-AU-63017-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3058 | Rope Access | 2014-05-03 10:30 | 2014-05-03 11:30 | [36 empty] | 4.95 | CML-5 | CML: Elbow | 3 | 2016-05-24 | 2016-09-17 | 2014-05-03 10:30 | 2.5 | 1.0198 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FH-43133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.3 | 4.7 | 5.2 | 4.6 | 0.35119
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-2 | 50-AU-63017-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3055 | Rope Access | 2014-05-03 10:30 | 2014-05-03 11:30 | [36 empty] | 5.125 | CML-2 | CML: Elbow | 3 | 2017-10-16 | 2018-04-05 | 2014-05-03 10:30 | 2.5 | 0.69433 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FH-43133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 5.2 | 5.1 | 0.17078
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-6 | 50-AU-63017-01E01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3059 | Rope Access | 2014-05-03 10:30 | 2014-05-03 11:30 | [36 empty] | 5.325 | CML-6 | CML: Elbow | 3 | 2018-08-08 | 2019-02-27 | 2014-05-03 10:30 | 2.5 | 0.58584 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 6 O'Clock | 50 | 5.54 | 50-FH-43133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5.2 | 5 | 5.3 | 0.34034
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-4 | 50-AU-63017-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3057 | Rope Access | 2014-05-03 10:30 | 2014-05-03 11:30 | [36 empty] | 5.875 | CML-4 | CML: Equal Tee | 3 | 2019-10-12 | 2020-06-17 | 2014-05-03 10:30 | 2.5 | 0.47735 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-FH-43133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.7 | 6.9 | 5.8 | 0.75
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-1 | 50-AU-63017-01E01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3054 | Rope Access | 2014-05-03 10:30 | 2014-05-03 11:30 | [36 empty] | 5.675 | CML-1 | CML: Fitting | 3 | 2083-06-03 | 2090-12-07 | 2014-05-03 10:30 | 2.5 | 0.0434 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-FH-43133-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 5.6 | 5.5 | 5.9 | 0.17078
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-2 | 50-AU-63017-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3061 | Rope Access | 2014-05-03 11:30 | 2014-05-03 12:00 | [36 empty] | 5.075 | CML-2 | CML: Elbow | 3 | 2017-10-16 | 2018-04-05 | 2014-05-03 11:30 | 2.5 | 0.69425 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FH-43132-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 4.9 | 5.2 | 0.20616
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-3 | 50-AU-63017-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3062 | Rope Access | 2014-05-03 11:30 | 2014-05-03 12:00 | [36 empty] | 5.575 | CML-3 | CML: Pipe Length | 3 | 2025-01-31 | 2026-05-03 | 2014-05-03 11:30 | 2.5 | 0.26034 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-FH-43132-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.3 | 6 | 5.4 | 0.30957
AD01 | Montara_Topside | No | Flare (43) | Pipework | 50-AU-63017-01E01 | CML-1 | 50-AU-63017-01E01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3060 | Rope Access | 2014-05-03 11:30 | 2014-05-03 12:00 | [36 empty] | 6.1 | CML-1 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-05-03 11:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43132-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.5 | 6.3 | 5.7 | 5.9 | 0.36515
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63017-01E01 | CML-2 | 50-AU-63017-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8491 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 7.375 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 6 O'Clock | 25 | 6.35 | 25-AU-63017-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.4 | 7.3 | 7.3 | 7.5 | 0.095743
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 24241 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 16.225 | CML-3 | CML: Elbow | 3 | 2085-04-24 | 2073-10-17 | 2014-09-24 07:00 | 7.9 | 0 | A4: Left Quadrant |  | 12.09 | 7.9 | 9.0519 | 15.6 | 9 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 16.8 | 16.4 | 16.1 | 15.6 | 0.5058
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-10 | 50-PW-44015-01X01 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10293 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.475 | CML-10 | CML: Elbow | 3 | 2017-05-19 | 2017-10-21 | 2013-11-10 | 2.5 | 0.76605 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 6 | 5.4 | 0.3594
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3485 | Rope Access | 2014-05-14 11:00 | 2014-05-14 12:00 | [36 empty] | 5.975 | CML-1 | CML: type TBC | 3 | 2045-01-07 | 2048-09-12 | 2014-05-14 11:00 | 2.5 | 0.09454 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-DH-56025-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.4 | 6.4 | 5.4 | 5.7 | 0.5058
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-5 | 50-PW-44015-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5715 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 5.5 | CML-5 | CML: Pipe Length | 3 | 2022-11-16 | 2023-11-21 | 2014-06-22 10:00 | 2.5 | 0.32116 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.81322 | 6 | 5.2 | 5.3 | 5.5 | 0.3559
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56140-01C02 | CML-3 | 80-DH-56140-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21075 | Rope Access | 2014-05-15 09:30 | 2014-05-15 11:00 | [36 empty] | 11.125 | CML-3 | CML: type TBC | 3 |  |  | 2014-05-15 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 10.5 | 3 O'Clock | 80 |  | 80-DH-56140-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 |  | 11.7 | 10.5 | 11.3 | 11 | 0.5058
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-15 | 250-PG-23003-06C02-PA CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20261 | Rope access | 2014-06-02 13:00 | 2014-06-02 15:00 | [36 empty] | 5.975 | CML-15 | CML: type TBC | 3 | 2046-10-03 | 2050-08-21 | 2014-06-02 13:00 | 2.5 | 0.08962 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-DC-57005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.4 | 6.1 | 6.6 | 0.5058
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1741 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.6 | CML-8 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 6 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.5 | 8.3 | 7.1 | 7.5 | 0.50332
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-2 | 80-CG-38459-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21532 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 14.6 | CML-2 | CML: Reducer | 6 | 2074-01-04 | 2073-09-17 | 2014-07-17 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 14.1 | 12 O'Clock | 100 | 8.56 | 100-PG-20056-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.6 |  | 14.1 | 14.5 | 14.5 | 15.3 | 0.50332
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-24 | 100-DH-56082-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 3392 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.4 | CML-24 | CML: type TBC | 3 | 2023-10-04 | 2024-02-06 | 2014-05-10 09:30 | 2.5 | 0.34013 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.9 | 6.5 | 6.5 | 5.7 | 0.50332
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-11 | 50-PL-23041-06C03 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10224 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 15.0333 | CML-11 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 0 | A4: Left Quadrant |  | 5.07 |  |  | 14.5 | 9 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  |  | 15.5 | 15.1 | 14.5 | 0.50332
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-4 | 150-PG-23043-06C02-P CML-4 | yes | FPSO 2016 | Pipe Wall Thickness | 24436 | Re-check as requested by N.Sequera | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.735mm/ yr | [35 empty] | 9.35 | CML-4 | CML: Elbow | 3 | 2021-12-09 | 2020-08-25 | 2016-07-02 07:00 | 4.7 | 0.73499 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.7 | 3 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | -2.3464 | 9.9 | 8.7 | 9.3 | 9.5 | 0.5
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-12 | 300-PG-20048-03C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21482 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | Check Corrosion Rate of 0.558mm/ yr | 38 | Kirstie Albone | 2017-03-23 12:46 | [32 empty] | 12.65 | CML-12 | CML: Pipe Length | 6 | 2018-11-05 | 2017-08-13 | 2014-06-28 09:30 | 3.3 | 2.0185 | A1: Outside Quadrant |  | 8.27 | 3.3 | 5.785 | 12.1 | 12 O'Clock | 200 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 12.1 | 12.5 | 13.3 | 12.7 | 0.5
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43303-01C02 | CML-4 | 50-FL-43303-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20460 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 6.25 | CML-4 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-FL-43303-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.9 | 6.1 | 6.3 | 5.7 | 0.5
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-18 | 50-CG-38452-09C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2262 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 7.75 | CML-18 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 7.2 | 9 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8.4 | 7.6 | 7.8 | 7.2 | 0.5
PW03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7717 |  | 2015-01-09 13:00 | 2015-01-09 15:00 |  |  | Administrator | 2015-09-08 09:32 | [32 empty] | 5.575 | CML-4 | CML: Pipe Length | 3 | 2027-10-19 | 2029-05-05 | 2015-01-09 13:00 | 2.5 | 0.21122 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.3787 | 5.7 | 5.2 | 6 | 5.4 | 0.35
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43151-01C02 | CML-4 | 80-FH-43151-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2238 |  | 2014-03-15 07:00 | 2014-03-15 17:00 | [36 empty] | 6.15 | CML-4 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 3 O'Clock | 80 | 5.49 | 80-FH-43151-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 5.5 | 6.7 | 6.1 | 0.5
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44004-01C02 | CML-11 | 250-PW-44004-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22755 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 5.95 | CML-11 | CML: Elbow | 3 | 2019-04-18 | 2019-04-02 | 2015-04-29 07:00 | 2.5 | 0.65432 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.1 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.93365 | 6.5 | 5.8 | 5.1 | 6.4 | 0.6455
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43119-01C02 | CML-6 | 80-FH-43119-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12833 |  | 2014-01-18 10:00 | 2014-01-18 11:30 | [36 empty] | 5.55 | CML-6 | CML: Elbow | 3 | 2019-10-25 | 2018-12-31 | 2014-01-18 10:00 | 0.54 | 0.77285 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5 | 3 O'Clock | 80 | 5.49 | 80-FH-43119-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.46 |  | 5.6 | 5 | 5.4 | 6.2 | 0.5
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-8 | 150-FH-43518-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5523 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 7.75 | CML-8 | CML: Pipe Length | 3 | 2066-11-16 | 2057-10-28 | 2014-06-01 07:00 | 1.23 | 0.10991 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 6 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 | -1.8043 | 8 | 8 | 7 | 8 | 0.5
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-10 | 150-PG-23506-25C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2784 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.55 | CML-10 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 22.3 | 9 O'Clock | 50 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.42 |  | 22.3 | 23.3 | 22.3 | 22.3 | 0.5
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-20 | 200-PG-23013-09C03-A CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 20004 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 20.45 | CML-20 | CML: type TBC | 6 | 2021-02-27 | 2019-07-10 | 2014-01-10 | 10.22 | 1.3421 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 19.8 | 12 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.58 |  | 19.8 | 20.4 | 20.6 | 21 | 0.5
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-16 | 250-PG-23003-06C02-PA CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 3232 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.05 | CML-16 | CML: type TBC | 3 | 2033-10-06 | 2035-12-13 | 2014-05-09 07:00 | 2.5 | 0.14929 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6 | 6.2 | 6.6 | 0.5
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20503-03C03-P | CML-2 | 50-PF-20503-03C03-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7743 |  | 2015-01-10 10:00 | 2015-01-10 12:00 | [36 empty] | 8.55 | CML-2 | CML: Elbow | 6 | 2025-05-20 | 2025-02-25 | 2015-01-10 10:00 | 2.5 | 0.52106 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 12 O'Clock | 50 | 8.74 | 50-PF-20503-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 9.1 | 8.7 | 8.5 | 0.5
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56451-01S01 | CML-5 | 25-DH-56451-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8072 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 7.65 | CML-5 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0 | A1: Outside Quadrant |  | 5.35 |  |  | 6.4 | 12 O'Clock | 25 | 6.35 | 25-DH-56451-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.4 | 7.4 | 9.5 | 7.3 | 1.3128
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56451-01S01 | CML-4 | 25-DH-56451-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8071 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 9.375 | CML-4 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0 | A4: Left Quadrant |  | 5.35 |  |  | 8.6 | 9 O'Clock | 25 | 6.35 | 25-DH-56451-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 9.5 | 10 | 9.4 | 8.6 | 0.57951
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56451-01S01 | CML-3 | 25-DH-56451-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8070 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 8.2 | CML-3 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0 | A1: Outside Quadrant |  | 5.35 |  |  | 6.4 | 12 O'Clock | 25 | 6.35 | 25-DH-56451-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.4 | 8 | 9.3 | 9.1 | 1.3292
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56451-01S01 | CML-2 | 25-DH-56451-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8069 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 7.375 | CML-2 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0.0912 | A1: Outside Quadrant |  | 5.35 |  |  | 6.2 | 12 O'Clock | 25 | 6.35 | 25-DH-56451-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.2 | 7.1 | 8.2 | 8 | 0.91788
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-21 | 400-FH-43508-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 6570 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.55 | CML-21 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 9 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.6 | 9 | 9.4 | 10.2 | 0.5
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-52 | 150-WC-40006-01C02 CML-52 |  | FPSO 2015 | Pipe Wall Thickness | 8976 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.65 | CML-52 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.9 | 5.4 | 5.4 | 0.28868
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56451-01S01 | CML-1 | 25-DH-56451-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8068 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 7.275 | CML-1 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0 | A2: Right Quadrant |  | 5.35 |  |  | 6.6 | 6 O'Clock | 25 | 6.35 | 25-DH-56451-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 7.8 | 6.6 | 6.6 | 8.1 | 0.78899
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-7 | 50-PW-44040-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23242 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.55 | CML-7 | CML: Elbow | 3 | 2026-10-31 | 2028-04-09 | 2015-05-11 07:00 | 2.5 | 0.22642 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | -0.089024 | 6.1 | 5.7 | 5.3 | 5.1 | 0.44347
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-10 | 80-CG-38486-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21419 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 17.75 | CML-10 | CML: Equal Tee | 6 | 2099-05-30 | 2086-05-30 | 2014-07-12 07:30 | 4.1 | 0 | A1: Outside Quadrant |  | 6.7 | 4.1 | 5.4 | 17.2 | 12 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.1 |  | 17.2 | 17.6 | 18.4 | 17.8 | 0.5
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 8792 | LAGGING REMOVAL REQUIRED | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.725 | CML-3 | CML: type TBC | 3 | 2020-05-05 | 2020-04-16 | 2015-02-15 09:30 | 2.5 | 0.55534 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 6 O'Clock | 200 | 6.35 | 200-PL-43307-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.6 | 5.4 | 6 | 0.27538
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56452-01S01 | CML-4 | 25-DH-56452-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8076 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 9.125 | CML-4 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0 | A2: Right Quadrant |  | 5.35 |  |  | 7.6 | 3 O'Clock | 25 | 6.35 | 25-DH-56452-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 9.4 | 7.6 | 9.5 | 10 | 1.05
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-FH-43507-01C02 | CML-12 | 100-FH-43507-01C02 CML-12 | Yes | FPSO 2013 | Pipe Wall Thickness | 10738 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 9.275 | CML-12 | CML: type TBC | 3 | 2034-04-13 | 2028-11-12 | 2013-11-19 | 2.5 | 0.29883 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PG-23063-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.8 | 9.4 | 8.6 | 9.3 | 0.49917
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56452-01S01 | CML-5 | 25-DH-56452-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8077 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 6.875 | CML-5 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0 | A3: Inside Quadrant |  | 5.35 |  |  | 6.5 | 6 O'Clock | 25 | 6.35 | 25-DH-56452-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.6 | 7.4 | 6.5 | 7 | 0.4113
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56452-01S01 | CML-3 | 25-DH-56452-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8075 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 8.025 | CML-3 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0 | A1: Outside Quadrant |  | 5.35 |  |  | 6.9 | 12 O'Clock | 25 | 6.35 | 25-DH-56452-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.9 | 7.5 | 9.8 | 7.9 | 1.2527
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56452-01S01 | CML-2 | 25-DH-56452-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8074 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 7.5 | CML-2 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0 | A1: Outside Quadrant |  | 5.35 |  |  | 6.6 | 12 O'Clock | 25 | 6.35 | 25-DH-56452-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.6 | 7.2 | 7.6 | 8.6 | 0.84063
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57008-01C02 | CML-4 | 80-DC-57008-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23276 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 6.475 | CML-4 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 12 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.1 | 6.7 | 7.2 | 0.5909
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-22 | 300-PG-20506-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 13236 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.125 | CML-22 | CML: type TBC | 6 | 2022-12-08 | 2021-03-22 | 2014-02-04 15:00 | 4.9 | 0.98361 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 9 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14.1 | 14.8 | 14 | 13.6 | 0.49917
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-21 | 25-FG-45455-01C02-E CML-21 |  | FPSO 2016 | Pipe Wall Thickness | 24366 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 9.375 | CML-21 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2016-06-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 6 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.3 | 9.8 | 8.7 | 9.7 | 0.49917
RP01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-DH-56452-01S01 | CML-1 | 25-DH-56452-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8073 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 6.975 | CML-1 | CML: type TBC | 1 |  |  | 2015-01-22 07:30 |  | 0 | A1: Outside Quadrant |  | 5.35 |  |  | 6.8 | 12 O'Clock | 25 | 6.35 | 25-DH-56452-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 6.8 | 7 | 7.2 | 6.9 | 0.17078
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-11 | 25-DO-62300-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 2438 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 5.85 | CML-11 | CML: Elbow | 3 | 2020-01-03 | 2019-12-16 | 2015-05-21 | 2.5 | 0.5838 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 3 O'Clock | 25 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.1 | 5.2 | 6 | 6.1 | 0.43589
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-7 | 25-DO-62300-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 2434 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 5.725 | CML-7 | CML: Pipe Length | 3 | 2020-01-03 | 2019-12-16 | 2015-05-21 | 2.5 | 0.5838 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 3 O'Clock | 25 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.2 | 6 | 6 | 0.37749
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-12 | 25-DO-62300-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 2439 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 5.875 | CML-12 | CML: Elbow | 3 | 2020-08-19 | 2020-07-31 | 2015-05-21 | 2.5 | 0.53303 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 6 O'Clock | 25 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.1 | 6.1 | 5.3 | 6 | 0.38622
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-9 | 25-DO-62300-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 2436 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 5.7 | CML-9 | CML: Pipe Length | 3 | 2020-08-19 | 2020-07-31 | 2015-05-21 | 2.5 | 0.53303 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 12 O'Clock | 25 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.9 | 5.8 | 5.8 | 0.2708
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-8 | 250-DC-57064-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23094 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.225 | CML-8 | CML: Pipe Length | 3 | 2029-12-08 | 2029-10-25 | 2015-05-07 07:00 | 2.5 | 0.23288 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 6 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | -0.35096 | 6.4 | 6.4 | 5.9 | 6.2 | 0.23629
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-7 | 300-PG-23001-03C03 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10957 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 13.875 | CML-7 | CML: Pipe Length | 6 | 2018-07-22 | 2017-09-09 | 2014-01-09 | 5.22 | 1.7592 | A4: Left Quadrant |  | 8.27 | 5.22 | 6.745 | 13.2 | 9 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.98 |  | 14.3 | 13.8 | 14.2 | 13.2 | 0.49917
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-8 | 25-DO-62300-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 2435 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 5.475 | CML-8 | CML: Pipe Length | 3 | 2020-08-19 | 2020-07-31 | 2015-05-21 | 2.5 | 0.53303 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.3 | 12 O'Clock | 25 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.8 | 5.4 | 5.4 | 0.22174
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-6 | 25-DO-62300-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 2433 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 5.925 | CML-6 | CML: Reducer | 3 | 2022-05-01 | 2022-04-07 | 2015-05-21 | 2.5 | 0.4315 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 3 O'Clock | 40 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.2 | 5.5 | 6.4 | 5.6 | 0.44253
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-12 | 50-PW-44040-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23247 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.475 | CML-12 | CML: Equal Tee | 3 | 2026-10-31 | 2028-04-09 | 2015-05-11 07:00 | 2.5 | 0.22642 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.3561 | 5.4 | 5.4 | 6 | 5.1 | 0.37749
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40503-1CG | CML-2 | 150-WC-40503-1CG CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8631 | Rope Access / Material Class Not Selectable. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-02-10 09:30 | 2015-02-10 10:30 |  |  | Administrator | 2015-09-08 12:45 | [32 empty] | 11.525 | CML-2 | CML: Pipe Length | 3 | 2066-08-12 | 2049-06-08 | 2015-02-10 09:30 | 2.5 | 0.15911 | A3: Inside Quadrant |  | 7.97 | 2.5 | 5.235 | 10.7 | 6 O'Clock | 150 | 10.97 | 150-WC-40503-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11.7 | 11.7 | 10.7 | 12 | 0.56789
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1540 |  | 2014-04-06 16:30 | 2014-04-06 17:00 | [36 empty] | 7.625 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40029-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.3 | 8.3 | 7.2 | 7.7 | 0.49917
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-10 | 25-DO-62300-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 2437 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 5.95 | CML-10 | CML: Elbow | 3 | 2027-03-13 | 2027-02-04 | 2015-05-21 | 2.5 | 0.27921 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 25 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 5.9 | 6.1 | 5.8 | 6 | 0.1291
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 876 |  | 2014-04-06 16:30 | 2014-04-06 17:00 | [36 empty] | 7.625 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-06 16:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40029-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.3 | 8.3 | 7.2 | 7.7 | 0.49917
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71324-01K01 | CML-2 | 80-WF-71324-01K01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5955 |  | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 6.25 | CML-2 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 5.9 | 6 O'Clock | 80 | 2.5 | 80-WF-71324-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 6 | 5.9 | 6.7 | 0.36968
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71310-01K01 | CML-3 | 80-WF-71310-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5488 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 5.95 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 5.9 | 9 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 5.9 | 6 | 5.9 | 0.057735
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-16 | 50-GN-67002-01E01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 9075 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 6.575 | CML-16 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 6.7 | 7.1 | 5.9 | 0.49917
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-24 | 50-AU-63015-01E01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 9055 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6.025 | CML-24 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6.2 | 5.9 | 6 | 0.12583
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-16 | 50-AU-63015-01E01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 9047 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6.4 | CML-16 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 6.2 | 6.8 | 5.9 | 0.42426
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-15 | 50-AU-63015-01E01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 9046 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6 | CML-15 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.3 | 5.9 | 5.9 | 5.9 | 0.2
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-37 | 50-AI-63004-01E01 CML-37 |  | FPSO 2015 | Pipe Wall Thickness | 9028 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.125 | CML-37 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 5.9 | 6.6 | 6.1 | 0.3304
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-35 | 50-AI-63004-01E01 CML-35 |  | FPSO 2015 | Pipe Wall Thickness | 9026 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.05 | CML-35 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.1 | 6 | 5.9 | 0.1291
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-33 | 50-AI-63004-01E01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 9024 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.95 | CML-33 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 5.9 | 6 | 0.057735
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-30 | 50-AI-63004-01E01 CML-30 |  | FPSO 2015 | Pipe Wall Thickness | 9021 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.025 | CML-30 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 6.1 | 5.9 | 6 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-26 | 50-AI-63004-01E01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 9017 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.25 | CML-26 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 6.5 | 5.9 | 5.9 | 0.41231
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-22 | 50-AI-63004-01E01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 9013 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.125 | CML-22 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6.5 | 5.9 | 6.1 | 0.263
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-21 | 50-AI-63004-01E01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 9012 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.075 | CML-21 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.5 | 5.9 | 5.9 | 6 | 0.28723
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-25 | 100-DH-56082-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 3393 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 8.125 | CML-25 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.7 | 3 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.8 | 7.7 | 8.8 | 8.2 | 0.49917
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67011-01E01 | CML-5 | 50-GN-67011-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8763 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 6.05 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 6 | 5.9 | 6.2 | 0.1291
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-13 | 50-GN-67004-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8618 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6.175 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-09 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.5 | 6.2 | 6.1 | 0.25
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-1 | 50-GN-67004-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8606 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6.05 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-09 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 5.9 | 6.1 | 6.1 | 0.1
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63038-01E01 | CML-6 | 50-AI-63038-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8572 |  | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.175 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-AI-63038-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.2 | 5.9 | 6.4 | 0.20616
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63038-01E01 | CML-4 | 50-AI-63038-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8570 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.075 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-AI-63038-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.3 | 6.1 | 5.9 | 6 | 0.17078
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-4 | 25-DO-62300-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 2431 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 6.85 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-21 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 3 O'Clock | 40 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 6.5 | 7.2 | 6.7 | 0.31091
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-11 | 50-AI-63009-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8533 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.275 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 6.2 | 7 | 0.49917
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-12 | 50-AI-63009-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8534 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.15 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 6.1 | 6 | 5.9 | 0.31091
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67003-01E01 | CML-3 | 50-GN-67003-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8498 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.225 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-GN-67003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 5.9 | 6.6 | 6.4 | 0.3304
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63020-01E01 | CML-3 | 50-AU-63020-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8483 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.375 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-AU-63020-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 5.9 | 6.7 | 6.5 | 0.34034
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67007-01E01 | CML-2 | 50-GN-67007-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8473 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.1 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-GN-67007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 5.9 | 6.4 | 6.2 | 0.24495
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67008-01E01 | CML-2 | 50-GN-67008-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8464 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 5.975 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-GN-67008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 5.9 | 6 | 6 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63021-01E01 | CML-6 | 50-AU-63021-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8448 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.4 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-AU-63021-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.7 | 6.5 | 6.5 | 0.34641
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63021-01E01 | CML-3 | 50-AU-63021-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8445 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.375 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-AU-63021-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.6 | 6 | 7 | 0.51881
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63022-01E01 | CML-3 | 50-AU-63022-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8441 |  | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.25 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-AU-63022-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 6.7 | 5.9 | 6 | 0.36968
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40406-01C02 | CML-2 | 50-WC-40406-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8434 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 6.05 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-WC-40406-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 5.9 | 6.2 | 5.9 | 0.17321
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63037-01E01 | CML-5 | 50-AI-63037-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8401 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 5.9 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-AI-63037-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 5.9 | 5.9 | 5.9 | 0
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23411-03C02-P | CML-2 | 50-PG-23411-03C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8386 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.175 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.1 | 6.7 | 6 | 0.3594
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63030-01E01 | CML-6 | 50-AI-63030-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8347 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.25 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-AI-63030-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.5 | 5.9 | 6.7 | 5.9 | 0.41231
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63030-01E01 | CML-5 | 50-AI-63030-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8346 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.15 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-AI-63030-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.4 | 6.4 | 5.9 | 0.28868
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63040-01E01 | CML-3 | 50-AI-63040-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8319 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.15 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-AI-63040-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.5 | 6.1 | 6.1 | 0.25166
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63001-01E01 | CML-7 | 50-AI-63001-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8314 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.3 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-AI-63001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 5.9 | 6.2 | 6.7 | 0.33665
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63013-01E01 | CML-3 | 50-AI-63013-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8302 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.35 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-AI-63013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 6.7 | 6.4 | 5.9 | 0.33166
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-20 | 50-WD-53010-01E01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 8263 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.925 | CML-20 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 5.9 | 5.9 | 5.9 | 0.05
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53015-01E01 | CML-7 | 50-WD-53015-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8233 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.15 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.1 | 6.2 | 6.4 | 0.20817
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53015-01E01 | CML-2 | 50-WD-53015-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8228 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 5.95 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-WD-53015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6 | 5.9 | 5.9 | 0.057735
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53012-01E01 | CML-7 | 50-WD-53012-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8215 | Reducing Hose Coupling | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.275 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-WD-53012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.7 | 6.5 | 6 | 0.38622
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53016-01E01 | CML-5 | 50-WD-53016-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8206 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.125 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-WD-53016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6.3 | 6.3 | 5.9 | 0.20616
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69006-01S01 | CML-3 | 50-OL-69006-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8192 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.875 | CML-3 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 8.1 | 7 | 6.5 | 0.93229
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-3 | 25-DO-62300-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 2430 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 6.9 | CML-3 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2015-05-21 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 3 O'Clock | 40 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 6.6 | 7 | 7 | 0.2
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53008-01E01 | CML-8 | 50-WD-53008-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8173 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.125 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-WD-53008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 6 | 6 | 5.9 | 0.32016
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-11 | 50-WD-53007-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8150 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.35 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 5.9 | 6.2 | 6.6 | 0.36968
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-11 | 100-OL-69002-01S01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8132 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.325 | CML-11 | CML: type TBC | 1 | 2061-09-15 | 2049-08-01 | 2015-01-23 07:30 | 2.5 | 0.07284 | A2: Right Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.9 | 3 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 5.9 | 6 | 6.7 | 0.43493
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-5 | 100-OL-69002-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8126 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.325 | CML-5 | CML: type TBC | 1 | 2061-09-15 | 2049-08-01 | 2015-01-23 07:30 | 2.5 | 0.07284 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.9 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.5 | 6.5 | 6.4 | 0.28723
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-1 | 100-OL-69002-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8122 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.5 | CML-1 | CML: type TBC | 1 | 2061-09-15 | 2049-08-01 | 2015-01-23 07:30 | 2.5 | 0.07284 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.9 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.6 | 7 | 6.5 | 0.45461
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-19 | 100-OL-69001-01S01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8121 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.175 | CML-19 | CML: type TBC | 1 | 2061-09-15 | 2049-08-01 | 2015-01-23 07:30 | 2.5 | 0.07284 | A3: Inside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.3 | 6.6 | 5.9 | 5.9 | 0.34034
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-15 | 100-OL-69001-01S01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8117 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.725 | CML-15 | CML: type TBC | 1 | 2061-09-15 | 2049-08-01 | 2015-01-23 07:30 | 2.5 | 0.07284 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.9 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.9 | 7.5 | 6.6 | 0.66521
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-13 | 100-OL-69001-01S01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8115 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.6 | CML-13 | CML: type TBC | 1 | 2061-09-15 | 2049-08-01 | 2015-01-23 07:30 | 2.5 | 0.07284 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.9 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.8 | 6.8 | 6.9 | 0.46904
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-9 | 100-OL-69001-01S01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8111 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.15 | CML-9 | CML: type TBC | 1 | 2061-09-15 | 2049-08-01 | 2015-01-23 07:30 | 2.5 | 0.07284 | A4: Left Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6.5 | 6.2 | 5.9 | 0.26458
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-7 | 100-OL-69001-01S01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8109 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.8 | CML-7 | CML: type TBC | 1 | 2061-09-15 | 2049-08-01 | 2015-01-23 07:30 | 2.5 | 0.07284 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.9 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 7.4 | 7.2 | 6.7 | 0.66833
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-2 | 100-OL-69001-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8104 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.2 | CML-2 | CML: type TBC | 1 | 2061-09-15 | 2049-08-01 | 2015-01-23 07:30 | 2.5 | 0.07284 | A3: Inside Quadrant |  | 5.02 | 2.5 | 3.3838 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.5 | 6 | 5.9 | 6.4 | 0.29439
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69004-01S01 | CML-7 | 80-OL-69004-01S01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8098 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.3 | CML-7 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 5.9 | 12 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.3 | 6.5 | 6.5 | 0.28284
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69003-01S01 | CML-11 | 80-OL-69003-01S01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8089 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 5.95 | CML-11 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 5.9 | 9 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 6 | 5.9 | 0.057735
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-1 | 25-DO-62300-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 2428 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 7.15 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-21 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 6 O'Clock | 40 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7.3 | 7 | 7.2 | 0.1291
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-2 | 25-DO-62300-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 2429 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 8.6 | CML-2 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-21 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 12 O'Clock | 40 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.4 | 8.5 | 9.2 | 0.40825
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-9 | 200-PW-44018-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23281 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.55 | CML-9 | CML: Elbow | 3 | 2033-06-19 | 2035-10-20 | 2015-05-12 07:00 | 2.5 | 0.14902 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6 | 5.6 | 5.4 | 0.34157
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-11 | 80-CG-38459-09C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23708 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | Check Corrosion Rate of 0.762mm/ yr | [35 empty] | 5.975 | CML-11 | CML: Elbow | 3 | 2051-05-21 | 2055-10-22 | 2015-10-30 07:00 | 2.5 | 0.07869 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 40 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.3 | 5.3 | 5.9 | 6.4 | 0.49917
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20013-01C02-P | CML-2 | 200-PL-20013-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21212 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 6.725 | CML-2 | CML: Fitting | 3 | 2099-06-30 | 2098-11-12 | 2014-07-14 07:30 | 2.5 | 0.0447 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 9 O'Clock | 200 | 6.35 | 200-PL-20013-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.6 | 7.4 | 6.6 | 6.3 | 0.4717
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-14 | 50-DH-56062-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 9101 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.125 | CML-14 | CML: type TBC | 3 | 2019-01-28 | 2019-09-07 | 2015-03-02 07:00 | 2.5 | 0.53669 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.8 | 5.1 | 5 | 0.49917
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57300-01C02 | CML-5 | 50-DC-57300-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20295 | Reviewed on 24/11/14. FFS. Repeat | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 6.05 | CML-5 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-10-17 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-DC-57300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.1 | 6 | 6.2 | 0.1291
PW03 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 200-PW-44018-01X01 | CML-9 | 200-PW-44018-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8614 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.575 | CML-9 | CML: type TBC | 3 | 2028-07-20 | 2030-03-05 | 2015-02-09 07:30 | 2.5 | 0.20071 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.9 | 5.8 | 0.3304
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3177 | Rope Access | 2014-05-07 13:00 | 2014-05-07 14:00 | [36 empty] | 7.625 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 3 O'Clock | 50 | 5.54 | 50-DH-56052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8 | 7.1 | 8.1 | 7.3 | 0.49917
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-5 | 25-DO-62300-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 2432 |  | 2015-05-21 | 2015-05-21 | [36 empty] | 11.125 | CML-5 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-21 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.1 | 12 O'Clock | 40 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.1 | 10.9 | 11.4 | 12.1 | 0.84212
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20129 | Rope Access | 2014-05-07 13:00 | 2014-05-07 14:00 | [36 empty] | 7.625 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 3 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 | -3253.7135 | 8 | 7.1 | 8.1 | 7.3 | 0.49917
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-12 | 200-FH-43003-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12535 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.625 | CML-12 | CML: Pipe Length | 3 | 2026-02-11 | 2024-07-28 | 2014-01-18 11:30 | 1.34 | 0.3942 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.1 | 9 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 7.1 | 7 | 6.3 | 6.1 | 0.49917
FL02 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FL-43454-01C02-P | CML-2 | 50-FL-43454-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21447 | Protective mesh removed | 2014-06-29 07:00 | 2014-06-29 08:00 | [36 empty] | 7.975 | CML-2 | CML: Reducing Tee | 1 | 2077-07-06 | 2050-06-18 | 2014-06-29 07:00 | 0.7 | 0 | A4: Left Quadrant |  | 6.11 | 0.7 | 3.405 | 7.3 | 9 O'Clock | 150 | 7.11 | 150-PG-20043-01D01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 8 | 8.5 | 8.1 | 7.3 | 0.49917
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-15 | 150-PG-20054-01C03-P CML-15 | Yes | FPSO 2015 | Pipe Wall Thickness | 23353 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 7.425 | CML-15 | CML: Elbow | 6 | 2017-11-08 | 2017-03-17 | 2015-07-20 07:00 | 2.5 | 1.9063 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 6.9 | 12 O'Clock | 100 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 | 0.093891 | 6.9 | 7.1 | 7.8 | 7.9 | 0.49917
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-14 | 50-CG-38465-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20877 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 6.875 | CML-14 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-04 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 80 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.5 | 7 | 7.1 | 5.9 | 0.68496
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38462-01C02 | CML-1 | 50-CG-38462-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20829 | Reviewed on 20/11/14. FFS. This line has not been RBI assessed. CML to be rechecked Oct. 18 based on other line on this circuit which are a 48m interval | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 15:37 | [32 empty] | 6.375 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 20 | 5.54 | 50-CG-38462-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.3 | 5.9 | 6.1 | 6.2 | 0.62915
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62300-01C02 | CML-13 | 25-DO-62300-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 2440 | Does not exist on site | 2015-05-21 | 2015-05-21 | [37 empty] | CML-13 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-21 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-DO-62300-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56130-01C02 | CML-8 | 50-DH-56130-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21060 | Rope Access | 2014-05-15 13:00 | 2014-05-15 14:00 | [36 empty] | 5.425 | CML-8 | CML: type TBC | 3 | 2018-10-15 | 2019-05-13 | 2014-05-15 13:00 | 2.5 | 0.5655 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DH-56130-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5 | 5.5 | 6.1 | 0.49917
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23405-03C02-P | CML-9 | 100-PG-23405-03C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 23861 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.425 | CML-9 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A1: Outside Quadrant |  |  | 2.7 |  | 6.1 | 12 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 6.6 | 6.7 | 6.3 | 0.27538
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23405-03C02-P | CML-2 | 100-PG-23405-03C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 23854 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.425 | CML-2 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A4: Left Quadrant |  |  | 2.7 |  | 6.1 | 9 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 6.5 | 6.5 | 6.1 | 0.22174
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-15 | 150-FG-45505-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 22355 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 26.4 | CML-15 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.1 | 8.6 | 7.5 | 8.5 | 0.49917
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56012-01C02 | CML-4 | 80-DH-56012-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3470 | Rope Access | 2014-05-13 10:30 | 2014-05-13 12:00 | [36 empty] | 5.075 | CML-4 | CML: type TBC | 3 | 2017-01-02 | 2017-06-03 | 2014-05-13 10:30 | 2.5 | 0.83233 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 9 O'Clock | 80 | 5.49 | 80-DH-56012-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 4.8 | 5.8 | 4.7 | 0.49917
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-9 | 300-FL-43080-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2388 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 7.075 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.8 | 6.8 | 7 | 0.49917
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-13 | 200-PL-20019-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21264 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.775 | CML-13 | CML: Elbow | 3 | 2115-12-08 | 2115-03-09 | 2014-09-30 07:00 | 2.5 | 0.03753 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.8 | 6.8 | 6.3 | 7.2 | 0.36856
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-8 | 150-WC-40006-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8999 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.8 | CML-8 | CML: type TBC | 3 | 2051-04-21 | 2055-05-15 | 2015-02-28 07:00 | 2.5 | 0.08018 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.9 | 5.9 | 5.4 | 0.2708
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56141-01C02 | CML-2 | 50-DH-56141-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21069 | Rope Access | 2014-05-15 08:00 | 2014-05-15 09:00 | [36 empty] | 4.775 | CML-2 | CML: type TBC | 3 |  |  | 2014-05-15 08:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 4.3 | 3 O'Clock | 80 |  | 80-DH-56141-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 5.3 | 4.3 | 5.1 | 4.4 | 0.49917
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-5 | 80-FL-43015-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22948 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.275 | CML-5 | CML: Elbow | 3 | 2021-09-21 | 2022-09-09 | 2015-05-02 07:00 | 2.5 | 0.35964 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 6 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 | 0.70192 | 4.9 | 5.8 | 4.8 | 5.6 | 0.49917
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-7 | 100-DH-56086-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20966 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 8.875 | CML-7 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.5 | 12 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 8.6 | 8.8 | 9.6 | 0.49917
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-11 | 100-PG-23503-03C03-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2727 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 11.175 | CML-11 | CML: Pipe Length | 6 | 2020-03-13 | 2020-07-11 | 2014-03-13 09:00 | 5.66 | 0.80578 | A3: Inside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.5 | 6 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.84 |  | 11.2 | 11.3 | 10.5 | 11.7 | 0.49917
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-13 | 300-PG-20506-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 13227 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 13.825 | CML-13 | CML: type TBC | 6 | 2019-12-28 | 2018-10-22 | 2014-02-04 15:00 | 4.9 | 1.424 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.3 | 9 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 13.7 | 14.5 | 13.8 | 13.3 | 0.49917
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45305-03C02 | CML-4 | 100-FG-45305-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22080 | Rope Access | 2014-05-25 09:30 | 2014-05-25 10:30 | [36 empty] | 6.175 | CML-4 | CML: type TBC | 3 | 2042-03-13 | 2040-01-27 | 2014-05-25 09:30 | 2.5 | 0.12221 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-FG-45305-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.5 | 5.9 | 6.4 | 0.32016
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45305-03C02 | CML-2 | 100-FG-45305-03C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22078 | Rope Access | 2014-05-25 09:30 | 2014-05-25 10:30 | [36 empty] | 6.025 | CML-2 | CML: type TBC | 3 | 2042-03-13 | 2040-01-27 | 2014-05-25 09:30 | 2.5 | 0.12221 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.76 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-FG-45305-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.3 | 5.9 | 5.9 | 6 | 0.1893
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-20 | 100-FG-45304-03C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 22076 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6 | CML-20 | CML: type TBC | 3 | 2042-03-10 | 2040-01-24 | 2014-05-25 07:00 | 2.5 | 0.12225 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.76 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 6 | 6 | 5.9 | 0.08165
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-5 | 25-DO-62301-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 2544 | 2off CML''s at 6 & 9 O''clock too corroded to take readings. Refer to photo in the GVI | 2015-05-22 | 2015-05-22 | [36 empty] | 6.05 | CML-5 | CML: Elbow | 3 | 2030-04-13 | 2030-02-27 | 2015-05-22 | 2.5 | 0.22812 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.2 |  |  | 0.21213
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-11 | 25-DO-62301-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 2550 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.15 | CML-11 | CML: Elbow | 3 | 2035-02-06 | 2034-12-10 | 2015-05-22 | 2.5 | 0.17743 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.5 | 6.1 | 0.23805
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20027-03C03-P | CML-2 | 80-PG-20027-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21325 | Protective mesh removed | 2014-06-27 09:30 | 2014-06-27 10:30 | [36 empty] | 12.675 | CML-2 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2014-06-27 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 12 | 9 O'Clock | 80 | 11.13 | 80-PG-20027-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.7 | 13.2 | 12.8 | 12 | 0.49917
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-11 | 80-CG-38459-09C02-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22773 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 18.025 | CML-11 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2015-04-29 07:00 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.5 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.6 | -4.1253 | 18 | 17.9 | 17.5 | 18.7 | 0.49917
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-7 | 250-PG-20036-01C03-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23395 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 8.025 | CML-7 | CML: Elbow | 6 | 2022-01-28 | 2021-08-01 | 2015-07-21 07:00 | 2.5 | 0.78118 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 7.6 | 9 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | 0.78499 | 7.7 | 8.7 | 8.1 | 7.6 | 0.49917
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23742 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.075 | CML-2 | CML: Elbow | 3 | 2057-09-12 | 2046-03-15 | 2015-10-30 07:00 | 2.5 | 0.14082 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 12 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.4 | 9.1 | 9.2 | 9.6 | 0.49917
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-20 | 300-PF-20003-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21758 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.475 | CML-20 | CML: Fitting | 6 | 2040-01-05 | 2035-03-25 | 2014-10-01 07:00 | 4.9 | 0.35205 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 15 | 14.5 | 14.6 | 13.8 | 0.49917
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-5 | 250-PG-23005-06C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10051 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 16.575 | CML-5 | CML: Elbow | 6 | 2015-03-09 | 2014-11-07 | 2013-11-06 | 8.6 | 5.4519 | A1: Outside Quadrant |  | 12.26 | 8.6 | 10.43 | 15.9 | 12 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 15.9 | 17 | 16.5 | 16.9 | 0.49917
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-8 | 250-PG-23004-06C03-A CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23375 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 37.125 | CML-8 | CML: Pipe Length | 6 | 2359-02-25 | 2293-02-06 | 2015-07-21 07:00 | 8.55 | 0.02807 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.2 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.65 | 0.65687 | 19.3 | 18.4 | 18.2 | 18.9 | 0.49666
DH01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-DH-56137-01C02 | CML-4 | 50-DH-56137-01C02 CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24304 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 17.3 | CML-4 | CML: Reducing Tee | 3 | 2054-10-24 | 2049-02-10 | 2016-05-27 07:00 | 1.88 | 0 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 16.7 | 3 O'Clock | 40 | 6.02 | 100-FG-45008-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.82 |  | 17.6 | 16.7 | 17.1 | 17.8 | 0.49666
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-13 | 150-WC-40006-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7978 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:10 | [32 empty] | 5.65 | CML-13 | CML: Elbow | 3 | 2067-08-31 | 2073-12-25 | 2015-01-18 10:30 | 2.5 | 0.05508 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.5 | 5.7 | 5.4 | 0.26458
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20053-01C03-P | CML-2 | 80-PG-20053-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21509 | Protective mesh removed | 2014-06-29 08:00 | 2014-06-29 09:00 | [36 empty] | 11.8 | CML-2 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2014-06-29 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 11.2 | 6 O'Clock | 80 | 11.13 | 80-PG-20053-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 12.4 | 11.9 | 11.2 | 11.7 | 0.49666
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40512-1CG | CML-5 | 150-WC-40512-1CG CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5478 | Rope Access | 2014-05-28 10:00 | 2014-05-28 11:30 | [36 empty] | 11.15 | CML-5 | CML: Straight | 3 | 2062-09-19 | 2046-10-18 | 2014-05-28 10:00 | 2.5 | 0.17169 | A2: Right Quadrant |  | 7.97 | 2.5 | 5.235 | 10.8 | 3 O'Clock | 150 | 10.97 | 150-WC-40512-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.3 | 10.8 | 10.9 | 11.6 | 0.36968
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38477-01C02-P | CML-12 | 50-CG-38477-01C02-P CML-12 | no | FPSO 2015 | Pipe Wall Thickness | 23413 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 17.9 | CML-12 | CML: Pipe Length | 3 | 2023-11-11 | 2022-05-15 | 2015-07-22 07:00 | 14.06 | 0.40177 | A4: Left Quadrant |  | 15.26 | 14.06 | 14.66 | 17.4 | 9 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.34 | -0.35012 | 18.1 | 17.6 | 18.5 | 17.4 | 0.49666
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7824 |  | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:44 | [32 empty] | 5.475 | CML-1 | CML: Reducer | 3 | 2027-11-24 | 2029-06-13 | 2015-01-13 13:00 | 2.5 | 0.20979 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.7 | 5.8 | 5.2 | 0.32016
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-19 | 200-FH-43025-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2492 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 7.4 | CML-19 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 3 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.7 | 6.8 | 7.2 | 7.9 | 0.49666
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43029-01C02 | CML-1 | 400-FH-43029-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10017 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.7 | CML-1 | CML: Pipe Length | 3 | 2016-08-22 | 2016-03-18 | 2013-11-04 | 2.48 | 1.6846 | A1: Outside Quadrant |  | 4.92 | 2.48 | 3.205 | 7.2 | 12 O'Clock | 400 | 7.92 | 400-FH-43029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.72 |  | 7.2 | 7.9 | 7.4 | 8.3 | 0.49666
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56112-01C02 | CML-2 | 50-DH-56112-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21013 | Rope Access | 2014-05-19 14:00 | 2014-07-20 15:00 | [36 empty] | 5.4 | CML-2 | CML: type TBC | 3 | 2017-05-19 | 2017-10-21 | 2014-05-19 14:00 | 2.5 | 0.76606 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56112-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.3 | 5.5 | 6 | 0.49666
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-10 | 100-PW-20021-01C02-P CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22828 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.6 | CML-10 | CML: Elbow | 3 | 2020-09-23 | 2020-12-20 | 2015-04-30 07:00 | 2.5 | 0.48089 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.54478 | 5.7 | 6 | 5.1 | 5.6 | 0.37417
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20014-01C02-P | CML-5 | 200-PL-20014-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21224 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 6.475 | CML-5 | CML: Fitting | 3 | 2099-09-15 | 2099-01-27 | 2014-07-15 07:30 | 2.5 | 0.04459 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 6 O'Clock | 200 | 6.35 | 200-PL-20014-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.3 | 6.3 | 6.6 | 0.20616
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-8 | 50-CG-38001-09C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10921 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.3 | CML-8 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.7176 | A2: Right Quadrant |  | 5.74 |  |  | 7.7 | 3 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.7 | 8.9 | 7.7 | 8.2 | 8.4 | 0.49666
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56120-01C02 | CML-1 | 50-DH-56120-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21033 | Rope Access | 2014-05-19 08:00 | 2014-05-19 09:00 | [36 empty] | 5.4 | CML-1 | CML: type TBC | 3 | 2018-11-05 | 2019-06-06 | 2014-05-19 08:00 | 2.5 | 0.55941 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-DH-56120-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.1 | 5 | 5.4 | 5.1 | 0.49666
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-7 | 100-DH-56082-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 3375 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 5.6 | CML-7 | CML: type TBC | 3 | 2016-08-29 | 2016-10-07 | 2014-05-10 09:30 | 2.5 | 1.0842 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 6.1 | 5.9 | 5.4 | 0.49666
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43104-01C02 | CML-9 | 100-FH-43104-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12760 |  | 2014-01-25 07:00 | 2014-01-25 09:00 | [36 empty] | 5.7 | CML-9 | CML: type TBC | 3 | 2015-09-01 | 2015-09-28 | 2014-01-25 07:00 | 2.5 | 1.5624 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 12 O'Clock | 100 | 6.02 | 100-FH-43104-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.7 | 6.1 | 6 | 0.49666
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-6 | 80-PW-44034-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23083 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.5 | CML-6 | CML: Elbow | 3 | 2028-03-21 | 2029-12-10 | 2015-05-07 07:00 | 2.5 | 0.20183 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 3 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 2.3146 | 5.4 | 5.1 | 5.5 | 6 | 0.37417
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-3 | 50-DO-62002-01S01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2988 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.2 | CML-3 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 6.5 | 5.9 | 6 | 0.29439
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-3 | 50-DO-62002-01S01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22267 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.2 | CML-3 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.4 | 6.5 | 5.9 | 6 | 0.29439
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-9 | 200-PL-20019-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23480 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 6.5 | CML-9 | CML: Fitting | 3 | 2178-07-19 | 2177-05-04 | 2015-07-24 07:00 | 2.5 | 0.0233 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 | -0.36869 | 6.3 | 6.5 |  | 6.7 | 0.2
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-3 | 150-FH-43518-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2703 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.7 | CML-3 | CML: Elbow | 3 | 2055-01-13 | 2047-12-27 | 2014-03-12 09:00 | 1.23 | 0.14119 | A2: Right Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 3 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 | 0 | 8 | 7 | 8.1 | 7.7 | 0.49666
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-3 | 150-FH-43518-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 342 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.7 | CML-3 | CML: Elbow | 3 | 2054-12-24 | 2047-12-10 | 2014-03-12 | 1.23 | 0.14137 | A2: Right Quadrant |  | 4.11 | 1.23 | 2.2256 | 7 | 3 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 |  | 8 | 7 | 8.1 | 7.7 | 0.49666
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-17 | 250-PW-20022-01C03-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2060 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.875 | CML-17 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.7 | 6 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 11.7 | 10.4 | 9.7 | 11.7 | 0.99457
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-28 | 300-PW-44003-01C03 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 22893 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.2 | CML-28 | CML: Pipe Length | 6 | 2037-12-05 | 2035-02-01 | 2015-05-01 07:00 | 2.5 | 0.31839 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 | -0.18814 | 11.3 | 10 | 9.7 | 9.8 | 0.74386
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-21 | 100-DC-57036-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 1427 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 6.6 | CML-21 | CML: type TBC | 3 | 2038-05-02 | 2039-02-27 | 2014-04-07 07:00 | 2.5 | 0.14116 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 3 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 5.9 | 7.4 | 7.2 | 0.8124
DN01 | Montara_Topside | No | Open Drain (56) | Pipework | 50-DN-56101-01C02 | CML-1 | 50-DN-56101-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 841 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 6.225 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-02 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.2 | 6.6 | 5.9 | 0.28723
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-12 | 250-PW-20022-01C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2055 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.6 | CML-12 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.7 | 6 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 11 | 11.3 | 9.7 | 10.4 | 0.70711
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-17 | 300-PF-20501-03C03-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23531 | Re-check | 2015-07-29 07:00 | 2015-07-29 12:00 | [36 empty] | 13.9 | CML-17 | CML: Elbow | 6 | 2036-08-28 | 2032-06-24 | 2015-07-29 07:00 | 4.9 | 0.40283 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 | -0.12007 | 14.1 | 13.4 | 13.6 | 14.5 | 0.49666
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8995 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.45 | CML-4 | CML: type TBC | 3 | 2029-01-06 | 2030-09-09 | 2015-02-28 07:00 | 2.5 | 0.19473 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.9 | 5.3 | 5.4 | 0.31091
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-8 | 250-PL-20006-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 13178 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.55 | CML-8 | CML: Pipe Length | 3 | 2062-11-10 | 2062-07-01 | 2014-01-21 13:00 | 2.5 | 0.07781 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.7 | 6.7 | 6.5 | 0.19149
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57043-01C02 | CML-8 | 50-DC-57043-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2153 | Rope Access | 2014-03-29 13:00 | 2014-03-29 15:00 | [36 empty] | 6.025 | CML-8 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-03-29 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-DC-57043-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 5.9 | 6 | 6.1 | 0.095743
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-9 | 50-DC-57025-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2120 |  | 2014-03-29 07:00 | 2014-03-29 08:00 | [36 empty] | 6.125 | CML-9 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-29 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6 | 6.1 | 6.5 | 5.9 | 0.263
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5659 | Rope access | 2014-06-21 11:00 | 2014-06-21 12:00 | [36 empty] | 7.5 | CML-2 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-21 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 3 O'Clock | 200 | 6.35 | 200-FH-43503-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.5 | 7.1 | 8.2 | 7.2 | 0.49666
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-7 | 25-DO-62301-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 2546 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.075 | CML-7 | CML: Elbow | 3 | 2035-02-06 | 2034-12-10 | 2015-05-22 | 2.5 | 0.17743 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.1 | 6.2 | 0.095743
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-8 | 50-WC-40071-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1943 | Rope Access. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Mar. 2020). RBI to be updated | 2014-03-26 09:30 | 2014-03-26 10:30 |  |  | Administrator | 2015-09-08 12:57 | [32 empty] | 6.525 | CML-8 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 7.7 | 6.5 | 5.9 | 6 | 0.82614
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-13 | 25-DO-62301-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 2552 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.375 | CML-13 | CML: Elbow | 3 | 2043-10-10 | 2043-07-21 | 2015-05-22 | 2.5 | 0.12674 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.1 | 6.5 | 6.5 | 0.1893
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43021-01C02 | CML-2 | 80-FH-43021-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20413 | Reviewed 24/11/14. Repeat on Oct. 15. | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-24 17:42 | [32 empty] | 5.5 | CML-2 | CML: Elbow | 3 | 2020-03-30 | 2021-01-15 | 2014-10-06 07:00 | 2.5 | 0.43744 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-FH-43021-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 | 1.0139 | 5.6 | 4.9 | 5.4 | 6.1 | 0.49666
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-11 | 250-PG-20036-01C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21369 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | Check Corrosion Rate of 0.331mm/ yr | 41 | Kirstie Albone | 2017-03-23 15:18 | [32 empty] | 9.5 | CML-11 | CML: Elbow | 6 | 2033-11-14 | 2032-09-15 | 2014-07-14 07:30 | 2.5 | 0.33075 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.9 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 10.1 | 9.4 | 8.9 | 9.6 | 0.49666
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-11 | 50-DC-57056-03C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1143 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.075 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 6.4 | 5.9 | 5.9 | 0.23629
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-4 | 50-DC-57056-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1136 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.2 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 6.5 | 5.9 | 6.3 | 0.2582
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23024-03C03 | CML-9 | 50-PG-23024-03C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10041 | Rope Access | 2014-01-06 | 2014-01-06 | [36 empty] | 9.1 | CML-9 | CML: Elbow | 6 | 2032-10-29 | 2030-08-13 | 2014-01-06 | 0.97 | 0.4 | A1: Outside Quadrant |  | 2.74 | 0.97 | 1.855 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-PG-23024-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.53 |  | 8.5 | 9.7 | 9.2 | 9 | 0.49666
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-21 | 50-DC-57020-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 2463 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 6.325 | CML-21 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 3 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 5.9 | 6.4 | 6.8 | 0.37749
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-17 | 50-DC-57020-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2459 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 6.125 | CML-17 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 9 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.2 | 6.2 | 5.9 | 0.15
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-23 | 100-DC-57075-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 2442 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | [36 empty] | 6.45 | CML-23 | CML: type TBC | 3 | 2036-11-20 | 2037-08-31 | 2014-03-20 07:00 | 2.5 | 0.14985 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 6 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 6.6 | 5.9 | 6.6 | 0.36968
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57075-01C02 | CML-1 | 100-DC-57075-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2420 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | [36 empty] | 6.05 | CML-1 | CML: type TBC | 3 | 2036-11-20 | 2037-08-31 | 2014-03-20 07:00 | 2.5 | 0.14985 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 12 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 6.3 | 6 | 0.17321
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-7 | 100-DC-57037-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2358 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 6.275 | CML-7 | CML: type TBC | 3 | 2036-09-30 | 2037-07-09 | 2014-03-18 13:00 | 2.5 | 0.15075 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 12 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.6 | 6.3 | 6.3 | 0.28723
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PG-44022-01C03-P | CML-3 | 50-PG-44022-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5846 | Protective mesh removed | 2014-06-25 07:00 | 2014-06-25 09:00 | [36 empty] | 12.1 | CML-3 | CML: Reducer | 6 | 2075-10-24 | 2074-08-12 | 2014-06-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 11.5 | 6 O'Clock | 50 | 8.74 | 50-PG-44022-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 12.7 | 12.2 | 11.5 | 12 | 0.49666
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-10 | 250-PW-20022-01C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2053 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.35 | CML-10 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.7 | 12 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.7 | 10.2 | 10.8 | 10.7 | 0.50662
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-10 | 50-CG-38452-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12973 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 11.2667 | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.7 | 9 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  |  | 11.5 | 11.6 | 10.7 | 0.49329
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-9 | 25-DO-62301-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 2548 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.5 | CML-9 | CML: Elbow | 3 | 2064-01-05 | 2063-08-23 | 2015-05-22 | 2.5 | 0.07604 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.2 | 6.6 | 6.6 | 0.2
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-6 | 25-DO-62301-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 2545 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.55 | CML-6 | CML: Elbow | 3 | 2064-01-05 | 2063-08-23 | 2015-05-22 | 2.5 | 0.07604 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.8 | 6.8 | 0.3
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-4 | 25-DO-62301-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 2543 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.575 | CML-4 | CML: Elbow | 3 | 2064-01-05 | 2063-08-23 | 2015-05-22 | 2.5 | 0.07604 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 6.2 | 6.6 | 6.8 | 0.263
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-14 | 25-DO-62301-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 2553 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 9.05 | CML-14 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-22 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 9 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9 | 9.2 | 9.3 | 8.7 | 0.26458
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-3 | 25-DO-62301-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 2542 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 9.275 | CML-3 | CML: Equal Tee | 3 | 2051-11-30 | 2051-08-19 | 2015-05-22 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.1 | 6 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.4 | 9.1 | 9.1 | 9.5 | 0.20616
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-12 | 25-DO-62301-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 2551 | Does not exist on site | 2015-05-22 | 2015-05-22 | [37 empty] | CML-12 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-22 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-10 | 25-DO-62301-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 2549 | Does not exist on site | 2015-05-22 | 2015-05-22 | [37 empty] | CML-10 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-22 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-8 | 25-DO-62301-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 2547 | Does not exist on site | 2015-05-22 | 2015-05-22 | [37 empty] | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-22 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-2 | 25-DO-62301-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 2541 | CML too corroded to take readings. Refer to photo in the GVI | 2015-05-22 | 2015-05-22 | [37 empty] | CML-2 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-22 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62301-01C02 | CML-1 | 25-DO-62301-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 2540 | CML too corroded to take readings. Refer to photo in the GVI | 2015-05-22 | 2015-05-22 | [37 empty] | CML-1 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-05-22 | 2.5 | 0 |  |  | 3.35 | 2.5 | 2.5281 |  | 9 O'Clock | 25 | 6.35 | 25-DO-62301-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
VA01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 25-VA-23054-01C02 | CML-17 | 25-VA-23054-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2563 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 13.2333 | CML-17 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 12.9 | 9 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  |  | 13 | 13.8 | 12.9 | 0.49329
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8881 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.675 | CML-5 | CML: type TBC | 3 | 2051-02-17 | 2055-03-06 | 2015-02-25 09:30 | 2.5 | 0.08055 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.9 | 5.5 | 5.4 | 0.263
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-11 | 25-FG-45455-01C02-E CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20350 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 6.65 | CML-11 | CML: Elbow | 3 | 2019-01-18 | 2018-08-10 | 2014-10-09 07:00 | 2.5 | 0.818 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6 | 12 O'Clock | 80 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.7 | 7.2 | 6.7 | 0.49329
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-6 | 150-FH-43518-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2706 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.15 | CML-6 | CML: Pipe Length | 3 | 2022-05-23 | 2020-11-14 | 2014-03-12 09:00 | 1.23 | 0.65459 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 | 0 | 7.1 | 7.8 | 6.6 | 7.1 | 0.49329
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-6 | 150-FH-43518-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 345 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.15 | CML-6 | CML: Pipe Length | 3 | 2022-05-19 | 2020-11-10 | 2014-03-12 | 1.23 | 0.65546 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.6 | 6 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.37 |  | 7.1 | 7.8 | 6.6 | 7.1 | 0.49329
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-22 | 50-PL-45016-03C03 CML-22 |  | FPSO 2013 | Pipe Wall Thickness | 10462 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 7.85 | CML-22 | CML: type TBC | 6 | 2015-11-06 | 2015-07-28 | 2013-11-13 | 0.99 | 3.1854 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.3 | 12 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.31 |  | 7.3 | 7.8 | 8.5 | 7.8 | 0.49329
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-45 | 250-PG-23003-06C02-PA CML-45 |  | FPSO 2014 | Pipe Wall Thickness | 3261 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.95 | CML-45 | CML: type TBC | 3 | 2033-10-06 | 2035-12-13 | 2014-05-09 07:00 | 2.5 | 0.14929 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.2 | 5.7 | 6.5 | 0.49329
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-8 | 150-WC-40006-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 22752 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 5.775 | CML-8 | CML: Reducing Tee | 3 | 2021-02-24 | 2021-02-04 | 2015-04-29 07:00 | 2.5 | 0.49728 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 1.1671 | 5.4 | 6 | 5.8 | 5.9 | 0.263
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-10 | 200-FH-43012-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2840 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 11.4667 | CML-10 | CML: Equal Tee | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 10.9 | 6 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.56 |  | 11.7 | 11.8 | 10.9 |  | 0.49329
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-3 | 200-PL-20034-03C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21600 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 7.925 | CML-3 | CML: Elbow | 3 | 2020-08-21 | 2019-05-25 | 2014-06-28 13:00 | 3.61 | 0.63229 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 7.5 | 3 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.89 |  | 8.1 | 7.5 | 8.3 | 7.8 | 0.35
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-8 | 400-FH-43500-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5644 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 10.05 | CML-8 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 9.5 | 12 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 9.5 | 9.8 | 10.6 | 10.3 | 0.49329
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-VA-23057-01C02 | CML-5 | 200-VA-23057-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3149 | Rope Access | 2014-05-02 14:00 | 2014-05-02 15:00 | [36 empty] | 8.05 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-05-02 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 6 O'Clock | 200 | 6.35 | 200-VA-23057-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.6 | 8.1 | 7.4 | 8.1 | 0.49329
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43512-01C02 | CML-31 | 350-FL-43512-01C02 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 6545 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.65 | CML-31 | CML: Elbow | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 9 | 3 O'Clock | 350 | 7.92 | 350-FL-43512-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.7 | 9 | 9.7 | 10.2 | 0.49329
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-12 | 250-PG-23004-06C03-A CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23379 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 18.95 | CML-12 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2015-07-21 07:00 | 8.55 | 0 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.3 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.75 | 0.13137 | 19.5 | 19 | 18.3 | 19 | 0.49329
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23015-06C03-A | CML-18 | 250-PG-23015-06C03-A CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 13050 |  | 2014-01-11 13:00 | 2014-01-11 15:00 | [36 empty] | 18.375 | CML-18 | CML: Pipe Length | 6 | 2036-05-16 | 2031-12-27 | 2014-01-11 13:00 | 8.55 | 0.42264 | A1: Outside Quadrant |  | 12.26 | 8.55 | 10.405 | 18 | 12 O'Clock | 250 | 18.26 | 250-PG-23015-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.45 |  | 18 | 18.2 | 19.1 | 18.2 | 0.49244
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 250-PG-23039-06D01 | CML-2 | 250-PG-23039-06D01 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10704 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 9.025 | CML-2 | CML: type TBC | 1 | 2035-06-01 | 2034-04-16 | 2013-11-07 | 5.6 | 0 | A1: Outside Quadrant |  | 6.8 | 5.6 | 5.7125 | 9 | 9 O'Clock | 250 | 7.8 | 250-PG-23039-06D01 | 30 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 9 | 9 | 9.1 | 9 | 0.05
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-8 | 50-PF-20301-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3006 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.175 | CML-8 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8.6 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.99 | 0 | 9.2 | 9.8 | 9.1 | 8.6 | 0.49244
PG02 | Montara_Topside | No | Separation (20) | Pipework | 300-PG-20025-03D01-P | CML-1 | 300-PG-20025-03D01-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22796 |  | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 7.45 | CML-1 | CML: Reducer | 1 | 2038-04-25 | 2030-11-12 | 2015-04-29 07:00 | 3.86 | 0 | A1: Outside Quadrant |  | 5.35 | 3.86 | 4.605 | 7.3 | 12 O'Clock | 300 | 6.35 | 300-PG-20025-03D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.44 | -0.35784 | 7.3 | 7.5 | 7.5 | 7.5 | 0.1
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-8 | 50-PF-20301-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 22285 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.175 | CML-8 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8.6 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.99 |  | 9.2 | 9.8 | 9.1 | 8.6 | 0.49244
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-1 | 200-FH-43004-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12541 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 8.225 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.6 | 6 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.2 | 8.8 | 7.6 | 8.3 | 0.49244
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-5 | 300-PG-23400-01C03-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23419 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 8.95 | CML-5 | CML: Elbow | 6 | 2020-03-06 | 2020-10-12 | 2015-07-22 07:00 | 5.22 | 0.75215 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 8.7 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.48 | 0 | 8.7 | 9.1 | 8.9 | 9.1 | 0.19149
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-5 | 300-PG-23400-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20039 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 8.975 | CML-5 | CML: Elbow | 6 | 2016-07-20 | 2016-10-30 | 2014-05-29 07:00 | 5.22 | 1.622 | A2: Right Quadrant |  | 4.31 | 5.22 | 4.765 | 8.7 | 3 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.48 | 0.94908 | 8.9 | 8.7 | 9.3 | 9 | 0.25
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-4 | 300-PG-23400-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20038 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 9.575 | CML-4 | CML: Pipe Length | 6 | 2016-07-20 | 2016-10-30 | 2014-05-29 07:00 | 5.22 | 1.622 | A4: Left Quadrant |  | 4.31 | 5.22 | 4.765 | 8.7 | 9 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.48 | 0.47454 | 10.1 | 10.5 | 9 | 8.7 | 0.86168
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-1 | 300-PG-23400-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20035 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 9.4 | CML-1 | CML: Pipe Length | 6 | 2016-07-20 | 2016-10-30 | 2014-05-29 07:00 | 5.22 | 1.622 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 8.7 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.48 | 0 | 8.7 | 9.5 | 9.5 | 9.9 | 0.50332
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-1 | 300-PG-23400-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 518 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 9.425 | CML-1 | CML: Pipe Length | 6 | 2015-11-20 | 2016-02-08 | 2014-03-13 09:00 | 5.22 | 2.0592 | A2: Right Quadrant |  | 4.31 | 5.22 | 4.765 | 8.7 | 3 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.48 |  | 9.7 | 8.7 | 9.2 | 10.1 | 0.60759
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-11 | 250-PW-20022-01C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2054 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.4 | CML-11 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.7 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10.8 | 9.7 | 10.5 | 10.6 | 0.48305
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-4 | 300-PW-44003-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21846 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 9.975 | CML-4 | CML: Elbow | 6 | 2031-02-16 | 2029-01-27 | 2014-10-19 07:00 | 2.5 | 0.44064 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.7 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 10.2 | 9.7 | 10.1 | 9.9 | 0.22174
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62302-01C02 | CML-3 | 25-DO-62302-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 2535 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 5.975 | CML-3 | CML: Pipe Length | 3 | 2030-04-13 | 2030-02-27 | 2015-05-22 | 2.5 | 0.22812 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 3 O'Clock | 25 | 6.35 | 25-DO-62302-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 5.9 | 6.1 | 6 | 0.095743
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-32 | 200-PW-44018-01X01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 8956 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.475 | CML-32 | CML: type TBC | 3 | 2028-12-20 | 2030-08-21 | 2015-02-26 09:00 | 2.5 | 0.19532 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.4 | 5.9 | 5.2 | 0.29861
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62302-01C02 | CML-2 | 25-DO-62302-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 2534 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 5.9 | CML-2 | CML: Pipe Length | 3 | 2030-04-13 | 2030-02-27 | 2015-05-22 | 2.5 | 0.22812 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 25 | 6.35 | 25-DO-62302-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 5.9 | 5.9 | 5.9 | 0
FG05 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-FG-45452-01C02-H | CML-1 | 50-FG-45452-01C02-H CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24313 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.25 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2016-05-27 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 50 | 5.54 | 50-FG-45452-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.4 | 6.4 | 6.2 | 0.19149
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9004-AS20-00 | CML-5 | 0100-AI-63L9004-AS20-00 CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24281 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.275 | CML-5 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6 | 6 O'Clock | 25 | 3.38 | 0100-AI-63L9004-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6.4 | 6 | 6.2 | 0.22174
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-3 | 25-PG-23300-25C02 CML-3 | Yes | FPSO 2014 | Pipe Wall Thickness | 20670 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 8.975 | CML-3 | CML: Pipe Length | 3 | 2021-04-04 | 2019-11-05 | 2014-05-27 09:30 | 4.4 | 0.59754 | A1: Outside Quadrant |  | 6.09 | 4.4 | 5.245 | 8.5 | 12 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 8.5 | 9.4 | 9.4 | 8.6 | 0.49244
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-10 | 50-PL-23022-03C03 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1866 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.475 | CML-10 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 12 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.1 | 9.9 | 9.9 | 0.49244
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-17 | 200-PG-23008-15S01-A CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 20976 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 5.475 | CML-17 | CML: type TBC | 3 | 2017-01-28 | 2017-03-13 | 2014-05-16 13:00 | 2.5 | 0.96069 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 12 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 6.2 | 5.3 | 0.49244
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62302-01C02 | CML-4 | 25-DO-62302-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 2536 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.4 | CML-4 | CML: Elbow | 3 | 2035-02-06 | 2034-12-10 | 2015-05-22 | 2.5 | 0.17743 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 25 | 6.35 | 25-DO-62302-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6 | 6.3 | 6.8 | 0.33665
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62302-01C02 | CML-7 | 25-DO-62302-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 2539 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.2 | CML-7 | CML: Elbow | 3 | 2043-10-10 | 2043-07-21 | 2015-05-22 | 2.5 | 0.12674 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 25 | 6.35 | 25-DO-62302-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.1 | 6.3 | 6.3 | 0.11547
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62302-01C02 | CML-6 | 25-DO-62302-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 2538 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.4 | CML-6 | CML: Elbow | 3 | 2064-01-05 | 2063-08-23 | 2015-05-22 | 2.5 | 0.07604 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 25 | 6.35 | 25-DO-62302-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.5 | 6.5 | 0.14142
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62302-01C02 | CML-1 | 25-DO-62302-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 2533 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.625 | CML-1 | CML: Pipe Length | 3 | 2064-01-05 | 2063-08-23 | 2015-05-22 | 2.5 | 0.07604 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 25 | 6.35 | 25-DO-62302-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.2 | 6.7 | 7.1 | 0.37749
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43119-01C02 | CML-3 | 80-FH-43119-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12830 |  | 2014-01-18 10:00 | 2014-01-18 11:30 | [36 empty] | 5.675 | CML-3 | CML: Elbow | 3 | 2029-12-03 | 2027-10-25 | 2014-01-18 10:00 | 0.54 | 0.29968 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 12 O'Clock | 80 | 5.49 | 80-FH-43119-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.3 | 5.5 | 6.4 | 5.5 | 0.49244
Marine | Mantara_Marine | No | Diesel Oil (62) | Pipework | 25-DO-62302-01C02 | CML-5 | 25-DO-62302-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 2537 |  | 2015-05-22 | 2015-05-22 | [36 empty] | 6.95 | CML-5 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-05-22 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 3 O'Clock | 25 | 6.35 | 25-DO-62302-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.1 | 6.7 | 6.9 | 7.1 | 0.19149
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56118-01C02 | CML-3 | 50-DH-56118-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21022 | Rope Access | 2014-05-19 11:00 | 2014-05-19 12:00 | [36 empty] | 5.375 | CML-3 | CML: type TBC | 3 | 2017-05-18 | 2017-10-21 | 2014-05-19 11:00 | 2.5 | 0.76633 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.3 | 5.4 | 4.8 | 6 | 0.49244
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57025-01C02 | CML-2 | 50-DC-57025-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22936 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 6.15 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-05-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 | -0.45739 | 6 | 6.2 | 6.4 | 6 | 0.19149
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43079-01C02 | CML-2 | 50-FL-43079-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3045 | Rope Access | 2014-05-03 07:00 | 2014-05-03 08:00 | [36 empty] | 5.775 | CML-2 | CML: type TBC | 3 | 2021-08-24 | 2022-07-13 | 2014-05-03 07:00 | 2.5 | 0.36902 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FL-43079-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.8 | 6.4 | 5.2 | 0.49244
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56123-01C02 | CML-2 | 50-DH-56123-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1827 |  | 2014-04-29 14:30 | 2014-04-29 15:00 | [36 empty] | 6.125 | CML-2 | CML: Elbow | 3 | 2082-08-15 | 2090-01-18 | 2014-04-29 14:30 | 2.5 | 0.0439 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DH-56123-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.2 | 6.7 | 6.1 | 0.49244
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-10 | 50-CG-38452-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1743 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.575 | CML-10 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 9 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 8 | 8 | 7.2 | 7.1 | 0.49244
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-26 | 350-FL-43511-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 2307 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 8.025 | CML-26 | CML: type TBC | 3 | 2020-05-04 | 2019-06-05 | 2014-03-17 08:00 | 2.5 | 0.78214 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.3 | 3 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.2 | 7.3 | 8.2 | 8.4 | 0.49244
WC01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-WC-40006-01C02 | CML-12 | 150-WC-40006-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 6239 | Rope Access | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 5.775 | CML-12 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2 | 2.5 | 2.25 | 5.4 | 12 O'Clock | 50 | 2.5 | 50-WF-71333-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 5.9 | 6 | 0.263
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-GN-67300-01E01 | CML-6 | 25-GN-67300-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22490 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 6.35 | CML-6 | CML: Elbow | 3 | 2034-02-22 | 2033-12-28 | 2015-04-20 07:00 | 2.5 | 0.1856 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.6 | 6.2 | 6.6 | 0.3
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20044-03C03-P | CML-8 | 80-PG-20044-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21456 | Protective mesh removed | 2014-06-29 09:30 | 2014-06-29 11:00 | [36 empty] | 11.825 | CML-8 | CML: Elbow | 6 | 2323-04-04 | 2276-01-17 | 2014-06-29 09:30 | 2.5 | 0.02783 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 11.1 | 3 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 12 | 11.1 | 12 | 12.2 | 0.49244
WF01 | Montara_Topside | No | Fire Water (71) | Pipework | 80-WF-71322-01K01 | CML-3 | 80-WF-71322-01K01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 5989 | Rope Access | 2015-03-17 07:00 | 2015-03-17 15:00 | [36 empty] | 6.1 | CML-3 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-17 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2 | 2.5 | 2.25 | 6 | 9 O'Clock | 80 | 2.5 | 80-WF-71322-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6.2 | 6.1 | 6 | 0.08165
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-25 | 50-GN-67002-01E01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 9084 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 6.1 | CML-25 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6.1 | 6 | 6 | 0.14142
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67002-01E01 | CML-2 | 50-GN-67002-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 9061 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 6.15 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.2 | 6.4 | 6 | 0.19149
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-27 | 50-AU-63015-01E01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 9058 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6.1 | CML-27 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.2 | 6 | 6 | 0.11547
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-21 | 50-AU-63015-01E01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 9052 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6.1 | CML-21 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6.2 | 6.1 | 6 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-20 | 50-AU-63015-01E01 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 9051 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6.2 | CML-20 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6.2 | 6 | 6.3 | 0.14142
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-38 | 50-AI-63004-01E01 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 9029 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.325 | CML-38 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6 | 6.6 | 6.6 | 0.32016
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-32 | 50-AI-63004-01E01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 9023 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.35 | CML-32 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.7 | 6.6 | 6 | 6.1 | 0.35119
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-28 | 50-AI-63004-01E01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 9019 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.625 | CML-28 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 6 | 6.7 | 6.9 | 0.4272
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-9 | 50-AI-63004-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 9000 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.175 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6.2 | 6.4 | 6 | 0.17078
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63023-01E01 | CML-2 | 50-AU-63023-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8863 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 07:00 | 2015-02-25 08:00 | [36 empty] | 6.3 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-AU-63023-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.2 | 6 | 6.8 | 0.34641
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-1 | 80-SC-55002-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8831 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 6.6 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 6 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 6.9 | 6 | 6.6 | 0.42426
FG02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-FG-45455-01C02-E | CML-8 | 25-FG-45455-01C02-E CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 23860 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.675 | CML-8 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A3: Inside Quadrant |  |  | 2.7 |  | 6.2 | 6 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.1 | 7.1 | 6.2 | 6.3 | 0.49244
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67011-01E01 | CML-10 | 50-GN-67011-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8768 |  | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 6.2 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-GN-67011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.3 | 6.3 | 6.2 | 6 | 0.14142
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43110-01C02 | CML-3 | 200-FH-43110-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12794 |  | 2014-01-18 13:30 | 2014-01-18 14:30 | [36 empty] | 6.375 | CML-3 | CML: Elbow | 3 | 2022-06-28 | 2021-05-22 | 2014-01-18 13:30 | 1.34 | 0.55169 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 6 | 3 O'Clock | 200 | 6.35 | 200-FH-43110-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 6.2 | 6 | 7.1 | 6.2 | 0.49244
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-8 | 50-FG-45019-03C02 CML-8 | yes | FPSO 2013 | Pipe Wall Thickness | 10490 | Deck Level | 2013-11-15 | 2013-11-15 | [36 empty] | 4.875 | CML-8 | CML: type TBC | 3 | 2014-08-20 | 2014-08-17 | 2013-11-15 | 2.5 | 2.4916 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.4 | 3 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.9 |  | 4.5 | 4.4 | 5.3 | 5.3 | 0.49244
PW03 | Montara_Topside | Yes | Fire Water (71) | Pipework | 200-PW-44018-01X01 | CML-11 | 200-PW-44018-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5496 | Pipe Schedule Estimated. Rope Access | 2015-03-15 07:00 | 2015-03-15 15:00 | [36 empty] | 5.525 | CML-11 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-15 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2 | 2.5 | 2.25 | 5.2 | 6 O'Clock | 80 | 2.5 | 80-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.4 | 5.2 | 5.9 | 0.29861
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-1 | 50-PL-23516-03C03 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7789 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:02 | [32 empty] | 9.025 | CML-1 | CML: Elbow | 6 | 2043-02-15 | 2042-07-22 | 2015-01-13 07:00 | 2.5 | 0.20988 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.4 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.6 | 9 | 9.1 | 8.4 | 0.49244
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-3 | 50-PL-23514-01C03 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8636 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:18 | [32 empty] | 8.875 | CML-3 | CML: Elbow | 6 | 2037-06-20 | 2037-01-02 | 2015-02-10 11:30 | 2.5 | 0.25925 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 6 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.5 | 8.9 | 8.3 | 8.8 | 0.49244
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20503-03C03-P | CML-3 | 50-PF-20503-03C03-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7744 |  | 2015-01-10 10:00 | 2015-01-10 12:00 | [36 empty] | 9.125 | CML-3 | CML: Elbow | 6 | 2055-04-20 | 2054-06-30 | 2015-01-10 10:00 | 2.5 | 0.14887 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.5 | 12 O'Clock | 50 | 8.74 | 50-PF-20503-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 8.5 | 9.2 | 9.7 | 9.1 | 0.49244
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-25 | 300-PF-20501-03C03-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 21701 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.525 | CML-25 | CML: Pipe Length | 6 | 2046-12-29 | 2040-12-14 | 2014-09-28 07:00 | 4.9 | 0.27886 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.5 | 13.9 | 15.1 | 14.6 | 0.49244
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-35 | 300-PF-20001-03C03-P CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 21173 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 14.925 | CML-35 | CML: Fitting | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.3 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 14.3 | 15 | 15.5 | 14.9 | 0.49244
VA01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-VA-23054-01C02 | CML-20 | 25-VA-23054-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 22885 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 13.475 | CML-20 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2015-05-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 13.1 | 6 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.6 | -1.317 | 14.2 | 13.3 | 13.1 | 13.3 | 0.49244
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20031-01C03-P | CML-2 | 150-PG-20031-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 23864 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.775 | CML-2 | CML: Elbow | 6 | 2030-02-09 | 2027-09-04 | 2014-09-26 07:00 | 2.5 | 0.50706 | A3: Inside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.3 | 6 O'Clock | 150 | 10.97 | 150-PG-20031-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 11.2 | 11.2 | 10.3 | 10.4 | 0.49244
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40512-1CG | CML-4 | 150-WC-40512-1CG CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5477 | Rope Access | 2014-05-28 10:00 | 2014-05-28 11:30 | [36 empty] | 11.5 | CML-4 | CML: Elbow | 3 | 2098-02-09 | 2070-10-05 | 2014-05-28 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 7.97 | 2.5 | 5.235 | 11 | 9 O'Clock | 150 | 10.97 | 150-WC-40512-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11.5 | 11.6 | 11.9 | 11 | 0.37417
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-10 | 80-DH-56074-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20955 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 5.8 | CML-10 | CML: Elbow | 3 | 2023-07-02 | 2024-09-03 | 2014-05-24 07:00 | 2.5 | 0.29626 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.2 | 5.2 | 5.6 | 6.2 | 0.4899
PG05 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1044 |  | 2014-03-20 13:00 | 2014-03-20 14:00 | Check Corrosion Rate of 1.185mm/ yr | [35 empty] | 5.8 | CML-3 | CML: type TBC | 3 | 2016-08-29 | 2016-08-20 | 2014-03-20 13:00 | 2.5 | 1.1853 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 3 O'Clock | 300 | 6.35 | 300-WC-40043-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 6 | 6.4 | 0.4899
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45044-03C02 | CML-7 | 50-FG-45044-03C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7795 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 16:03 | [32 empty] | 9.2 | CML-7 | CML: Elbow | 6 | 2085-07-27 | 2084-03-07 | 2015-01-13 07:00 | 2.5 | 0.08642 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9 | 9.6 | 9.6 | 8.6 | 0.4899
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-17 | 300-PF-20500-03C03-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21637 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.3 | CML-17 | CML: Pipe Length | 6 | 2035-03-02 | 2031-04-03 | 2014-09-27 07:00 | 4.9 | 0.43049 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 13.7 | 14.7 | 14.7 | 14.1 | 0.4899
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-14 | 200-PL-20035-03C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21346 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.925 | CML-14 | CML: Elbow | 3 | 2020-08-14 | 2019-05-20 | 2014-06-27 13:00 | 3.61 | 0.6339 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.5 | 6 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.89 |  | 7.9 | 8 | 7.5 | 8.3 | 0.3304
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-2 | 200-PG-20300-03C03-P CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24482 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.483mm/ yr |  | Kirstie Albone | 2017-03-23 10:09 | Loss within CA no further action required, include in next inspection | [31 empty] | 11.675 | CML-2 | CML: Elbow | 6 | 2032-11-16 | 2029-05-10 | 2016-07-09 07:00 | 3.3 | 0.48268 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 11.2 | 12 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 | 1.0282 | 11.2 | 12.3 | 11.8 | 11.4 | 0.48563
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-15 | 50-PW-44040-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23250 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.35 | CML-15 | CML: Pipe Length | 3 | 2026-10-31 | 2028-04-09 | 2015-05-11 07:00 | 2.5 | 0.22642 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0 | 5.5 | 5.7 | 5.1 | 5.1 | 0.3
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-3 | 200-FH-43037-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12672 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 7.075 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.2 | 6.8 | 7.7 | 6.6 | 0.48563
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-5 | 200-PG-23065-09C02-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 617 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.825 | CML-5 | CML: Pipe Length | 3 | 2037-08-22 | 2030-01-07 | 2014-03-12 09:00 | 10.17 | 0.33371 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 18 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.83 |  | 18.9 | 18 | 18.6 | 19.8 | 0.75
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-2 | 50-CG-38001-09C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10915 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.325 | CML-2 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.7176 | A1: Outside Quadrant |  | 5.74 |  |  | 7.7 | 12 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.7 | 7.7 | 8.6 | 8.8 | 8.2 | 0.48563
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-8 | 50-DH-56062-01C02 CML-8 | yes | FPSO 2015 | Pipe Wall Thickness | 9095 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.025 | CML-8 | CML: type TBC | 3 | 2017-09-15 | 2018-03-02 | 2015-03-02 07:00 | 2.5 | 0.70797 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 5.2 | 4.3 | 5.3 | 5.3 | 0.48563
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-18 | 50-FG-45501-01C02 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 6601 | Rope Access. Line is FFS although the CRs reported are higher than expected. Maintain RBI frequency at 36m. Next inspection in Mar. 2018 | 2015-03-30 07:00 | 2015-03-30 15:00 |  |  | Administrator | 2015-09-07 14:35 | [32 empty] | 5.525 | CML-18 | CML: Pipe Length | 3 | 2020-12-02 | 2021-09-22 | 2015-03-30 07:00 | 2.5 | 0.40477 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.8 | 5.8 | 5.7 | 4.8 | 0.48563
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56066-01C02 | CML-4 | 50-DH-56066-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3281 | Rope Access | 2014-05-09 14:00 | 2014-05-09 15:00 | [36 empty] | 5.725 | CML-4 | CML: type TBC | 3 | 2018-09-11 | 2019-04-06 | 2014-05-09 14:00 | 2.5 | 0.57533 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DH-56066-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6 | 6 | 5.9 | 5 | 0.48563
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-17 | 150-WC-40006-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 9076 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.625 | CML-17 | CML: type TBC | 3 | 2051-05-15 | 2055-06-11 | 2015-03-01 09:30 | 2.5 | 0.08004 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 5.4 | 5.9 | 0.263
WC01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22815 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.7 | CML-2 | CML: Elbow | 3 | 2024-04-08 | 2024-08-17 | 2015-04-30 07:00 | 2.5 | 0.32408 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 6 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 2.5808 | 5.6 | 5.8 | 5.4 | 6 | 0.2582
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-7 | 50-PL-23052-09C03 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10171 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.275 | CML-7 | CML: type TBC | 6 | 2016-10-25 | 2016-05-08 | 2013-11-09 | 2.81 | 2.4258 | A2: Right Quadrant |  | 5.07 | 2.81 | 3.94 | 10 | 6 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.19 |  | 11 | 10 | 10 | 10.1 | 0.48563
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23046-06C03 | CML-1 | 80-PG-23046-06C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20578 | Rope Access | 2014-05-27 07:00 | 2014-05-27 08:00 | [36 empty] | 11.275 | CML-1 | CML: Pipe Length | 6 | 2076-08-15 | 2067-10-13 | 2014-05-27 07:00 | 2.8 | 0.1317 | A2: Right Quadrant |  | 5.13 | 2.8 | 3.965 | 11 | 9 O'Clock | 80 | 11.13 | 80-PG-23046-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 12 | 11 | 11.1 | 11 | 0.48563
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-12 | 50-PW-44013-01X01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22731 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.55 | CML-12 | CML: Reducing Tee | 3 | 2030-06-17 | 2032-04-15 | 2015-04-28 07:00 | 2.5 | 0.17823 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0 | 5.9 | 5.2 | 5.5 | 5.6 | 0.28868
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-3 | 200-PL-20035-03C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21338 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.8 | CML-3 | CML: Elbow | 3 | 2020-08-14 | 2019-05-20 | 2014-06-27 13:00 | 3.61 | 0.6339 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 7.5 | 9 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.89 |  | 8 | 7.6 | 8.1 | 7.5 | 0.29439
WC01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 5922 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 5.7 | CML-5 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 5.4 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.6 | 5.8 | 5.4 | 0.2582
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-1 | 200-PG-23008-15S01-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20916 | Rope Access | 2014-05-21 08:00 | 2014-05-21 09:00 | [36 empty] | 5.375 | CML-1 | CML: Elbow | 3 | 2020-11-07 | 2021-09-19 | 2014-05-21 08:00 | 2.5 | 0.40174 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 9 O'Clock | 80 | 5.49 | 80-DH-56034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.1 | 5.1 | 5.2 | 5.1 | 0.48563
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-5 | 150-FL-43514-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20498 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.075 | CML-5 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.8 | 9 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.9 | 6.8 | 7.8 | 6.8 | 0.48563
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-5 | 150-FH-43026-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23504 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 7.375 | CML-5 | CML: Pipe Length | 3 | 520099 | 433841 | 2015-07-28 07:00 | 1.03 | 0.00464 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 7.1 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.07 | -0.26449 | 8.1 | 7.1 | 7.2 | 7.1 | 0.48563
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56141-01C02 | CML-11 | 50-DH-56141-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 5452 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 3.475mm/ yr | [34 empty] | Low alarm breach | 18.725 | CML-11 | CML: Elbow | 3 | 2018-11-11 | 2016-07-27 | 2014-05-28 07:00 | 2.5 | 3.4753 | A4: Left Quadrant |  | 18.44 | 2.5 | 10.47 | 18 | 9 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.5 |  | 19 | 19 | 18.9 | 18 | 0.48563
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56046-01C02 | CML-2 | 80-DH-56046-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20936 | Rope Access | 2014-05-17 09:30 | 2014-05-17 11:00 | [36 empty] | 5.325 | CML-2 | CML: type TBC | 3 | 2017-01-17 | 2017-06-20 | 2014-05-17 09:30 | 2.5 | 0.82293 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 9 O'Clock | 80 | 5.49 | 80-DH-56046-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.6 | 5.8 | 5.2 | 4.7 | 0.48563
WC01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-WC-40006-01C02 | CML-11 | 150-WC-40006-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5928 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 5.75 | CML-11 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 5.4 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.8 | 5.8 | 5.4 | 0.25166
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-6 | 150-FG-45505-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22346 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.975 | CML-6 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.7 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 7.7 | 8.7 | 0.48563
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-6 | 150-FG-45505-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22345 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.975 | CML-6 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.7 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 7.7 | 8.7 | 0.48563
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-6 | 150-FG-45505-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22344 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.975 | CML-6 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.7 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 7.7 | 8.7 | 0.48563
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-6 | 150-FG-45505-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22343 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.975 | CML-6 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.7 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 7.7 | 8.7 | 0.48563
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-6 | 150-FG-45505-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22342 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.975 | CML-6 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.7 | 6 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.8 | 7.7 | 8.7 | 0.48563
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-16 | 80-CG-38459-09C02-P CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10112 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 17.575 | CML-16 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2013-11-07 | 5.22 | 0 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 17.1 | 12 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.88 |  | 17.1 | 17.3 | 18.2 | 17.7 | 0.48563
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-6 | 200-PG-23065-09C02-A CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 618 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.95 | CML-6 | CML: Pipe Length | 3 | 2052-10-12 | 2040-05-25 | 2014-03-12 09:00 | 10.17 | 0.20536 | A3: Inside Quadrant |  | 15.26 | 10.17 | 12.715 | 18.1 | 6 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.93 |  | 20.1 | 18.3 | 18.1 | 19.3 | 0.92916
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-16 | 200-PG-23065-09C02-A CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 430 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.075 | CML-16 | CML: Elbow | 3 | 2052-10-12 | 2040-05-25 | 2014-03-12 09:00 | 10.17 | 0.20536 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 18.1 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.93 |  | 18.7 | 18.1 | 20 | 19.5 | 0.84212
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-12 | 250-PW-44509-01C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 22047 |  | 2014-10-20 07:00 | 2014-10-20 15:00 | [36 empty] | 10.1 | CML-12 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-10-20 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.8 | 6 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.9 | 9.8 | 9.8 | 9.9 | 0.53541
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-9 | 80-PW-44016-01C02-P CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 22911 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.425 | CML-9 | CML: Elbow | 3 | 2028-02-11 | 2029-10-29 | 2015-05-02 07:00 | 2.5 | 0.20327 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.17892 | 5.4 | 5.8 | 5.1 | 5.4 | 0.28723
WC01 | Montara_Topside | Yes | Potable Water (53) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8283 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.775 | CML-7 | CML: type TBC | 3 | 2049-05-05 | 2053-03-13 | 2015-01-26 07:30 | 2.5 | 0.08456 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.9 | 5.9 | 5.9 | 0.25
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-13 | 50-PF-20301-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 3011 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.3 | CML-13 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8.6 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.99 | 0 | 9.4 | 9.7 | 9.5 | 8.6 | 0.48305
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-13 | 50-PF-20301-03C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 22290 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.3 | CML-13 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8.6 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.99 |  | 9.4 | 9.7 | 9.5 | 8.6 | 0.48305
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-23 | 50-PW-44040-01C02 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 23258 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.325 | CML-23 | CML: Elbow | 3 | 2026-10-31 | 2028-04-09 | 2015-05-11 07:00 | 2.5 | 0.22642 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0 | 5.2 | 5.3 | 5.1 | 5.7 | 0.263
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-6 | 50-CG-38487-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20845 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 9.3 | CML-6 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-10-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.9 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | -1.444 | 8.9 | 9.2 | 10 | 9.1 | 0.48305
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23085 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.45 | CML-8 | CML: Elbow | 3 | 2033-04-28 | 2035-08-23 | 2015-05-07 07:00 | 2.5 | 0.15008 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 1.6024 | 5.2 | 5.2 | 5.7 | 5.7 | 0.28868
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 23806 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.7 | CML-6 | CML: Reducing Tee | 3 | 2027-11-29 | 2027-10-21 | 2014-09-25 07:00 | 2.5 | 0.26543 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.8 | 6.9 | 6 | 7.1 | 0.48305
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-1 | 100-PG-23503-03C03-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2717 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 11.9 | CML-1 | CML: Elbow | 6 | 2068-02-11 | 2070-10-05 | 2014-03-13 09:00 | 5.66 | 0 | A3: Inside Quadrant |  | 5.13 | 5.66 | 5.395 | 11.5 | 6 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.84 |  | 12.6 | 11.7 | 11.5 | 11.8 | 0.48305
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-4 | 250-PW-20022-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2047 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.4 | CML-4 | CML: Pipe Length | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.8 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.5 | 9.8 | 10.5 | 10.8 | 0.42426
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-14 | 300-PG-20004-03C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 6137 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 12.4 | CML-14 | CML: Fitting | 6 | 2018-10-11 | 2017-07-25 | 2014-07-11 07:30 | 3.3 | 2.0442 | A1: Outside Quadrant |  | 8.27 | 3.3 | 5.785 | 12 | 12 O'Clock | 200 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 12 | 12.2 | 13.1 | 12.3 | 0.48305
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-4 | 100-DH-56009-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3427 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.1 | CML-4 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 4.7 | 6 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.9 | 5 | 4.7 | 5.8 | 0.48305
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-32 | 50-DH-56137-01C02 CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 21116 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 5.6 | CML-32 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.2 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.5 | 6.3 | 5.2 | 0.48305
PW03 | Montara_Topside | Yes | Potable Water (53) | Pipework | 200-PW-44018-01X01 | CML-21 | 200-PW-44018-01X01 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 8160 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.575 | CML-21 | CML: type TBC | 3 | 2028-02-28 | 2029-09-28 | 2015-01-24 07:30 | 2.5 | 0.20604 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.6 | 5.9 | 5.6 | 0.28723
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-8 | 250-PG-23005-06C03 CML-8 |  | FPSO 2013 | Pipe Wall Thickness | 10054 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 17.25 | CML-8 | CML: Pipe Length | 6 | 2016-02-04 | 2015-08-03 | 2013-11-06 | 8.6 | 3.6038 | A2: Right Quadrant |  | 12.26 | 8.6 | 10.43 | 16.7 | 3 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 17.6 | 16.7 | 17.7 | 17 | 0.47958
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-10 | 200-PL-20008-01C02-H CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 8807 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.3 | CML-10 | CML: Fitting | 3 | 2032-05-25 | 2032-04-04 | 2015-02-21 07:00 | 2.5 | 0.20268 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.6 | 6 | 6 | 6.6 | 0.34641
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56116-01C02 | CML-7 | 50-DH-56116-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5217 | Rope Access | 2014-05-20 09:30 | 2014-05-20 11:00 | [36 empty] | 5.15 | CML-7 | CML: Elbow | 3 | 2016-11-30 | 2017-04-17 | 2014-05-20 09:30 | 2.5 | 0.86758 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56116-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.7 | 4.8 | 5.4 | 4.7 | 0.47958
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56138-01C02 | CML-3 | 50-DH-56138-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22311 | Rope Access | 2014-05-06 14:00 | 2014-05-06 15:00 | [36 empty] | 5.85 | CML-3 | CML: type TBC | 3 | 2025-03-11 | 2026-06-16 | 2014-05-06 14:00 | 2.5 | 0.25796 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.6 | 5.3 | 6.2 | 6.3 | 0.47958
PW03 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PW-44018-01X01 | CML-22 | 200-PW-44018-01X01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 22840 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.625 | CML-22 | CML: Elbow | 3 | 2021-08-15 | 2021-11-22 | 2015-04-30 07:00 | 2.5 | 0.42862 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.54478 | 5.7 | 5.8 | 5.2 | 5.8 | 0.28723
FG02 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 25-FG-45455-01C02-E | CML-7 | 25-FG-45455-01C02-E CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8128 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.45 | CML-7 | CML: type TBC | 1 | 2303-03-05 | 2230-06-04 | 2015-01-23 07:30 | 2.5 | 0.01214 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 6.7 | 7 | 0.47958
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20367 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-24 10:37 | [32 empty] | 6.45 | CML-5 | CML: Elbow | 3 | 2028-03-29 | 2028-02-18 | 2014-10-06 07:00 | 2.5 | 0.2595 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.7 | 7 | 6 | 6.1 | 0.47958
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56024-01C02 | CML-1 | 80-DH-56024-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3488 | Rope Access | 2014-05-14 13:00 | 2014-05-14 14:00 | [36 empty] | 5.35 | CML-1 | CML: type TBC | 3 | 2018-03-28 | 2018-10-19 | 2014-05-14 13:00 | 2.5 | 0.61964 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-DH-56024-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.1 | 5.4 | 6 | 0.47958
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-5 | 250-PG-23003-06C02-PA CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 9092 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.85 | CML-5 | CML: type TBC | 3 | 2051-06-03 | 2055-07-02 | 2015-03-02 07:00 | 2.5 | 0.07993 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 5.6 | 6.5 | 5.4 | 0.47958
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-16 | 200-PL-20008-01C02-H CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8813 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.35 | CML-16 | CML: Elbow | 3 | 2039-12-28 | 2039-10-18 | 2015-02-21 07:00 | 2.5 | 0.14477 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.7 | 6.3 | 6.3 | 0.25166
WC01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6670 |  | 2015-03-31 07:00 | 2015-03-31 15:00 |  |  | Nestor | 2014-11-20 12:33 | [32 empty] | 5.675 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-31 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 5.4 | 9 O'Clock | 150 | 3 | 150-WF-71346-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 6 | 5.6 | 5.4 | 0.25
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-13 | 50-FG-45020-03C02 CML-13 | yes | FPSO 2013 | Pipe Wall Thickness | 10585 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.95 | CML-13 | CML: type TBC | 3 | 2014-10-08 | 2014-10-04 | 2013-11-17 | 2.5 | 2.2462 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.5 | 3 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.7 | 4.5 | 5 | 5.6 | 0.47958
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-7 | 250-PG-20036-01C03-P CML-7 | yes | FPSO 2016 | Pipe Wall Thickness | 24412 | Re-check as requested by N.Sequera | 2016-07-06 07:00 | 2016-07-06 15:00 | Check Corrosion Rate of 0.539mm/ yr | 41 | Kirstie Albone | 2017-03-23 15:07 | [32 empty] | 8.05 | CML-7 | CML: Elbow | 6 | 2025-12-21 | 2025-04-04 | 2016-07-06 07:00 | 2.5 | 0.53881 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.6 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | 0 | 8.1 | 8.7 | 7.6 | 7.8 | 0.47958
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23020-01C03 | CML-4 | 50-PL-23020-01C03 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10118 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8.625 | CML-4 | CML: type TBC | 6 | 2018-06-23 | 2018-05-19 | 2013-11-08 | 2.5 | 1.2319 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 8.2 | 3 O'Clock | 50 | 8.74 | 50-PL-23020-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.6 | 8.2 | 8.4 | 9.3 | 0.47871
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1754 | Rope access | 2014-04-27 07:00 | 2014-04-27 08:00 | [36 empty] | 5.175 | CML-5 | CML: Elbow | 3 | 2016-05-04 | 2016-08-26 | 2014-04-27 07:00 | 2.5 | 1.0388 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-FH-43117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5 | 4.6 | 5.4 | 5.7 | 0.47871
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-5 | 50-CG-38474-01C02-P CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24467 | Re-check as requested by N.Sequera | 2016-07-07 07:00 | 2016-07-07 15:00 | Check Corrosion Rate of 0.529mm/ yr | [35 empty] | 4.525 | CML-5 | CML: Elbow | 3 | 2019-02-28 | 2019-10-12 | 2016-07-07 07:00 | 2.5 | 0.52866 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.9 | 6 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 | -0.28854 | 4.4 | 4.9 | 3.9 | 4.9 | 0.47871
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43141-01C02 | CML-1 | 150-FH-43141-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10652 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.725 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2013-11-18 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.3 | 9 O'Clock | 100 | 6.02 | 100-FH-43141-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 7.4 | 6.7 | 6.3 | 0.47871
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56138-01C02 | CML-4 | 50-DH-56138-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22312 | Rope Access | 2014-05-06 14:00 | 2014-05-06 15:00 | [36 empty] | 5.875 | CML-4 | CML: type TBC | 3 | 2025-03-11 | 2026-06-16 | 2014-05-06 14:00 | 2.5 | 0.25796 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-DH-56138-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.3 | 6.1 | 6.4 | 0.47871
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-11 | 50-FH-43011-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 7961 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.875 | CML-11 | CML: Elbow | 3 | 2018-11-17 | 2018-02-26 | 2015-01-18 08:00 | 2.5 | 0.99156 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 6.3 | 9 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.1 | 7.4 | 6.7 | 6.3 | 0.47871
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-1 | 50-DH-56013-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1850 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 6.375 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 6.9 | 6.6 | 5.8 | 0.47871
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56013-01C02 | CML-1 | 50-DH-56013-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22330 | Rope Access | 2014-05-06 08:00 | 2014-05-06 09:00 | [36 empty] | 6.375 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 6.9 | 6.6 | 5.8 | 0.47871
WC01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-WC-40006-01C02 | CML-16 | 150-WC-40006-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 22834 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.725 | CML-16 | CML: Elbow | 3 | 2024-04-08 | 2024-08-17 | 2015-04-30 07:00 | 2.5 | 0.32408 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 1.0896 | 5.8 | 6 | 5.7 | 5.4 | 0.25
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56555-01C02 | CML-4 | 50-DH-56555-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21126 | Reviewed 20/11/14. FFS. Re check Oct.18. Review RBI to include this line. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-20 16:44 | [32 empty] | 6.425 | CML-4 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-10-08 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56555-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.8 | 6.3 | 6.8 | 5.8 | 0.47871
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-19 | 200-PW-44018-01X01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8943 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.475 | CML-19 | CML: type TBC | 3 | 2028-12-20 | 2030-08-21 | 2015-02-26 09:00 | 2.5 | 0.19532 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.2 | 5.3 | 5.8 | 0.27538
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-3 | 200-PG-23065-09C02-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 417 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.125 | CML-3 | CML: Pipe Length | 3 | 2052-10-12 | 2040-05-25 | 2014-03-12 09:00 | 10.17 | 0.20536 | A4: Left Quadrant |  | 15.26 | 10.17 | 12.715 | 18.1 | 9 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.93 |  | 19.8 | 19.5 | 19.1 | 18.1 | 0.74106
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20504-03C03-P | CML-1 | 50-PF-20504-03C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7746 |  | 2015-01-10 13:00 | 2015-01-10 16:00 | [36 empty] | 8.725 | CML-1 | CML: Elbow | 6 | 2029-02-15 | 2028-10-27 | 2015-01-10 13:00 | 2.5 | 0.39691 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.1 | 12 O'Clock | 50 | 8.74 | 50-PF-20504-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 9.1 | 9.1 | 8.6 | 0.47871
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-15 | 200-PW-44018-01X01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23287 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.4 | CML-15 | CML: Pipe Length | 3 | 2033-06-19 | 2035-10-20 | 2015-05-12 07:00 | 2.5 | 0.14902 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-DC-57008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 5.8 | 5.3 | 0.2708
PG03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 80-FG-45306-03C03-P | CML-3 | 80-FG-45306-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22087 | Protective mesh removed | 2014-07-02 11:00 | 2014-07-02 12:00 | [36 empty] | 10.375 | CML-3 | CML: Reducing Tee | 6 | 2021-09-14 | 2020-06-10 | 2014-07-02 11:00 | 2.5 | 1.0403 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 10 | 9 O'Clock | 80 | 11.13 | 80-FG-45306-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.5 | 11 | 10 | 10 | 0.47871
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44037-01C03 | CML-2 | 300-PW-44037-01C03 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 21912 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 10.375 | CML-2 | CML: Elbow | 6 | 2064-07-23 | 2058-08-19 | 2014-10-16 07:00 | 2.5 | 0.1526 | A3: Inside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.1 | 6 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.6 | 10.5 | 10.1 | 10.3 | 0.22174
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-2 | 300-PF-20501-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21678 | Protective mesh removed | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.075 | CML-2 | CML: Pipe Length | 6 | 2035-03-19 | 2031-04-17 | 2014-09-28 07:00 | 4.9 | 0.4296 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 13.7 | 14.2 | 14.7 | 13.7 | 0.47871
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 12624 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.175 | CML-5 | CML: type TBC | 3 | 2015-04-23 | 2015-07-06 | 2014-01-23 10:00 | 2.5 | 1.6056 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.2 | 5.4 | 5.6 | 0.47871
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-8 | 80-FH-43158-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12889 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.725 | CML-8 | CML: type TBC | 3 | 2020-01-23 | 2020-11-01 | 2014-01-22 11:00 | 2.5 | 0.44955 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.5 | 5.9 | 6.3 | 0.47871
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43141-01C02 | CML-3 | 150-FH-43141-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10654 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.675 | CML-3 | CML: type TBC | 3 | 2095-05-02 | 2098-01-14 | 2013-11-18 | 2.5 | 0.04294 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 6 O'Clock | 100 | 6.02 | 100-FH-43141-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.1 | 6.7 | 6 | 6.9 | 0.47871
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40509-1CG | CML-1 | 150-WC-40509-1CG CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8699 | Material Class Not Selectable | 2015-02-13 14:00 | 2015-02-13 15:00 |  |  | Administrator | 2015-09-08 11:25 | [32 empty] | 11.15 | CML-1 | CML: Elbow | 3 | 2098-02-09 | 2070-10-05 | 2015-02-13 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 7.97 | 2.5 | 5.235 | 11 | 12 O'Clock | 150 | 10.97 | 150-WC-40509-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11 | 11.2 | 11.3 | 11.1 | 0.1291
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-2 | 200-PL-20035-03C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21337 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.75 | CML-2 | CML: Elbow | 3 | 2020-08-14 | 2019-05-20 | 2014-06-27 13:00 | 3.61 | 0.6339 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 7.5 | 9 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.89 |  | 7.9 | 7.7 | 7.9 | 7.5 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-18 | 250-FH-43303-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 12956 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 9.275 | CML-18 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.6 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.5 | 8.6 | 9.7 | 9.3 | 0.47871
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-7 | 250-PG-23003-06C02-PA CML-7 | Yes | FPSO 2014 | Pipe Wall Thickness | 24245 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.325 | CML-7 | CML: Pipe Length | 3 | 2063-03-06 | 2055-03-16 | 2014-09-24 07:00 | 7.9 | 0.14439 | A1: Outside Quadrant |  | 12.09 | 7.9 | 9.0519 | 14.9 | 12 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 14.9 | 15.1 | 16 | 15.3 | 0.47871
PG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-PG-23071-01C03 | CML-7 | 100-PG-23071-01C03 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2405 | Rope Access | 2014-03-19 13:00 | 2014-03-19 14:00 | [36 empty] | 10.425 | CML-7 | CML: type TBC | 6 | 2020-05-20 | 2019-05-15 | 2014-03-19 13:00 | 2.5 | 1.2144 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 10 | 9 O'Clock | 150 | 10.97 | 150-PG-23071-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.4 | 11.1 | 10.2 | 10 | 0.47871
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-11 | 300-PG-20048-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21481 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | Check Corrosion Rate of 0.558mm/ yr | 38 | [34 empty] | 12.625 | CML-11 | CML: Pipe Length | 6 | 2018-11-05 | 2017-08-13 | 2014-06-28 09:30 | 3.3 | 2.0185 | A1: Outside Quadrant |  | 8.27 | 3.3 | 5.785 | 12.1 | 12 O'Clock | 200 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 12.1 | 12.4 | 13.2 | 12.8 | 0.47871
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38470-01C02-P | CML-8 | 50-CG-38470-01C02-P CML-8 | Yes | FPSO 2015 | Pipe Wall Thickness | 23614 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 6.375 | CML-8 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 12 O'Clock | 50 | 5.54 | 50-CG-38470-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.6 | 6.4 | 6.8 | 0.47871
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-14 | 150-FH-43026-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12654 |  | 2014-01-22 07:00 | 2014-01-22 10:00 | [36 empty] | 7.425 | CML-14 | CML: Elbow | 3 | 2032-01-25 | 2028-09-14 | 2014-01-22 07:00 | 1.03 | 0.32577 | A2: Right Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.9 | 3 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.87 |  | 8 | 6.9 | 7.6 | 7.2 | 0.47871
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-1 | 200-PG-20300-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5866 | Rope Access | 2014-06-25 09:30 | 2014-06-25 10:30 | [36 empty] | 11.125 | CML-1 | CML: Elbow | 6 | 2018-03-10 | 2017-04-28 | 2014-06-25 09:30 | 3.3 | 1.9684 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 10.6 | 12 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.6 | 11.3 | 11.7 | 10.9 | 0.47871
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-13 | 200-PW-44018-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8889 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.4 | CML-13 | CML: type TBC | 3 | 2028-12-11 | 2030-08-11 | 2015-02-25 09:30 | 2.5 | 0.19562 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.8 | 5.3 | 5.3 | 5.2 | 0.2708
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-10 | 50-PW-44040-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 23245 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.375 | CML-10 | CML: Fitting | 3 | 2026-10-31 | 2028-04-09 | 2015-05-11 07:00 | 2.5 | 0.22642 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0 | 5.3 | 5.1 | 5.4 | 5.7 | 0.25
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8405 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 5.725 | CML-1 | CML: type TBC | 3 | 2049-07-31 | 2053-06-17 | 2015-01-30 07:30 | 2.5 | 0.084 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AU-63016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6 | 5.7 | 5.8 | 0.25
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38002-09C02-P | CML-4 | 50-CG-38002-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20795 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 |  |  | Administrator | 2015-09-07 10:59 | [32 empty] | 10.9 | CML-4 | CML: Fitting | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 10.2 | 9 O'Clock | 50 | 8.74 | 50-CG-38002-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 11.2 | 11 | 11.2 | 10.2 | 0.4761
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-18 | 100-DH-56009-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 3441 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.3 | CML-18 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5 | 9 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.2 | 6 | 5 | 0.4761
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43170-01C02 | CML-3 | 250-FL-43170-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23070 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.5 | CML-3 | CML: Elbow | 3 | 2026-12-07 | 2026-10-31 | 2015-05-07 07:00 | 2.5 | 0.28463 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 9 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.19363 | 6.6 | 6.8 | 6.8 | 5.8 | 0.4761
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-6 | 150-WC-40006-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22500 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.7 | CML-6 | CML: Elbow | 3 | 2021-01-19 | 2020-12-30 | 2015-04-20 07:00 | 2.5 | 0.50378 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 3 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.4 | 5.7 | 6 | 0.24495
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-5 | 100-PW-20021-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22823 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.3 | CML-5 | CML: Elbow | 3 | 2020-09-23 | 2020-12-20 | 2015-04-30 07:00 | 2.5 | 0.48089 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.1 | 9 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.18159 | 5.4 | 5.1 | 5.6 | 5.1 | 0.24495
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-6 | 300-PW-44003-01C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21848 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 10.2 | CML-6 | CML: Elbow | 6 | 2034-08-07 | 2032-02-23 | 2014-10-19 07:00 | 2.5 | 0.3684 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.8 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.2 | 10.4 | 10.4 | 9.8 | 0.28284
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-5 | 150-PG-20009-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2699 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 11.5 | CML-5 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-12 09:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 10.8 | 9 O'Clock | 100 | 8.56 | 100-PG-20009-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 11.8 | 11.8 | 11.6 | 10.8 | 0.4761
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-5 | 150-PG-20009-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 670 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 11.5 | CML-5 | CML: Elbow | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 09:00 | 2.03 | 0 | A4: Left Quadrant |  | 1.11 | 2.03 | 1.57 | 10.8 | 9 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.77 | 0 | 11.8 | 11.8 | 11.6 | 10.8 | 0.4761
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20009-01C03-P | CML-5 | 150-PG-20009-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 388 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 11.5 | CML-5 | CML: Elbow | 6 | 2064-03-18 | 2068-10-23 | 2014-03-12 | 2.03 | 0 | A4: Left Quadrant |  | 1.11 | 2.03 | 1.57 | 10.8 | 9 O'Clock | 150 | 7.11 | 150-PG-20009-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.77 |  | 11.8 | 11.8 | 11.6 | 10.8 | 0.4761
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-3 | 200-PW-44018-01X01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22961 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 5.45 | CML-3 | CML: Reducing Tee | 3 | 2033-03-28 | 2035-07-19 | 2015-05-04 07:00 | 2.5 | 0.15072 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.35437 | 5.8 | 5.3 | 5.2 | 5.5 | 0.26458
WC01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-WC-40006-01C02 | CML-14 | 150-WC-40006-01C02 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 22832 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.75 | CML-14 | CML: Elbow | 3 | 2024-04-08 | 2024-08-17 | 2015-04-30 07:00 | 2.5 | 0.32408 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 3 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.18159 | 5.9 | 5.4 | 5.8 | 5.9 | 0.23805
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-11 | 50-CG-38476-01C02-H CML-11 | Yes | FPSO 2015 | Pipe Wall Thickness | 23643 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 6.35 | CML-11 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.3 | 6.7 | 6.7 | 5.7 | 0.47258
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-6 | 50-PW-44013-01X01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5730 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 5.45 | CML-6 | CML: Elbow | 3 | 2022-11-17 | 2023-11-23 | 2014-06-22 13:00 | 2.5 | 0.32105 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -1.463 | 5.2 | 5.8 | 5.3 | 5.5 | 0.26458
FG02 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 25-FG-45455-01C02-E | CML-15 | 25-FG-45455-01C02-E CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8136 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.65 | CML-15 | CML: type TBC | 1 | 2303-03-05 | 2230-06-04 | 2015-01-23 07:30 | 2.5 | 0.01214 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.6 | 7 | 7 | 0.47258
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-13 | 25-FG-45455-01C02-E CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20329 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 6.65 | CML-13 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 20 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.6 | 7 | 7 | 6 | 0.47258
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-1 | 150-FH-43026-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23500 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 7.15 | CML-1 | CML: Pipe Length | 3 | 2055-09-10 | 2048-01-27 | 2015-07-28 07:00 | 1.03 | 0.14372 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.8 | 6 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.77 | -0.26449 | 6.8 | 7.2 | 6.8 | 7.8 | 0.47258
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-19 | 150-WC-40006-01C02 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 9078 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.575 | CML-19 | CML: type TBC | 3 | 2051-05-15 | 2055-06-11 | 2015-03-01 09:30 | 2.5 | 0.08004 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.6 | 5.9 | 5.4 | 0.23629
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43014-01C02 | CML-5 | 250-FL-43014-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23077 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.45 | CML-5 | CML: Elbow | 3 | 2026-12-07 | 2026-10-31 | 2015-05-07 07:00 | 2.5 | 0.28463 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 6 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.58097 | 6.8 | 6.4 | 5.8 | 6.8 | 0.47258
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43027-01C02 | CML-7 | 150-FH-43027-01C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10569 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 7.2333 | CML-7 | CML: type TBC | 3 | 2018-08-02 | 2018-03-08 | 2013-11-16 | 2.5 | 0.89077 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.7 | 6 O'Clock | 150 | 7.11 | 150-FH-43027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  |  | 7.6 | 6.7 | 7.4 | 0.47258
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-12 | 200-PL-20019-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21263 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.375 | CML-12 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 8.3 | 7.5 | 7.3 | 6.4 | 0.78049
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-6 | 50-DH-56062-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 9093 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.475 | CML-6 | CML: type TBC | 3 | 2020-08-09 | 2021-05-18 | 2015-03-02 07:00 | 2.5 | 0.4225 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.8 | 5.8 | 4.8 | 5.5 | 0.4717
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-1 | 100-FG-45043-03C02-E CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 22647 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 4.975 | CML-1 | CML: Elbow | 3 | 2017-12-30 | 2017-05-14 | 2015-04-27 07:00 | 1.88 | 0.90293 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 4.3 | 12 O'Clock | 100 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.42 |  | 4.3 | 5.3 | 5.3 | 5 | 0.4717
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-18 | 50-FG-45023-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1166 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.175 | CML-18 | CML: type TBC | 3 | 2074-09-03 | 2081-03-31 | 2014-03-22 09:30 | 2.5 | 0.04959 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.5 | 6.2 | 6.5 | 0.4717
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38477-01C02-P | CML-14 | 50-CG-38477-01C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 13184 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 7.675 | CML-14 | CML: Elbow | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A3: Inside Quadrant |  | 3.35 | 3.61 | 3.0831 | 7 | 6 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.39 |  | 8 | 7.7 | 7 | 8 | 0.4717
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-17 | 50-CG-38452-09C02-P CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23757 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.775 | CML-17 | CML: Elbow | 3 | 2036-12-09 | 2030-10-31 | 2015-10-30 07:00 | 2.5 | 0.26507 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.9 | 8.1 | 8.9 | 9.2 | 0.4717
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-26 | 50-PF-20300-03C03-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 21592 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.275 | CML-26 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.6 | 9.3 | 9.6 | 8.6 | 0.4717
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23070-01C03-P | CML-5 | 300-PG-23070-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20602 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 10.075 | CML-5 | CML: Elbow | 6 | 2023-04-08 | 2022-02-15 | 2014-07-25 07:30 | 2.5 | 0.79213 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.4 | 3 O'Clock | 20 | 10.31 | 300-PG-23070-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.1 | 9.4 | 10.4 | 10.4 | 0.4717
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-4 | 80-CG-38486-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 6127 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 18.025 | CML-4 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.7 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.8 |  | 18.7 | 18 | 17.7 | 17.7 | 0.4717
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-2 | 150-FL-43174-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12900 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 7.125 | CML-2 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.7 | 6 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.8 | 7 | 6.7 | 7 | 0.4717
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-20 | 100-FG-45001-09C02 CML-20 | Yes | FPSO 2015 | Pipe Wall Thickness | 23325 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.075 | CML-20 | CML: type TBC | 3 | 2031-12-28 | 2027-01-14 | 2015-07-11 07:00 | 4.7 | 0.34591 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.4 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | -0.30151 | 11.2 | 10.4 | 11.2 | 11.5 | 0.4717
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23022-03C03 | CML-12 | 50-PL-23022-03C03 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1868 | Rope Access | 2014-03-25 08:30 | 2014-03-25 11:00 | [36 empty] | 9.575 | CML-12 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 08:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 12 O'Clock | 50 | 8.74 | 50-PL-23022-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 10 | 9.7 | 9.7 | 0.4717
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-11 | 50-PF-20300-03C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21577 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.2 | CML-11 | CML: type TBC | 6 | 2166-12-01 | 2163-12-19 | 2014-05-26 09:30 | 2.5 | 0.04062 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.8 | 9.3 | 9 | 8.7 | 0.46904
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-16 | 80-CG-38486-09C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2059 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 16.1 | CML-16 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 15.5 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13 |  | 16.6 | 15.5 | 16.3 | 16 | 0.46904
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-4 | 80-PW-44035-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23268 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.325 | CML-4 | CML: Elbow | 3 | 2028-04-28 | 2030-01-22 | 2015-05-12 07:00 | 2.5 | 0.20041 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 12 O'Clock | 20 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0 | 5.1 | 5.4 | 5.2 | 5.6 | 0.22174
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-1 | 25-PW-44026-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5754 | Rope access | 2014-06-23 07:00 | 2014-06-23 08:00 | [36 empty] | 6.6 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-PW-44026-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.7 | 7.2 | 6.4 | 0.46904
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44509-01C03-P | CML-11 | 250-PW-44509-01C03-P CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 22996 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.85 | CML-11 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2015-05-05 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.8 | 9 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 | -1.6675 | 9.8 | 9.9 | 9.9 | 9.8 | 0.057735
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-8 | 50-DH-56070-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3224 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.2 | CML-8 | CML: type TBC | 3 | 2017-11-12 | 2018-05-06 | 2014-05-09 07:00 | 2.5 | 0.68246 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.9 | 5 | 5 | 0.46904
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-12 | 50-FG-45021-03C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2624 | Rope Access | 2014-04-26 10:45 | 2014-04-26 13:00 | [36 empty] | 5.3 | CML-12 | CML: type TBC | 3 | 2018-06-29 | 2018-06-17 | 2014-04-26 10:45 | 2.5 | 0.59827 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.67824 | 5.1 | 6 | 5 | 5.1 | 0.46904
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-43 | 400-FH-43508-01C02 CML-43 |  | FPSO 2015 | Pipe Wall Thickness | 23562 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 8.2 | CML-43 | CML: Elbow | 3 | 258310 | 229699 | 2015-08-10 07:30 | 2.5 | 0.00912 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 7.9 | 3 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8 | 7.9 | 8 | 8.9 | 0.46904
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-22 | 300-PG-20005-03C03-P CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 23362 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 14.3 | CML-22 | CML: Reducing Tee | 6 | 2087-06-17 | 2074-02-21 | 2015-07-20 07:00 | 4.9 | 0.12646 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 | -2.2256 | 15 | 14.1 | 14 | 14.1 | 0.46904
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-8 | 50-PF-20300-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21574 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.2 | CML-8 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 9 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.7 | 9.1 | 9.4 | 8.6 | 0.46904
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-19 | 50-CG-24002-09C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2565 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 10.2 | CML-19 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 9.7 | 3 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.9 | 9.7 | 10.6 | 10.6 | 0.46904
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5610 |  | 2014-06-20 09:30 | 2014-06-20 11:00 | [36 empty] | 7.5 | CML-2 | CML: Elbow | 3 |  |  | 2014-06-20 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7.2 | 12 O'Clock | 150 |  | 150-PG-23402-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.2 | 7.3 | 8.2 | 7.3 | 0.46904
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67005-01E01 | CML-2 | 50-GN-67005-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8494 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.575 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-02-02 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 25 | 6.35 | 25-GN-67005-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.5 | 6.5 | 6.6 | 0.095743
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67005-01E01 | CML-1 | 50-GN-67005-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8493 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.95 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-02-02 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 25 | 6.35 | 25-GN-67005-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.3 | 7.3 | 6.6 | 6.6 | 0.40415
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67005-01E01 | CML-3 | 50-GN-67005-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8495 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.75 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-02-02 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 25 | 6.35 | 25-GN-67005-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.8 | 6.8 | 6.7 | 6.7 | 0.057735
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53009-01E01 | CML-2 | 50-WD-53009-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8176 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.45 | CML-2 | CML: type TBC | 3 | 2038-10-23 | 2038-08-16 | 2015-01-24 07:30 | 2.5 | 0.1515 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 25 | 6.35 | 25-WD-53009-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.9 | 6.3 | 6.5 | 0.34157
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53009-01E01 | CML-1 | 50-WD-53009-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8175 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.375 | CML-1 | CML: type TBC | 3 | 2055-09-28 | 2055-06-07 | 2015-01-24 07:30 | 2.5 | 0.0909 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 25 | 6.35 | 25-WD-53009-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.3 | 6.2 | 6.5 | 0.15
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53009-01E01 | CML-3 | 50-WD-53009-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8177 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 7.425 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.4 | 9 O'Clock | 25 | 6.35 | 25-WD-53009-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.4 | 7.4 | 7.5 | 7.4 | 0.05
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 50-WS-50839-1CG | CML-1 | 50-WS-50839-1CG CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10879 | Deck Level | 2014-01-05 | 2014-01-05 | Leaking Valve | [35 empty] | 3.625 | CML-1 | CML: type TBC | 3 | 2014-03-22 | 2014-02-17 | 2014-01-05 | 2.5 | 4.7718 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.925 | 3.5 | 12 O'Clock | 25 | 6.35 | 25-WS-50839-1LC | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.5 | 3.6 | 3.8 | 3.6 | 0.12583
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 50-WS-50839-1CG | CML-2 | 50-WS-50839-1CG CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10880 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 3.85 | CML-2 | CML: type TBC | 3 | 2014-04-02 | 2014-02-27 | 2014-01-05 | 2.5 | 4.6044 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.925 | 3.6 | 12 O'Clock | 25 | 6.35 | 25-WS-50839-1LC | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.1 |  | 3.6 | 3.8 | 4.1 | 3.9 | 0.20817
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-14 | 50-WS-50839-1CG CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12633 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.4 | CML-14 | CML: type TBC | 3 | 2017-11-20 | 2018-05-14 | 2014-01-23 10:00 | 2.5 | 0.67931 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.5 | 5.1 | 5.3 | 0.2582
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-2 | 50-WS-50839-1CG CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12621 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.4 | CML-2 | CML: type TBC | 3 | 2017-11-20 | 2018-05-14 | 2014-01-23 10:00 | 2.5 | 0.67931 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.4 | 5.7 | 5.4 | 0.24495
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-7 | 50-WS-50839-1CG CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12877 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 6.15 | CML-7 | CML: type TBC | 3 | 2132-08-06 | 2136-07-14 | 2014-02-03 08:00 | 2.5 | 0.02951 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 9 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.1 | 6.2 | 6.3 | 6 | 0.1291
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-6 | 50-WS-50839-1CG CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12876 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 6.15 | CML-6 | CML: type TBC | 3 | 2132-08-06 | 2136-07-14 | 2014-02-03 08:00 | 2.5 | 0.02951 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.2 | 6.2 | 0.1
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-11 | 50-WS-50839-1CG CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12881 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 6.05 | CML-11 | CML: type TBC | 3 | 2132-08-06 | 2136-07-14 | 2014-02-03 08:00 | 2.5 | 0.02951 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 9 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6 | 6 | 0.1
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-26 | 50-WS-50839-1CG CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 12719 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.4 | CML-26 | CML: type TBC | 3 | 2020-10-21 | 2020-10-01 | 2014-02-01 09:00 | 2.5 | 0.52063 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.7 | 6.5 | 6.4 | 0.29439
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-25 | 50-WS-50839-1CG CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 12718 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.4 | CML-25 | CML: type TBC | 3 | 2020-10-21 | 2020-10-01 | 2014-02-01 09:00 | 2.5 | 0.52063 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 12 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.8 | 6.5 | 6.3 | 0.33665
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-19 | 50-WS-50839-1CG CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 12712 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.525 | CML-19 | CML: type TBC | 3 | 2020-10-21 | 2020-10-01 | 2014-02-01 09:00 | 2.5 | 0.52063 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.8 | 6.7 | 6 | 6.6 | 0.3594
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-14 | 50-WS-50839-1CG CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12707 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.55 | CML-14 | CML: type TBC | 3 | 2020-10-21 | 2020-10-01 | 2014-02-01 09:00 | 2.5 | 0.52063 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.5 | 6.7 | 6 | 7 | 0.42032
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-10 | 50-WS-50839-1CG CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12629 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.4 | CML-10 | CML: type TBC | 3 | 2019-03-15 | 2019-10-28 | 2014-01-23 10:00 | 2.5 | 0.52492 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.5 | 5.2 | 5.3 | 0.18257
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-8 | 50-WS-50839-1CG CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12627 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.5 | CML-8 | CML: type TBC | 3 | 2021-08-12 | 2022-06-29 | 2014-01-23 10:00 | 2.5 | 0.37053 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.5 | 5.3 | 5.3 | 0.28284
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-16 | 50-WS-50839-1CG CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12635 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.5 | CML-16 | CML: type TBC | 3 | 2021-08-12 | 2022-06-29 | 2014-01-23 10:00 | 2.5 | 0.37053 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.6 | 5.6 | 5.5 | 0.14142
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-3 | 50-WS-50839-1CG CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12622 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.45 | CML-3 | CML: type TBC | 3 | 2021-08-12 | 2022-06-29 | 2014-01-23 10:00 | 2.5 | 0.37053 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 5.6 | 5.5 | 0.1291
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-18 | 50-WS-50839-1CG CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 12637 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.55 | CML-18 | CML: type TBC | 3 | 2027-06-21 | 2028-12-23 | 2014-01-23 10:00 | 2.5 | 0.21614 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.6 | 5.6 | 5.6 | 0.1
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-15 | 50-WS-50839-1CG CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12634 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.45 | CML-15 | CML: type TBC | 3 | 2027-06-21 | 2028-12-23 | 2014-01-23 10:00 | 2.5 | 0.21614 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.5 | 5.4 | 5.4 | 0.057735
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-20 | 50-WS-50839-1CG CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 12639 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.5 | CML-20 | CML: type TBC | 3 | 2027-06-21 | 2028-12-23 | 2014-01-23 10:00 | 2.5 | 0.21614 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.4 | 5.4 | 5.6 | 0.11547
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-1 | 50-WS-50839-1CG CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12620 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.4 | CML-1 | CML: type TBC | 3 | 2027-06-21 | 2028-12-23 | 2014-01-23 10:00 | 2.5 | 0.21614 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.4 | 0
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-7 | 50-WS-50839-1CG CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 12626 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.825 | CML-7 | CML: type TBC | 3 | 2062-08-10 | 2067-11-20 | 2014-01-23 10:00 | 2.5 | 0.06176 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 6.1 | 5.9 | 5.5 | 0.25
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-13 | 50-WS-50839-1CG CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12632 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.775 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-01-23 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 5.7 | 5.6 | 5.9 | 0.15
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-12 | 50-WS-50839-1CG CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12631 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.9 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-01-23 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6 | 6.2 | 5.7 | 0.24495
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-12 | 50-WS-50839-1CG CML-12 | yes | FPSO 2015 | Pipe Wall Thickness | 22673 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 4.7 | CML-12 | CML: Elbow | 3 | 2018-01-30 | 2018-08-01 | 2015-04-27 07:00 | 2.5 | 0.65095 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 6 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 | 0.47738 | 4.7 | 5 | 4.3 | 4.8 | 0.29439
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-5 | 50-WS-50839-1CG CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12604 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.05 | CML-5 | CML: Pipe Length | 3 | 2015-07-05 | 2015-09-26 | 2014-01-23 13:00 | 2.5 | 1.4505 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.2 | 4.8 | 5.6 | 0.44347
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-4 | 50-WS-50839-1CG CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22665 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 4.925 | CML-4 | CML: Elbow | 3 | 2020-04-21 | 2021-01-16 | 2015-04-27 07:00 | 2.5 | 0.44097 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 1.5117 | 4.7 | 5 | 4.7 | 5.3 | 0.28723
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-10 | 50-WS-50839-1CG CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12609 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.325 | CML-10 | CML: Elbow | 3 | 2015-10-05 | 2016-01-04 | 2014-01-23 13:00 | 2.5 | 1.2962 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 5.6 | 4.7 | 5.7 | 0.45
Marine | Montara_Topside | No | Flare (43) | Pipework | 50-WS-50839-1CG | CML-11 | 50-WS-50839-1CG CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12610 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.1 | CML-11 | CML: Pipe Length | 3 | 2015-10-05 | 2016-01-04 | 2014-01-23 13:00 | 2.5 | 1.2962 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.4 | 5 | 4.7 | 5.3 | 0.31623
Marine | Montara_Topside | No | Separation (20) | Pipework | 50-WS-50839-1CG | CML-5 | 50-WS-50839-1CG CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 13175 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.45 | CML-5 | CML: Pipe Length | 3 | 2020-06-23 | 2020-06-05 | 2014-01-21 13:00 | 2.5 | 0.54468 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 3 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6 | 6.5 | 7.1 | 0.47958
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 50-WS-50839-1CG | CML-4 | 50-WS-50839-1CG CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10882 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 4.025 | CML-4 | CML: type TBC | 3 | 2014-05-09 | 2014-04-01 | 2014-01-05 | 2.5 | 4.1021 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.925 | 3.9 | 12 O'Clock | 25 | 6.35 | 25-WS-50839-1LC | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4 | 4.2 | 4 | 0.12583
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 50-WS-50839-1CG | CML-3 | 50-WS-50839-1CG CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10881 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 4 | CML-3 | CML: type TBC | 3 | 2014-05-09 | 2014-04-01 | 2014-01-05 | 2.5 | 4.1021 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.925 | 3.9 | 12 O'Clock | 25 | 6.35 | 25-WS-50839-1LC | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 3.9 | 4 | 4.1 | 4 | 0.08165
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-12 | 150-FG-45002-03C02 CML-12 | yes | FPSO 2013 | Pipe Wall Thickness | 10415 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.55 | CML-12 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6 | 3 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7.4 | 6 | 6.6 | 6.2 | 0.61914
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-8 | 150-FG-45002-03C02 CML-8 | yes | FPSO 2013 | Pipe Wall Thickness | 10411 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.35 | CML-8 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6 | 6 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.6 | 6.1 | 6 | 6.7 | 0.35119
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-6 | 150-FG-45002-03C02 CML-6 | yes | FPSO 2013 | Pipe Wall Thickness | 10409 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 7.1 | CML-6 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6 | 12 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 7.7 | 7.1 | 7.6 | 0.77889
PL01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PL-44008-01C02 | CML-8 | 80-PL-44008-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5745 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 7.15 | CML-8 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.4 | 6 O'Clock | 40 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.8 | 7.4 | 6.4 | 7 | 0.59722
WC01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22938 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.675 | CML-4 | CML: Reducing Tee | 3 | 2055-01-18 | 2059-07-08 | 2015-05-02 07:00 | 2.5 | 0.07297 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57025-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.091479 | 5.9 | 5.6 | 5.8 | 5.4 | 0.22174
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-4 | 300-PG-23400-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 521 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 |  |  | John Wilson | 2017-03-24 09:40 | Anomaly to revisit 7/5/2018 | [31 empty] | 9.775 | CML-4 | CML: Pipe Length | 6 | 2016-01-18 | 2016-04-13 | 2014-03-13 09:00 | 5.22 | 1.9313 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 8.8 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.58 |  | 8.8 | 10.5 | 9.6 | 10.2 | 0.75
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-20 | 300-PF-20501-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21696 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.55 | CML-20 | CML: Pipe Length | 6 | 2086-07-01 | 2073-05-09 | 2014-09-28 07:00 | 4.9 | 0.12813 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 15 | 14.9 | 14.2 | 14.1 | 0.46547
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56029-01C02 | CML-1 | 80-DH-56029-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20907 | Rope Access | 2014-05-22 09:30 | 2014-05-22 11:00 | [36 empty] | 5.85 | CML-1 | CML: Elbow | 3 | 2028-09-22 | 2030-07-05 | 2014-05-22 09:30 | 2.5 | 0.19513 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 12 O'Clock | 80 | 5.49 | 80-DH-56029-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6 | 6.4 | 5.7 | 0.46547
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 25-WS-50840-1LC | CML-2 | 25-WS-50840-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10895 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 3.925 | CML-2 | CML: type TBC | 3 | 2014-04-13 | 2014-03-09 | 2014-01-05 | 2.5 | 4.4369 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.925 | 3.7 | 12 O'Clock | 25 | 6.35 | 25-WS-50840-1LC | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.7 | 4 | 4.1 | 3.9 | 0.17078
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63001-01E01 | CML-1 | 50-AI-63001-01E01 CML-1 |  | FPSO 2017 | Pipe Wall Thickness | 8308 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2017-03-29 06:28 | 2015-01-27 15:00 | [36 empty] | 7.25 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2017-03-29 06:28 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-AI-63001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 8.2 | 6.7 | 8 | 1.0149
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 25-WS-50840-1LC | CML-1 | 25-WS-50840-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10894 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 3.9 | CML-1 | CML: type TBC | 3 | 2014-04-13 | 2014-03-09 | 2014-01-05 | 2.5 | 4.4369 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.925 | 3.7 | 9 O'Clock | 25 | 6.35 | 25-WS-50840-1LC | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.2 |  | 3.9 | 4.1 | 3.9 | 3.7 | 0.1633
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-4 | 50-CG-38476-01C02-H CML-4 | Yes | FPSO 2015 | Pipe Wall Thickness | 23636 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 7.45 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 3 O'Clock | 40 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.5 | 6.8 | 7.6 | 7.9 | 0.46547
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56023-01C02 | CML-1 | 80-DH-56023-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3480 | Rope Access | 2014-05-14 08:00 | 2014-05-14 09:00 | [36 empty] | 5.05 | CML-1 | CML: type TBC | 3 | 2016-08-10 | 2016-12-24 | 2014-05-14 08:00 | 2.5 | 0.93527 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 3 O'Clock | 80 | 5.49 | 80-DH-56023-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.4 | 4.6 | 4.7 | 5.5 | 0.46547
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-15 | 25-FG-45455-01C02-E CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21818 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6.45 | CML-15 | CML: Elbow | 3 | 2253-01-17 | 2260-12-16 | 2014-10-11 07:00 | 2.5 | 0.01468 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.8 | 6.9 | 6.1 | 0.46547
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 25-WS-50840-1LC | CML-4 | 25-WS-50840-1LC CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10897 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 4 | CML-4 | CML: type TBC | 3 | 2014-04-26 | 2014-03-20 | 2014-01-05 | 2.5 | 4.2695 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.925 | 3.8 | 9 O'Clock | 25 | 6.35 | 25-WS-50840-1LC | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4 | 4.1 | 4.1 | 3.8 | 0.14142
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 25-WS-50840-1LC | CML-3 | 25-WS-50840-1LC CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10896 | Deck Level | 2014-01-05 | 2014-01-05 | [36 empty] | 4 | CML-3 | CML: type TBC | 3 | 2014-05-09 | 2014-04-01 | 2014-01-05 | 2.5 | 4.1021 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.925 | 3.9 | 6 O'Clock | 25 | 6.35 | 25-WS-50840-1LC | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.4 |  | 4.2 | 3.9 | 3.9 | 4 | 0.14142
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-12 | 150-WC-40006-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22756 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 5.675 | CML-12 | CML: Reducing Tee | 3 | 2021-02-24 | 2021-02-04 | 2015-04-29 07:00 | 2.5 | 0.49728 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 9 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.35012 | 5.9 | 5.8 | 5.6 | 5.4 | 0.22174
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-13 | 150-WC-40006-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22507 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.725 | CML-13 | CML: Elbow | 3 | 2021-01-19 | 2020-12-30 | 2015-04-20 07:00 | 2.5 | 0.50378 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 3 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.4 | 5.8 | 5.9 | 0.22174
PG01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-PG-20507-01C03-P | CML-1 | 150-PG-20507-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2845 | Rope Access | 2014-03-16 07:00 | 2014-03-16 09:00 | [36 empty] | 11.15 | CML-1 | CML: type TBC | 6 | 2031-06-26 | 2028-11-06 | 2014-03-16 07:00 | 2.5 | 0.46845 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 10.6 | 12 O'Clock | 150 | 10.97 | 150-FH-20507-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 10.6 | 11 | 11.3 | 11.7 | 0.46547
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-6 | 100-FL-43455-01C02-P CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 20489 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 5.45 | CML-6 | CML: Elbow | 3 | 2018-01-14 | 2018-03-11 | 2014-10-03 07:00 | 2.5 | 0.7609 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 6 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6.1 | 5.4 | 5 | 5.3 | 0.46547
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-17 | 150-WC-40006-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 9048 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.675 | CML-17 | CML: type TBC | 3 | 2051-05-13 | 2055-06-08 | 2015-03-01 07:00 | 2.5 | 0.08006 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.7 | 5.9 | 5.7 | 0.20616
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-25 | 50-AU-63015-01E01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 9056 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6.425 | CML-25 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.5 | 6.1 | 6.9 | 0.3594
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-19 | 50-AU-63015-01E01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 9050 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6.125 | CML-19 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 6.1 | 6.1 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-19 | 50-AI-63004-01E01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 9010 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.125 | CML-19 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.1 | 6.1 | 6.2 | 0.05
WC01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-WC-40006-01C02 | CML-15 | 150-WC-40006-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 6598 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.5 | CML-15 | CML: Pipe Length | 3 | 2053-01-31 | 2057-05-05 | 2015-03-30 07:00 | 2.5 | 0.07658 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.8 | 5.4 | 5.4 | 0.2
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63010-01E01 | CML-5 | 50-AI-63010-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8775 |  | 2015-02-15 13:00 | 2015-02-15 14:00 | [36 empty] | 6.3 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-AI-63010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.5 | 6.3 | 6.1 | 6.3 | 0.1633
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63010-01E01 | CML-4 | 50-AI-63010-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8774 |  | 2015-02-15 13:00 | 2015-02-15 14:00 | [36 empty] | 6.2 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-AI-63010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.2 | 6.1 | 6.1 | 0.14142
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63006-01E01 | CML-4 | 25-AI-63006-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8581 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-07 14:00 | 2015-02-07 16:00 | [36 empty] | 6.2 | CML-4 | CML: type TBC | 3 | 2039-05-31 | 2039-03-23 | 2015-02-07 14:00 | 2.5 | 0.14799 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 9 O'Clock | 25 | 6.35 | 25-AI-63006-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.3 | 6.2 | 6.2 | 6.1 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63006-01E01 | CML-2 | 25-AI-63006-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8579 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-07 14:00 | 2015-02-07 16:00 | [36 empty] | 6.45 | CML-2 | CML: type TBC | 3 | 2039-05-31 | 2039-03-23 | 2015-02-07 14:00 | 2.5 | 0.14799 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 25 | 6.35 | 25-AI-63006-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.8 | 6.1 | 6.7 | 6.2 | 0.35119
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63006-01E01 | CML-1 | 25-AI-63006-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8578 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-07 14:00 | 2015-02-07 16:00 | [36 empty] | 6.475 | CML-1 | CML: type TBC | 3 | 2039-05-31 | 2039-03-23 | 2015-02-07 14:00 | 2.5 | 0.14799 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 12 O'Clock | 25 | 6.35 | 25-AI-63006-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.8 | 6.5 | 6.5 | 0.28723
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-10 | 100-DH-56082-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 3378 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 6.35 | CML-10 | CML: type TBC | 3 | 2023-10-04 | 2024-02-06 | 2014-05-10 09:30 | 2.5 | 0.34013 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 12 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6.8 | 6.4 | 6.5 | 0.46547
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-12 | 150-WC-40006-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 9071 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.7 | CML-12 | CML: type TBC | 3 | 2051-05-15 | 2055-06-10 | 2015-03-01 09:30 | 2.5 | 0.08004 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.8 | 5.8 | 5.4 | 0.2
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-7 | 50-AI-63009-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8529 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.525 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.1 | 6.9 | 6.9 | 0.43493
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63021-01E01 | CML-7 | 50-AU-63021-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8449 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.55 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-AU-63021-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.8 | 6.5 | 6.1 | 6.8 | 0.33166
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23411-03C02-P | CML-3 | 50-PG-23411-03C02-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8387 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.2 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2015-01-30 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.2 | 6.1 | 6.3 | 0.08165
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 50-PG-23408-01C02-P | CML-1 | 50-PG-23408-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8379 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 6.225 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-PG-23408-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.1 | 6.5 | 6.2 | 0.1893
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63011-01E01 | CML-1 | 50-AI-63011-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8338 |  | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.275 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-AI-63011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.4 | 6.3 | 6.3 | 0.12583
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53003-01E01 | CML-8 | 50-WD-53003-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8298 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.5 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-WD-53003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.5 | 6.8 | 6.6 | 0.29439
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-32 | 50-WD-53010-01E01 CML-32 |  | FPSO 2015 | Pipe Wall Thickness | 8275 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.1 | CML-32 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.1 | 6.1 | 6.1 | 0
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-10 | 50-WD-53010-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8253 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.35 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.1 | 6.6 | 6.5 | 0.23805
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-9 | 50-WD-53010-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8252 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.525 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.9 | 6.1 | 6.3 | 6.8 | 0.38622
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53013-01E01 | CML-5 | 50-WD-53013-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8241 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.275 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-WD-53013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.1 | 6.2 | 6.4 | 0.15
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53012-01E01 | CML-6 | 50-WD-53012-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8214 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.225 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-WD-53012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.2 | 6.2 | 6.1 | 0.12583
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-9 | 150-WC-40006-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8933 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.5 | CML-9 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.4 | 5.4 | 5.4 | 0.2
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-12 | 100-OL-69002-01S01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8133 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.65 | CML-12 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.1 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.7 | 7.1 | 6.7 | 0.41231
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-6 | 100-OL-69001-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8108 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.65 | CML-6 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.1 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.6 | 7 | 6.9 | 0.40415
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69003-01S01 | CML-9 | 80-OL-69003-01S01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8087 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 21.5 | CML-9 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.49 | 2.5 | 3.1519 | 6.1 | 9 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.6 | 6.3 | 67 | 6.1 | 30.334
PW03 | Montara_Topside | Yes | Potable Water (53) | Pipework | 200-PW-44018-01X01 | CML-5 | 200-PW-44018-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8281 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 5.425 | CML-5 | CML: type TBC | 3 | 2028-03-17 | 2029-10-18 | 2015-01-26 07:30 | 2.5 | 0.20536 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.3 | 5.8 | 0.263
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23045-06C02-P | CML-2 | 150-PG-23045-06C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 24268 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 11.55 | CML-2 | CML: Reducer | 3 | 2131-03-15 | 2113-05-14 | 2014-09-24 07:00 | 4.7 | 0.0532 | A3: Inside Quadrant |  | 7.97 | 4.7 | 5.6494 | 10.9 | 6 O'Clock | 150 | 10.97 | 150-PG-23045-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 12 | 11.6 | 10.9 | 11.7 | 0.46547
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44014-01X01 | CML-5 | 50-PW-44014-01X01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2007 |  | 2014-03-27 10:00 | 2014-03-27 10:30 | [36 empty] | 5.425 | CML-5 | CML: Elbow | 3 | 2020-09-29 | 2021-07-13 | 2014-03-27 10:00 | 2.5 | 0.41447 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.6 | 5.7 | 5.2 | 0.263
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-28 | 300-PF-20501-03C03-P CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 21704 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.05 | CML-28 | CML: type TBC | 6 | 2031-12-16 | 2028-08-15 | 2014-09-28 07:00 | 4.9 | 0.50496 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14 | 13.6 | 13.9 | 14.7 | 0.46547
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-16 | 300-PF-20001-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21154 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.329mm/ yr | 40 | Kirstie Albone | 2017-03-23 16:14 | [32 empty] | 14.45 | CML-16 | CML: Fitting | 6 | 2041-11-11 | 2036-09-30 | 2014-07-16 07:30 | 4.9 | 0.32914 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 12 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 13.9 | 14.3 | 15 | 14.6 | 0.46547
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-23 | 50-CG-38001-09C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 10937 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 10.45 | CML-23 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0 | A3: Inside Quadrant |  | 5.74 |  |  | 9.9 | 6 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 9.9 | 10.6 | 10.3 | 9.9 | 11 | 0.46547
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-32 | 200-PG-23007-09C03-PA CML-32 |  | FPSO 2016 | Pipe Wall Thickness | 24453 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | Check Corrosion Rate of 0.362mm/ yr |  | John Wilson | 2017-03-23 09:36 | Loss within CA no further action required. | [31 empty] | 19.95 | CML-32 | CML: Fitting | 6 | 2042-02-05 | 2036-01-12 | 2016-07-03 07:00 | 10.22 | 0.36232 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 19.5 | 12 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.28 | 0 | 19.5 | 19.6 | 20.4 | 20.3 | 0.46547
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-24 | 300-PF-20500-03C03-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21644 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 17.05 | CML-24 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 16.6 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.7 |  | 16.6 | 17.7 | 16.9 | 17 | 0.46547
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-7 | 100-FG-45001-09C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10422 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.825 | CML-7 | CML: type TBC | 3 | 2016-07-15 | 2015-09-15 | 2013-11-13 | 4.7 | 2.0573 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.2 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 11 | 10.2 | 11.3 | 10.8 | 0.46458
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-5 | 300-PW-44003-01C03 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 21847 |  | 2014-10-19 07:00 | 2014-10-19 15:00 | [36 empty] | 11.7 | CML-5 | CML: Equal Tee | 6 | 2039-10-08 | 2036-09-17 | 2014-10-19 07:00 | 2.5 | 0.29617 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 9.9 | 3 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 11 | 9.9 | 13.5 | 12.4 | 1.5769
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57006-01C02 | CML-2 | 80-DC-57006-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20264 | Reviewed on 24/11/14. FFS. Repeat Oct.19 | 2014-10-11 07:00 | 2014-10-11 15:00 |  |  | Nestor | 2014-11-24 09:49 | [32 empty] | 6.975 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.1 | 3 O'Clock | 80 | 5.49 | 80-DC-57006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7.6 | 6.1 | 7.7 | 6.5 | 0.79739
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20017-01C02-P | CML-2 | 200-PL-20017-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21241 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 6.85 | CML-2 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-PL-20017-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.3 | 6.7 | 7 | 6.4 | 0.3873
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-5 | 250-FH-43303-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12943 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 7.275 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 9 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.3 | 7.1 | 7.9 | 6.8 | 0.46458
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38455-01C02-H | CML-1 | 50-CG-38455-01C02-H CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 23685 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 6.725 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 25 | 5.54 | 50-CG-38455-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7.2 | 6.1 | 6.9 | 6.7 | 0.46458
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56014-01C02 | CML-7 | 50-DH-56014-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22329 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 6.575 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.1 | 7.2 | 6.6 | 0.46458
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56014-01C02 | CML-7 | 50-DH-56014-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1849 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 6.575 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.1 | 7.2 | 6.6 | 0.46458
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-4 | 250-PW-44010-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21921 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 10.075 | CML-4 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.5 | 3 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.5 | 9.5 | 10.4 | 9.9 | 0.46458
PG01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 250-PW-44010-01C03-P | CML-4 | 250-PW-44010-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5823 | Protective mesh removed | 2014-06-24 09:30 | 2014-06-24 10:30 | [36 empty] | 10.075 | CML-4 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 9.5 | 3 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 |  | 10.5 | 9.5 | 10.4 | 9.9 | 0.46458
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44034-01C02-P | CML-7 | 80-PW-44034-01C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23084 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.325 | CML-7 | CML: Fitting | 3 | 2028-03-21 | 2029-12-10 | 2015-05-07 07:00 | 2.5 | 0.20183 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 2.4927 | 5.5 | 5.4 | 5.1 | 5.3 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-13 | 50-DH-56137-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21097 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.225 | CML-13 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 5.8 | 6 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.4 | 6.8 | 5.8 | 5.9 | 0.46458
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-2 | 50-PW-44015-01X01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5712 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 5.575 | CML-2 | CML: Elbow | 3 | 2022-11-16 | 2023-11-21 | 2014-06-22 10:00 | 2.5 | 0.32116 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -1.3012 | 5.7 | 5.8 | 5.6 | 5.2 | 0.263
PW03 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 200-PW-44018-01X01 | CML-5 | 200-PW-44018-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 22499 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.5 | CML-5 | CML: Pipe Length | 3 | 2019-09-22 | 2019-09-05 | 2015-04-20 07:00 | 2.5 | 0.60984 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 12 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.6 | 5.4 | 5.8 | 0.2582
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-57 | 300-PF-20001-03C03-P CML-57 |  | FPSO 2015 | Pipe Wall Thickness | 23488 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 12.725 | CML-57 | CML: Elbow | 6 | 2023-07-04 | 2021-06-08 | 2015-07-27 07:00 | 4.1 | 1.0073 | A2: Right Quadrant |  | 8.27 | 4.1 | 6.185 | 12.1 | 3 O'Clock | 250 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | -0.4854 | 12.7 | 12.1 | 13.2 | 12.9 | 0.46458
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-32 | 300-PF-20500-03C03-P CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 21652 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.375 | CML-32 | CML: Pipe Length | 6 | 2046-12-04 | 2040-11-24 | 2014-09-27 07:00 | 4.9 | 0.27944 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 13.9 | 14.2 | 14.4 | 15 | 0.46458
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8585 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-07 14:00 | 2015-02-07 16:00 | [36 empty] | 5.5 | CML-4 | CML: type TBC | 3 | 2028-07-04 | 2030-02-16 | 2015-02-07 14:00 | 2.5 | 0.20127 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63035-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.8 | 5.4 | 5.6 | 5.2 | 0.2582
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-4 | 250-PW-20041-03C03-P CML-4 | yes | FPSO 2014 | Pipe Wall Thickness | 21413 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 13.125 | CML-4 | CML: Elbow | 6 | 2021-05-21 | 2020-03-07 | 2014-07-12 07:30 | 4.1 | 1.078 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 11.5 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 12.9 | 13.4 | 14.7 | 11.5 | 1.3226
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-14 | 100-FG-45304-03C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 22070 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.4 | CML-14 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2014-05-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 6.1 | 6 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.5 | 6.1 | 6.9 | 0.38297
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 8791 | LAGGING REMOVAL REQUIRED | 2015-02-15 09:30 | 2015-02-15 12:00 | [36 empty] | 5.65 | CML-2 | CML: type TBC | 3 | 2020-05-05 | 2020-04-16 | 2015-02-15 09:30 | 2.5 | 0.55534 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 9 O'Clock | 200 | 6.35 | 200-PL-43307-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.8 | 5.6 | 5.4 | 0.19149
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8608 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.525 | CML-3 | CML: type TBC | 3 | 2050-03-05 | 2054-02-13 | 2015-02-09 07:30 | 2.5 | 0.08264 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.5 | 5.4 | 5.4 | 0.1893
PW03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23428 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 |  |  | Nestor | 2016-04-01 | [32 empty] | 5.375 | CML-8 | CML: Elbow | 3 | 2022-08-11 | 2022-11-30 | 2015-07-23 07:00 | 2.5 | 0.38259 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 9 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.076533 | 5.7 | 5.2 | 5.4 | 5.2 | 0.23629
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-26 | 200-PW-44018-01X01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 23261 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.475 | CML-26 | CML: Pipe Length | 3 | 2030-10-11 | 2032-08-22 | 2015-05-11 07:00 | 2.5 | 0.17496 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.089024 | 5.6 | 5.7 | 5.4 | 5.2 | 0.22174
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20031-01C03-P | CML-7 | 150-PG-20031-01C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 23869 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 10.525 | CML-7 | CML: Pipe Length | 6 | 2023-11-13 | 2022-05-06 | 2014-09-26 07:00 | 2.5 | 0.80978 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 9.9 | 3 O'Clock | 150 | 10.97 | 150-PG-20031-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 10.5 | 9.9 | 10.7 | 11 | 0.46458
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-18 | 80-CG-38459-09C02-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23715 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 16.925 | CML-18 | CML: Reducing Tee | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 16.3 | 9 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.8 |  | 16.9 | 17.1 | 17.4 | 16.3 | 0.46458
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-4 | 200-PG-23065-09C02-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 418 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.525 | CML-4 | CML: Elbow | 3 | 2118-05-25 | 2085-05-14 | 2014-03-12 09:00 | 10.17 | 0.07701 | A3: Inside Quadrant |  | 15.26 | 10.17 | 12.715 | 18.2 | 6 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.03 |  | 18.4 | 19.2 | 18.2 | 18.3 | 0.45735
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-7 | 50-DO-62002-01S01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2992 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.375 | CML-7 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.3 | 6.9 | 6.2 | 6.1 | 0.3594
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-2 | 50-DO-62002-01S01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2987 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.325 | CML-2 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.4 | 6.6 | 6.1 | 0.22174
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-7 | 50-DO-62002-01S01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22271 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.375 | CML-7 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.3 | 6.9 | 6.2 | 6.1 | 0.3594
DO02 | Montara_Topside | No | Diesel Oil (62) | Pipework | 50-DO-62002-01S01 | CML-2 | 50-DO-62002-01S01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 22266 | Deck Level | 2014-05-01 10:30 | 2014-05-01 11:00 | [36 empty] | 6.325 | CML-2 | CML: Elbow | 1 | 2043-10-24 | 2037-01-28 | 2014-05-01 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-DO-62002-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.4 | 6.6 | 6.1 | 0.22174
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-14 | 200-PG-23065-09C02-A CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23402 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 19.15 | CML-14 | CML: Pipe Length | 3 | 2094-04-24 | 2068-11-11 | 2015-07-22 07:00 | 10.17 | 0 | A1: Outside Quadrant |  | 15.26 | 10.17 | 12.715 | 18.3 | 12 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.13 | -0.6969 | 18.3 | 19.4 | 18.8 | 20.1 | 0.77675
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-13 | 150-FL-43174-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12911 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 8.1333 | CML-13 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.6 | 6 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  |  | 8.4 | 7.6 | 8.4 | 0.46188
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20061-01C03-P | CML-4 | 80-PG-20061-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21676 | Protective mesh removed | 2014-06-26 11:00 | 2014-06-26 12:00 | [36 empty] | 20.6 | CML-4 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-06-26 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 20.2 | 6 O'Clock | 80 | 11.13 | 80-PG-20061-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 |  | 21 | 20.2 | 20.2 | 21 | 0.46188
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-6 | 80-FH-43005-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12556 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 5.6667 | CML-6 | CML: type TBC | 3 | 2034-08-24 | 2037-02-12 | 2014-01-20 10:00 | 2.5 | 0.14074 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 6.2 |  | 0.46188
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-19 | 200-PG-23007-09C03-PA CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 20706 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | Check Corrosion Rate of 0.481mm/ yr |  | John Wilson | 2017-03-23 09:33 | Loss within CA no further actio required. | [31 empty] | 20.5 | CML-19 | CML: Fitting | 6 | 2035-01-07 | 2030-06-13 | 2014-06-30 13:00 | 10.22 | 0.48106 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 20.1 | 3 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.88 |  | 20.1 | 20.1 | 20.9 | 20.9 | 0.46188
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-23 | 200-PG-24001-09C02 CML-23 |  | FPSO 2013 | Pipe Wall Thickness | 10279 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 19.6333 | CML-23 | CML: Equal Tee | 3 | 2104-01-05 | 2073-09-17 | 2013-11-09 | 9.2 | 0 | A1: Outside Quadrant |  | 15.26 | 9.2 | 12.23 | 19.1 | 12 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 19.1 | 19.9 | 19.9 |  | 0.46188
CG02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38466-01C02 | CML-5 | 50-CG-38466-01C02 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 2519 |  | 2014-04-02 13:00 | 2014-04-02 14:00 | [36 empty] | 6 | CML-5 | CML: type TBC | 3 | 2076-12-28 | 2083-10-25 | 2014-04-02 13:00 | 2.5 | 0.04778 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 9 O'Clock | 50 | 5.54 | 50-CG-38466-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 | 5.5 |  | 6.1 | 6.4 | 5.5 | 0.45826
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45024-01C02 | CML-2 | 50-FG-45024-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20599 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 9.725 | CML-2 | CML: Elbow | 6 | 2021-06-29 | 2020-07-22 | 2014-07-25 07:30 | 2.5 | 0.96622 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 9.2 | 9 O'Clock | 300 | 10.31 | 300-PG-23070-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.3 | 9.8 | 9.6 | 9.2 | 0.45735
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-39 | 300-PF-20500-03C03-P CML-39 |  | FPSO 2014 | Pipe Wall Thickness | 21659 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 17.375 | CML-39 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 16.9 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12 |  | 17.3 | 18 | 16.9 | 17.3 | 0.45735
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-34 | 150-PG-23506-25C02 CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 20088 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.375 | CML-34 | CML: Pipe Length | 3 | 2019-02-24 | 2017-09-12 | 2014-05-29 07:00 | 15.88 | 1.0578 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.9 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.02 | -292.0012 | 22 | 21.3 | 20.9 | 21.3 | 0.45735
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 50-VA-80001-01C02 | CML-6 | 50-VA-80001-01C02 CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 3139 | Rope Access | 2014-05-02 09:30 | 2014-05-02 10:30 | [36 empty] | 5.075 | CML-6 | CML: type TBC | 3 | 2016-05-20 | 2016-09-14 | 2014-05-02 09:30 | 2.5 | 1.023 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-VA-80001-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5 | 5 | 5.7 | 0.45735
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-2 | 100-DH-56086-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20961 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 6.325 | CML-2 | CML: type TBC | 3 | 2028-09-22 | 2029-03-26 | 2014-05-16 13:00 | 2.5 | 0.22973 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.8 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.2 | 6.9 | 6.4 | 5.8 | 0.45735
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40071-01C02 | CML-12 | 50-WC-40071-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1947 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 6.325 | CML-12 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.5 | 6.3 | 6.1 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43110-01C02 | CML-4 | 200-FH-43110-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12795 |  | 2014-01-18 13:30 | 2014-01-18 14:30 | [36 empty] | 6.575 | CML-4 | CML: Elbow | 3 | 2026-02-13 | 2024-07-30 | 2014-01-18 13:30 | 1.34 | 0.39406 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.1 | 12 O'Clock | 200 | 6.35 | 200-FH-43110-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 6.1 | 6.5 | 6.5 | 7.2 | 0.45735
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-4 | 50-FG-45301-01C02 CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 5790 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.275 | CML-4 | CML: Elbow | 3 | 2016-11-05 | 2017-03-19 | 2014-06-23 13:00 | 2.5 | 0.88532 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.4 | 5.5 | 4.6 | 5.6 | 0.45735
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-23 | 300-PG-20004-03C03-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 6146 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 13.725 | CML-23 | CML: Fitting | 6 | 2025-05-14 | 2023-03-21 | 2014-07-11 07:30 | 4.9 | 0.78347 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.4 | 3 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 13.6 | 13.4 | 14.4 | 13.5 | 0.45735
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8311 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 5.675 | CML-4 | CML: type TBC | 3 | 2049-05-28 | 2053-04-08 | 2015-01-27 09:45 | 2.5 | 0.08441 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AI-63001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.7 | 5.8 | 5.8 | 0.1893
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43081-01C02 | CML-3 | 80-FH-43081-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20420 | CML Reviewed 19-11-14. Line is FFS. Repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-19 17:20 | [32 empty] | 6.425 | CML-3 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-06 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 3 O'Clock | 80 | 5.49 | 80-FH-43081-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | -0.72433 | 6.2 | 5.9 | 6.7 | 6.9 | 0.45735
FG02 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-FG-45455-01C02-E | CML-14 | 25-FG-45455-01C02-E CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 3437 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 6.325 | CML-14 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6 | 12 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.1 | 7 | 6.2 | 0.45735
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43070-01C02 | CML-6 | 300-FL-43070-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12699 |  | 2014-02-01 09:00 | 2014-02-01 12:00 | [36 empty] | 6.625 | CML-6 | CML: type TBC | 3 | 2023-10-05 | 2023-09-08 | 2014-02-01 09:00 | 2.5 | 0.37188 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 6 O'Clock | 300 | 6.35 | 300-FL-43070-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 7.1 | 6.1 | 6.9 | 0.45735
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-4 | 150-FL-43453-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2248 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.975 | CML-4 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.3 | 12 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7.3 | 7.1 | 7.2 | 0.45735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-15 | 200-PW-44018-01X01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 22917 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.4 | CML-15 | CML: Reducing Tee | 3 | 2033-03-08 | 2035-06-26 | 2015-05-02 07:00 | 2.5 | 0.15115 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.17892 | 5.4 | 5.3 | 5.2 | 5.7 | 0.21602
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-8 | 300-PF-20501-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21684 | Protective mesh removed. Reviewed on 1/12/14. FFS. Recheck on Sep.15 | 2014-09-28 07:00 | 2014-09-28 15:00 |  |  | Nestor | 2014-12-01 08:52 | [32 empty] | 13.725 | CML-8 | CML: Pipe Length | 6 | 2025-01-09 | 2022-12-09 | 2014-09-28 07:00 | 4.9 | 0.80644 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.2 | 3 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 14.2 | 13.2 | 13.5 | 14 | 0.45735
PW03 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8612 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.45 | CML-7 | CML: type TBC | 3 | 2028-07-20 | 2030-03-05 | 2015-02-09 07:30 | 2.5 | 0.20071 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.7 | 5.4 | 5.2 | 0.20817
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43019-01C02 | CML-1 | 80-FH-43019-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10620 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 6.975 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2013-11-17 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.5 | 12 O'Clock | 80 | 5.49 | 80-FH-43019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.7 | 7.2 | 7.5 | 0.45735
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-14 | 50-DC-57056-03C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1147 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.125 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.2 | 6.1 | 6.1 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-15 | 50-DC-57056-03C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1148 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.4 | CML-15 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 6.1 | 9 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.6 | 6.2 | 6.7 | 6.1 | 0.29439
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-9 | 50-DC-57056-03C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1141 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.125 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.1 | 6.1 | 6.2 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-15 | 150-FH-43026-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23514 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 6.825 | CML-15 | CML: Pipe Length | 3 | 2029-08-05 | 2026-09-05 | 2015-07-28 07:00 | 1.03 | 0.37553 | A4: Left Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.3 | 9 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.27 | 0.39674 | 6.6 | 7.3 | 7.1 | 6.3 | 0.45735
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-1 | 100-DH-56086-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20960 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 8.675 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 8.1 | 12 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.1 | 8.6 | 9.2 | 8.8 | 0.45735
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57019-01C02 | CML-9 | 50-DC-57019-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2417 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 6.4 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 12 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.5 | 6.5 | 6.5 | 0.2
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57019-01C02 | CML-2 | 50-DC-57019-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2410 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 6.575 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.1 | 6.1 | 6.9 | 7.2 | 0.56199
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-10 | 200-PL-20018-01C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 23882 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 19.95 | CML-10 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 40 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6 | 6.7 | 6.7 | 6.4 | 0.33166
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-16 | 100-DC-57038-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2379 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 6.575 | CML-16 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.1 | 9 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.7 | 6.7 | 6.8 | 6.1 | 0.32016
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-15 | 350-FL-43511-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2296 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 10.325 | CML-15 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 9.8 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10.1 | 10.6 | 10.8 | 9.8 | 0.45735
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43115-01C02 | CML-6 | 80-FH-43115-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12826 |  | 2014-01-20 09:00 | 2014-01-20 10:00 | [36 empty] | 5.575 | CML-6 | CML: type TBC | 3 | 2016-08-26 | 2017-01-11 | 2014-01-20 09:00 | 2.5 | 0.92276 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 9 O'Clock | 80 | 5.49 | 80-FH-43115-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.9 | 5.8 | 5.7 | 4.9 | 0.45735
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-17 | 150-WC-40006-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23226 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.6 | CML-17 | CML: Fitting | 3 | 2077-12-06 | 2085-06-10 | 2015-05-11 07:00 | 2.5 | 0.04631 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 1.3971 | 5.7 | 5.8 | 5.5 | 5.4 | 0.18257
WC01 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8194 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 5.65 | CML-5 | CML: type TBC | 1 | 2049-03-22 | 2041-04-15 | 2015-01-24 07:30 | 2.5 | 0.08484 | A4: Left Quadrant |  | 4.54 | 2.5 | 3.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 5.7 | 5.7 | 5.4 | 0.17321
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-18 | 50-DH-56070-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 3234 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.125 | CML-18 | CML: type TBC | 3 | 2084-08-21 | 2092-04-12 | 2014-05-09 07:00 | 2.5 | 0.04265 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.2 | 6.2 | 6.6 | 0.45735
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-26 | 150-WC-40006-01C02 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 9085 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 09:30 | 2015-03-01 11:00 | [36 empty] | 5.525 | CML-26 | CML: type TBC | 3 | 2051-05-15 | 2055-06-11 | 2015-03-01 09:30 | 2.5 | 0.08004 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-GN-67002-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.4 | 5.4 | 5.7 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43120-01C02 | CML-3 | 200-FH-43120-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12837 |  | 2014-02-06 07:00 | 2014-02-06 09:00 | [36 empty] | 7.325 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 12 O'Clock | 200 | 6.35 | 200-FH-43120-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.4 | 7.8 | 7.4 | 0.45735
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-1 | 300-FL-43080-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2380 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 7.025 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.1 | 6.9 | 6.5 | 7.6 | 0.45735
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-2 | 50-CG-38452-09C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3325 | Rope Access | 2014-05-08 07:00 | 2014-05-08 09:00 | [36 empty] | 7.625 | CML-2 | CML: type TBC | 3 | 2444-03-08 | 2410-06-27 | 2014-05-08 07:00 | 2.5 | 0.01069 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.1 | 12 O'Clock | 150 | 7.11 | 150-DH-56080-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 8.2 | 7.7 | 7.5 | 0.45735
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-11 | 50-CG-38452-09C02-P CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10196 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 7.625 | CML-11 | CML: type TBC | 6 | 2015-01-30 | 2015-01-19 | 2013-11-08 | 2.5 | 3.7412 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.1 | 6 O'Clock | 50 | 8.74 | 50-PL-23040-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.7 | 7.5 | 7.1 | 8.2 | 0.45735
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45044-03C02 | CML-7 | 50-FG-45044-03C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20791 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 9.075 | CML-7 | CML: Elbow | 6 | 2073-12-23 | 2072-10-24 | 2014-10-10 07:00 | 2.5 | 0.10296 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 6 O'Clock | 50 | 8.74 | 50-PL-23032-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9 | 9 | 8.6 | 9.7 | 0.45735
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-11 | 200-PG-23065-09C02-A CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 425 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.075 | CML-11 | CML: Pipe Length | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A4: Left Quadrant |  | 15.26 | 10.17 | 12.715 | 18.4 | 9 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.23 |  | 18.8 | 19.9 | 19.2 | 18.4 | 0.63966
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-21 | 50-PW-44040-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 23256 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.275 | CML-21 | CML: Pipe Length | 3 | 2026-10-31 | 2028-04-09 | 2015-05-11 07:00 | 2.5 | 0.22642 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | -0.17805 | 5.1 | 5.2 | 5.3 | 5.5 | 0.17078
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-7 | 200-PL-20010-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 23807 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.75 | CML-7 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 40 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.1 | 6.8 | 6.7 | 0.28868
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-10 | 50-PL-23052-09C03 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10174 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.575 | CML-10 | CML: type TBC | 6 | 2017-03-02 | 2016-08-27 | 2013-11-09 | 2.81 | 2.1991 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10.1 | 12 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.29 |  | 10.1 | 10.5 | 11.2 | 10.5 | 0.45735
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23009-09C02 | CML-2 | 200-PG-23009-09C02 CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 10912 | Deck Level | 2014-01-06 | 2014-01-06 | [36 empty] | 17.775 | CML-2 | CML: type TBC | 3 | 2018-01-17 | 2016-07-03 | 2014-01-06 | 9.3 | 1.9333 | A2: Right Quadrant |  | 15.26 | 9.3 | 12.28 | 17.1 | 3 O'Clock | 200 | 18.26 | 200-PG-23009-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 18 | 17.1 | 18.1 | 17.9 | 0.45735
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-2 | 200-PG-20300-03C03-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23357 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 12.8 | CML-2 | CML: Elbow | 6 | 2053-07-11 | 2046-04-10 | 2015-07-20 07:00 | 3.3 | 0.23419 | A2: Right Quadrant |  | 6.7 | 3.3 | 5 | 12.2 | 3 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 | -0.46807 | 12.8 | 12.2 | 13.3 | 12.9 | 0.45461
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-43 | 150-PG-23506-25C02 CML-43 |  | FPSO 2014 | Pipe Wall Thickness | 2817 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22 | CML-43 | CML: Pipe Length | 3 | 2022-02-05 | 2019-11-26 | 2014-03-15 09:00 | 15.88 | 0.69856 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 21.4 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.52 |  | 22.3 | 21.9 | 22.4 | 21.4 | 0.45461
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23005-06C03 | CML-18 | 250-PG-23005-06C03 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10064 | Deck Level | 2013-11-06 | 2013-11-06 | [36 empty] | 17.6 | CML-18 | CML: Elbow | 6 | 2016-09-24 | 2016-02-07 | 2013-11-06 | 8.6 | 2.9108 | A4: Left Quadrant |  | 12.26 | 8.6 | 10.43 | 17 | 9 O'Clock | 250 | 18.26 | 250-PG-23005-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 18.1 | 17.7 | 17.6 | 17 | 0.45461
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-10 | 200-PW-44018-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8934 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.475 | CML-10 | CML: type TBC | 3 | 2028-12-20 | 2030-08-21 | 2015-02-26 09:00 | 2.5 | 0.19532 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.7 | 5.5 | 5.2 | 0.20616
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56058-01C02 | CML-3 | 50-DH-56058-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3175 | Rope Access | 2014-05-07 09:30 | 2014-05-07 10:30 | [36 empty] | 6.4 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56058-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.5 | 6.4 | 6.9 | 5.8 | 0.45461
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-3 | 50-DH-56056-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20127 | Rope Access | 2014-05-07 09:30 | 2014-05-07 10:30 | [36 empty] | 6.4 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | -5256.1947 | 6.5 | 6.4 | 6.9 | 5.8 | 0.45461
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-VA-23054-01C02 | CML-8 | 25-VA-23054-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1477 | Rope access | 2014-04-29 10:00 | 2014-04-29 11:00 | [36 empty] | 4.9 | CML-8 | CML: type TBC | 3 | 2015-08-24 | 2015-11-20 | 2014-04-29 10:00 | 2.5 | 1.3615 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-VA-23054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.3 | 5.3 | 4.8 | 5.2 | 0.45461
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43115-01C02 | CML-1 | 80-FH-43115-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12821 |  | 2014-01-20 09:00 | 2014-01-20 10:00 | [36 empty] | 5.6 | CML-1 | CML: type TBC | 3 | 2017-04-25 | 2017-10-07 | 2014-01-20 09:00 | 2.5 | 0.76636 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 6 O'Clock | 80 | 5.49 | 80-FH-43115-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 6 | 5.5 | 5 | 5.9 | 0.45461
FG02 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8312 |  | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.6 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-AI-63001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 6.5 | 7 | 6 | 0.45461
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-26 | 200-PW-44018-01X01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 8922 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.475 | CML-26 | CML: type TBC | 3 | 2028-12-12 | 2030-08-13 | 2015-02-25 13:00 | 2.5 | 0.19557 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.2 | 5.5 | 5.7 | 0.20616
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-7 | 350-FL-43511-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2288 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 7.8 | CML-7 | CML: type TBC | 3 | 2021-09-02 | 2020-07-31 | 2014-03-17 08:00 | 2.5 | 0.65599 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 6 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.4 | 7.5 | 7.4 | 7.9 | 0.45461
WC01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 5042 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.547mm/ yr | [34 empty] | Low alarm breach | 5.6 | CML-2 | CML: type TBC | 3 | 2017-01-17 | 2016-05-09 | 2015-03-05 07:00 | 2.5 | 1.5465 | A4: Left Quadrant |  | 5.74 | 2.5 | 3.5737 | 5.4 | 9 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 5.6 | 5.7 | 5.4 | 0.14142
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-1 | 250-PG-20036-01C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21359 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | Check Corrosion Rate of 0.51mm/ yr | 41 | Kirstie Albone | 2017-03-23 15:10 | [32 empty] | 9.3 | CML-1 | CML: Elbow | 6 | 2026-09-10 | 2025-12-08 | 2014-07-14 07:30 | 2.5 | 0.50954 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 8.7 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.6 | 9.7 | 8.7 | 9.2 | 0.45461
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-1 | 80-PG-20046-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21460 | Protective mesh removed | 2014-06-28 08:00 | 2014-06-28 09:00 | [36 empty] | 10.8 | CML-1 | CML: Pipe Length | 6 | 2023-05-20 | 2021-11-11 | 2014-06-28 08:00 | 2.5 | 0.86521 | A4: Left Quadrant |  | 5.13 | 2.5 | 3.815 | 10.2 | 9 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.7 | 11.1 | 11.2 | 10.2 | 0.45461
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-11 | 50-CG-38487-09C02-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20811 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 11.3 | CML-11 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.7 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11.2 | 11.6 | 10.7 | 11.7 | 0.45461
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43115-01C02 | CML-5 | 80-FH-43115-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12825 |  | 2014-01-20 09:00 | 2014-01-20 10:00 | [36 empty] | 5.3 | CML-5 | CML: type TBC | 3 | 2015-11-01 | 2016-02-12 | 2014-01-20 09:00 | 2.5 | 1.2356 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 6 O'Clock | 80 | 5.49 | 80-FH-43115-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.6 | 5.2 | 4.7 | 5.7 | 0.45461
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20016-01C02-P | CML-7 | 200-PL-20016-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21238 | Protective mesh removed | 2014-07-15 07:30 | 2014-07-15 15:00 | [36 empty] | 6.625 | CML-7 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-07-15 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 200 | 6.35 | 200-PL-20016-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.8 | 6.7 | 6.6 | 0.17078
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-5 | 300-PG-23400-01C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 522 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 9.075 | CML-5 | CML: Elbow | 6 | 2016-03-27 | 2016-06-27 | 2014-03-13 09:00 | 5.22 | 1.8034 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 8.9 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.68 |  | 8.9 | 9.3 | 9.1 | 9 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43009-01C02 | CML-16 | 80-FH-43009-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12594 |  | 2014-02-05 08:00 | 2014-02-05 11:00 | [36 empty] | 5.5 | CML-16 | CML: Elbow | 3 | 2019-02-21 | 2018-05-30 | 2014-02-05 08:00 | 0.54 | 0.8637 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-FH-43009-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.36 |  | 4.9 | 5.4 | 5.9 | 5.8 | 0.45461
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-9 | 150-FH-43518-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2709 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.1 | CML-9 | CML: Elbow | 3 | 2020-12-02 | 2019-08-26 | 2014-03-12 09:00 | 1.23 | 0.78294 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.5 | 6 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.27 | 0 | 7.1 | 7.2 | 6.5 | 7.6 | 0.45461
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-9 | 150-FH-43518-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 348 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.1 | CML-9 | CML: Elbow | 3 | 2020-11-28 | 2019-08-23 | 2014-03-12 | 1.23 | 0.78398 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.5 | 6 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.27 |  | 7.1 | 7.2 | 6.5 | 7.6 | 0.45461
FG05 | Montara_Topside | No | Fuel Gas (45) | Pipework | 50-FG-45452-01C02-H | CML-2 | 50-FG-45452-01C02-H CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24314 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.775 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2016-05-27 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-FG-45452-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.5 | 6.7 | 6.2 | 6.7 | 0.53774
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9004-AS20-00 | CML-4 | 0100-AI-63L9004-AS20-00 CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24280 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.275 | CML-4 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.2 | 3 O'Clock | 25 | 3.38 | 0100-AI-63L9004-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.2 | 6.3 | 6.3 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23423 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 |  |  | Nestor | 2016-04-01 | [32 empty] | 5.55 | CML-3 | CML: Elbow | 3 | 2025-07-29 | 2025-12-23 | 2015-07-23 07:00 | 2.5 | 0.28928 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 3 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.2296 | 5.6 | 5.4 | 5.7 | 5.5 | 0.1291
SD01 | Montara_Topside | No | Steam (55) | Pipework | 150-SL-55001-01C02-H | CML-4 | 150-SL-55001-01C02-H CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23605 |  | 2015-09-28 07:00 | 2015-09-28 15:00 | [36 empty] | 6.675 | CML-4 | CML: Elbow | 3 | 2025-03-12 | 2024-04-09 | 2015-09-28 07:00 | 2.5 | 0.39109 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.2 | 3 O'Clock | 25 | 7.11 | 150-SL-55001-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.6 | 7.5 | 0.57373
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-8 | 25-PG-23300-25C02 CML-8 | Yes | FPSO 2014 | Pipe Wall Thickness | 20675 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 8.6 | CML-8 | CML: Elbow | 3 | 2017-08-29 | 2016-11-23 | 2014-05-27 09:30 | 4.4 | 1.1039 | A1: Outside Quadrant |  | 6.09 | 4.4 | 5.245 | 8 | 12 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 8 | 9.1 | 8.7 | 8.6 | 0.45461
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-17 | 50-CG-38487-09C02-P CML-17 | yes | FPSO 2016 | Pipe Wall Thickness | 24475 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | [36 empty] | 8.5 | CML-17 | CML: Elbow | 3 | 2039-08-08 | 2032-10-20 | 2016-07-09 07:00 | 2.5 | 0.23812 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8 | 12 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 | -0.12046 | 8 | 8.4 | 8.5 | 9.1 | 0.45461
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-16 | 300-PF-20500-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21636 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 15.4 | CML-16 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.8 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 14.8 | 15.4 | 15.9 | 15.5 | 0.45461
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43135-01C02 | CML-1 | 200-FH-43135-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7849 | Line is FFS. Current RBI frequency is 48m. Action: CML’s to Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-08 13:38 | [32 empty] | 8.9 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 12 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 9.3 | 8.8 | 9.2 | 0.45461
FG01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-FG-45024-01C02 | CML-4 | 50-FG-45024-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21229 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 9.6 | CML-4 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.2 | 9 O'Clock | 150 | 6.35 | 200-PL-20015-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.7 | 10.2 | 9.3 | 9.2 | 0.45461
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-13 | 200-PG-24001-09C02 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10269 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 17.7 | CML-13 | CML: Pipe Length | 3 | 2016-11-09 | 2015-09-15 | 2013-11-09 | 9.2 | 2.6298 | A3: Inside Quadrant |  | 15.26 | 9.2 | 12.23 | 17.1 | 6 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.9 |  | 18 | 18.1 | 17.1 | 17.6 | 0.45461
PG06 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3102 | Rope Access | 2014-05-04 10:00 | 2014-05-04 10:30 | [36 empty] | 5.65 | CML-2 | CML: Elbow | 3 | 2019-10-19 | 2020-06-25 | 2014-05-04 10:00 | 2.5 | 0.47597 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 15 | 5.54 | 50-CG-38005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.1 | 5.6 | 6.2 | 0.45092
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-4 | 250-DC-57064-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23090 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.325 | CML-4 | CML: Pipe Length | 3 | 2062-12-23 | 2062-08-13 | 2015-05-07 07:00 | 2.5 | 0.07763 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 | 0 | 6.4 | 6.4 | 6.2 | 6.3 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43171-01C02 | CML-4 | 80-FL-43171-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23098 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.35 | CML-4 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-05-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.8 | 3 O'Clock | 80 | 5.49 | 80-FL-43171-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | -0.17136 | 6.3 | 5.8 | 6.4 | 6.9 | 0.45092
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45004-03C02 | CML-4 | 150-FG-45004-03C02 CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24336 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 8.35 | CML-4 | CML: Elbow | 3 | 2059-07-07 | 2051-06-19 | 2016-06-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 3.305 | 7.8 | 6 O'Clock | 150 | 7.11 | 150-FG-45004-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.9 | 8.4 | 7.8 | 8.3 | 0.45092
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-24 | 150-WC-40006-01C02 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 23259 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.55 | CML-24 | CML: Elbow | 3 | 2055-08-01 | 2060-02-09 | 2015-05-11 07:00 | 2.5 | 0.07204 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.3561 | 5.4 | 5.5 | 5.7 | 5.6 | 0.1291
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56059-01C02 | CML-4 | 50-DH-56059-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3342 | Rope Access | 2014-05-08 11:00 | 2014-05-08 12:00 | [36 empty] | 5.25 | CML-4 | CML: type TBC | 3 | 2016-06-09 | 2016-10-05 | 2014-05-08 11:00 | 2.5 | 1.0048 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-DH-56059-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.6 | 5.5 | 4.6 | 5.3 | 0.45092
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-20 | 50-FG-45020-03C02 CML-20 |  | FPSO 2013 | Pipe Wall Thickness | 10592 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 5.25 | CML-20 | CML: type TBC | 3 | 2015-08-12 | 2015-08-07 | 2013-11-17 | 2.5 | 1.3822 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5 | 5.2 | 5.9 | 0.45092
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42311-01S01 | CML-6 | 40-CI-42311-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7509 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.825 | CML-6 | CML: type TBC | 1 | 2022-08-15 | 2019-11-24 | 2015-04-13 07:00 | 2.5 | 0.5036 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.2 | 12 O'Clock | 40 | 7.14 | 40-CI-42311-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 7.8 | 9.2 | 8.1 | 1.2393
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43091-01C02 | CML-3 | 80-FL-43091-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5828 | Rope access | 2014-06-24 10:30 | 2014-06-24 12:00 | [36 empty] | 5.65 | CML-3 | CML: Elbow | 3 | 2019-11-27 | 2020-08-29 | 2014-06-24 10:30 | 2.5 | 0.46043 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-FL-43091-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 6 | 5.7 | 5.9 | 0.45092
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-31 | 50-AI-63004-01E01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 9022 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.35 | CML-31 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.4 | 6.3 | 6.2 | 0.1291
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-5 | 80-SC-55002-01C02-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8835 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 6.975 | CML-5 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.2 | 12 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.5 | 8.5 | 6.7 | 1.0372
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67006-01E01 | CML-6 | 50-GN-67006-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8751 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 6.35 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-15 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.4 | 6.5 | 6.3 | 0.1291
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56014-01C02 | CML-1 | 50-DH-56014-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 22323 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 6.25 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 6.9 | 6.2 | 0.45092
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-9 | 50-AI-63009-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8531 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.4 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.8 | 6.3 | 6.3 | 0.2708
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56014-01C02 | CML-1 | 50-DH-56014-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1843 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 6.25 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6 | 6.9 | 6.2 | 0.45092
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67007-01E01 | CML-1 | 50-GN-67007-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8472 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.5 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-GN-67007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.7 | 6.6 | 6.5 | 0.21602
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67008-01E01 | CML-6 | 50-GN-67008-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8468 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.475 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-GN-67008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.7 | 6.6 | 6.2 | 0.22174
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67008-01E01 | CML-4 | 50-GN-67008-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8466 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.325 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-GN-67008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 6.5 | 6.3 | 0.12583
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63022-01E01 | CML-4 | 50-AU-63022-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8442 |  | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.275 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-AU-63022-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.3 | 6.3 | 6.2 | 0.05
RP01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 50-WC-40406-01C02 | CML-4 | 50-WC-40406-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8436 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 6.375 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-WC-40406-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 6.3 | 6.2 | 6.3 | 0.22174
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63016-01E01 | CML-7 | 50-AU-63016-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8411 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.775 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-AU-63016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.6 | 6.8 | 6.2 | 6.5 | 0.60208
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63031-01E01 | CML-2 | 50-AI-63031-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8396 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.475 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-AI-63031-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.5 | 6.6 | 6.6 | 0.1893
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63040-01E01 | CML-2 | 50-AI-63040-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8318 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.425 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-AI-63040-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.6 | 6.2 | 6.6 | 0.20616
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63001-01E01 | CML-9 | 50-AI-63001-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8316 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.375 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-AI-63001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.2 | 6.2 | 6.6 | 0.20616
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63001-01E01 | CML-3 | 50-AI-63001-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8310 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.35 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-AI-63001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 6.5 | 6.4 | 0.1291
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63044-01E01 | CML-4 | 50-AI-63044-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8307 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.55 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63044-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.6 | 6.8 | 6.2 | 0.25166
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-8 | 50-WD-53011-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8284 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.625 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 7.3 | 6.3 | 6.2 | 0.49917
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-13 | 50-WD-53010-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8256 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.275 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 6.2 | 6.4 | 0.095743
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-2 | 50-WD-53010-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8245 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.6 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 7.4 | 6.3 | 6.2 | 0.54772
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53013-01E01 | CML-4 | 50-WD-53013-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8240 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.7 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 9 O'Clock | 50 | 5.54 | 50-WD-53013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 7.2 | 6.9 | 6.2 | 0.4397
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-VA-23056-01C02 | CML-3 | 50-VA-23056-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8063 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 6.75 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-22 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-VA-23056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.7 | 7.4 | 6.4 | 0.45092
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-9 | 100-OL-69002-01S01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8130 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.5 | CML-9 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.2 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.5 | 6.8 | 6.5 | 0.24495
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-2 | 100-OL-69002-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8123 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.575 | CML-2 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.7 | 6.8 | 6.2 | 0.263
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-8 | 100-OL-69001-01S01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8110 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.4 | CML-8 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 6.5 | 6.2 | 6.2 | 0.24495
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69004-01S01 | CML-10 | 80-OL-69004-01S01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8101 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 7.05 | CML-10 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.49 | 2.5 | 3.1519 | 6.2 | 9 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.1 | 7.3 | 7.6 | 6.2 | 0.60277
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69004-01S01 | CML-9 | 80-OL-69004-01S01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8100 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.325 | CML-9 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 6.2 | 12 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 6.5 | 6.3 | 0.12583
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69003-01S01 | CML-10 | 80-OL-69003-01S01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8088 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.6 | CML-10 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 6.2 | 12 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.9 | 7 | 6.3 | 0.40825
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69003-01S01 | CML-4 | 80-OL-69003-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8082 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.325 | CML-4 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 6.2 | 12 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 6.5 | 6.3 | 0.12583
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-1 | 80-PW-44035-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23265 |  | 2015-05-12 07:00 | 2015-05-12 15:00 | [36 empty] | 5.3 | CML-1 | CML: Fitting | 3 | 2028-04-28 | 2030-01-22 | 2015-05-12 07:00 | 2.5 | 0.20041 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 6 O'Clock | 80 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0 | 5.4 | 5.3 | 5.1 | 5.4 | 0.14142
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20027-03C03-P | CML-1 | 80-PG-20027-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21324 | Protective mesh removed | 2014-06-27 09:30 | 2014-06-27 10:30 | [36 empty] | 11.95 | CML-1 | CML: Pipe Length | 6 | 2099-09-17 | 2086-07-24 | 2014-06-27 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 5.13 | 2.5 | 3.815 | 11.6 | 3 O'Clock | 80 | 11.13 | 80-PG-20027-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 11.7 | 11.6 | 12.6 | 11.9 | 0.45092
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38005-01C02 | CML-5 | 50-CG-38005-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3105 | Rope Access | 2014-05-04 10:00 | 2014-05-04 10:30 | [36 empty] | 6.25 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-05-04 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 15 | 5.54 | 50-CG-38005-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.8 | 6.2 | 5.7 | 6.3 | 0.45092
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23082 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.55 | CML-5 | CML: Elbow | 3 | 2077-07-26 | 2085-01-13 | 2015-05-07 07:00 | 2.5 | 0.04658 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 1.9585 | 5.7 | 5.4 | 5.5 | 5.6 | 0.1291
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-14 | 25-FG-45455-01C02-E CML-14 | Yes | FPSO 2014 | Pipe Wall Thickness | 5782 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 6.55 | CML-14 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 12 O'Clock | 25 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.5 | 6.6 | 7.1 | 0.45092
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-16 | 50-PF-20301-03C03-P CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 3014 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.85 | CML-16 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8.3 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.69 | 0 | 9.4 | 8.9 | 8.8 | 8.3 | 0.45092
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-16 | 50-PF-20301-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 22293 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.85 | CML-16 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A4: Left Quadrant |  | 2.18 | 3.61 | 2.895 | 8.3 | 9 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.69 |  | 9.4 | 8.9 | 8.8 | 8.3 | 0.45092
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-24 | 50-PF-20301-03C03-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 3022 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.35 | CML-24 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 8.8 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.19 | 0 | 9.3 | 8.8 | 9.4 | 9.9 | 0.45092
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-24 | 50-PF-20301-03C03-P CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 22301 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.35 | CML-24 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A2: Right Quadrant |  | 2.18 | 3.61 | 2.895 | 8.8 | 3 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.19 |  | 9.3 | 8.8 | 9.4 | 9.9 | 0.45092
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-15 | 50-CG-38452-09C02-P CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23755 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.65 | CML-15 | CML: Elbow | 3 | 2036-12-09 | 2030-10-31 | 2015-10-30 07:00 | 2.5 | 0.26507 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 8.6 | 8.1 | 8.7 | 9.2 | 0.45092
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23241 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.425 | CML-6 | CML: Fitting | 3 | 2030-10-11 | 2032-08-22 | 2015-05-11 07:00 | 2.5 | 0.17496 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.089024 | 5.3 | 5.2 | 5.6 | 5.6 | 0.20616
PG05 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-PG-23003-06C02-PA | CML-9 | 250-PG-23003-06C02-PA CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10149 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of 0.317mm/ yr | [35 empty] | 5.8667 | CML-9 | CML: Elbow | 3 | 2022-12-27 | 2024-01-06 | 2013-11-09 | 2.5 | 0.31739 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.9 | 6.3 | 5.4 |  | 0.45092
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-24 | 200-PG-23065-09C02-A CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 438 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.2 | CML-24 | CML: Elbow | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A1: Outside Quadrant |  | 15.26 | 10.17 | 12.715 | 18.5 | 12 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.33 |  | 18.5 | 20 | 19.5 | 18.8 | 0.67823
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 250-DC-57064-01C02 | CML-4 | 250-DC-57064-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20284 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6.725 | CML-4 | CML: Pipe Length | 3 | 2048-05-11 | 2048-02-08 | 2014-10-11 07:00 | 2.5 | 0.1101 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 250 | 6.35 | 250-DC-57064-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 7.8 | 6.5 | 6.4 | 0.72744
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-7 | 50-FL-43454-01C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22992 |  | 2015-05-05 07:00 | 2015-05-05 15:00 | [36 empty] | 9.55 | CML-7 | CML: Pipe Length | 6 | 2199-08-23 | 2189-01-19 | 2015-05-05 07:00 | 2.5 | 0.03633 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.2 | 12 O'Clock | 250 | 9.27 | 250-PW-44509-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | 0.18528 | 9.2 | 9.3 | 10.2 | 9.5 | 0.45092
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-4 | 50-DH-56137-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20730 | Protective mesh removed/Rope Access | 2014-07-25 07:30 | 2014-07-25 15:00 | [36 empty] | 18.25 | CML-4 | CML: Reducing Tee | 6 | 2074-01-04 | 2073-09-17 | 2014-07-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 17.6 | 9 O'Clock | 100 | 8.56 | 100-PG-23406-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.1 |  | 18.5 | 18.3 | 18.6 | 17.6 | 0.45092
PG06 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23008-15S01-A | CML-8 | 200-PG-23008-15S01-A CML-8 | Yes | FPSO 2013 | Pipe Wall Thickness | 10094 | Deck Level | 2013-11-07 | 2013-11-07 | [35 empty] | Low alarm breach | 20.625 | CML-8 | CML: Pipe Length | 1 | 2014-11-28 | 2014-03-31 | 2013-11-07 | 14.06 | 5.9915 | A1: Outside Quadrant |  | 22.01 | 14.06 | 18.035 | 20.4 | 9 O'Clock | 200 | 23.01 | 200-PG-23008-15S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.34 |  | 20.4 | 20.4 | 21.3 | 20.4 | 0.45
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-8 | 200-PG-23065-09C02-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 620 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.325 | CML-8 | CML: Pipe Length | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 18.5 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.33 |  | 19.8 | 18.5 | 19.3 | 19.7 | 0.5909
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23122 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 5.425 | CML-4 | CML: Pipe Length | 3 | 2030-10-02 | 2032-08-12 | 2015-05-10 07:00 | 2.5 | 0.17521 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57044-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.089713 | 5.2 | 5.3 | 5.6 | 5.6 | 0.20616
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-9 | 150-FG-45505-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 22349 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 8.025 | CML-9 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 12 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8.4 | 8.4 | 7.8 | 0.45
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-8 | 50-FG-45301-01C02 CML-8 | Yes | FPSO 2014 | Pipe Wall Thickness | 5794 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 5.975 | CML-8 | CML: Elbow | 3 | 2026-11-08 | 2028-04-18 | 2014-06-23 13:00 | 2.5 | 0.22604 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 6.2 | 6.2 | 6.2 | 0.45
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23096 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.575 | CML-2 | CML: Elbow | 3 | 2077-07-26 | 2085-01-13 | 2015-05-07 07:00 | 2.5 | 0.04658 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 12 O'Clock | 80 | 5.49 | 80-FL-43171-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.68545 | 5.4 | 5.7 | 5.6 | 5.6 | 0.12583
WC01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-WC-40006-01C02 | CML-6 | 150-WC-40006-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 5923 | Rope Access | 2015-03-16 07:00 | 2015-03-16 15:00 | [36 empty] | 5.575 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 5.4 | 9 O'Clock | 100 | 3 | 100-WF-71327-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.6 | 5.7 | 5.4 | 0.12583
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-25 | 100-FG-45001-09C02 CML-25 |  | FPSO 2013 | Pipe Wall Thickness | 10440 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.225 | CML-25 | CML: type TBC | 3 | 2015-12-26 | 2015-04-20 | 2013-11-13 | 4.7 | 2.4997 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 10 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 10 | 10.9 | 10 | 10 | 0.45
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-17 | 50-DH-56109-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21006 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.225 | CML-17 | CML: Elbow | 3 | 2016-07-30 | 2016-12-02 | 2014-05-24 10:30 | 2.5 | 0.95989 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.6 | 5.2 | 5.5 | 4.6 | 0.45
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56001-01C02 | CML-1 | 80-DH-56001-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3415 | Rope Access | 2014-05-11 11:00 | 2014-05-11 12:00 | [36 empty] | 5.275 | CML-1 | CML: type TBC | 3 | 2018-03-12 | 2018-10-01 | 2014-05-11 11:00 | 2.5 | 0.62518 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 12 O'Clock | 80 | 5.49 | 80-DH-56001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.9 | 5 | 5.3 | 0.45
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44036-01C02-P | CML-2 | 80-PW-44036-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 22960 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 5.25 | CML-2 | CML: Reducing Tee | 3 | 2028-02-27 | 2029-11-15 | 2015-05-04 07:00 | 2.5 | 0.20269 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 12 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.35437 | 5.1 | 5.2 | 5.4 | 5.3 | 0.1291
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 100-PG-23405-03C02-P | CML-3 | 100-PG-23405-03C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 23855 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 6.6 | CML-3 | CML: type TBC | 3 |  |  | 2014-09-26 07:00 | 2.7 | 0 | A2: Right Quadrant |  |  | 2.7 |  | 6.4 | 3 O'Clock | 200 |  | 200-PG-23405-03C02-P | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.4 | 6.8 | 6.7 | 0.18257
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-2 | 250-PL-20006-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13172 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 6.5 | CML-2 | CML: Pipe Length | 3 | 2051-11-30 | 2051-08-19 | 2014-01-21 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 3 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.4 | 6.6 | 6.5 | 0.08165
FG02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 25-FG-45455-01C02-E | CML-4 | 25-FG-45455-01C02-E CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20366 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-24 10:37 | [32 empty] | 6.625 | CML-4 | CML: Elbow | 3 | 2028-03-29 | 2028-02-18 | 2014-10-06 07:00 | 2.5 | 0.2595 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 7 | 6.6 | 6 | 0.45
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23211 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.425 | CML-2 | CML: Fitting | 3 | 2033-06-09 | 2035-10-08 | 2015-05-11 07:00 | 2.5 | 0.14923 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 1.2225 | 5.2 | 5.6 | 5.6 | 5.3 | 0.20616
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-20 | 250-PW-20041-03C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21429 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.55 | CML-20 | CML: Fitting | 6 | 2021-05-21 | 2020-03-07 | 2014-07-12 07:30 | 4.1 | 1.078 | A3: Inside Quadrant |  | 6.7 | 4.1 | 5.4 | 11.5 | 6 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 12.8 | 13.1 | 11.5 | 12.8 | 0.71414
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-32 | 50-CG-38001-09C02 CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 10947 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 9.225 | CML-32 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 0.23122 | A2: Right Quadrant |  | 5.74 |  |  | 8.6 | 3 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 8.6 | 9.6 | 8.6 | 9.2 | 9.5 | 0.45
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56053-01C02 | CML-1 | 80-DH-56053-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20940 | Rope Access | 2014-05-21 14:00 | 2014-05-21 15:00 | [36 empty] | 5.325 | CML-1 | CML: Elbow | 3 | 2017-02-02 | 2017-07-08 | 2014-05-21 14:00 | 2.5 | 0.81321 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 6 O'Clock | 80 | 5.49 | 80-DH-56053-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.6 | 5.3 | 4.7 | 5.7 | 0.45
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-10 | 25-FG-45455-01C02-E CML-10 |  | FPSO 2016 | Pipe Wall Thickness | 24355 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.525 | CML-10 | CML: Elbow | 3 | 2039-03-19 | 2039-01-09 | 2016-06-06 07:00 | 2.5 | 0.14914 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 3 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.8 | 5.9 | 6.9 | 6.5 | 0.45
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-9 | 150-WC-40006-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 23086 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.5 | CML-9 | CML: Elbow | 3 | 2077-07-26 | 2085-01-13 | 2015-05-07 07:00 | 2.5 | 0.04658 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 1.4244 | 5.6 | 5.4 | 5.4 | 5.6 | 0.11547
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-16 | 100-FG-45001-09C02 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10431 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.125 | CML-16 | CML: type TBC | 3 | 2015-04-25 | 2014-10-22 | 2013-11-13 | 4.7 | 3.3845 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 9.6 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 10.1 | 9.6 | 10.1 | 10.7 | 0.45
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-6 | 250-PG-20036-01C03-P CML-6 | yes | FPSO 2016 | Pipe Wall Thickness | 24411 | Re-check as requested by N.Sequera | 2016-07-06 07:00 | 2016-07-06 15:00 | Check Corrosion Rate of 0.539mm/ yr | 41 | Kirstie Albone | 2017-03-23 15:03 | [32 empty] | 8.125 | CML-6 | CML: Elbow | 6 | 2025-12-21 | 2025-04-04 | 2016-07-06 07:00 | 2.5 | 0.53881 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.6 | 12 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 | 0.10399 | 7.6 | 8.1 | 8.1 | 8.7 | 0.45
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-20 | 200-PL-20035-03C02-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 21352 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 8.15 | CML-20 | CML: Fitting | 3 | 2021-11-11 | 2020-05-30 | 2014-06-27 13:00 | 3.61 | 0.54068 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 7.6 | 3 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.99 |  | 8.3 | 7.6 | 8.9 | 7.8 | 0.58023
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56011-01C02 | CML-3 | 50-DH-56011-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1836 | Rope Access | 2014-05-06 09:30 | 2014-05-06 10:30 | [36 empty] | 5.275 | CML-3 | CML: type TBC | 3 | 2016-10-11 | 2017-02-20 | 2014-05-06 09:30 | 2.5 | 0.90337 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 5.8 | 4.7 | 5.3 | 0.45
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56011-01C02 | CML-3 | 50-DH-56011-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22316 | Rope Access | 2014-05-06 09:30 | 2014-05-06 10:30 | [36 empty] | 5.275 | CML-3 | CML: type TBC | 3 | 2016-10-11 | 2017-02-20 | 2014-05-06 09:30 | 2.5 | 0.90337 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.3 | 5.8 | 4.7 | 5.3 | 0.45
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-5 | 200-PL-20035-03C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21340 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.95 | CML-5 | CML: Pipe Length | 3 | 2021-11-11 | 2020-05-30 | 2014-06-27 13:00 | 3.61 | 0.54068 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 7.6 | 3 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.99 |  | 8.2 | 7.6 | 8.1 | 7.9 | 0.26458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-16 | 250-FH-43303-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12954 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.725 | CML-16 | CML: type TBC | 3 | 2030-04-23 | 2030-03-09 | 2014-01-27 10:00 | 2.5 | 0.22773 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.3 | 6.7 | 6.2 | 6.7 | 0.45
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23516-03C03 | CML-4 | 50-PL-23516-03C03 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7792 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-13 07:00 | 2015-01-13 09:00 |  |  | Administrator | 2015-09-08 15:57 | [32 empty] | 8.425 | CML-4 | CML: Elbow | 6 | 2025-06-10 | 2025-03-17 | 2015-01-13 07:00 | 2.5 | 0.51853 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 7.9 | 9 O'Clock | 50 | 8.74 | 50-PL-23516-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.4 | 9 | 8.4 | 7.9 | 0.45
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45305-03C02 | CML-8 | 100-FG-45305-03C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 22084 | Rope Access | 2014-05-25 09:30 | 2014-05-25 10:30 | [36 empty] | 6.525 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2014-05-25 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 6.2 | 3 O'Clock | 100 | 6.02 | 100-FG-45305-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.2 | 7.3 | 6.4 | 0.5252
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-17 | 100-FG-45304-03C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 22073 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.55 | CML-17 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2014-05-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.76 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.9 | 6.3 | 6.8 | 6.2 | 0.35119
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-10 | 100-FG-45304-03C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 22066 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.425 | CML-10 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2014-05-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 6.2 | 6 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.3 | 6.2 | 6.7 | 0.22174
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-7 | 100-FG-45304-03C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22063 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.375 | CML-7 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2014-05-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 6.2 | 3 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.2 | 6.5 | 6.6 | 0.20616
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45300-01C02 | CML-22 | 50-FG-45300-01C02 CML-22 | yes | FPSO 2015 | Pipe Wall Thickness | 7845 | This line is reporting higher CR than expected. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. Action: To recheck this line in a year (Jan. 2016) to confirm current CR. | 2015-01-13 13:00 | 2015-01-13 16:00 |  |  | Administrator | 2015-09-06 22:41 | [32 empty] | 5.075 | CML-22 | CML: Elbow | 3 | 2019-04-11 | 2019-11-27 | 2015-01-13 13:00 | 2.5 | 0.51831 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-FG-45300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.6 | 5.3 | 4.7 | 0.45
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-39 | 50-DH-56062-01C02 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 9126 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 6.225 | CML-39 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.6 | 6 | 6.6 | 5.7 | 0.45
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45024-01C02 | CML-10 | 50-FG-45024-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20828 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.575 | CML-10 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 3 O'Clock | 50 | 8.74 | 50-CG-38488-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.6 | 9.2 | 9.3 | 10.2 | 0.45
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-10 | 50-CG-38452-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 13100 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 20.875 | CML-10 | CML: type TBC | 3 | 2015-12-23 | 2015-04-30 | 2014-01-10 09:00 | 15.88 | 2.3693 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 6 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 |  | 21.1 | 20.5 | 20.5 | 21.4 | 0.45
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-13 | 200-PL-20035-03C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 21345 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.975 | CML-13 | CML: Pipe Length | 3 | 2021-11-11 | 2020-05-30 | 2014-06-27 13:00 | 3.61 | 0.54068 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.6 | 6 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.99 |  | 8.2 | 8.1 | 7.6 | 8 | 0.263
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40512-1CG | CML-3 | 150-WC-40512-1CG CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5476 | Rope Access | 2014-05-28 10:00 | 2014-05-28 11:30 | [36 empty] | 11.675 | CML-3 | CML: Elbow | 3 | 2098-02-09 | 2070-10-05 | 2014-05-28 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 7.97 | 2.5 | 5.235 | 11.1 | 9 O'Clock | 150 | 10.97 | 150-WC-40512-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.4 | 12.2 | 12 | 11.1 | 0.51235
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-13 | 200-PG-23065-09C02-A CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 427 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.675 | CML-13 | CML: Elbow | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 18.5 | 6 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.33 |  | 18.7 | 18.5 | 18.5 | 19 | 0.23629
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-15 | 200-PG-23065-09C02-A CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 429 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 18.675 | CML-15 | CML: Pipe Length | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A4: Left Quadrant |  | 15.26 | 10.17 | 12.715 | 18.5 | 9 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.33 |  | 18.8 | 18.8 | 18.6 | 18.5 | 0.15
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23051-09C02-A | CML-9 | 200-PG-23051-09C02-A CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 13114 |  | 2014-02-07 11:00 | 2014-02-07 13:00 | [36 empty] | 18.875 | CML-9 | CML: type TBC | 3 | 2026-10-28 | 2022-05-13 | 2014-02-07 11:00 | 9.3 | 0.66771 | A2: Right Quadrant |  | 15.26 | 9.3 | 12.28 | 17.8 | 3 O'Clock | 200 | 18.26 | 200-PG-23051-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 19.4 | 17.8 | 18.6 | 19.7 | 0.85391
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-34 | 150-PG-23506-25C02 CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 2808 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 21.475 | CML-34 | CML: Pipe Length | 3 | 2019-01-13 | 2017-08-12 | 2014-03-15 09:00 | 15.88 | 1.0796 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 21.1 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.22 |  | 22 | 21.1 | 21.1 | 21.7 | 0.45
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38486-09C02-P |  | 80-CG-38486-09C02-P |  | FPSO 2015 | Pipe Wall Thickness | 23650 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 15.95 | 80-CG-38486-01C02-H | Piping | 3 | 2043-04-25 |  | 2015-10-28 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 15.5 | 3 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13 |  | 15.7 | 15.5 | 16.1 | 16.5 | 0.44347
VA01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-VA-23057-01C02 | CML-1 | 200-VA-23057-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3145 | Rope Access | 2014-05-02 14:00 | 2014-05-02 15:00 | [36 empty] | 8.15 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-05-02 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 6 O'Clock | 200 | 6.35 | 200-VA-23057-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 8.3 | 8.3 | 7.5 | 8.5 | 0.44347
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38491-09C02 | CML-5 | 50-CG-38491-09C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2544 |  | 2014-04-03 10:00 | 2014-04-03 11:00 | [36 empty] | 9.35 | CML-5 | CML: type TBC | 3 | 2144-04-16 | 2110-04-25 | 2014-04-03 10:00 | 2.5 | 0.04765 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 6 O'Clock | 50 | 8.74 | 50-CG-38491-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.5 | 9.7 | 8.7 | 9.5 | 0.44347
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-32 | 100-DC-57036-01C02 CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 1438 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 6.4 | CML-32 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 6 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  |  | 6.6 | 6.2 | 6.4 | 0.2
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-9 | 100-DC-57036-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1415 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 6.45 | CML-9 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 6 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.2 | 7 | 0.37859
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57027-01C02 | CML-2 | 50-DC-57027-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1401 | Rope access | 2014-04-05 15:00 | 2014-04-05 16:00 | [36 empty] | 6.5 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 15:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-DC-57027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 6.8 | 6.2 | 6.5 | 0.24495
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-1 | 50-FG-45020-03C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2600 | Rope Access | 2014-04-26 09:30 | 2014-04-26 10:45 | [36 empty] | 9.65 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-04-26 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 9 | 9 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 | -2.0481 | 9.8 | 10 | 9.8 | 9 | 0.44347
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-13 | 300-PG-23002-03C03-A CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10109 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 13.65 | CML-13 | CML: Pipe Length | 6 | 2016-07-08 | 2015-12-30 | 2013-11-07 | 5.22 | 2.9154 | A4: Left Quadrant |  | 8.27 | 5.22 | 6.745 | 13 | 9 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.78 |  | 14 | 13.8 | 13.8 | 13 | 0.44347
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-18 | 250-PW-20040-03C03-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23467 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 12.375 | CML-18 | CML: Fitting | 6 | 2028-10-13 | 2026-06-18 | 2015-07-24 07:00 | 4.1 | 0.55918 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 11.5 | 9 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 | 0 | 13.2 | 12.6 | 12.2 | 11.5 | 0.71356
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43176-01C02 | CML-7 | 300-FL-43176-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20437 | Protective mesh removed/Rope access | 2014-06-27 10:30 | 2014-06-27 12:00 | [36 empty] | 10.25 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-27 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 9.8 | 3 O'Clock | 300 | 6.35 | 300-FL-43176-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.3 |  | 10 | 9.8 | 10.8 | 10.4 | 0.44347
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38472-01C02 | CML-4 | 50-CG-38472-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23659 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 11.35 | CML-4 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.9 | 3 O'Clock | 50 | 5.54 | 50-CG-38472-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 11.1 | 10.9 | 11.9 | 11.5 | 0.44347
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56044-01C02 | CML-2 | 80-DH-56044-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20932 | Rope Access | 2014-05-16 09:30 | 2014-05-16 11:00 | [36 empty] | 5.05 | CML-2 | CML: type TBC | 3 | 2016-08-17 | 2017-01-01 | 2014-05-16 09:30 | 2.5 | 0.92975 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.6 | 9 O'Clock | 80 | 5.49 | 80-DH-56044-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.6 | 5.2 | 4.8 | 4.6 | 0.44347
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38463-01C02 | CML-8 | 50-CG-38463-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 3119 | Rope Access | 2014-05-04 08:00 | 2014-05-04 09:00 | [36 empty] | 5.45 | CML-8 | CML: Elbow | 3 | 2017-10-20 | 2018-04-10 | 2014-05-04 08:00 | 2.5 | 0.69249 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-CG-38463-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.7 | 4.9 | 5.9 | 5.3 | 0.44347
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-2 | 50-PW-44040-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23237 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.275 | CML-2 | CML: Pipe Length | 3 | 2026-10-31 | 2028-04-09 | 2015-05-11 07:00 | 2.5 | 0.22642 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.17805 | 5.4 | 5.3 | 5.1 | 5.3 | 0.12583
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-13 | 80-PW-44016-01C02-P CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22915 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.25 | CML-13 | CML: Elbow | 3 | 2028-02-11 | 2029-10-29 | 2015-05-02 07:00 | 2.5 | 0.20327 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 | 0.53676 | 5.1 | 5.3 | 5.3 | 5.3 | 0.1
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-48 | 50-DH-56070-01C02 CML-48 |  | FPSO 2014 | Pipe Wall Thickness | 3264 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 7.25 | CML-48 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.5 | 7.1 | 7.7 | 6.7 | 0.44347
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45007-03C02-E | CML-2 | 100-FG-45007-03C02-E CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24309 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.25 | CML-2 | CML: Elbow | 3 | 2054-10-24 | 2049-02-10 | 2016-05-27 07:00 | 1.88 | 0 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 6.7 | 12 O'Clock | 100 | 6.02 | 100-FG-45007-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.82 |  | 6.7 | 7.5 | 7.7 | 7.1 | 0.44347
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-20 | 300-WS-50805-1LC CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 10820 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 11.95 | CML-20 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 11.7 | 9 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 11.7 | 12.1 | 12.3 | 11.7 | 0.3
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-22 | 300-WS-50805-1LC CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 10822 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.3 | CML-22 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 11.8 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.9 | 12 | 11.8 | 12.5 | 0.49666
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45043-03C02-E | CML-12 | 100-FG-45043-03C02-E CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 22658 | Laggimg Removed By Bellis | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 5.85 | CML-12 | CML: Elbow | 3 | 2028-07-27 | 2026-06-26 | 2015-04-27 07:00 | 1.88 | 0.27298 | A2: Right Quadrant |  | 3.02 | 1.88 | 2.45 | 5.5 | 3 O'Clock | 50 | 6.02 | 100-FG-45043-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.62 |  | 5.7 | 5.5 | 5.7 | 6.5 | 0.44347
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-6 | 150-FH-43518-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5521 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 7.15 | CML-6 | CML: Pipe Length | 3 | 2032-05-20 | 2029-03-04 | 2014-06-01 07:00 | 1.23 | 0.30975 | A3: Inside Quadrant |  | 4.11 | 1.23 | 2.2256 | 6.8 | 6 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.57 | -0.90216 | 7 | 7.8 | 6.8 | 7 | 0.44347
VA01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-VA-23054-01C02 | CML-15 | 25-VA-23054-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 22006 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 13.45 | CML-15 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 12.9 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 13.3 | 13.9 | 12.9 | 13.7 | 0.44347
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-4 | 50-CG-38452-09C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1698 | Rope Access | 2014-04-13 09:15 | 2014-04-13 10:15 | [36 empty] | 7.85 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 09:15 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.2 | 3 O'Clock | 50 | 5.54 | 50-WC-40018-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8 | 7.2 | 8 | 8.2 | 0.44347
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-15 | 300-PF-20001-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21153 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | Check Corrosion Rate of 0.329mm/ yr | 40 | Kirstie Albone | 2017-03-23 16:13 | [32 empty] | 14.45 | CML-15 | CML: Fitting | 6 | 2041-11-11 | 2036-09-30 | 2014-07-16 07:30 | 4.9 | 0.32914 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 3 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.9 | 13.9 | 14.7 | 14.3 | 0.44347
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-13 | 50-DC-57056-03C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1146 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.375 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 6.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.4 | 6.3 | 6.6 | 0.17078
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-7 | 50-CG-38452-09C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20336 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.65 | CML-7 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 6 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8.2 | 7.8 | 7.2 | 7.4 | 0.44347
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23004-06C03-A | CML-21 | 250-PG-23004-06C03-A CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 13021 |  | 2014-01-11 15:00 | 2014-01-11 18:00 | [36 empty] | 18.85 | CML-21 | CML: Elbow | 6 | 2110-07-06 | 2091-12-17 | 2014-01-11 15:00 | 8.55 | 0 | A3: Inside Quadrant |  | 12.26 | 8.55 | 10.405 | 18.4 | 6 O'Clock | 250 | 18.26 | 250-PG-23004-06C03 | 100 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.85 |  | 19.4 | 19 | 18.4 | 18.6 | 0.44347
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-41 | 300-PF-20501-03C03-P CML-41 |  | FPSO 2014 | Pipe Wall Thickness | 21717 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 17.35 | CML-41 | CML: type TBC | 6 | 2107-02-11 | 2090-04-05 | 2014-09-28 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 16.9 | 9 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12 |  | 17.9 | 17.5 | 17.1 | 16.9 | 0.44347
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43091-01C02 | CML-2 | 80-FL-43091-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5827 | Rope access | 2014-06-24 10:30 | 2014-06-24 12:00 | [36 empty] | 8.05 | CML-2 | CML: Reducer | 3 | 2043-04-25 | 2046-10-17 | 2014-06-24 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.7 | 12 O'Clock | 80 | 5.49 | 80-FL-43091-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 7.9 | 7.9 | 8.7 | 0.44347
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-4 | 200-PL-20035-03C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21339 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.925 | CML-4 | CML: Elbow | 3 | 2021-11-11 | 2020-05-30 | 2014-06-27 13:00 | 3.61 | 0.54068 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 7.6 | 3 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.99 |  | 8.2 | 7.6 | 7.9 | 8 | 0.25
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-10 | 100-DC-57038-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2373 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 6.375 | CML-10 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 9 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.7 | 6.3 | 6.3 | 6.2 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-10 | 100-DC-57037-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2361 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 6.55 | CML-10 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 6 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.5 | 7.1 | 6.2 | 6.4 | 0.3873
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-3 | 100-DC-57037-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2354 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 6.5 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.2 | 6 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.6 | 6.2 | 6.6 | 0.2
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-16 | 100-DC-57307-01C03 CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 2324 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.975mm/ yr | [35 empty] | 6.35 | CML-16 | CML: type TBC | 6 | 2015-06-14 | 2015-06-10 | 2014-03-17 13:00 | 2.5 | 2.975 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 6.2 | 3 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.2 | 6.5 | 6.4 | 0.1291
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-7 | 100-DC-57307-01C03 CML-7 | yes | FPSO 2014 | Pipe Wall Thickness | 2315 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.975mm/ yr | [35 empty] | 6.825 | CML-7 | CML: type TBC | 6 | 2015-06-14 | 2015-06-10 | 2014-03-17 13:00 | 2.5 | 2.975 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.2 | 6 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.4 | 7 | 6.2 | 6.7 | 0.5058
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23095 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.55 | CML-1 | CML: Fitting | 3 | 2077-07-26 | 2085-01-13 | 2015-05-07 07:00 | 2.5 | 0.04658 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 12 O'Clock | 80 | 5.49 | 80-FL-43171-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.17136 | 5.4 | 5.6 | 5.6 | 5.6 | 0.1
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-23 | 300-PG-20506-03C03-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 13237 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 13.475 | CML-23 | CML: type TBC | 6 | 2018-06-09 | 2017-07-14 | 2014-02-04 15:00 | 4.9 | 1.8644 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13 | 12 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 13 | 13.9 | 13.8 | 13.2 | 0.44253
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-10 | 200-PL-20035-03C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21333 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 7.9 | CML-10 | CML: Reducer | 3 | 2021-11-11 | 2020-05-30 | 2014-06-27 13:00 | 3.61 | 0.54068 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 7.6 | 9 O'Clock | 150 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.99 |  | 8.1 | 7.9 | 8 | 7.6 | 0.21602
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-21 | 300-WS-50805-1LC CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 10821 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.4 | CML-21 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 12 | 3 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.6 | 12 | 12.8 | 12.2 | 0.36515
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8871 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 08:00 | 2015-02-25 09:00 | [36 empty] | 5.45 | CML-3 | CML: type TBC | 3 | 2051-02-16 | 2055-03-05 | 2015-02-25 08:00 | 2.5 | 0.08056 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AU-63019-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.6 | 5.4 | 0.1
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-64 | 150-WC-40006-01C02 CML-64 |  | FPSO 2015 | Pipe Wall Thickness | 8988 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.45 | CML-64 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.4 | 5.6 | 0.1
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-6 | 80-CG-38459-09C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23703 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 6.375 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 3 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.1 | 5.9 | 6.8 | 6.7 | 0.44253
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-13 | 50-CG-38452-09C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 23798 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 7.625 | CML-13 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 6 O'Clock | 300 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.3 | 8.1 | 7.2 | 7.9 | 0.44253
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-21 | 200-PL-20019-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 21272 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.35 | CML-21 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 3 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.2 | 6.5 | 7 | 8.7 | 0.94692
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-18 | 250-PW-20040-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21402 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.4 | CML-18 | CML: Fitting | 6 | 2021-05-21 | 2020-03-07 | 2014-07-12 07:30 | 4.1 | 1.078 | A3: Inside Quadrant |  | 6.7 | 4.1 | 5.4 | 11.5 | 6 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 13.2 | 12.6 | 11.5 | 12.3 | 0.70711
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-5 | 150-PG-23506-25C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2779 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 22.025 | CML-5 | CML: Pipe Length | 3 | 2027-01-22 | 2023-08-11 | 2014-03-15 09:00 | 15.88 | 0.44454 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21.6 | 12 O'Clock | 50 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.72 |  | 21.6 | 21.7 | 22.3 | 22.5 | 0.44253
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56039-01C02 | CML-3 | 80-DH-56039-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20920 | Rope Access | 2014-05-21 11:00 | 2014-05-21 12:00 | [36 empty] | 5.325 | CML-3 | CML: Elbow | 3 | 2018-05-02 | 2018-11-27 | 2014-05-21 11:00 | 2.5 | 0.60755 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-DH-56039-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5 | 4.9 | 5.6 | 5.8 | 0.44253
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-12 | 50-PW-44013-01X01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5736 | Rope access | 2014-06-22 13:00 | 2014-06-22 14:00 | [36 empty] | 5.45 | CML-12 | CML: Reducing Tee | 3 | 2022-11-17 | 2023-11-23 | 2014-06-22 13:00 | 2.5 | 0.32105 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.81277 | 5.4 | 5.2 | 5.6 | 5.6 | 0.19149
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-8 | 250-FH-43303-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12946 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 7.5 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8 | 7 | 7.3 | 7.7 | 0.4397
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-24 | 150-FG-45505-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 22364 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 8.1 | CML-24 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.6 | 3 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8.6 | 7.6 | 8.3 | 7.9 | 0.4397
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20120 | Rope Access | 2014-05-07 07:00 | 2014-05-07 08:00 | [36 empty] | 5.9 | CML-3 | CML: type TBC | 3 | 2033-08-24 | 2035-10-26 | 2014-05-07 07:00 | 2.5 | 0.15017 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 6.1 | 6.4 | 5.4 | 0.4397
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-3 | 250-PG-23003-06C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3168 | Rope Access | 2014-05-07 07:00 | 2014-05-07 08:00 | [36 empty] | 5.9 | CML-3 | CML: type TBC | 3 | 2033-08-24 | 2035-10-26 | 2014-05-07 07:00 | 2.5 | 0.15017 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 6.1 | 6.4 | 5.4 | 0.4397
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-4 | 200-PG-24001-09C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10260 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 20.8 | CML-4 | CML: Pipe Length | 3 | 2104-01-05 | 2073-09-17 | 2013-11-09 | 9.2 | 0 | A3: Inside Quadrant |  | 15.26 | 9.2 | 12.23 | 20.3 | 6 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 21.3 | 20.6 | 20.3 | 21 | 0.4397
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-6 | 300-PG-20004-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 6129 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 21.15 | CML-6 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 20.9 | 9 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16 |  | 21 | 21.8 | 20.9 | 20.9 | 0.43589
WC01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-WC-40006-01C02 | CML-3 | 150-WC-40006-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23212 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.475 | CML-3 | CML: Fitting | 3 | 2077-12-06 | 2085-06-10 | 2015-05-11 07:00 | 2.5 | 0.04631 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 1.7464 | 5.4 | 5.6 | 5.5 | 5.4 | 0.095743
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-34 | 200-PW-44018-01X01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 23553 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 5.325 | CML-34 | CML: Pipe Length | 3 | 2033-01-02 | 2035-02-09 | 2015-08-10 07:30 | 2.5 | 0.15506 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.6 | 5.2 | 5.3 | 0.1893
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-12 | 50-CG-38487-09C02-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20812 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 11.85 | CML-12 | CML: Reducing Tee | 3 | 2075-10-24 | 2059-08-12 | 2014-07-18 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 11.6 | 9 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 11.7 | 11.6 | 12.5 | 11.6 | 0.43589
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 400-WC-40501-1CG | CML-31 | 400-WC-40501-1CG CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 5472 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | Check Corrosion Rate of 10.446mm/ yr | [34 empty] | Low alarm breach | 11.5 | CML-31 | CML: Elbow | 3 | 2015-03-24 | 2014-06-19 | 2014-05-28 07:00 | 2.5 | 10.4461 | A3: Inside Quadrant |  | 18.44 | 2.5 | 10.47 | 11.1 | 6 O'Clock | 400 | 21.44 | 400-WC-40501-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 11.5 | 11.4 | 11.1 | 12 | 0.37417
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-4 | 200-PW-44018-01X01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23081 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 5.475 | CML-4 | CML: Elbow | 3 | 2033-04-28 | 2035-08-23 | 2015-05-07 07:00 | 2.5 | 0.15008 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 20 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 2.8488 | 5.2 | 5.6 | 5.6 | 5.5 | 0.1893
DH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-DH-56137-01C02 | CML-8 | 50-DH-56137-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1880 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 16.8 | CML-8 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 16.3 | 3 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.8 |  |  | 16.3 | 17 | 17.1 | 0.43589
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-13 | 100-FG-45001-09C02 CML-13 | Yes | FPSO 2015 | Pipe Wall Thickness | 23318 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.05 | CML-13 | CML: type TBC | 3 | 2031-12-28 | 2027-01-14 | 2015-07-11 07:00 | 4.7 | 0.34591 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.4 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 | -0.36181 | 11.3 | 10.4 | 11.2 | 11.3 | 0.43589
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-25 | 50-FG-45021-03C02 CML-25 |  | FPSO 2013 | Pipe Wall Thickness | 10553 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.25 | CML-25 | CML: type TBC | 3 | 2015-01-30 | 2015-01-26 | 2013-11-16 | 2.5 | 1.825 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 4.7 | 5.6 | 5.6 | 0.43589
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-8 | 250-PG-23003-06C02-PA CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2034 |  | 2014-03-27 14:30 | 2014-03-27 15:00 | [36 empty] | 5.65 | CML-8 | CML: type TBC | 3 | 2040-08-31 | 2043-11-03 | 2014-03-27 14:30 | 2.5 | 0.10964 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-DH-56106-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.3 | 5.4 | 5.5 | 0.43589
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-19 | 300-WS-50805-1LC CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 10819 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.225 | CML-19 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 12 | 9 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.5 | 12.1 | 12.3 | 12 | 0.22174
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-23 | 300-WS-50805-1LC CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 10823 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.7 | CML-23 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 12.2 | 12 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 12.2 | 12.9 | 12.8 | 12.9 | 0.33665
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-1 | 150-FG-45002-03C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10404 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.45 | CML-1 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.2 | 9 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 6.7 | 6.3 | 6.2 | 0.23805
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22909 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.325 | CML-7 | CML: Elbow | 3 | 2033-03-08 | 2035-06-26 | 2015-05-02 07:00 | 2.5 | 0.15115 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.17892 | 5.2 | 5.3 | 5.2 | 5.6 | 0.1893
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-47 | 300-PF-20001-03C03-P CML-47 |  | FPSO 2014 | Pipe Wall Thickness | 21185 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 21.35 | CML-47 | CML: Reducer | 6 | 2090-02-10 | 2081-10-05 | 2014-07-16 07:30 | 6.6 | 0 | A3: Inside Quadrant |  | 8.27 | 6.6 | 7.435 | 21.1 | 9 O'Clock | 400 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.5 |  | 22 | 21.2 | 21.1 | 21.1 | 0.43589
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-2 | 300-PG-20037-03C03-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21377 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | Check Corrosion Rate of 0.436mm/ yr | [35 empty] | 14.15 | CML-2 | CML: Pipe Length | 6 | 2033-11-28 | 2030-07-16 | 2014-06-29 13:00 | 5.33 | 0.43591 | A3: Inside Quadrant |  | 8.27 | 5.33 | 6.8 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.47 |  | 14.3 | 14.7 | 13.8 | 13.8 | 0.43589
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-3 | 150-PG-23043-06C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 24272 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 13.425 | CML-3 | CML: Equal Tee | 3 | 2076-02-10 | 2066-08-14 | 2014-09-24 07:00 | 4.7 | 0 | A3: Inside Quadrant |  | 7.97 | 4.7 | 5.6494 | 13 | 6 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 13.1 | 13.8 | 13 | 13.8 | 0.43493
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-4 | 300-PG-23400-01C03-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23418 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | Check Corrosion Rate of 0.612mm/ yr |  | John Wilson | 2017-03-24 09:32 | Anomily raised to revisit 7/5/2018 | [31 empty] | 9.7 | CML-4 | CML: Pipe Length | 6 | 2021-09-22 | 2022-06-21 | 2015-07-22 07:00 | 5.22 | 0.612 | A3: Inside Quadrant |  | 4.31 | 5.22 | 4.765 | 9 | 6 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.78 | -0.26134 | 9.6 | 9.8 | 9 | 10.4 | 0.57735
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-PG-20054-01C03-P | CML-16 | 150-PG-20054-01C03-P CML-16 | yes | FPSO 2014 | Pipe Wall Thickness | 21527 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 8.425 | CML-16 | CML: Pipe Length | 6 | 2016-04-09 | 2015-11-09 | 2014-06-26 13:00 | 2.5 | 2.9627 | A4: Left Quadrant |  | 4.97 | 2.5 | 3.735 | 7.8 | 9 O'Clock | 100 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.6 | 8.8 | 8.5 | 7.8 | 0.43493
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-2 | 150-PG-23043-06C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23458 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 9.325 | CML-2 | CML: Elbow | 3 | 2019-05-04 | 2018-06-10 | 2015-07-24 07:00 | 4.7 | 1.0578 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.7 | 3 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | -0.72277 | 9.4 | 8.7 | 9.5 | 9.7 | 0.43493
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-14 | 250-PG-20036-01C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21372 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | Check Corrosion Rate of 0.42mm/ yr | 41 | Kirstie Albone | 2017-03-23 15:14 | [32 empty] | 9.175 | CML-14 | CML: Elbow | 6 | 2029-07-08 | 2028-08-07 | 2014-07-14 07:30 | 2.5 | 0.42014 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 8.8 | 3 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9 | 8.8 | 9.1 | 9.8 | 0.43493
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-4 | 80-CG-38459-09C02-P CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 24263 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 19.275 | CML-4 | CML: Elbow | 3 | 2086-02-10 | 2064-10-05 | 2014-09-24 07:00 | 7 | 0 | A1: Outside Quadrant |  | 11.27 | 7 | 9.135 | 18.7 | 12 O'Clock | 150 | 14.27 | 150-PG-23026-09C02-P | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.7 |  | 18.7 | 19.7 | 19.2 | 19.5 | 0.43493
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-22 | 200-PG-23008-15S01-A CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 9109 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.725 | CML-22 | CML: type TBC | 3 | 2025-07-04 | 2026-10-21 | 2015-03-02 07:00 | 2.5 | 0.25122 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 6.1 | 5.9 | 5.8 | 5.1 | 0.43493
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 22328 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 5.775 | CML-6 | CML: type TBC | 3 | 2033-08-02 | 2035-10-02 | 2014-05-06 07:00 | 2.5 | 0.15061 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 6.4 | 5.4 | 5.6 | 0.43493
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-6 | 300-WS-50805-1LC CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10806 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 15.05 | CML-6 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 13 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.5 |  | 16.3 | 14.9 | 13 | 16 | 1.4933
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-6 | 250-PG-23003-06C02-PA CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1848 | Rope Access | 2014-05-06 07:00 | 2014-05-06 08:00 | [36 empty] | 5.775 | CML-6 | CML: type TBC | 3 | 2033-08-02 | 2035-10-02 | 2014-05-06 07:00 | 2.5 | 0.15061 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56014-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.7 | 6.4 | 5.4 | 5.6 | 0.43493
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9004-AS20-00 | CML-6 | 0100-AI-63L9004-AS20-00 CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24282 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.325 | CML-6 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.3 | 9 O'Clock | 25 | 3.38 | 0100-AI-63L9004-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.3 | 6.4 | 6.3 | 0.05
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-11 | 80-FH-43007-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12572 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.775 | CML-11 | CML: Pipe Length | 3 | 2048-03-30 | 2043-10-19 | 2014-01-18 07:00 | 0.54 | 0.14203 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.4 | 6 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.86 |  | 6.4 | 5.6 | 5.4 | 5.7 | 0.43493
PL02 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20008-01C02-H | CML-22 | 200-PL-20008-01C02-H CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 8819 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.575 | CML-22 | CML: Elbow | 3 | 2146-04-17 | 2145-04-27 | 2015-02-21 07:00 | 2.5 | 0.02895 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.5 | 6.4 | 7.1 | 0.3594
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-7 | 150-WC-40006-01C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8752 |  | 2015-02-15 07:00 | 2015-02-15 09:00 | [36 empty] | 5.475 | CML-7 | CML: type TBC | 3 | 2050-07-13 | 2054-07-06 | 2015-02-15 07:00 | 2.5 | 0.08185 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67006-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.4 | 5.5 | 5.4 | 0.095743
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-3 | 300-WS-50805-1LC CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10803 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 14.825 | CML-3 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 13 | 12 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.5 |  | 13 | 14.6 | 16 | 15.7 | 1.3574
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-18 | 300-WS-50805-1LC CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 10818 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 14.875 | CML-18 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 13.6 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 15.1 | 14 | 13.6 | 16.8 | 1.4315
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42313-01S01 | CML-6 | 40-CI-42313-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7521 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.95 | CML-6 | CML: type TBC | 1 | 2023-09-20 | 2020-09-01 | 2015-04-13 07:00 | 2.5 | 0.45003 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.3 | 12 O'Clock | 40 | 7.14 | 40-CI-42313-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 8.3 | 9.3 | 7.9 | 1.2477
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 | yes | FPSO 2013 | Pipe Wall Thickness | 10669 | Deck Level. High CR CML was rechecked. Latest CR with WT values reported in Jan 15 indicates a CR of 0.3982 | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 16:02 | [32 empty] | 4.825 | CML-2 | CML: Pipe Length | 3 | 2014-06-19 | 2014-07-30 | 2013-11-17 | 2.5 | 2.8941 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 12 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 4.2 | 5 | 4.9 | 5.2 | 0.43493
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 0200-DC-57L9006-AC21-00 | CML-11 | 0200-DC-57L9006-AC21-00 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 5051 |  | 2015-03-05 07:00 | 2015-03-05 14:00 | Check Corrosion Rate of 1.13mm/ yr | [35 empty] | 7.275 | CML-11 | CML: type TBC | 3 | 2018-07-14 | 2017-08-02 | 2015-03-05 07:00 | 2.5 | 1.1298 | A3: Inside Quadrant |  | 5.74 | 2.5 | 3.5737 | 6.3 | 6 O'Clock | 50 | 8.74 | 0200-DC-57L9006-AC21-00 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.4 | 7.5 | 6.3 | 7.9 | 0.68496
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-24 | 50-AI-63004-01E01 CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 9015 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.7 | CML-24 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.8 | 6.8 | 6.3 | 6.9 | 0.2708
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-10 | 50-AI-63004-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 9001 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.45 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 12 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.6 | 6.5 | 6.4 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43150-01C02 | CML-1 | 80-FH-43150-01C02 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24395 | Lagging removed | 2016-06-08 07:00 | 2016-06-08 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 5.175 | CML-1 | CML: Elbow | 3 | 2026-07-03 | 2028-01-11 | 2016-06-08 07:00 | 2.5 | 0.22827 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 3 O'Clock | 80 | 5.49 | 80-FH-43150-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 4.8 | 5.5 | 5.6 | 0.43493
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67010-01E01 | CML-10 | 50-GN-67010-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8713 |  | 2015-02-14 07:00 | 2015-02-14 09:00 | [36 empty] | 6.425 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 9 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 6.5 | 6.4 | 6.3 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-5 | 50-AI-63009-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8527 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.525 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 12 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.7 | 6.6 | 6.5 | 0.17078
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63020-01E01 | CML-7 | 50-AU-63020-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8487 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.575 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 9 O'Clock | 50 | 5.54 | 50-AU-63020-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.6 | 6.7 | 6.3 | 0.1893
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67008-01E01 | CML-7 | 50-GN-67008-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8469 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.55 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-GN-67008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.8 | 6.5 | 6.3 | 6.6 | 0.20817
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-12 | 50-WD-53011-01E01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8288 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.575 | CML-12 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 12 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.5 | 6.8 | 6.7 | 0.22174
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-4 | 50-WD-53010-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8247 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.575 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.3 | 6.7 | 6.6 | 0.1893
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53013-01E01 | CML-7 | 50-WD-53013-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8243 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.45 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-WD-53013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.4 | 6.3 | 6.4 | 0.17321
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53013-01E01 | CML-6 | 50-WD-53013-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8242 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.45 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-WD-53013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.6 | 6.3 | 6.4 | 6.5 | 0.1291
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53013-01E01 | CML-3 | 50-WD-53013-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8239 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.625 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 9 O'Clock | 50 | 5.54 | 50-WD-53013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.9 | 7 | 6.3 | 0.37749
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53013-01E01 | CML-2 | 50-WD-53013-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8238 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.725 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 12 O'Clock | 50 | 5.54 | 50-WD-53013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.8 | 7 | 6.8 | 0.29861
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-8 | 50-WD-53014-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8223 |  | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.925 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.5 | 6.3 | 6.5 | 7.4 | 0.61305
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-5 | 50-WD-53014-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8220 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.45 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 6.3 | 6.3 | 6.7 | 0.19149
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69006-01S01 | CML-10 | 50-OL-69006-01S01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8199 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.6 | CML-10 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.54 | 2.5 | 3.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 7 | 6.3 | 6.6 | 0.29439
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69006-01S01 | CML-4 | 50-OL-69006-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8193 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 7.125 | CML-4 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 6.3 | 12 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7.2 | 8.1 | 6.9 | 0.75
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-17 | 300-WS-50805-1LC CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 10817 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 14 | CML-17 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 13.9 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.4 |  | 14 | 14 | 13.9 | 14.1 | 0.08165
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-25 | 50-WD-53007-01E01 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 8164 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.75 | CML-25 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.1 | 6.4 | 6.3 | 7.2 | 0.46547
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-23 | 50-WD-53007-01E01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 8162 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.8 | CML-23 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7 | 6.5 | 6.3 | 7.4 | 0.49666
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-7 | 50-WD-53007-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8146 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.95 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.4 | 6.3 | 6.7 | 7.4 | 0.54467
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-10 | 100-OL-69002-01S01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8131 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.575 | CML-10 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.3 | 3 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.1 | 6.3 | 6.4 | 6.5 | 0.3594
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69002-01S01 | CML-3 | 100-OL-69002-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8124 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.675 | CML-3 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.3 | 12 O'Clock | 100 | 6.02 | 100-OL-69002-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.7 | 6.9 | 6.8 | 0.263
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-12 | 100-OL-69001-01S01 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 8114 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.625 | CML-12 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.3 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.4 | 7.2 | 6.6 | 0.40311
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-16 | 300-WS-50805-1LC CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 10816 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 14.05 | CML-16 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 14 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 14 | 14.1 | 14 | 14.1 | 0.057735
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-9 | 300-WS-50805-1LC CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10809 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 15.225 | CML-9 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 14.8 | 9 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.3 |  | 15 | 15.5 | 15.6 | 14.8 | 0.38622
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-14 | 300-WS-50805-1LC CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 10814 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.05 | CML-14 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 15.9 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.4 |  | 17.6 | 17.4 | 15.9 | 17.3 | 0.77675
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FL-43014-01C02 | CML-3 | 250-FL-43014-01C02 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23075 |  | 2015-05-07 07:00 | 2015-05-07 15:00 | [36 empty] | 6.425 | CML-3 | CML: Elbow | 3 | 2026-12-07 | 2026-10-31 | 2015-05-07 07:00 | 2.5 | 0.28463 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.8 | 12 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | 0.19366 | 5.8 | 6.5 | 6.6 | 6.8 | 0.43493
PW03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-PW-44018-01X01 | CML-19 | 200-PW-44018-01X01 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 7732 |  | 2015-01-09 13:00 | 2015-01-09 15:00 |  |  | Administrator | 2015-09-08 09:36 | [32 empty] | 5.4 | CML-19 | CML: Pipe Length | 3 | 2027-10-19 | 2029-05-05 | 2015-01-09 13:00 | 2.5 | 0.21122 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.50494 | 5.5 | 5.6 | 5.3 | 5.2 | 0.18257
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-2 | 80-DC-57002-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20231 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.05 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.3 | 9 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.3 | 8.1 | 6.5 | 6.3 | 0.8226
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-4 | 200-FH-43004-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12544 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 6.575 | CML-4 | CML: type TBC | 3 | 2030-08-26 | 2030-07-11 | 2014-02-01 07:00 | 2.5 | 0.2232 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 7.2 | 6.4 | 6.5 | 6.2 | 0.43493
DC01 | Montara_Topside | No | Flare (43) | Pipework | 250-PL-43310-01C02 |  | 250-PL-43310-01C02 |  | FPSO 2014 | Pipe Wall Thickness | 21799 |  | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 6.55 | 250-PL-43310-01C02 | Piping | 3 | 2116-05-10 |  | 2014-10-02 07:00 |  | 0.03738 | A3: Inside Quadrant |  |  | 2.5 |  | 6.3 | 6 O'Clock | 250 | 6.35 | Pipework | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.8 | 6.7 | 6.3 | 6.4 | 0.23805
WC01 | Montara_Topside | Yes | Nitrogen (67) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 22498 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 5.5 | CML-4 | CML: Elbow | 3 | 2021-01-19 | 2020-12-30 | 2015-04-20 07:00 | 2.5 | 0.50378 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.4 | 3 O'Clock | 25 | 6.35 | 25-GN-67301-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.6 | 5.4 | 5.5 | 5.5 | 0.08165
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-5 | 150-FL-43174-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 6279 |  | 2015-03-19 07:00 | 2015-03-19 15:00 | [36 empty] | 3.925 | CML-5 | CML: type TBC | 0.5 | 2013-06-01 | 2015-12-01 | 2015-03-19 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2 | 2.5 | 2.25 | 3.5 | 3 O'Clock | 25 | 2.5 | 25-WF-71357-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 3.7 | 3.5 | 4 | 4.5 | 0.43493
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43303-01C02 | CML-5 | 50-FL-43303-01C02 CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 20461 | Reviewed 24/11/14. FFS. Repeat on Oct.15. | 2014-10-05 07:00 | 2014-10-05 15:00 |  |  | Nestor | 2014-11-24 11:56 | [32 empty] | 4.825 | CML-5 | CML: Elbow | 3 | 2016-06-19 | 2016-10-17 | 2014-10-05 07:00 | 2.5 | 0.99554 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.2 | 6 O'Clock | 50 | 5.54 | 50-FL-43303-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.7 |  | 5.2 | 4.9 | 4.2 | 5 | 0.43493
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56009-01C02 | CML-19 | 100-DH-56009-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 3442 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 5.275 | CML-19 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 4.7 | 6 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.2 | 5.5 | 4.7 | 5.7 | 0.43493
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-4 | 100-PW-20021-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21807 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.6 | CML-4 | CML: Elbow | 3 | 2019-04-05 | 2019-06-15 | 2014-10-11 07:00 | 2.5 | 0.60186 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.6 | 5.2 | 6.3 | 0.49666
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-24 | 200-PL-20019-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21275 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.35 | CML-24 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.6 | 6.5 | 7.5 | 7.8 | 0.58023
FG02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-FG-45455-01C02-E | CML-13 | 25-FG-45455-01C02-E CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5750 | Rope access | 2014-06-22 14:00 | 2014-06-22 16:00 | [36 empty] | 6.625 | CML-13 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-06-22 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6 | 9 O'Clock | 80 | 5.49 | 80-PL-44008-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.8 | 7 | 6.7 | 6 | 0.43493
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-11 | 150-WC-40006-01C02 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8935 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.5 | CML-11 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 5.5 | 5.6 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-8 | 200-FH-43025-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2481 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 6.875 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.8 | 7.5 | 6.5 | 6.7 | 0.43493
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-16 | 100-FG-45304-03C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 22072 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 6.525 | CML-16 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2014-05-25 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.76 | 6.3 | 6 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 6.7 | 6.3 | 6.6 | 0.17078
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8870 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 08:00 | 2015-02-25 09:00 | [36 empty] | 5.5 | CML-2 | CML: type TBC | 3 | 2051-02-16 | 2055-03-05 | 2015-02-25 08:00 | 2.5 | 0.08056 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-AU-63019-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 5.5 | 5.6 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43007-01C02 | CML-5 | 80-FH-43007-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12566 |  | 2014-01-18 07:00 | 2014-01-18 10:00 | [36 empty] | 5.725 | CML-5 | CML: Pipe Length | 3 | 2029-11-29 | 2027-10-22 | 2014-01-18 07:00 | 0.54 | 0.29984 | A3: Inside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-FH-43007-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 5.8 | 6.3 | 5.3 | 5.5 | 0.43493
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-2 | 80-FH-43005-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12552 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 5.525 | CML-2 | CML: type TBC | 3 | 2016-08-26 | 2017-01-11 | 2014-01-20 10:00 | 2.5 | 0.9226 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 6 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.9 | 5.7 | 4.9 | 5.6 | 0.43493
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20915 | Rope Access | 2014-05-21 09:30 | 2014-05-21 11:00 | [36 empty] | 5.475 | CML-2 | CML: Elbow | 3 | 2020-11-08 | 2021-09-20 | 2014-05-21 09:30 | 2.5 | 0.40167 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.1 | 12 O'Clock | 80 | 5.49 | 80-DH-56033-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.3 | 6.1 | 5.4 | 0.43493
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43113-01C02 | CML-1 | 80-FH-43113-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20428 | Rope Access | 2014-05-25 14:00 | 2014-05-25 15:00 | [36 empty] | 5.975 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-25 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-FH-43113-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 6.6 | 5.6 | 5.9 | 0.43493
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40504-1CG | CML-2 | 150-WC-40504-1CG CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8633 | Rope Access / Material Class Not Selectable. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Feb.. 2020). RBI to be updated | 2015-02-10 10:30 | 2015-02-10 11:30 |  |  | Administrator | 2015-09-08 12:47 | [32 empty] | 11.6 | CML-2 | CML: Pipe Length | 3 | 2098-02-09 | 2070-10-05 | 2015-02-10 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 7.97 | 2.5 | 5.235 | 11.2 | 6 O'Clock | 150 | 10.97 | 150-WC-40504-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.8 | 11.2 | 11.2 | 12.2 | 0.4899
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23032-01C03 | CML-6 | 50-PL-23032-01C03 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20790 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 8.875 | CML-6 | CML: Elbow | 6 | 2032-09-07 | 2032-04-24 | 2014-10-10 07:00 | 2.5 | 0.3236 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.3 | 6 O'Clock | 50 | 8.74 | 50-PL-23032-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 9.3 | 8.8 | 8.3 | 9.1 | 0.43493
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20046-03C03-P | CML-5 | 80-PG-20046-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21464 | Protective mesh removed | 2014-06-28 08:00 | 2014-06-28 09:00 | [36 empty] | 11.125 | CML-5 | CML: Fitting | 6 | 2034-12-22 | 2031-09-09 | 2014-06-28 08:00 | 2.5 | 0.40004 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.7 | 6 O'Clock | 80 | 11.13 | 80-PG-20046-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11.2 | 10.9 | 10.7 | 11.7 | 0.43493
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20059-01C02 | CML-6 | 200-PL-20059-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2871 | Rope Access | 2014-03-25 11:00 | 2014-03-25 12:00 | [36 empty] | 6.9 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-25 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 200 | 6.35 | 200-PL-20059-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.1 | 7.2 | 6.5 | 6.8 | 0.31623
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-30 | 50-DH-56070-01C02 CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 3246 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.3 | CML-30 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.9 | 6.3 | 5.9 | 6.1 | 0.43205
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-12 | 50-CG-38476-01C02-H CML-12 | Yes | FPSO 2015 | Pipe Wall Thickness | 23644 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 8.3 | CML-12 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.9 | 3 O'Clock | 100 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.1 | 7.9 | 8.9 | 8.3 | 0.43205
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-13 | 300-WS-50805-1LC CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10813 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 16.8 | CML-13 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 16.2 | 3 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.7 |  | 16.4 | 16.2 | 16.9 | 17.7 | 0.66833
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-1 | 50-DC-57451-01C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1372 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 7.175 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 12 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7.6 | 7.8 | 7 | 0.67515
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-4 | 50-CG-38454-01C02-H CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 23668 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 9.1 | CML-4 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.5 | 3 O'Clock | 100 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.5 | 8.5 | 9.1 | 9.3 | 0.43205
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-10 | 300-WS-50805-1LC CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10810 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 16.725 | CML-10 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 16.2 | 3 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.7 |  | 16.8 | 16.2 | 17.3 | 16.6 | 0.45735
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-12 | 300-WS-50805-1LC CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10812 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.1 | CML-12 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 16.3 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.8 |  | 17.8 | 17.7 | 16.3 | 16.6 | 0.76158
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-2 | 50-PF-20300-03C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21568 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.2 | CML-2 | CML: type TBC | 6 | 2057-04-09 | 2056-06-05 | 2014-05-26 09:30 | 2.5 | 0.14218 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.6 | 12 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 8.6 | 9.2 | 9.4 | 9.6 | 0.43205
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43507-01C02 | CML-10 | 100-FH-43507-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8596 |  | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-08 14:58 | [32 empty] | 8.1 | CML-10 | CML: Equal Tee | 3 | 2063-07-07 | 2057-06-06 | 2015-02-08 11:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.5 | 6 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.16 |  | 8.3 | 8.5 | 7.5 | 8.1 | 0.43205
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-13 | 250-PW-20022-01C03-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2056 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.4 | CML-13 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.9 | 12 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 11.4 | 10 | 10.3 | 0.68799
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-6 | 300-PG-20506-03C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13220 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.2 | CML-6 | CML: type TBC | 6 | 2022-12-08 | 2021-03-22 | 2014-02-04 15:00 | 4.9 | 0.98361 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 12 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 13.6 | 14.6 | 14.4 | 14.2 | 0.43205
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38472-01C02 | CML-2 | 50-CG-38472-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23657 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5 | CML-2 | CML: Elbow | 3 | 2021-03-21 | 2022-01-21 | 2015-10-30 07:00 | 2.5 | 0.38931 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-CG-38472-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.6 | 4.6 | 5 | 4.8 | 0.43205
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-1 | 300-WS-50805-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10801 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.025 | CML-1 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 16.3 | 3 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.8 |  | 17 | 16.3 | 17.6 | 17.2 | 0.54391
WC01 | Montara_Topside | Yes | Steam (55) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23606 |  | 2015-09-28 07:00 | 2015-09-28 15:00 | [36 empty] | 5.45 | CML-5 | CML: Equal Tee | 3 | 2019-09-07 | 2019-03-12 | 2015-09-28 07:00 | 2.5 | 0.73491 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 5.4 | 6 O'Clock | 50 | 7.11 | 150-SL-55001-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 5.4 | 5.5 | 0.057735
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56122-01C02 | CML-3 | 50-DH-56122-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1823 |  | 2014-04-29 14:00 | 2014-04-29 14:30 | [36 empty] | 6.2 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-29 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 6 O'Clock | 50 | 5.54 | 50-DH-56122-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.8 | 6.2 | 5.8 | 6 | 0.43205
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-30 | 200-PL-20010-01C02-P CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 23830 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.775 | CML-30 | CML: Fitting | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 9 O'Clock | 200 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.8 | 6.8 | 7 | 6.5 | 0.20616
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56026-01C02 | CML-2 | 80-DH-56026-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3476 | Rope Access | 2014-05-13 13:00 | 2014-05-13 14:00 | [36 empty] | 9.4 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-13 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 8.8 | 12 O'Clock | 80 | 5.49 | 80-DH-56026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 8.8 | 9.8 | 9.4 | 9.6 | 0.43205
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20002-03C03-P | CML-3 | 300-PF-20002-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 6515 | Protective mesh removed | 2014-07-24 07:30 | 2014-07-24 15:00 |  |  | Administrator | 2015-09-08 15:10 | [32 empty] | 14.4 | CML-3 | CML: Fitting | 6 | 2036-03-31 | 2032-02-21 | 2014-07-24 07:30 | 4.9 | 0.4101 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 6 O'Clock | 300 | 14.27 | 300-PF-20002-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14.8 | 14.4 | 13.8 | 14.6 | 0.43205
CG04 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-CG-38452-09C02-P | CML-10 | 50-CG-38452-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20969 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 7.8 | CML-10 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.2 | 3 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8 | 7.2 | 7.8 | 8.2 | 0.43205
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PL-20006-01C02-P | CML-16 | 250-PL-20006-01C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 13186 |  | 2014-01-21 13:00 | 2014-01-21 18:00 | [36 empty] | 8.225 | CML-16 | CML: Tee | 3 | 2040-10-24 | 2046-01-30 | 2014-01-21 13:00 | 3.61 | 0 | A2: Right Quadrant |  | 3.35 | 3.61 | 3.0831 | 7.7 | 3 O'Clock | 250 | 6.35 | 250-PL-20006-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.09 |  | 8.5 | 7.7 | 8.6 | 8.1 | 0.4113
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57019-01C02 | CML-11 | 50-DC-57019-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2419 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 6.5 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 6 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.4 | 6.9 | 6.3 | 6.4 | 0.2708
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57019-01C02 | CML-10 | 50-DC-57019-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2418 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 6.575 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.3 | 3 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.3 | 6.5 | 6.8 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-13 | 100-DC-57038-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2376 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 7.3 | CML-13 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.3 | 9 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.7 | 7.4 | 7.8 | 6.3 | 0.68799
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-25 | 100-DC-57307-01C03 CML-25 | no | FPSO 2014 | Pipe Wall Thickness | 2333 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.849mm/ yr | [35 empty] | 6.575 | CML-25 | CML: type TBC | 6 | 2015-07-17 | 2015-07-13 | 2014-03-17 13:00 | 2.5 | 2.849 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 6.3 | 3 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.6 | 6.3 | 6.8 | 6.6 | 0.20616
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-27 | 100-DC-57307-01C03 CML-27 | no | FPSO 2014 | Pipe Wall Thickness | 2335 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.849mm/ yr | [35 empty] | 6.575 | CML-27 | CML: type TBC | 6 | 2015-07-17 | 2015-07-13 | 2014-03-17 13:00 | 2.5 | 2.849 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 6.3 | 3 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.5 | 6.3 | 7 | 6.5 | 0.29861
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 150-DC-57041-01C02 | CML-1 | 150-DC-57041-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2280 |  | 2014-03-16 14:30 | 2014-03-16 15:00 | Check Corrosion Rate of 1.024mm/ yr | [35 empty] | 6.65 | CML-1 | CML: type TBC | 3 | 2017-11-29 | 2017-07-24 | 2014-03-16 14:30 | 2.5 | 1.0244 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.3 | 12 O'Clock | 150 | 7.11 | 150-DC-57041-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.8 | 6.7 | 6.8 | 0.23805
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-3 | 200-FH-43004-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12543 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 6.625 | CML-3 | CML: type TBC | 3 | 2065-02-15 | 2064-09-30 | 2014-02-01 07:00 | 2.5 | 0.0744 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 9 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.2 | 6.3 | 6.7 | 6.3 | 0.4272
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-10 | 300-PG-20502-01C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 23897 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 11.325 | CML-10 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.7 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.7 | 11.4 | 11.6 | 11.6 | 0.4272
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-10 | 300-PG-20502-01C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20757 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 11.325 | CML-10 | CML: type TBC | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.7 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 10.7 | 11.4 | 11.6 | 11.6 | 0.4272
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-4 | 300-WS-50805-1LC CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10804 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.225 | CML-4 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 16.4 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.9 |  | 17.7 | 17.3 | 16.4 | 17.5 | 0.57373
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-4 | 300-PG-20506-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 13218 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.225 | CML-4 | CML: type TBC | 6 | 2022-12-08 | 2021-03-22 | 2014-02-04 15:00 | 4.9 | 0.98361 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.6 | 6 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 14.5 | 14.5 | 13.6 | 14.3 | 0.4272
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-19 | 100-PW-20021-01C02-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21822 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.7 | CML-19 | CML: Elbow | 3 | 2019-04-05 | 2019-06-15 | 2014-10-11 07:00 | 2.5 | 0.60186 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.8 | 6.2 | 5.6 | 0.41633
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-1 | 150-PG-23043-06C02-P CML-1 | yes | FPSO 2016 | Pipe Wall Thickness | 24434 | Re-check as requested by N.Sequera | 2016-07-02 07:00 | 2016-07-02 15:00 | Check Corrosion Rate of 0.735mm/ yr | [35 empty] | 9.275 | CML-1 | CML: Elbow | 3 | 2021-12-09 | 2020-08-25 | 2016-07-02 07:00 | 4.7 | 0.73499 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.7 | 3 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 | -2.8679 | 9.6 | 8.7 | 9.6 | 9.2 | 0.4272
WC01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-WC-40006-01C02 | CML-1 | 150-WC-40006-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 22944 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.45 | CML-1 | CML: Reducing Tee | 3 | 2077-02-10 | 2084-07-12 | 2015-05-02 07:00 | 2.5 | 0.04691 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | -0.17548 | 5.4 | 5.4 | 5.5 | 5.5 | 0.057735
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-16 | 200-PL-20035-03C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21348 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 8.05 | CML-16 | CML: Fitting | 3 | 2023-08-15 | 2021-11-13 | 2014-06-27 13:00 | 3.61 | 0.44746 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.7 | 12 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.09 |  | 7.7 | 8.1 | 8.3 | 8.1 | 0.25166
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45024-01C02 | CML-15 | 50-FG-45024-01C02 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 23584 | Re-check of line as requested by ops supervisor | 2015-09-10 07:00 | 2015-09-10 09:00 | [36 empty] | 9.525 | CML-15 | CML: Elbow | 3 | 2075-10-24 | 2059-08-12 | 2015-09-10 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 9.2 | 6 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 | -0.53207 | 9.6 | 9.2 | 9.2 | 10.1 | 0.4272
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-11 | 300-WS-50805-1LC CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10811 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.05 | CML-11 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 16.6 | 9 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.1 |  | 16.9 | 17.3 | 17.4 | 16.6 | 0.36968
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-1 | 200-FH-43012-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2831 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 8.725 | CML-1 | CML: Reducer | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 8.4 | 6 O'Clock | 80 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.06 |  | 9.3 | 8.4 | 8.4 | 8.8 | 0.4272
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43109-01C02 | CML-1 | 200-FH-43109-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12785 |  | 2014-01-18 14:30 | 2014-01-18 15:30 | [36 empty] | 6.575 | CML-1 | CML: Pipe Length | 3 | 2076-12-13 | 2069-03-28 | 2014-01-18 14:30 | 1.34 | 0.0788 | A1: Outside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.3 | 3 O'Clock | 200 | 6.35 | 200-FH-43109-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.96 |  | 6.3 | 6.3 | 7.2 | 6.5 | 0.4272
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23048-09C02 | CML-8 | 50-PG-23048-09C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20590 |  | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.125 | CML-8 | CML: Reducer | 3 | 2042-10-10 | 2035-02-25 | 2014-07-18 11:00 | 2.5 | 0.21239 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.5 | 3 O'Clock | 50 | 8.74 | 50-PG-23048-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.4 | 8.5 | 9.2 | 9.4 | 0.4272
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-8 | 200-PL-20034-03C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21605 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.025 | CML-8 | CML: Reducer | 3 | 2023-08-25 | 2021-11-21 | 2014-06-28 13:00 | 3.61 | 0.44632 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 7.7 | 3 O'Clock | 150 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.09 |  | 8.1 | 7.7 | 8.2 | 8.1 | 0.22174
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-34 | 150-WC-40006-01C02 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 8958 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.45 | CML-34 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 5.4 | 5.5 | 0.057735
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-24002-09C02 | CML-2 | 50-CG-24002-09C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2548 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 11.125 | CML-2 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.74 | 2.5 | 4.12 | 10.6 | 6 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.1 |  | 11 | 11.6 | 10.6 | 11.3 | 0.4272
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-14 | 200-PW-44018-01X01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 23249 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.375 | CML-14 | CML: Fitting | 3 | 2030-10-11 | 2032-08-22 | 2015-05-11 07:00 | 2.5 | 0.17496 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0 | 5.3 | 5.6 | 5.4 | 5.2 | 0.17078
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-13 | 200-PW-44018-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 6596 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 5.425 | CML-13 | CML: Pipe Length | 3 | 2029-10-01 | 2031-07-03 | 2015-03-30 07:00 | 2.5 | 0.18598 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.4 | 5.5 | 5.2 | 0.17078
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38494-01C02 | CML-2 | 25-CG-38494-01C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10385 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.175 | CML-2 | CML: type TBC | 3 | 2017-04-04 | 2017-03-24 | 2013-11-12 | 2.5 | 1.0015 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 9 O'Clock | 25 | 6.35 | 25-CG-38494-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 | 5.9 | 5.9 | 6.1 | 6.8 | 5.9 | 0.4272
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56004-01C02 | CML-4 | 80-DH-56004-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 3407 | Rope Access | 2014-05-11 07:00 | 2014-05-11 09:00 | [36 empty] | 7.925 | CML-4 | CML: type TBC | 3 |  |  | 2014-05-11 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 7.3 | 3 O'Clock | 100 |  | 100-DH-56004-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 8.2 | 7.3 | 8 | 8.2 | 0.4272
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-19 | 250-PW-20022-01C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2062 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.375 | CML-19 | CML: Fitting | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 9.9 | 12 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 |  | 9.9 | 10.2 | 10.6 | 10.8 | 0.40311
PW03 | Montara_Topside | Yes | Fire Water (71) | Pipework | 200-PW-44018-01X01 | CML-10 | 200-PW-44018-01X01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6219 |  | 2015-03-18 07:00 | 2015-03-18 15:00 | [36 empty] | 5.425 | CML-10 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-18 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 5.2 | 6 O'Clock | 100 | 3 | 100-WF-71359-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.5 | 5.2 | 5.4 | 0.17078
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56064-01C02 | CML-3 | 50-DH-56064-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3273 | Rope Access | 2014-05-09 13:00 | 2014-05-09 14:00 | [36 empty] | 5.475 | CML-3 | CML: type TBC | 3 | 2021-10-19 | 2022-09-13 | 2014-05-09 13:00 | 2.5 | 0.36229 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-DH-56064-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 6.1 | 5.2 | 5.4 | 5.2 | 0.4272
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-44 | 50-DH-56070-01C02 CML-44 |  | FPSO 2014 | Pipe Wall Thickness | 3260 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.975 | CML-44 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.6 | 5.7 | 5.7 | 5.9 | 0.4272
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-2 | 300-WS-50805-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10802 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.125 | CML-2 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 16.6 | 3 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.1 |  | 17.5 | 16.6 | 17.4 | 17 | 0.4113
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-15 | 300-WS-50805-1LC CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 10815 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.725 | CML-15 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 16.7 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.2 |  | 18.1 | 18.2 | 16.7 | 17.9 | 0.69462
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-2 | 150-FG-45002-03C02 CML-2 |  | FPSO 2013 | Pipe Wall Thickness | 10405 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.625 | CML-2 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.3 | 6 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.8 | 6.6 | 6.3 | 6.8 | 0.23629
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-21 | 100-DH-56086-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 20980 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 6.225 | CML-21 | CML: type TBC | 3 | 2041-06-27 | 2042-05-31 | 2014-05-16 13:00 | 2.5 | 0.12531 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.3 | 6.8 | 5.9 | 5.9 | 0.4272
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-31 | 50-FG-45023-01C02 CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 1179 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 7.025 | CML-31 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.3 | 7.3 | 7.1 | 0.4272
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-9 | 80-PW-44016-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21941 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.55 | CML-9 | CML: Elbow | 3 | 2027-06-04 | 2029-01-20 | 2014-10-10 07:00 | 2.5 | 0.21328 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.5 | 5.6 | 5.9 | 0.28868
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-1 | 300-PG-23400-01C03-P CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24457 | Re-check as requested by N.Sequera | 2016-07-05 07:00 | 2016-07-05 15:00 | Check Corrosion Rate of 0.391mm/ yr |  | John Wilson | 2017-03-24 09:38 | Anomily to re visit 7/5/2018 | [31 empty] | 9.75 | CML-1 | CML: Pipe Length | 6 | 2026-06-07 | 2027-08-06 | 2016-07-05 07:00 | 5.22 | 0.39074 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 9.1 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.88 | 0 | 9.1 | 10 | 9.6 | 10.3 | 0.51962
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-1 | 300-PG-23400-01C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23415 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 9.875 | CML-1 | CML: Pipe Length | 6 | 2022-05-31 | 2023-03-21 | 2015-07-22 07:00 | 5.22 | 0.56528 | A3: Inside Quadrant |  | 4.31 | 5.22 | 4.765 | 9.1 | 6 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.88 | -0.34845 | 9.7 | 10.5 | 9.1 | 10.2 | 0.61305
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-1 | 200-PG-23008-15S01-A CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21012 | Rope Access | 2014-05-19 14:00 | 2014-07-20 15:00 | [36 empty] | 5.4 | CML-1 | CML: type TBC | 3 | 2020-02-01 | 2020-10-19 | 2014-05-19 14:00 | 2.5 | 0.4555 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DH-56112-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 6 | 5.1 | 5.4 | 0.42426
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-36 | 200-PL-20019-01C02 CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 21287 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.05 | CML-36 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.6 | 7.3 | 7.5 | 0.42032
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-4 | 200-FH-43131-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 607 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.4 | CML-4 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-03-15 09:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 6 O'Clock | 200 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 | 12614397.0512 | 7.9 | 7.6 | 7 | 7.1 | 0.42426
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-3 | 200-FH-43003-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12526 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 6.6 | CML-3 | CML: Pipe Length | 3 | 2026-02-11 | 2024-07-28 | 2014-01-18 11:30 | 1.34 | 0.3942 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 6.1 | 6 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.76 |  | 6.9 | 7 | 6.1 | 6.4 | 0.42426
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-8 | 300-WS-50805-1LC CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10808 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.9 | CML-8 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 17.3 | 12 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 |  | 17.3 | 18.2 | 18.2 | 17.9 | 0.42426
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-7 | 300-WS-50805-1LC CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10807 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 18.175 | CML-7 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 17.3 | 3 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.8 |  | 18.2 | 17.3 | 18.5 | 18.7 | 0.61847
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9005-AS20-00 | CML-1 | 0100-AS-63L9005-AS20-00 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24285 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.475 | CML-1 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.4 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9005-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.6 | 6.5 | 6.4 | 0.095743
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9005-AS20-00 | CML-6 | 0100-AS-63L9005-AS20-00 CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24290 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.475 | CML-6 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.4 | 6 O'Clock | 25 | 3.38 | 0100-AS-63L9005-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.4 | 6.4 | 6.5 | 0.095743
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9005-AS20-00 | CML-5 | 0100-AS-63L9005-AS20-00 CML-5 |  | FPSO 2016 | Pipe Wall Thickness | 24289 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.5 | CML-5 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.4 | 6 O'Clock | 25 | 3.38 | 0100-AS-63L9005-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.6 | 6.4 | 6.5 | 0.08165
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9005-AS20-00 | CML-4 | 0100-AS-63L9005-AS20-00 CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24288 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.525 | CML-4 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.4 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9005-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.5 | 6.7 | 6.4 | 0.12583
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-19 | 150-WC-40006-01C02 CML-19 |  | FPSO 2015 | Pipe Wall Thickness | 8915 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 5.45 | CML-19 | CML: type TBC | 3 | 2051-02-20 | 2055-03-10 | 2015-02-25 13:00 | 2.5 | 0.08053 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 5.5 | 5.4 | 0.057735
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-26 | 50-PF-20301-03C03-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 3024 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.2 | CML-26 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.6 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.99 | 0 | 8.6 | 9.3 | 9.6 | 9.3 | 0.42426
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-26 | 50-PF-20301-03C03-P CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 22303 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.2 | CML-26 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A1: Outside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.6 | 12 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.99 |  | 8.6 | 9.3 | 9.6 | 9.3 | 0.42426
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-15 | 200-PL-20018-01C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 23887 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 7.025 | CML-15 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 3 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 | 0 | 7.1 | 6.6 | 7.2 | 7.2 | 0.28723
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50805-1LC | CML-5 | 300-WS-50805-1LC CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10805 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 19.4 | CML-5 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 18.8 | 6 O'Clock | 300 | 10.31 | 300-WS-50805-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 16.3 |  | 19.9 | 19.8 | 18.8 | 19.1 | 0.53541
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42312-01S01 | CML-5 | 40-CI-42312-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7514 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.8 | CML-5 | CML: type TBC | 1 | 2025-02-09 | 2021-08-25 | 2015-04-13 07:00 | 2.5 | 0.39645 | A4: Left Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.4 | 9 O'Clock | 40 | 7.14 | 40-CI-42312-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.8 | 9 | 8 | 6.4 | 1.0708
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42309-01S01 | CML-7 | 40-CI-42309-01S01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7503 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.5 | CML-7 | CML: type TBC | 1 | 2025-02-09 | 2021-08-25 | 2015-04-13 07:00 | 2.5 | 0.39645 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.4 | 12 O'Clock | 40 | 7.14 | 40-CI-42309-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.9 | 7.9 | 7.8 | 0.73485
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-27 | 50-AI-63004-01E01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 9018 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.625 | CML-27 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.4 | 6.7 | 6.7 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-4 | 200-FH-43012-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2834 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.4 | CML-4 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 7 | 6 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.66 |  | 7.9 | 7.6 | 7 | 7.1 | 0.42426
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67010-01E01 | CML-9 | 50-GN-67010-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8712 |  | 2015-02-14 07:00 | 2015-02-14 09:00 | [36 empty] | 6.425 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-14 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.4 | 6.4 | 6.4 | 0.05
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67004-01E01 | CML-18 | 50-GN-67004-01E01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8623 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 6.775 | CML-18 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-09 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.2 | 7.1 | 6.4 | 6.4 | 0.43493
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63038-01E01 | CML-3 | 50-AI-63038-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8569 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.525 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 12 O'Clock | 50 | 5.54 | 50-AI-63038-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.6 | 6.6 | 6.5 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63020-01E01 | CML-9 | 50-AU-63020-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8489 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.475 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-AU-63020-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.5 | 6.4 | 6.5 | 0.05
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67007-01E01 | CML-9 | 50-GN-67007-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8480 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.45 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-GN-67007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.5 | 6.4 | 6.4 | 0.057735
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63012-01E01 | CML-4 | 50-AI-63012-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8454 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.45 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63012-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.4 | 6.5 | 6.4 | 0.057735
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 50-CI-42315-01S01 | CML-7 | 50-CI-42315-01S01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8418 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 8.1 | CML-7 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.54 | 2.5 | 3.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-CI-42315-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 9.7 | 6.4 | 9.2 | 7.1 | 1.5979
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63016-01E01 | CML-6 | 50-AU-63016-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8410 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.6 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-AU-63016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 7.1 | 6.5 | 0.33665
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63016-01E01 | CML-4 | 50-AU-63016-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8408 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.525 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-AU-63016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.6 | 6.6 | 6.4 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63016-01E01 | CML-2 | 50-AU-63016-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8406 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.6 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-AU-63016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 6.7 | 6.9 | 0.24495
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63030-01E01 | CML-2 | 50-AI-63030-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8343 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.5 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-AI-63030-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 6.4 | 6.5 | 6.5 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63011-01E01 | CML-3 | 50-AI-63011-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8340 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.475 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-AI-63011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.4 | 6.4 | 6.6 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-15 | 50-AI-63450-01E01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8334 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.475 | CML-15 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.4 | 6.5 | 6.5 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-4 | 50-AI-63450-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8323 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.525 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 12 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.5 | 6.7 | 6.5 | 0.12583
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-3 | 50-AI-63450-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8322 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.575 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.8 | 6.4 | 6.7 | 6.4 | 0.20616
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63001-01E01 | CML-8 | 50-AI-63001-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8315 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-27 09:45 | 2015-01-27 15:00 | [36 empty] | 6.875 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-27 09:45 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-AI-63001-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7 | 6.4 | 7.1 | 7 | 0.32016
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53003-01E01 | CML-7 | 50-WD-53003-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8297 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.525 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-WD-53003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.7 | 6.4 | 6.5 | 0.12583
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-22 | 50-WD-53010-01E01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 8265 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.525 | CML-22 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.4 | 6.5 | 6.7 | 0.12583
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-15 | 50-WD-53010-01E01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8258 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.925 | CML-15 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.7 | 6.8 | 6.4 | 6.8 | 0.55
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53013-01E01 | CML-1 | 50-WD-53013-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8237 | Reducing Hose Coupling | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.625 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 12 O'Clock | 50 | 5.54 | 50-WD-53013-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.7 | 6.7 | 6.7 | 0.15
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-14 | 100-OL-69001-01S01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8116 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.625 | CML-14 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.4 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.6 | 7 | 6.5 | 0.263
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-11 | 100-OL-69001-01S01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8113 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.8 | CML-11 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.4 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.8 | 7.1 | 6.9 | 0.29439
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-10 | 100-OL-69001-01S01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8112 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.6 | CML-10 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.4 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.5 | 6.9 | 6.6 | 0.21602
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-4 | 100-OL-69001-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8106 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.625 | CML-4 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.4 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.5 | 7 | 6.6 | 0.263
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 80-OL-69004-01S01 | CML-3 | 80-OL-69004-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8094 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.675 | CML-3 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.49 | 2.5 | 3.1519 | 6.4 | 12 O'Clock | 80 | 5.49 | 80-OL-69004-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.6 | 7.2 | 6.5 | 0.3594
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-5 | 150-WC-40006-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8866 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 07:00 | 2015-02-25 08:00 | [36 empty] | 5.45 | CML-5 | CML: type TBC | 3 | 2051-02-15 | 2055-03-04 | 2015-02-25 07:00 | 2.5 | 0.08056 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AU-63023-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.5 | 5.5 | 5.4 | 0.057735
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-32 | 300-WS-50806-1LC CML-32 |  | FPSO 2014 | Pipe Wall Thickness | 10771 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.275 | CML-32 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 11 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 12.7 | 11 | 12.2 | 13.2 | 0.94296
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-24 | 300-WS-50806-1LC CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 10763 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.325 | CML-24 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 11.9 | 9 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 12.7 | 12.6 | 12.1 | 11.9 | 0.38622
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-5 | 300-WS-50806-1LC CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10744 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.425 | CML-5 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 11.9 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 12.5 | 11.9 | 12.3 | 13 | 0.45735
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-35 | 300-WS-50806-1LC CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 10774 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.3 | CML-35 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 12 | 9 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.2 | 12.3 | 12.7 | 12 | 0.29439
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-33 | 300-WS-50806-1LC CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 10772 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.475 | CML-33 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 12 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.4 | 12 | 12.8 | 12.7 | 0.3594
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-30 | 300-WS-50806-1LC CML-30 |  | FPSO 2014 | Pipe Wall Thickness | 10769 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.2 | CML-30 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 12 | 12 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12 | 12.1 | 12.2 | 12.5 | 0.21602
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20018-01C02-P | CML-15 | 200-PL-20018-01C02-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21251 | Protective mesh removed | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 7.025 | CML-15 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 3 O'Clock | 200 | 6.35 | 200-PL-20018-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.1 | 6.6 | 7.2 | 7.2 | 0.28723
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20059-01C02 | CML-5 | 200-PL-20059-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2870 | Rope Access | 2014-03-25 11:00 | 2014-03-25 12:00 | [36 empty] | 7.025 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-25 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 12 O'Clock | 200 | 6.35 | 200-PL-20059-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.2 | 7.1 | 7.2 | 0.28723
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-15 | 300-PG-23002-03C03-A CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10111 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 13.3 | CML-15 | CML: Elbow | 6 | 2015-12-04 | 2015-07-03 | 2013-11-07 | 5.22 | 3.6041 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 12.7 | 6 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.48 |  | 13.6 | 13.6 | 12.7 | 13.3 | 0.42426
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57048-03C02 | CML-2 | 50-DC-57048-03C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7614 |  | 2015-01-07 07:00 | 2015-01-07 08:00 | [36 empty] | 6.575 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2043-08-12 | 2015-01-07 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57048-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.9 | 6.5 | 6.5 | 6.4 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-1 | 80-DC-57002-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20230 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 6.525 | CML-1 | CML: Pipe Length | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.4 | 9 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.5 | 6.5 | 6.4 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-12 | 80-DC-57002-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 20241 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7 | CML-12 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.4 | 6 O'Clock | 20 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.8 | 7 | 6.4 | 6.8 | 0.58878
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20022-01C03-P | CML-20 | 250-PW-20022-01C03-P CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 2063 | Rope Access | 2014-03-28 07:00 | 2014-03-28 09:00 | [36 empty] | 10.375 | CML-20 | CML: Fitting | 6 | 2081-02-10 | 2077-04-05 | 2014-03-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 10 | 3 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 10 | 10.6 | 10.9 | 0.45
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-1 | 300-PG-20004-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6124 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.1 | CML-1 | CML: Fitting | 6 | 2026-12-02 | 2024-06-28 | 2014-07-11 07:30 | 4.9 | 0.69342 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 12 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 13.5 | 14.1 | 14.4 | 14.4 | 0.42426
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23041-06C03 | CML-3 | 50-PL-23041-06C03 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10216 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 9.6 | CML-3 | CML: type TBC | 6 |  |  | 2013-11-08 |  | 4.7222 | A4: Left Quadrant |  | 5.07 |  |  | 9 | 9 O'Clock | 50 | 11.07 | 50-PL-23041-06C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  |  | 9.9 | 9.9 | 9.6 | 9 | 0.42426
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-28 | 200-PL-20019-01C02 CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 21279 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.925 | CML-28 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.9 | 7.2 | 7 | 0.25
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20059-01C02 | CML-1 | 200-PL-20059-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2866 | Rope Access | 2014-03-25 11:00 | 2014-03-25 12:00 | [36 empty] | 6.925 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-25 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 12 O'Clock | 200 | 6.35 | 200-PL-20059-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.9 | 7.1 | 7.1 | 0.23629
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45501-01C02 | CML-10 | 50-FG-45501-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 6593 | Rope Access. Line is FFS although the CRs reported are higher than expected. Maintain RBI frequency at 36m. Next inspection in Mar. 2018 | 2015-03-30 07:00 | 2015-03-30 15:00 |  |  | Administrator | 2015-09-07 14:35 | [32 empty] | 5.2 | CML-10 | CML: Elbow | 3 | 2019-04-29 | 2019-12-16 | 2015-03-30 07:00 | 2.5 | 0.51417 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.6 | 5.3 | 5.3 | 5.6 | 0.42426
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-39 | 200-PL-20019-01C02 CML-39 |  | FPSO 2014 | Pipe Wall Thickness | 21290 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.925 | CML-39 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 12 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7 | 7 | 7.1 | 0.22174
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-4 | 50-DC-57450-01C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20320 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 6.95 | CML-4 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 25 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.6 | 7.3 | 7.5 | 6.4 | 0.53229
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-15 | 50-CG-38465-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 20878 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 7 | CML-15 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-04 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 3 O'Clock | 50 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.1 | 6.4 | 8 | 6.5 | 0.73485
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-42 | 150-WC-40006-01C02 CML-42 |  | FPSO 2015 | Pipe Wall Thickness | 8966 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.425 | CML-42 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.5 | 5.4 | 0.05
FH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-PW-44026-01C02 | CML-3 | 25-PW-44026-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5756 | Rope access | 2014-06-23 07:00 | 2014-06-23 08:00 | [36 empty] | 6.8 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 12 O'Clock | 50 | 5.54 | 50-PW-44026-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.7 | 7.4 | 6.7 | 0.42426
PW03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-PW-44018-01X01 | CML-22 | 200-PW-44018-01X01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 7735 |  | 2015-01-09 13:00 | 2015-01-09 15:00 |  |  | Administrator | 2015-09-08 09:37 | [32 empty] | 5.4 | CML-22 | CML: Pipe Length | 3 | 2027-10-19 | 2029-05-05 | 2015-01-09 13:00 | 2.5 | 0.21122 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.50494 | 5.4 | 5.6 | 5.4 | 5.2 | 0.1633
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23515-01C03 | CML-8 | 50-PL-23515-01C03 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8657 |  | 2015-02-12 07:00 | 2015-02-12 11:00 |  |  | Administrator | 2015-06-05 15:51 | [32 empty] | 9.1 | CML-8 | CML: Elbow | 6 | 2278-10-11 | 2273-09-03 | 2015-02-12 07:00 | 2.5 | 0.0235 | A4: Left Quadrant |  | 2.74 | 2.5 | 2.62 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-PL-23515-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9 | 9.7 | 9 | 8.7 | 0.42426
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-3 | 300-PW-44003-01C03 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 22868 | Rope Access | 2015-05-01 07:00 | 2015-05-01 15:00 | [36 empty] | 10.375 | CML-3 | CML: Elbow | 6 | 2061-08-25 | 2056-01-23 | 2015-05-01 07:00 | 2.5 | 0.16181 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 10 | 9 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 | -1.5052 | 10.7 | 10.5 | 10.3 | 10 | 0.29861
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-23 | 200-PL-20019-01C02 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21274 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 6.725 | CML-23 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 40 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.7 | 6.8 | 6.6 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56058-01C02 | CML-1 | 50-DH-56058-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3173 | Rope Access | 2014-05-07 09:30 | 2014-05-07 10:30 | [36 empty] | 5.2 | CML-1 | CML: type TBC | 3 | 2016-10-14 | 2017-02-24 | 2014-05-07 09:30 | 2.5 | 0.90072 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56058-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.5 | 5 | 5.6 | 4.7 | 0.42426
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56056-01C02 | CML-1 | 50-DH-56056-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20125 | Rope Access | 2014-05-07 09:30 | 2014-05-07 10:30 | [36 empty] | 5.2 | CML-1 | CML: type TBC | 3 | 2016-10-14 | 2017-02-24 | 2014-05-07 09:30 | 2.5 | 0.90072 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 15768.5753 | 5.5 | 5 | 5.6 | 4.7 | 0.42426
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-29 | 300-WS-50806-1LC CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 10768 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.575 | CML-29 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 12 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 13.1 | 12 | 12.6 | 12.6 | 0.45
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-14 | 50-PW-44040-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1989 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.45 | CML-14 | CML: Fitting | 3 | 2020-09-28 | 2021-07-12 | 2014-03-27 07:00 | 2.5 | 0.41465 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.7 | 5.7 | 5.2 | 0.28868
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-38 | 150-WC-40006-01C02 CML-38 |  | FPSO 2015 | Pipe Wall Thickness | 8962 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.425 | CML-38 | CML: type TBC | 3 | 2051-03-10 | 2055-03-30 | 2015-02-26 09:00 | 2.5 | 0.08042 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.5 | 5.4 | 0.05
PG02 | Montara_Topside | No | Separation (20) | Pipework | 250-PG-20042-01D01-P | CML-9 | 250-PG-20042-01D01-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21442 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 6.475 | CML-9 | CML: Reducer | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.35 | 2.5 | 3.925 | 6.4 | 12 O'Clock | 500 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.5 | 6.5 | 6.5 | 0.05
PG02 | Montara_Topside | No | Separation (20) | Pipework | 250-PG-20042-01D01-P | CML-1 | 250-PG-20042-01D01-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21434 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 6.45 | CML-1 | CML: Reducer | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.35 | 2.5 | 3.925 | 6.4 | 6 O'Clock | 500 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.5 | 6.4 | 6.5 | 0.057735
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44013-01X01 | CML-11 | 50-PW-44013-01X01 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10325 | Deck Level | 2013-11-10 | 2013-11-10 | [36 empty] | 5.4 | CML-11 | CML: Elbow | 3 | 2017-05-19 | 2017-10-21 | 2013-11-10 | 2.5 | 0.76605 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.6 | 5.2 | 5.4 | 0.1633
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 | Yes | FPSO 2015 | Pipe Wall Thickness | 7854 | Line is FFS. Current RBI frequency is 48m. Action: CML’s to Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-14 07:00 | 2015-01-14 08:00 |  |  | Administrator | 2015-09-08 13:39 | [32 empty] | 6.6 | CML-6 | CML: Elbow | 3 | 2055-01-14 | 2054-09-25 | 2015-01-14 07:00 | 2.5 | 0.09244 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 200 | 6.35 | 200-FH-43135-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.8 | 7.1 | 6.3 | 0.42426
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-3 | 300-PG-20037-03C03-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21378 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | Check Corrosion Rate of 0.436mm/ yr | [35 empty] | 14.2 | CML-3 | CML: Pipe Length | 6 | 2033-11-28 | 2030-07-16 | 2014-06-29 13:00 | 5.33 | 0.43591 | A4: Left Quadrant |  | 8.27 | 5.33 | 6.8 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.47 |  | 14.7 | 13.9 | 14.4 | 13.8 | 0.42426
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-21 | 300-WS-50806-1LC CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 10760 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.55 | CML-21 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 12 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.9 | 12 | 12.5 | 12.8 | 0.40415
DH01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-DH-56141-01C02 | CML-6 | 50-DH-56141-01C02 CML-6 |  | FPSO 2016 | Pipe Wall Thickness | 24306 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 17.9 | CML-6 | CML: Reducing Tee | 3 | 2054-10-24 | 2049-02-10 | 2016-05-27 07:00 | 1.88 | 0 | A1: Outside Quadrant |  | 3.02 | 1.88 | 2.45 | 17.5 | 12 O'Clock | 40 | 6.02 | 100-FG-45008-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.62 |  | 17.5 | 18.1 | 17.6 | 18.4 | 0.42426
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-28 | 300-WS-50806-1LC CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 10767 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 13.05 | CML-28 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 12.1 | 9 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 15 | 12.7 | 12.4 | 12.1 | 1.3229
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FL-43455-01C02-P | CML-5 | 100-FL-43455-01C02-P CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 20488 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.75 | CML-5 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-10-03 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.3 | 12 O'Clock | 100 | 6.02 | 100-FL-43455-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 8.3 | 7.6 | 7.8 | 0.42032
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38477-01C02-P | CML-13 | 50-CG-38477-01C02-P CML-13 | no | FPSO 2015 | Pipe Wall Thickness | 23414 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | [36 empty] | 17.95 | CML-13 | CML: Pipe Length | 3 | 2023-11-11 | 2022-05-15 | 2015-07-22 07:00 | 14.06 | 0.40177 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 17.4 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.34 | 0 | 17.9 | 17.4 | 18.4 | 18.1 | 0.42032
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23402-01C02-PA | CML-3 | 150-PG-23402-01C02-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5611 |  | 2014-06-20 09:30 | 2014-06-20 11:00 | [36 empty] | 7.075 | CML-3 | CML: Elbow | 3 |  |  | 2014-06-20 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.4 | 3 O'Clock | 150 |  | 150-PG-23402-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.5 | 6.4 | 6.8 | 7.6 | 0.57373
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-17 | 300-WS-50806-1LC CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 10756 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.45 | CML-17 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 12.1 | 12 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 12.1 | 12.5 | 12.6 | 12.6 | 0.23805
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43300-01C02 | CML-2 | 50-FL-43300-01C02 CML-2 | yes | FPSO 2014 | Pipe Wall Thickness | 20449 | Reviewed on 24/11/14. FFS. Repeat on Oct.17. | 2014-10-05 07:00 | 2014-10-05 15:00 |  |  | Nestor | 2014-11-24 11:11 | [32 empty] | 5.05 | CML-2 | CML: Elbow | 3 | 2017-10-06 | 2018-03-26 | 2014-10-05 07:00 | 2.5 | 0.69836 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 9 O'Clock | 50 | 5.54 | 50-FL-43300-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.5 | 4.8 | 5.3 | 4.6 | 0.42032
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56110-01C02 | CML-1 | 50-DH-56110-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21008 | Rope Access | 2014-05-24 13:00 | 2014-05-24 14:00 | [36 empty] | 5.35 | CML-1 | CML: Elbow | 3 | 2017-06-08 | 2017-11-13 | 2014-05-24 13:00 | 2.5 | 0.75544 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DH-56110-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 4.8 | 5.3 | 5.5 | 5.8 | 0.42032
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-4 | 300-WS-50806-1LC CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10743 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.5 | CML-4 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 12.1 | 6 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 12.4 | 12.5 | 12.1 | 13 | 0.37417
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-34 | 300-WS-50806-1LC CML-34 |  | FPSO 2014 | Pipe Wall Thickness | 10773 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.3 | CML-34 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 12.2 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.7 |  | 12.2 | 12.2 | 12.4 | 12.4 | 0.11547
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56051-01C02 | CML-2 | 80-DH-56051-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20939 | Rope Access | 2014-05-16 08:00 | 2014-05-16 09:00 | [36 empty] | 5.25 | CML-2 | CML: type TBC | 3 | 2017-07-23 | 2018-01-16 | 2014-05-16 08:00 | 2.5 | 0.72094 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.8 | 3 O'Clock | 80 | 5.49 | 80-DH-56051-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.5 | 4.8 | 5.7 | 5 | 0.42032
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-4 | 150-PG-23043-06C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23460 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 9.25 | CML-4 | CML: Elbow | 3 | 2019-08-12 | 2018-09-03 | 2015-07-24 07:00 | 4.7 | 1.0112 | A3: Inside Quadrant |  | 7.97 | 4.7 | 5.6494 | 8.8 | 6 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 | -0.12046 | 9.3 | 9.8 | 8.8 | 9.1 | 0.42032
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-25 | 200-PL-20035-03C02-P CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 21357 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 8.675 | CML-25 | CML: Fitting | 3 | 2026-04-22 | 2024-02-03 | 2014-06-27 13:00 | 3.61 | 0.35424 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 7.8 | 9 O'Clock | 250 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 |  | 9.4 | 9 | 8.5 | 7.8 | 0.68981
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-20 | 100-DH-56086-01C02 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 20979 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 7.05 | CML-20 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.3 | 7.5 | 6.8 | 6.6 | 0.42032
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-5 | 100-VA-80006-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2174 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 5.55 | CML-5 | CML: type TBC | 3 | 2016-04-10 | 2016-05-14 | 2014-03-30 13:00 | 2.5 | 1.2306 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 3 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.5 | 5 | 6 | 5.7 | 0.42032
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-15 | 200-PG-23008-15S01-A CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21004 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 5.65 | CML-15 | CML: Reducing Tee | 3 | 2020-03-05 | 2020-11-25 | 2014-05-24 10:30 | 2.5 | 0.44931 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.1 | 5.6 | 6.1 | 5.8 | 0.42032
FG02 | Montara_Topside | Yes | Lube Oil (69) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8105 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.45 | CML-3 | CML: type TBC | 1 | 2303-03-05 | 2230-06-04 | 2015-01-23 07:30 | 2.5 | 0.01214 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6 | 12 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.3 | 7 | 6.5 | 0.42032
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45004-03C02 | CML-2 | 150-FG-45004-03C02 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24334 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.25 | CML-2 | CML: Elbow | 3 | 2058-04-03 | 2050-06-04 | 2016-06-06 07:00 | 2.5 | 0.10274 | A1: Outside Quadrant |  | 4.11 | 2.5 | 3.305 | 6.8 | 12 O'Clock | 150 | 7.11 | 150-FG-45004-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.8 | 7.3 | 7.1 | 0.42032
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56109-01C02 | CML-11 | 50-DH-56109-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 21000 | Rope Access | 2014-05-24 10:30 | 2014-05-24 12:00 | [36 empty] | 7.95 | CML-11 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-05-24 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.5 | 12 O'Clock | 50 | 5.54 | 50-DH-56109-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8.5 | 7.8 | 8 | 0.42032
FG04 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 150-FG-45003-03C02 | CML-7 | 150-FG-45003-03C02 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 22931 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | Check Corrosion Rate of 0.49mm/ yr | [35 empty] | 5.05 | CML-7 | CML: Elbow | 3 | 2019-08-13 | 2020-04-12 | 2015-05-02 07:00 | 2.5 | 0.48994 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0 | 4.6 | 5.6 | 4.9 | 5.1 | 0.42032
PW03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 200-PW-44018-01X01 | CML-29 | 200-PW-44018-01X01 CML-29 |  | FPSO 2015 | Pipe Wall Thickness | 23548 |  | 2015-08-10 07:30 | 2015-08-16 14:30 | [36 empty] | 5.325 | CML-29 | CML: Elbow | 3 | 2033-01-02 | 2035-02-09 | 2015-08-10 07:30 | 2.5 | 0.15506 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-FG-45501-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.2 | 5.5 | 0.15
PW03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 200-PW-44018-01X01 | CML-11 | 200-PW-44018-01X01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 23298 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 5.375 | CML-11 | CML: Pipe Length | 3 | 2032-02-07 | 2034-02-09 | 2015-07-04 09:30 | 2.5 | 0.16256 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -0.2135 | 5.5 | 5.5 | 5.2 | 5.3 | 0.15
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-12 | 50-FH-43016-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12611 |  | 2014-01-23 13:00 | 2014-01-23 15:00 | [36 empty] | 5.35 | CML-12 | CML: Elbow | 3 | 2016-06-28 | 2016-10-27 | 2014-01-23 13:00 | 2.5 | 0.98756 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 3 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.1 | 4.9 | 5.8 | 5.6 | 0.42032
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23514-01C03 | CML-14 | 50-PL-23514-01C03 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8647 |  | 2015-02-10 11:30 | 2015-02-10 15:00 |  |  | Administrator | 2015-09-06 21:22 | [32 empty] | 8.225 | CML-14 | CML: Elbow | 6 | 2024-09-03 | 2024-06-16 | 2015-02-10 11:30 | 2.5 | 0.55385 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 7.8 | 3 O'Clock | 50 | 8.74 | 50-PL-23514-01C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 |  | 8.8 | 7.8 | 8.2 | 8.1 | 0.41932
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-4 | 200-PL-20034-03C02-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21601 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.175 | CML-4 | CML: Elbow | 3 | 2026-05-04 | 2024-02-13 | 2014-06-28 13:00 | 3.61 | 0.35334 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 7.8 | 3 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 |  | 8.5 | 7.8 | 8.5 | 7.9 | 0.37749
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-10 | 25-PG-23300-25C02 CML-10 | Yes | FPSO 2014 | Pipe Wall Thickness | 20677 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 8.675 | CML-10 | CML: Elbow | 3 | 2018-02-02 | 2017-03-31 | 2014-05-27 09:30 | 4.4 | 1.0027 | A2: Right Quadrant |  | 6.09 | 4.4 | 5.245 | 8.1 | 3 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 8.8 | 8.1 | 8.7 | 9.1 | 0.41932
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-18 | 100-FG-45001-09C02 CML-18 | Yes | FPSO 2015 | Pipe Wall Thickness | 23323 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.225 | CML-18 | CML: type TBC | 3 | 2054-07-05 | 2043-07-19 | 2015-07-11 07:00 | 4.7 | 0.15637 | A4: Left Quadrant |  | 8.13 | 4.7 | 6.415 | 10.8 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | -0.42211 | 11.8 | 11.2 | 11.1 | 10.8 | 0.41932
FL02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-FL-43454-01C02-P | CML-4 | 50-FL-43454-01C02-P CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23026 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 9.675 | CML-4 | CML: Elbow | 6 | 2090-03-16 | 2085-11-02 | 2015-05-06 07:00 | 2.5 | 0.0881 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 9.1 | 9 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 | 0.46218 | 9.7 | 9.8 | 10.1 | 9.1 | 0.41932
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-14 | 200-PW-44018-01X01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 7979 | Reviewed. Line holed in Apr 15. New line is being fabricated | 2015-01-18 10:30 | 2015-01-18 14:00 |  |  | Administrator | 2015-06-05 15:10 | [32 empty] | 5.375 | CML-14 | CML: Elbow | 3 | 2030-04-02 | 2032-03-18 | 2015-01-18 10:30 | 2.5 | 0.17747 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 12 O'Clock | 80 | 5.49 | 80-PL-44513-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 5.5 | 5.5 | 0.15
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45030-03C03 | CML-5 | 50-PL-45030-03C03 CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10468 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8.775 | CML-5 | CML: type TBC | 6 | 2019-11-25 | 2019-03-02 | 2013-11-13 | 0.99 | 1.1945 | A3: Inside Quadrant |  | 2.74 | 0.99 | 1.865 | 8.2 | 6 O'Clock | 50 | 8.74 | 50-PL-45030-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.21 |  | 9.2 | 8.9 | 8.2 | 8.8 | 0.41932
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-8 | 50-DC-57451-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1379 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 6.6 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 12 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.6 | 6.8 | 6.6 | 0.1633
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-7 | 50-DC-57451-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1378 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 7.6 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 9 | 7.4 | 7.6 | 6.4 | 1.0708
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-9 | 300-PG-20506-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 13223 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.225 | CML-9 | CML: type TBC | 6 | 2026-12-26 | 2024-07-18 | 2014-02-04 15:00 | 4.9 | 0.68999 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 9 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14.1 | 14.8 | 14.2 | 13.8 | 0.41932
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-9 | 200-PL-20034-03C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21606 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.275 | CML-9 | CML: Reducer | 3 | 2026-05-04 | 2024-02-13 | 2014-06-28 13:00 | 3.61 | 0.35334 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 7.8 | 9 O'Clock | 150 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 |  | 8.3 | 8.3 | 8.7 | 7.8 | 0.36856
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-27 | 50-PW-44040-01C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 2002 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.525 | CML-27 | CML: Fitting | 3 | 2020-09-28 | 2021-07-12 | 2014-03-27 07:00 | 2.5 | 0.41465 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.2 | 5.5 | 5.8 | 0.25
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-6 | 200-PL-20035-03C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21341 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 8 | CML-6 | CML: Pipe Length | 3 | 2026-04-22 | 2024-02-03 | 2014-06-27 13:00 | 3.61 | 0.35424 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 7.8 | 9 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 |  | 7.9 | 8.2 | 8.1 | 7.8 | 0.18257
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44021-01X01 | CML-3 | 200-PW-44021-01X01 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10708 | Deck Level. Line is FFS. High CR. Line rechecked (refer to Jan. 15 values) | 2013-11-10 | 2013-11-10 |  |  | Administrator | 2015-09-13 11:05 | [32 empty] | 5.325 | CML-3 | CML: Elbow | 3 | 2014-11-25 | 2014-11-21 | 2013-11-10 | 2.5 | 2.5911 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.2 | 9 O'Clock | 20 | 6.35 | 200-PW-44021-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.5 | 5.2 | 0.15
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20035-03C02-P | CML-8 | 200-PL-20035-03C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23471 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 8 | CML-8 | CML: Fitting | 3 | 2039-03-17 | 2034-10-10 | 2015-07-24 07:00 | 3.61 | 0.17707 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 7.8 | 3 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.19 | -0.46586 | 8.1 | 7.8 | 8 | 8.1 | 0.14142
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-31 | 300-WS-50806-1LC CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 10770 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.725 | CML-31 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 12.4 | 12 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 12.4 | 12.7 | 12.7 | 13.1 | 0.28723
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-7 | 300-WS-50806-1LC CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10746 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 13.275 | CML-7 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 12.4 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  | 13.6 | 12.4 | 13.6 | 13.5 | 0.58523
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-5 | 50-CG-38452-09C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1699 | Rope Access | 2014-04-13 09:15 | 2014-04-13 10:15 | [36 empty] | 7.675 | CML-5 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 09:15 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 12 O'Clock | 50 | 5.54 | 50-WC-40018-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.8 | 8.1 | 7.7 | 0.41932
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 350-FL-43511-01C02 | CML-19 | 350-FL-43511-01C02 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2300 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 7.825 | CML-19 | CML: type TBC | 3 | 2021-09-02 | 2020-07-31 | 2014-03-17 08:00 | 2.5 | 0.65599 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 7.4 | 9 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 7.7 | 8.4 | 7.8 | 7.4 | 0.41932
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-1 | 150-FH-43136-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2762 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.275 | CML-1 | CML: Pipe Length | 3 | 2024-12-31 | 2022-11-30 | 2014-03-13 09:00 | 1.03 | 0.5244 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.7 | 12 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.67 |  | 6.7 | 7.7 | 7.3 | 7.4 | 0.41932
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-26 | 200-PW-44018-01X01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 23235 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.4 | CML-26 | CML: Fitting | 3 | 2033-06-09 | 2035-10-08 | 2015-05-11 07:00 | 2.5 | 0.14923 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 2.445 | 5.5 | 5.5 | 5.2 | 5.4 | 0.14142
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML-2 | 80-DH-56004-01C02 CML-2 | yes | FPSO 2015 | Pipe Wall Thickness | 6411 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 3.725 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 12 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.3 | 3.6 | 4.3 | 3.7 | 0.41932
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-6 | 300-PL-20011-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 23791 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 7.325 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 40 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.3 | 6.9 | 8.4 | 6.7 | 0.75884
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-7 | 50-DC-57056-03C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1139 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.55 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 6.4 | 6 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.4 | 6.4 | 6.7 | 0.17321
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57020-01C02 | CML-18 | 50-DC-57020-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2460 |  | 2014-03-20 09:30 | 2014-03-20 11:30 | [36 empty] | 6.8 | CML-18 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-20 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.4 | 9 O'Clock | 50 | 5.54 | 50-DC-57020-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.6 | 7.7 | 6.4 | 0.60553
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-6 | 100-DC-57038-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2369 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 6.425 | CML-6 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.4 | 6 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 6.4 | 6.5 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-4 | 100-DC-57038-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2367 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 6.7 | CML-4 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.4 | 3 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 7 | 7 | 0.34641
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-21 | 100-DC-57307-01C03 CML-21 | no | FPSO 2014 | Pipe Wall Thickness | 2329 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.723mm/ yr | [35 empty] | 6.675 | CML-21 | CML: type TBC | 6 | 2015-08-22 | 2015-08-18 | 2014-03-17 13:00 | 2.5 | 2.7229 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.4 | 12 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.6 | 6.8 | 6.9 | 0.22174
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-20 | 100-DC-57307-01C03 CML-20 | no | FPSO 2014 | Pipe Wall Thickness | 2328 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.723mm/ yr | [35 empty] | 6.85 | CML-20 | CML: type TBC | 6 | 2015-08-22 | 2015-08-18 | 2014-03-17 13:00 | 2.5 | 2.7229 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.4 | 6 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.4 | 7 | 6.4 | 6.6 | 0.44347
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-16 | 150-WC-40006-01C02 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8892 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.425 | CML-16 | CML: type TBC | 3 | 2051-02-17 | 2055-03-06 | 2015-02-25 09:30 | 2.5 | 0.08055 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.4 | 5.4 | 5.4 | 0.05
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38452-09C02-P | CML-6 | 50-CG-38452-09C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 13096 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 21.075 | CML-6 | CML: Pipe Length | 3 | 2015-12-23 | 2015-04-30 | 2014-01-10 09:00 | 15.88 | 2.3693 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 20.5 | 9 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.62 |  | 21.1 | 21.2 | 21.5 | 20.5 | 0.41932
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-2 | 200-FH-43012-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2832 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 9.475 | CML-2 | CML: Reducer | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 8.9 | 6 O'Clock | 150 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.56 |  | 9.9 | 9.6 | 8.9 | 9.5 | 0.41932
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-12 | 300-PG-23002-03C03-A CML-12 |  | FPSO 2013 | Pipe Wall Thickness | 10108 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 13.925 | CML-12 | CML: Elbow | 6 | 2018-07-13 | 2017-09-01 | 2013-11-07 | 5.22 | 1.7676 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 13.5 | 12 O'Clock | 300 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.28 |  | 13.5 | 13.8 | 14.5 | 13.9 | 0.41932
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44037-01C03 | CML-3 | 300-PW-44037-01C03 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 22956 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 9.3 | CML-3 | CML: Elbow | 6 | 2024-01-24 | 2022-10-31 | 2015-05-04 07:00 | 2.5 | 0.73282 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 8.9 | 9 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | 2.0075 | 9.4 | 9.5 | 9.4 | 8.9 | 0.2708
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-13 | 50-PW-44015-01X01 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5723 | Rope access | 2014-06-22 10:00 | 2014-06-22 12:00 | [36 empty] | 5.4 | CML-13 | CML: Reducing Tee | 3 | 2022-11-16 | 2023-11-21 | 2014-06-22 10:00 | 2.5 | 0.32116 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -1.3012 | 5.5 | 5.5 | 5.2 | 5.4 | 0.14142
PW03 | Montara_Topside | Yes | Fire Water (71) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 6400 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 5.35 | CML-2 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 5.2 | 9 O'Clock | 150 | 3 | 150-WF-71335-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.3 | 5.4 | 5.2 | 0.1291
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-17 | 50-DH-56062-01C02 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 9104 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 7.325 | CML-17 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.5 | 7.6 | 6.7 | 7.5 | 0.41932
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-1 | 50-CG-38452-09C02-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3120 | Rope Access | 2014-05-04 07:00 | 2014-05-04 08:00 | [36 empty] | 7.825 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-05-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.2 | 6 O'Clock | 200 | 6.35 | 200-WC-40009-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 8 | 8.1 | 7.2 | 8 | 0.41932
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-10 | 250-PG-20036-01C03-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21368 | Protective mesh removed/ Rope access | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 8.525 | CML-10 | CML: Elbow | 6 | 2018-12-09 | 2018-08-16 | 2014-07-14 07:30 | 2.5 | 1.2247 | A4: Left Quadrant |  | 3.27 | 2.5 | 2.885 | 7.9 | 9 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.8 | 8.7 | 8.7 | 7.9 | 0.41932
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-1 | 100-FG-45001-09C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10416 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 13.025 | CML-1 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2013-11-13 | 4.7 | 0 | A4: Left Quadrant |  | 8.13 | 4.7 | 6.415 | 12.4 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 13.3 | 13.2 | 13.2 | 12.4 | 0.41932
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8574 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.425 | CML-2 | CML: type TBC | 3 | 2049-11-16 | 2053-10-15 | 2015-02-04 07:30 | 2.5 | 0.08332 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63034-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 5.4 | 5.5 | 5.4 | 0.05
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-3 | 100-PG-23503-03C03-A CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5511 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 11.425 | CML-3 | CML: Elbow | 6 | 2029-12-28 | 2030-10-18 | 2014-06-01 07:00 | 5.66 | 0.32974 | A4: Left Quadrant |  | 5.13 | 5.66 | 5.395 | 10.8 | 9 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.14 | -1.3702 | 11.6 | 11.6 | 11.7 | 10.8 | 0.41932
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43003-01C02 | CML-2 | 200-FH-43003-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12525 |  | 2014-01-18 11:30 | 2014-01-18 13:30 | [36 empty] | 10.5333 | CML-2 | CML: Tee | 3 | 2063-07-07 | 2057-06-06 | 2014-01-18 11:30 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 10.2 | 3 O'Clock | 200 | 6.35 | 200-FH-43003-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.86 |  | 10.4 | 10.2 | 11 |  | 0.41633
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20039-01C03-P | CML-6 | 250-PW-20039-01C03-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5838 | Protective mesh removed/Rope access | 2014-06-24 13:00 | 2014-06-24 15:00 | [36 empty] | 10.075 | CML-6 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2014-06-24 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.27 | 2.5 | 2.885 | 10 | 9 O'Clock | 250 | 9.27 | 250-PW-20039-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.3 | 10 | 10 | 10 | 0.15
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20502-01C03-P | CML-11 | 300-PG-20502-01C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 23898 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 11.3 | CML-11 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.8 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 11.2 | 11.4 | 11.8 | 0.41633
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-20502-01C03-P | CML-11 | 300-PG-20502-01C03-P CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 20758 |  | 2014-09-26 07:00 | 2014-09-26 15:00 | [36 empty] | 11.3 | CML-11 | CML: type TBC | 6 | 2091-07-06 | 2082-06-18 | 2014-09-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.8 | 12 O'Clock | 300 | 10.31 | 300-PG-20502-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 10.8 | 11.2 | 11.4 | 11.8 | 0.41633
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-25 | 50-PW-44040-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 2000 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.525 | CML-25 | CML: Pipe Length | 3 | 2020-09-28 | 2021-07-12 | 2014-03-27 07:00 | 2.5 | 0.41465 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.2 | 5.5 | 5.8 | 0.25
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-5 | 100-PW-20021-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21808 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.45 | CML-5 | CML: Elbow | 3 | 2019-04-05 | 2019-06-15 | 2014-10-11 07:00 | 2.5 | 0.60186 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.7 | 5.4 | 5.5 | 0.20817
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-1 | 50-FH-43011-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7951 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.5 | CML-1 | CML: Elbow | 3 | 2018-01-09 | 2017-06-01 | 2015-01-18 08:00 | 2.5 | 1.1752 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 6 | 6 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 7 | 6.4 | 6 | 6.6 | 0.41633
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-8 | 300-PG-20048-03C03-P CML-8 |  | FPSO 2016 | Pipe Wall Thickness | 24479 | Re-check as requested by N.Sequera | 2016-07-09 07:00 | 2016-07-09 15:00 | Check Corrosion Rate of 0.441mm/ yr | 38 | Kirstie Albone | 2017-03-23 12:52 | [32 empty] | 13.4 | CML-8 | CML: Elbow | 6 | 2034-08-27 | 2030-11-01 | 2016-07-09 07:00 | 4.9 | 0.44085 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.9 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8 | 0.51408 | 12.9 | 13.3 | 13.5 | 13.9 | 0.41633
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-18 | 100-PW-20021-01C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21821 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 5.375 | CML-18 | CML: Elbow | 3 | 2019-04-05 | 2019-06-15 | 2014-10-11 07:00 | 2.5 | 0.60186 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.2 | 6 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.3 | 5.2 | 5.6 | 0.17078
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-18 | 300-WS-50806-1LC CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 10757 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 12.575 | CML-18 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 12.5 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 12.5 | 12.5 | 12.7 | 12.6 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56114-01C02 | CML-6 | 50-DH-56114-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5231 | Rope Access | 2014-05-20 11:00 | 2014-05-20 12:00 | [36 empty] | 9.1 | CML-6 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-20 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.6 | 9 O'Clock | 50 | 5.54 | 50-DH-56114-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.2 | 9 | 9.6 | 8.6 | 0.41633
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PG-20036-01C03-P | CML-6 | 250-PG-20036-01C03-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23394 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-21 07:00 | 2015-07-21 15:00 | [36 empty] | 8.2 | CML-6 | CML: Elbow | 6 | 2022-08-17 | 2022-02-07 | 2015-07-21 07:00 | 2.5 | 0.7344 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 7.7 | 6 O'Clock | 250 | 9.27 | 250-PG-20036-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 | 0.58874 | 8.7 | 8.1 | 7.7 | 8.3 | 0.41633
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-8 | 50-CG-38452-09C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1810 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 7.7 | CML-8 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-04-29 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 6 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.8 | 7.6 | 7.2 | 8.2 | 0.41633
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56002-01C02 | CML-3 | 80-DH-56002-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3422 | Rope Access | 2014-05-11 14:00 | 2014-05-11 14:30 | [36 empty] | 6.05 | CML-3 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-11 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-DH-56002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.8 | 6.4 | 5.6 | 6.4 | 0.41231
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-2 | 200-PW-44018-01X01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8878 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.35 | CML-2 | CML: type TBC | 3 | 2028-12-11 | 2030-08-11 | 2015-02-25 09:30 | 2.5 | 0.19562 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.5 | 5.2 | 5.4 | 5.3 | 0.1291
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43016-01C02 | CML-6 | 50-FH-43016-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22667 |  | 2015-04-27 07:00 | 2015-04-27 15:00 | [36 empty] | 7.05 | CML-6 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-04-27 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 3 O'Clock | 50 | 5.54 | 50-FH-43016-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 | 1.4322 | 6.8 | 6.6 | 7.4 | 7.4 | 0.41231
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-4 | 150-FG-45002-03C02 CML-4 |  | FPSO 2013 | Pipe Wall Thickness | 10407 | Deck Level | 2013-11-12 | 2013-11-12 |  |  | Nestor | 2016-04-27 11:12 | This is where comment goes | [31 empty] | 6.65 | CML-4 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.4 | 12 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.6 | 6.8 | 6.8 | 0.19149
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57024-01C02 | CML-1 | 50-DC-57024-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2873 | Rope Access | 2014-04-24 13:00 | 2014-04-24 14:00 | Check Corrosion Rate of 1.382mm/ yr | [35 empty] | 4.95 | CML-1 | CML: type TBC | 3 | 2017-02-25 | 2016-08-14 | 2014-04-24 13:00 | 0.37 | 1.3818 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 4.3 | 12 O'Clock | 50 | 5.54 | 50-DC-57024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.93 |  | 4.3 | 5.3 | 5 | 5.2 | 0.45092
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-22 | 80-CG-38459-09C02-P CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 23066 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 15.15 | CML-22 | CML: Pipe Length | 6 | 2099-09-17 | 2086-07-24 | 2015-05-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 14.7 | 12 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.2 |  | 14.7 | 14.9 | 15.5 | 15.5 | 0.41231
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-3 | 300-PG-23400-01C03-P CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23417 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-22 07:00 | 2015-07-22 15:00 | Check Corrosion Rate of 0.519mm/ yr |  | John Wilson | 2017-03-24 09:39 | Anomily to re visit 7/5/2018 | [31 empty] | 9.725 | CML-3 | CML: Pipe Length | 6 | 2023-03-23 | 2024-02-06 | 2015-07-22 07:00 | 5.22 | 0.51856 | A1: Outside Quadrant |  | 4.31 | 5.22 | 4.765 | 9.2 | 12 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.98 | 0.26134 | 9.2 | 9.7 | 9.4 | 10.6 | 0.61847
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-4 | 200-PG-23008-15S01-A CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5229 | Rope Access | 2014-05-20 11:00 | 2014-05-20 12:00 | [36 empty] | 5.65 | CML-4 | CML: Elbow | 3 | 2020-02-07 | 2020-10-26 | 2014-05-20 11:00 | 2.5 | 0.45437 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 9 O'Clock | 50 | 5.54 | 50-DH-56114-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 5.7 | 6.1 | 5.1 | 0.41231
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56142-01C02 | CML-4 | 25-DH-56142-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7525 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 6.65 | CML-4 | CML: Equal Tee | 3 | 2061-04-16 | 2060-12-09 | 2015-04-13 07:00 | 2.5 | 0.08036 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 25 | 6.35 | 25-DH-56142-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 7.2 | 6.2 | 6.6 | 0.41231
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-1 | 250-PG-23003-06C02-PA CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 7680 | Re-check. Line is FFS. This CR is reported from values measured in Nov. 2013. Latest CR with WT values reported in Jan 15 indicates a maximum CR of 0.958 mm/yr for this line. Current RBI frequency is 48m Action: Re-check point to confirm values in Jan. 2016 | 2015-01-08 13:00 | 2015-01-08 15:00 |  |  | Administrator | 2015-09-06 16:18 | [32 empty] | 4.55 | CML-1 | CML: Elbow | 3 | 2016-08-01 | 2016-12-04 | 2015-01-08 13:00 | 2.5 | 0.95833 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4 | 12 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.5 | 0.69933 | 4 | 4.6 | 4.6 | 5 | 0.41231
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38474-01C02-P | CML-8 | 50-CG-38474-01C02-P CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23632 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 4.75 | CML-8 | CML: Pipe Length | 3 | 2019-04-26 | 2019-12-14 | 2015-10-28 07:00 | 2.5 | 0.51473 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 9 O'Clock | 50 | 5.54 | 50-CG-38474-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 4.7 | 5.3 | 4.7 | 4.3 | 0.41231
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56027-01C02 | CML-1 | 80-DH-56027-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20897 | Rope Access | 2014-05-22 11:00 | 2014-05-22 12:00 | [36 empty] | 5.55 | CML-1 | CML: Elbow | 3 | 2019-05-10 | 2020-01-17 | 2014-05-22 11:00 | 2.5 | 0.50315 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 12 O'Clock | 80 | 5.49 | 80-DH-56027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.6 | 6 | 5.6 | 0.41231
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-18 | 50-PL-23052-09C03 CML-18 |  | FPSO 2013 | Pipe Wall Thickness | 10182 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.35 | CML-18 | CML: type TBC | 6 | 2016-04-13 | 2015-11-21 | 2013-11-09 | 2.81 | 2.8792 | A3: Inside Quadrant |  | 5.07 | 2.81 | 3.94 | 9.8 | 6 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.99 |  | 10.4 | 10.8 | 9.8 | 10.4 | 0.41231
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38489-01C02-P | CML-5 | 50-CG-38489-01C02-P CML-5 | yes | FPSO 2014 | Pipe Wall Thickness | 20862 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 5.45 | CML-5 | CML: Elbow | 3 | 2020-12-09 | 2021-09-30 | 2014-10-02 07:00 | 2.5 | 0.40365 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 3 O'Clock | 50 | 5.54 | 50-CG-38489-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.4 | 5 | 5.4 | 6 | 0.41231
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-16 | 25-FG-45455-01C02-E CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21819 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6.35 | CML-16 | CML: Elbow | 3 | 2253-01-17 | 2260-12-16 | 2014-10-11 07:00 | 2.5 | 0.01468 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.6 | 6.8 | 0.41231
WC01 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 150-WC-40006-01C02 | CML-2 | 150-WC-40006-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8568 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.475 | CML-2 | CML: type TBC | 3 | 2049-11-16 | 2053-10-15 | 2015-02-04 07:30 | 2.5 | 0.08332 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-AI-63038-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.5 | 5.5 | 5.4 | 5.5 | 0.05
WC01 | Montara_Topside | Yes | Separation (20) | Pipework | 150-WC-40006-01C02 | CML-4 | 150-WC-40006-01C02 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 23455 | Re-check on line / Selected CML''s as Per RBI 2014 Report cml 4 only | 2015-07-23 07:00 | 2015-07-23 15:00 | [36 empty] | 5.4 | CML-4 | CML: Elbow | 3 | 2025-07-29 | 2025-12-23 | 2015-07-23 07:00 | 2.5 | 0.28928 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 9 O'Clock | 100 | 6.02 | 100-PL-20069-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 | 0.098388 | 5.4 | 5.4 | 5.4 | 5.4 | 0
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-17 | 50-CG-38001-09C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 10931 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.275 | CML-17 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.5525 | A3: Inside Quadrant |  | 5.74 |  |  | 7.8 | 6 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.8 | 8.3 | 8.8 | 7.8 | 8.2 | 0.4113
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-15 | 300-PF-20500-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21635 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.775 | CML-15 | CML: Pipe Length | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.4 | 9 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 15.3 | 14.9 | 14.5 | 14.4 | 0.4113
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-13 | 300-WS-50806-1LC CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10752 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 14.725 | CML-13 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 12.5 | 9 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10 |  | 15.4 | 16.9 | 14.1 | 12.5 | 1.8733
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9004-AS20-00 | CML-2 | 0100-AI-63L9004-AS20-00 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24278 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.55 | CML-2 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.5 | 3 O'Clock | 25 | 3.38 | 0100-AI-63L9004-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.5 | 6.6 | 6.6 | 0.057735
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9004-AS20-00 | CML-1 | 0100-AI-63L9004-AS20-00 CML-1 |  | FPSO 2016 | Pipe Wall Thickness | 24277 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.575 | CML-1 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.5 | 6 O'Clock | 25 | 3.38 | 0100-AI-63L9004-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.5 | 6.5 | 6.7 | 0.095743
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9005-AS20-00 | CML-3 | 0100-AS-63L9005-AS20-00 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24287 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.55 | CML-3 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.5 | 9 O'Clock | 25 | 3.38 | 0100-AS-63L9005-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.5 | 6.6 | 6.5 | 0.057735
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AS-63L9005-AS20-00 | CML-2 | 0100-AS-63L9005-AS20-00 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24286 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.525 | CML-2 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.5 | 6 O'Clock | 25 | 3.38 | 0100-AS-63L9005-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.5 | 6.5 | 6.6 | 0.05
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PG-20056-01C03-P | CML-4 | 100-PG-20056-01C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21534 | Protective mesh removed/ Rope access | 2014-07-17 07:30 | 2014-07-17 15:00 | [36 empty] | 8.725 | CML-4 | CML: Fitting | 6 | 2032-05-15 | 2032-04-11 | 2014-07-17 07:30 | 2.5 | 0.31947 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 8.2 | 9 O'Clock | 100 | 8.56 | 100-PG-20056-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.7 |  | 8.8 | 9.2 | 8.7 | 8.2 | 0.4113
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-25 | 300-WS-50806-1LC CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 10764 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 14.8 | CML-25 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 12.6 | 9 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.1 |  | 13.4 | 16.2 | 17 | 12.6 | 2.1292
SD01 | Montara_Topside | No | Steam (55) | Pipework | 150-SL-55001-01C02-H | CML-3 | 150-SL-55001-01C02-H CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 23604 |  | 2015-09-28 07:00 | 2015-09-28 15:00 | [36 empty] | 6.725 | CML-3 | CML: Elbow | 3 | 2030-12-27 | 2029-08-12 | 2015-09-28 07:00 | 2.5 | 0.26216 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.5 | 6 O'Clock | 25 | 7.11 | 150-SL-55001-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.5 | 6.5 | 7.2 | 0.3304
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38476-01C02-H | CML-10 | 50-CG-38476-01C02-H CML-10 | Yes | FPSO 2015 | Pipe Wall Thickness | 23642 | lagging removal? Or may be coated with nansulate | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.175 | CML-10 | CML: Pipe Length | 3 | 2022-02-16 | 2023-01-23 | 2015-10-28 07:00 | 2.5 | 0.34869 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38476-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.1 | 4.7 | 5.2 | 5.7 | 0.4113
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-46 | 200-PG-23008-15S01-A CML-46 |  | FPSO 2014 | Pipe Wall Thickness | 3262 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 5.625 | CML-46 | CML: type TBC | 3 | 2019-11-21 | 2020-08-01 | 2014-05-09 07:00 | 2.5 | 0.46919 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.7 | 6.1 | 5.1 | 5.6 | 0.4113
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-27 | 300-WS-50806-1LC CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 10766 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 14.95 | CML-27 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 12.7 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 13.4 | 12.7 | 17 | 16.7 | 2.2159
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43301-01C02 | CML-2 | 50-FL-43301-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20452 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.775 | CML-2 | CML: Elbow | 3 | 2030-06-15 | 2032-04-12 | 2014-10-05 07:00 | 2.5 | 0.17831 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 9 O'Clock | 50 | 5.54 | 50-FL-43301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6.3 | 5.8 | 5.7 | 5.3 | 0.4113
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-16 | 300-WS-50806-1LC CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 10755 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 14.25 | CML-16 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 12.7 | 12 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.2 |  | 12.7 | 14.1 | 15.7 | 14.5 | 1.2369
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-23 | 300-WS-50806-1LC CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 10762 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 13.2667 | CML-23 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 13.2 | 12 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 13.2 | 13.3 | 13.3 |  | 0.057735
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42309-01S01 | CML-5 | 40-CI-42309-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7501 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.7 | CML-5 | CML: type TBC | 1 | 2026-12-09 | 2022-12-07 | 2015-04-13 07:00 | 2.5 | 0.34288 | A3: Inside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.5 | 6 O'Clock | 40 | 7.14 | 40-CI-42309-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 8.7 | 7.5 | 6.5 | 8.1 | 0.93808
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42310-01S01 | CML-5 | 40-CI-42310-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7494 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.9 | CML-5 | CML: type TBC | 1 | 2026-12-09 | 2022-12-07 | 2015-04-13 07:00 | 2.5 | 0.34288 | A3: Inside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.5 | 6 O'Clock | 40 | 7.14 | 40-CI-42310-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 9.1 | 8.5 | 6.5 | 7.5 | 1.1431
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42310-01S01 | CML-2 | 40-CI-42310-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7491 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.825 | CML-2 | CML: type TBC | 1 | 2026-12-09 | 2022-12-07 | 2015-04-13 07:00 | 2.5 | 0.34288 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.5 | 12 O'Clock | 40 | 7.14 | 40-CI-42310-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7.2 | 9.4 | 8.2 | 1.2606
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56071-01C02 | CML-1 | 50-DH-56071-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3416 | Rope Access | 2014-05-11 13:00 | 2014-05-11 14:00 | [36 empty] | 6.125 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-11 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-DH-56071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 6.2 | 6.6 | 6.1 | 0.4113
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-2 | 250-WC-40017-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2065 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | Check Corrosion Rate of 1.033mm/ yr | [35 empty] | 6.15 | CML-2 | CML: type TBC | 3 | 2017-02-20 | 2017-02-10 | 2014-03-28 09:30 | 2.5 | 1.0328 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.5 | 3 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 5.5 | 6.2 | 6.6 | 0.46547
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-39 | 50-AI-63004-01E01 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 9030 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.575 | CML-39 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.5 | 6.6 | 6.6 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63018-01E01 | CML-28 | 50-AU-63018-01E01 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 8924 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 13:00 | 2015-02-25 15:00 | [36 empty] | 6.825 | CML-28 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-25 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-AU-63018-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.9 | 6.9 | 6.5 | 7 | 0.22174
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-6 | 80-SC-55002-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8836 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 6.9 | CML-6 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.5 | 6 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.5 | 6.6 | 6.5 | 7 | 0.45461
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-4 | 50-AI-63009-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8526 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.8 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.1 | 6.8 | 6.8 | 6.5 | 0.24495
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67003-01E01 | CML-5 | 50-GN-67003-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8500 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.525 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-GN-67003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.5 | 6.6 | 6.5 | 0.05
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67003-01E01 | CML-2 | 50-GN-67003-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8497 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 6.6 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-GN-67003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.7 | 6.5 | 6.6 | 0.08165
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-8 | 300-WS-50806-1LC CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10747 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 13.4 | CML-8 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 13.2 | 9 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.7 |  | 13.5 | 13.5 | 13.4 | 13.2 | 0.14142
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63016-01E01 | CML-5 | 50-AU-63016-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8409 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.575 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-AU-63016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.5 | 6.6 | 6.6 | 0.05
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63037-01E01 | CML-2 | 50-AI-63037-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8398 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.675 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-AI-63037-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.5 | 7.2 | 6.5 | 0.35
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-17 | 50-AI-63450-01E01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8336 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.575 | CML-17 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.5 | 6.6 | 6.7 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-16 | 50-AI-63450-01E01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8335 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.7 | CML-16 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.5 | 6.6 | 7.1 | 0.2708
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-13 | 50-WD-53011-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8289 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.6 | CML-13 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.6 | 6.5 | 6.7 | 0.08165
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53011-01E01 | CML-11 | 50-WD-53011-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8287 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.75 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 12 O'Clock | 50 | 5.54 | 50-WD-53011-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.6 | 6.6 | 7.3 | 0.36968
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53008-01E01 | CML-2 | 50-WD-53008-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8167 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 7 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-WD-53008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.4 | 6.7 | 7.4 | 6.5 | 0.46904
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-22 | 50-WD-53007-01E01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 8161 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.925 | CML-22 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 6.8 | 6.5 | 7.4 | 0.37749
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-18 | 50-WD-53007-01E01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8157 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.7 | CML-18 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.9 | 6.7 | 6.5 | 6.7 | 0.1633
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-15 | 50-WD-53007-01E01 CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 8154 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.75 | CML-15 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 12 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.6 | 7.2 | 6.7 | 0.31091
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-16 | 100-OL-69001-01S01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8118 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 6.65 | CML-16 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.5 | 6 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.8 | 6.5 | 6.7 | 0.1291
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-9 | 300-WS-50806-1LC CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10748 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 15.475 | CML-9 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 13.5 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11 |  | 15.2 | 13.5 | 15.3 | 17.9 | 1.8154
FL02 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43454-01C02-P | CML-19 | 50-FL-43454-01C02-P CML-19 | Yes | FPSO 2014 | Pipe Wall Thickness | 20522 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 6.325 | CML-19 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 3 O'Clock | 25 | 5.54 | 50-FL-43454-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.6 | 5.8 | 6.7 | 6.2 | 0.4113
FG02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5621 | Rope Access | 2014-06-20 13:00 | 2014-06-20 15:00 | [36 empty] | 6.525 | CML-2 | CML: Pipe Length | 3 | 2024-12-29 | 2024-11-29 | 2014-06-20 13:00 | 2.5 | 0.33221 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.4 | 6.9 | 6 | 6.8 | 0.4113
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57030-01C02 | CML-1 | 50-DC-57030-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20277 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.05 | CML-1 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-DC-57030-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 6.5 | 7.3 | 7.4 | 0.40415
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57030-01C02 | CML-2 | 50-DC-57030-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20278 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.025 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 6 O'Clock | 50 | 5.54 | 50-DC-57030-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.9 | 7.1 | 6.5 | 7.6 | 0.45735
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45301-01C02 | CML-24 | 50-FG-45301-01C02 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 5810 | Rope access | 2014-06-23 13:00 | 2014-06-23 15:00 | [36 empty] | 6.475 | CML-24 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-06-23 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 25 | 5.54 | 50-FG-45301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.6 | 6.2 | 6.1 | 7 | 0.4113
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-18 | 80-PW-44016-01C02-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21950 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.425 | CML-18 | CML: Elbow | 3 | 2027-06-04 | 2029-01-20 | 2014-10-10 07:00 | 2.5 | 0.21328 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.6 | 5.5 | 5.2 | 5.4 | 0.17078
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-12 | 250-FH-43303-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12950 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.825 | CML-12 | CML: type TBC | 3 | 2064-02-06 | 2063-09-23 | 2014-01-27 10:00 | 2.5 | 0.07591 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.3 | 6.3 | 6.9 | 6.8 | 0.4113
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-3 | 300-WS-50806-1LC CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10742 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 15.25 | CML-3 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 14 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.5 |  | 15.5 | 14 | 14.8 | 16.7 | 1.1446
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-13 | 50-PW-44040-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1988 |  | 2014-03-27 07:00 | 2014-03-27 09:00 | [36 empty] | 5.35 | CML-13 | CML: Pipe Length | 3 | 2020-09-28 | 2021-07-12 | 2014-03-27 07:00 | 2.5 | 0.41465 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.5 | 5.2 | 5.4 | 0.1291
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-17 | 200-PW-44018-01X01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 23252 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.375 | CML-17 | CML: Pipe Length | 3 | 2030-10-11 | 2032-08-22 | 2015-05-11 07:00 | 2.5 | 0.17496 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.089024 | 5.4 | 5.4 | 5.5 | 5.2 | 0.12583
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-14 | 80-CG-38459-09C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21500 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | [36 empty] | 17.775 | CML-14 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-06-28 10:45 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.3 | 6 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.4 |  | 17.7 | 18.3 | 17.3 | 17.8 | 0.4113
FG04 | Montara_Topside | Yes | Produced Water (44) | Pipework | 150-FG-45003-03C02 | CML-20 | 150-FG-45003-03C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23255 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.075 | CML-20 | CML: Elbow | 3 | 2019-09-11 | 2020-05-15 | 2015-05-11 07:00 | 2.5 | 0.48372 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 | 0 | 5.1 | 5 | 4.6 | 5.6 | 0.4113
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-5 | 200-PW-44018-01X01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8873 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 08:00 | 2015-02-25 09:00 | [36 empty] | 5.375 | CML-5 | CML: type TBC | 3 | 2028-12-10 | 2030-08-11 | 2015-02-25 08:00 | 2.5 | 0.19564 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-AU-63019-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.5 | 5.4 | 0.12583
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-3 | 80-FL-43015-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20408 | Reviewed on 20/11/14. Line is FFS. Repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-20 11:25 | [32 empty] | 5.425 | CML-3 | CML: Elbow | 3 | 2020-03-30 | 2021-01-15 | 2014-10-06 07:00 | 2.5 | 0.43744 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.4 | 4.9 | 5.5 | 5.9 | 0.4113
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-7 | 50-FG-45019-03C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2598 | Rope Access | 2014-04-26 08:00 | 2014-04-26 09:00 | [36 empty] | 5.525 | CML-7 | CML: type TBC | 3 | 2018-06-29 | 2018-06-16 | 2014-04-26 08:00 | 2.5 | 0.59848 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5 | 6 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 | -0.44969 | 5.5 | 5.6 | 5 | 6 | 0.4113
PG02 | Montara_Topside | No | Separation (20) | Pipework | 250-PG-20042-01D01-P | CML-4 | 250-PG-20042-01D01-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21437 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 7.025 | CML-4 | CML: Elbow | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 5.35 | 2.5 | 3.925 | 6.5 | 9 O'Clock | 250 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.2 | 7.2 | 7.2 | 6.5 | 0.35
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43091-01C02 | CML-4 | 80-FL-43091-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5829 | Rope access | 2014-06-24 10:30 | 2014-06-24 12:00 | [36 empty] | 5.725 | CML-4 | CML: Elbow | 3 | 2024-05-18 | 2025-08-28 | 2014-06-24 10:30 | 2.5 | 0.2725 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-FL-43091-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.7 | 5.2 | 6.2 | 5.8 | 0.4113
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40403-01C02 | CML-5 | 100-WC-40403-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20385 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 5.9 | CML-5 | CML: Elbow | 3 | 2022-10-05 | 2023-01-26 | 2014-10-18 07:00 | 2.5 | 0.37637 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 9 O'Clock | 80 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.5 | 5.7 | 5.9 | 5.5 | 0.43205
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43100-01C02 | CML-4 | 100-FH-43100-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12731 |  | 2014-01-24 09:00 | 2014-01-24 10:00 | [36 empty] | 5.775 | CML-4 | CML: Pipe Length | 3 | 2016-08-04 | 2016-09-11 | 2014-01-24 09:00 | 2.5 | 1.1071 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 12 O'Clock | 100 | 6.02 | 100-FH-43100-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.8 | 5.7 | 6.3 | 0.4113
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45305-03C02 | CML-3 | 100-FG-45305-03C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22079 | Rope Access | 2014-05-25 09:30 | 2014-05-25 10:30 | [36 empty] | 6.55 | CML-3 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2014-05-25 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 6.5 | 3 O'Clock | 100 | 6.02 | 100-FG-45305-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.5 | 6.6 | 6.6 | 0.057735
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-6 | 300-PL-20011-01C02-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21202 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 7.325 | CML-6 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 40 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.3 | 6.9 | 8.4 | 6.7 | 0.75884
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43119-01C02 | CML-4 | 80-FH-43119-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12831 |  | 2014-01-18 10:00 | 2014-01-18 11:30 | [36 empty] | 5.725 | CML-4 | CML: Pipe Length | 3 | 2024-03-25 | 2022-11-06 | 2014-01-18 10:00 | 0.54 | 0.4574 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-FH-43119-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.66 |  | 5.7 | 5.2 | 6.2 | 5.8 | 0.4113
FG01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FG-45024-01C02 | CML-10 | 50-FG-45024-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2291 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 9.675 | CML-10 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-03-17 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.92 | 2.5 | 3.215 | 9.2 | 3 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.7 | 9.2 | 9.6 | 10.2 | 0.4113
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-4 | 300-PG-23001-03C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10954 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.025 | CML-4 | CML: Elbow | 6 | 2020-07-23 | 2019-05-10 | 2014-01-09 | 5.22 | 1.266 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 13.5 | 12 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.28 |  | 13.5 | 14.5 | 14.1 | 14 | 0.4113
FL01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 150-FL-43174-01C02 | CML-4 | 150-FL-43174-01C02 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 5315 | Pipe Schedule Estimated. Rope Access | 2015-03-13 07:00 | 2015-03-13 15:00 | [36 empty] | 3.775 | CML-4 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-13 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.4 | 6 O'Clock | 150 | 3 | 150-WF-71310-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.9 |  | 3.9 | 3.5 | 3.4 | 4.3 | 0.4113
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43174-01C02 | CML-5 | 150-FL-43174-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12903 |  | 2014-02-05 09:00 | 2014-02-05 11:00 | [36 empty] | 8.075 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-02-05 09:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.6 | 6 O'Clock | 100 | 6.02 | 100-FL-43174-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 8 | 8.6 | 7.6 | 8.1 | 0.4113
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56102-01C02 | CML-1 | 50-DH-56102-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8058 |  | 2015-01-22 07:30 | 2015-01-22 15:00 | [36 empty] | 5.425 | CML-1 | CML: type TBC | 3 | 2021-03-22 | 2022-01-22 | 2015-01-22 07:30 | 2.5 | 0.38913 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 12 O'Clock | 50 | 5.54 | 50-DH-56102-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.3 | 5.8 | 5.7 | 0.4113
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43302-01C02 | CML-1 | 50-FL-43302-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20454 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 5.925 | CML-1 | CML: Fitting | 3 | 2042-08-16 | 2045-10-03 | 2014-10-05 07:00 | 2.5 | 0.10401 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 3 O'Clock | 50 | 5.54 | 50-FL-43302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.3 | 5.4 | 5.8 | 6.2 | 0.4113
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-8 | 200-PL-20010-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 23808 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 7.275 | CML-8 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 40 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.1 | 7 | 8.3 | 6.7 | 0.70415
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-26 | 300-WS-50806-1LC CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 10765 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 15.525 | CML-26 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 14.5 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12 |  | 15.1 | 14.5 | 15.1 | 17.4 | 1.2816
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-5 | 50-DC-57451-01C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1376 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 7.125 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 3 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.2 | 6.5 | 7.3 | 7.5 | 0.43493
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57042-01C02 | CML-4 | 50-DC-57042-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1371 | Rope access | 2014-04-05 09:30 | 2014-04-05 10:30 | [36 empty] | 6.975 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57042-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7.1 | 6.9 | 7.4 | 0.37749
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-50 | 200-PL-20019-01C02 CML-50 |  | FPSO 2014 | Pipe Wall Thickness | 21301 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.275 | CML-50 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.4 | 7.3 | 6.7 | 7.7 | 0.41932
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-6 | 300-WS-50806-1LC CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10745 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 15.9 | CML-6 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 14.7 | 6 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.2 |  | 17.1 | 16.7 | 14.7 | 15.1 | 1.1776
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-10 | 300-WS-50806-1LC CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10749 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.4 | CML-10 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 15.3 | 12 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.8 |  | 15.3 | 17.3 | 17.1 | 19.9 | 1.8938
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45051-03C02 | CML-8 | 150-FG-45051-03C02 CML-8 | yes | FPSO 2016 | Pipe Wall Thickness | 24382 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 7.075 | CML-8 | CML: Pipe Length | 3 | 2047-04-26 | 2041-05-25 | 2016-06-06 07:00 | 2.5 | 0.13589 | A4: Left Quadrant |  | 4.11 | 2.5 | 3.305 | 6.7 | 9 O'Clock | 150 | 7.11 | 150-FG-45051-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.6 | 7.2 | 6.8 | 6.7 | 0.4113
CG01 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-CG-38490-09C02 | CML-2 | 50-CG-38490-09C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2530 |  | 2014-04-03 07:00 | 2014-04-03 08:00 | [36 empty] | 9.075 | CML-2 | CML: type TBC | 3 | 2144-03-27 | 2110-04-10 | 2014-04-03 07:00 | 2.5 | 0.04767 | A4: Left Quadrant |  | 5.74 | 2.5 | 4.12 | 8.7 | 9 O'Clock | 50 | 8.74 | 50-CG-38490-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.6 | 8.8 | 9.2 | 8.7 | 0.4113
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20049-03C03-P | CML-15 | 300-PG-20049-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21501 | Protective mesh removed | 2014-06-28 10:45 | 2014-06-28 12:00 | Check Corrosion Rate of 0.53mm/ yr | 39 | Kirstie Albone | 2017-03-23 13:23 | [32 empty] | 14.075 | CML-15 | CML: Fitting | 6 | 2031-01-29 | 2027-11-26 | 2014-06-28 10:45 | 4.9 | 0.53013 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 9 O'Clock | 300 | 14.27 | 300-PG-20049-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 14.2 | 13.8 | 14.6 | 13.7 | 0.4113
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40512-1CG | CML-2 | 150-WC-40512-1CG CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5475 | Rope Access | 2014-05-28 10:00 | 2014-05-28 11:30 | [36 empty] | 11.55 | CML-2 | CML: Elbow | 3 | 2098-02-09 | 2070-10-05 | 2014-05-28 10:00 | 2.5 | 0 | A4: Left Quadrant |  | 7.97 | 2.5 | 5.235 | 11.3 | 9 O'Clock | 150 | 10.97 | 150-WC-40512-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 11.9 | 11.4 | 11.6 | 11.3 | 0.26458
PW03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7859 |  | 2015-01-14 08:00 | 2015-01-14 09:00 | [36 empty] | 5.325 | CML-1 | CML: Pipe Length | 3 | 2027-12-01 | 2029-06-21 | 2015-01-14 08:00 | 2.5 | 0.20951 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 15 | 5.54 | 50-CG-38009-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.2 | 5.3 | 5.5 | 0.12583
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-12 | 300-WS-50806-1LC CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10751 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.125 | CML-12 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 16.6 | 12 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.1 |  | 16.6 | 17.2 | 17.2 | 17.5 | 0.37749
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-11 | 300-WS-50806-1LC CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10750 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.225 | CML-11 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A1: Outside Quadrant |  | 7.31 | 2.5 | 4.905 | 16.6 | 12 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.1 |  | 16.6 | 16.8 | 17.5 | 18 | 0.64485
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-22 | 300-WS-50806-1LC CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 10761 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.175 | CML-22 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 16.7 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.2 |  | 17.7 | 16.7 | 17.2 | 17.1 | 0.4113
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-9 | 300-PG-23001-03C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10959 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14 | CML-9 | CML: Elbow | 6 | 2021-08-16 | 2020-03-29 | 2014-01-09 | 5.22 | 1.1016 | A3: Inside Quadrant |  | 8.27 | 5.22 | 6.745 | 13.6 | 6 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.38 |  | 14.4 | 13.7 | 13.6 | 14.3 | 0.40825
DH01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-DH-56137-01C02 | CML-2 | 50-DH-56137-01C02 CML-2 | Yes | FPSO 2015 | Pipe Wall Thickness | 23307 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 19.8 | CML-2 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A4: Left Quadrant |  | 8.13 | 4.7 | 6.415 | 19.4 | 9 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.7 | -1.2663 | 20.1 | 19.5 | 20.2 | 19.4 | 0.40825
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-12 | 200-FH-43025-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2485 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 8.2 | CML-12 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8 | 8.8 | 8.1 | 0.40825
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38487-09C02-P | CML-16 | 50-CG-38487-09C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20855 | Covers Removed | 2014-10-02 07:00 | 2014-10-02 15:00 | [36 empty] | 8.7 | CML-16 | CML: Fitting | 3 | 2037-12-13 | 2031-08-01 | 2014-10-02 07:00 | 2.5 | 0.25415 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.4 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | 0.96264 | 8.6 | 8.4 | 8.5 | 9.3 | 0.40825
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-5 | 200-FH-43012-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2835 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 8.2 | CML-5 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.6 | 3 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.26 |  | 8.3 | 7.6 | 8.5 | 8.4 | 0.40825
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-4 | 100-WC-40027-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 836 |  | 2014-04-02 09:00 | 2014-04-02 10:00 | Check Corrosion Rate of 0.622mm/ yr |  | Nestor | 2016-04-01 | [32 empty] | 6.1 | CML-4 | CML: Fitting | 3 | 2019-01-28 | 2019-04-06 | 2014-04-02 09:00 | 2.5 | 0.62153 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 6 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 6.2 | 5.5 | 6.4 | 0.40825
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44001-01C02-P | CML-20 | 80-PW-44001-01C02-P CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23229 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.7 | CML-20 | CML: Fitting | 3 | 2043-12-23 | 2047-07-14 | 2015-05-11 07:00 | 2.5 | 0.09777 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0.87321 | 6.4 | 5.6 | 5.5 | 5.3 | 0.48305
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-5 | 50-DC-57056-03C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1137 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.575 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.52 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.6 | 6.6 | 6.6 | 6.5 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57019-01C02 | CML-7 | 50-DC-57019-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2415 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 6.6 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.5 | 9 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.7 | 6.5 | 6.5 | 0.11547
CG04 | Montara_Topside | Yes | Flare (43) | Pipework | 50-CG-38452-09C02-P | CML-10 | 50-CG-38452-09C02-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2509 | Rope Access | 2014-03-24 13:00 | 2014-03-24 14:30 | [36 empty] | 7.3 | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 200 | 6.35 | 200-FH-43504-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7.9 | 7.1 | 7 | 0.40825
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44015-01X01 | CML-13 | 50-PW-44015-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 22718 | Rope Access | 2015-04-28 07:00 | 2015-04-28 15:00 | [36 empty] | 5.375 | CML-13 | CML: Reducing Tee | 3 | 2030-06-17 | 2032-04-15 | 2015-04-28 07:00 | 2.5 | 0.17823 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-PW-44015-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0 | 5.2 | 5.5 | 5.4 | 5.4 | 0.12583
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-12 | 100-DC-57037-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2363 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 6.775 | CML-12 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.5 | 12 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 7.1 | 6.7 | 6.8 | 0.25
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-8 | 100-DC-57037-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2359 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 6.85 | CML-8 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.5 | 9 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.1 | 7 | 6.8 | 6.5 | 0.26458
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-1 | 100-DC-57037-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2352 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 6.75 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.5 | 9 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.7 | 6.7 | 7.1 | 6.5 | 0.25166
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-24 | 100-DC-57307-01C03 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 2332 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.597mm/ yr | [35 empty] | 6.9 | CML-24 | CML: type TBC | 6 | 2015-09-30 | 2015-09-26 | 2014-03-17 13:00 | 2.5 | 2.5969 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 6.5 | 3 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 6.5 | 6.8 | 7.3 | 0.33665
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-23 | 100-DC-57307-01C03 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 2331 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.597mm/ yr | [35 empty] | 6.75 | CML-23 | CML: type TBC | 6 | 2015-09-30 | 2015-09-26 | 2014-03-17 13:00 | 2.5 | 2.5969 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.5 | 6 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 6.7 | 6.5 | 6.8 | 0.20817
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-41 | 200-PL-20019-01C02 CML-41 |  | FPSO 2014 | Pipe Wall Thickness | 21292 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.225 | CML-41 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.2 | 7.6 | 6.7 | 7.4 | 0.38622
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20010-01C02-P | CML-9 | 200-PL-20010-01C02-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 23809 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.825 | CML-9 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 40 | 6.35 | 200-PL-20010-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.8 | 6.9 | 6.9 | 6.7 | 0.095743
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-1 | 50-CG-38458-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23729 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 4.9 | CML-1 | CML: Elbow | 3 | 2019-05-01 | 2019-12-19 | 2015-10-30 07:00 | 2.5 | 0.51356 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.3 | 3 O'Clock | 50 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 5.1 | 4.3 | 5 | 5.2 | 0.40825
PG05 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 250-PG-23003-06C02-PA | CML-17 | 250-PG-23003-06C02-PA CML-17 |  | FPSO 2013 | Pipe Wall Thickness | 10545 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.4 | CML-17 | CML: type TBC | 3 | 2015-04-22 | 2015-04-17 | 2013-11-16 | 2.5 | 1.6077 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.5 | 5.7 | 4.8 | 5.6 | 0.40825
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56028-01C02 | CML-4 | 80-DH-56028-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20901 | Rope Access | 2014-05-22 07:00 | 2014-05-22 08:00 | [36 empty] | 5.6 | CML-4 | CML: Equal Tee | 3 | 2019-05-09 | 2020-01-16 | 2014-05-22 07:00 | 2.5 | 0.50339 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-DH-56028-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5.7 | 5.9 | 5 | 0.40825
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8882 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.3 | CML-6 | CML: type TBC | 3 | 2028-12-11 | 2030-08-11 | 2015-02-25 09:30 | 2.5 | 0.19562 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.4 | 5.2 | 0.11547
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56021-01C02 | CML-1 | 80-DH-56021-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 3478 | Rope Access | 2014-05-14 07:00 | 2014-05-14 08:00 | [36 empty] | 5.9 | CML-1 | CML: type TBC | 3 | 2028-05-18 | 2030-02-13 | 2014-05-14 07:00 | 2.5 | 0.19969 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-DH-56021-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6 | 6.1 | 5.3 | 6.2 | 0.40825
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-14 | 50-WC-40032-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 1248 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 5.875 | CML-14 | CML: type TBC | 3 | 2074-11-29 | 2081-07-05 | 2014-03-23 13:00 | 2.5 | 0.0494 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 3 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 5.5 | 6.1 | 6.2 | 0.3304
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-8 | 50-DH-56137-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21092 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6 | CML-8 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 5.6 | 9 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 6.4 | 6.3 | 5.6 | 0.40825
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8876 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 08:00 | 2015-02-25 09:00 | [36 empty] | 5.3 | CML-8 | CML: type TBC | 3 | 2028-12-10 | 2030-08-11 | 2015-02-25 08:00 | 2.5 | 0.19564 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AU-63019-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.4 | 5.4 | 0.11547
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43303-01C02 | CML-2 | 50-FL-43303-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20458 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | [36 empty] | 6.1 | CML-2 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 9 O'Clock | 50 | 5.54 | 50-FL-43303-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.7 | 6 | 5.9 | 5.8 | 0.40825
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2888 | Rope Access | 2014-04-25 07:00 | 2014-04-25 08:00 | [36 empty] | 6.6 | CML-3 | CML: Elbow | 3 | 2023-04-21 | 2023-03-25 | 2014-04-25 07:00 | 2.5 | 0.38914 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 250 | 6.35 | 250-FL-43170-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 6.7 | 6 | 6.8 | 0.40825
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43026-01C02 | CML-20 | 150-FH-43026-01C02 CML-20 |  | FPSO 2015 | Pipe Wall Thickness | 23519 | Re-check | 2015-07-28 07:00 | 2015-07-28 15:00 | [36 empty] | 6.9 | CML-20 | CML: Fitting | 3 | 2029-08-05 | 2026-09-05 | 2015-07-28 07:00 | 1.03 | 0.37553 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.3 | 12 O'Clock | 150 | 7.11 | 150-FH-43026-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.27 | 0.69194 | 6.3 | 7.1 | 7.2 | 7 | 0.40825
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-6 | 100-FG-45001-09C02 CML-6 | Yes | FPSO 2015 | Pipe Wall Thickness | 23311 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.1 | CML-6 | CML: type TBC | 3 | 2034-12-09 | 2029-03-13 | 2015-07-11 07:00 | 4.7 | 0.29852 | A3: Inside Quadrant |  | 8.13 | 4.7 | 6.415 | 10.5 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 | -0.24121 | 11.2 | 11.4 | 10.5 | 11.3 | 0.40825
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43084-01C02 | CML-5 | 150-FL-43084-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2570 | Rope Access | 2014-04-08 07:30 | 2014-04-08 08:30 | [36 empty] | 9.1 | CML-5 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-04-08 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 8.5 | 6 O'Clock | 150 | 7.11 | 150-FL-43084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6 |  | 9.3 | 9.2 | 8.5 | 9.4 | 0.40825
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38486-09C02-P |  | 80-CG-38486-09C02-P |  | FPSO 2015 | Pipe Wall Thickness | 23654 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 10.4 | 80-CG-38486-01C02-H | Piping | 3 | 2043-04-25 |  | 2015-10-28 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 10 | 12 O'Clock | 80 | 5.49 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10 | 10.1 | 10.7 | 10.8 | 0.40825
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-42 | 300-PF-20501-03C03-P CML-42 |  | FPSO 2014 | Pipe Wall Thickness | 21718 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.4 | CML-42 | CML: type TBC | 6 | 2086-07-01 | 2073-05-09 | 2014-09-28 07:00 | 4.9 | 0.12813 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.1 | 6 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 15 | 14.3 | 14.1 | 14.2 | 0.40825
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-2 | 300-WS-50806-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10741 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.125 | CML-2 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 16.7 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.2 |  | 17.7 | 16.7 | 16.9 | 17.2 | 0.43493
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-13 | 80-DH-56074-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20958 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 5.2 | CML-13 | CML: Elbow | 3 | 2017-02-12 | 2017-07-19 | 2014-05-24 07:00 | 2.5 | 0.80704 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.7 | 12 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.7 | 5.2 | 5.2 | 0.40825
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44035-01C02-P | CML-3 | 80-PW-44035-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21926 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 5.7 | CML-3 | CML: Elbow | 3 | 2034-10-03 | 2037-03-28 | 2014-10-09 07:00 | 2.5 | 0.14002 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 20 | 5.49 | 80-PW-44035-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 6 | 5.3 | 5.3 | 6.2 | 0.46904
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40054-01C02 | CML-2 | 50-WC-40054-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2093 |  | 2014-03-28 11:30 | 2014-03-28 12:00 | [36 empty] | 5.85 | CML-2 | CML: type TBC | 3 | 2075-12-09 | 2082-08-25 | 2014-03-28 11:30 | 2.5 | 0.04859 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-WC-40054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.8 | 5.9 | 5.5 | 6.2 | 0.28868
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 250-PG-23039-06D01 | CML-1 | 250-PG-23039-06D01 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10703 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 9.975 | CML-1 | CML: type TBC | 1 | 2035-06-01 | 2034-04-16 | 2013-11-07 | 5.6 | 0 | A3: Inside Quadrant |  | 6.8 | 5.6 | 5.7125 | 9.6 | 6 O'Clock | 250 | 7.8 | 250-PG-23039-06D01 | 30 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 9.9 | 10.1 | 9.6 | 10.3 | 0.29861
VA01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-VA-43519-01C02 | CML-2 | 50-VA-43519-01C02 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7755 |  | 2015-01-11 09:30 | 2015-01-11 10:30 | [36 empty] | 5.7 | CML-2 | CML: Reducer | 3 | 2033-11-08 | 2036-01-18 | 2015-01-11 09:30 | 2.5 | 0.14863 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-VA-43519-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 6 | 6.1 | 0.40825
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57029-01C02 | CML-2 | 50-DC-57029-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20275 | Rope Access | 2014-05-26 07:00 | 2014-05-26 08:00 | Check Corrosion Rate of 1.158mm/ yr | [35 empty] | 4.6 | CML-2 | CML: type TBC | 3 | 2017-11-16 | 2017-03-28 | 2014-05-26 07:00 | 0.37 | 1.1581 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 4.4 | 12 O'Clock | 50 | 5.54 | 50-DC-57029-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.03 |  | 4.4 | 4.7 | 4.5 | 4.8 | 0.18257
PW03 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7754 |  | 2015-01-11 09:30 | 2015-01-11 10:30 | [36 empty] | 5.3 | CML-1 | CML: Elbow | 3 | 2027-11-04 | 2029-05-23 | 2015-01-11 09:30 | 2.5 | 0.21055 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-VA-43519-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.4 | 5.4 | 0.11547
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-13 | 50-WC-40032-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 1247 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 5.8 | CML-13 | CML: type TBC | 3 | 2074-11-29 | 2081-07-05 | 2014-03-23 13:00 | 2.5 | 0.0494 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.7 | 5.9 | 5.5 | 6.1 | 0.2582
PG05 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-PG-23003-06C02-PA | CML-2 | 250-PG-23003-06C02-PA CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1525 |  | 2014-04-03 11:00 | 2014-04-03 12:00 | [36 empty] | 5.8 | CML-2 | CML: Fitting | 3 | 2031-08-20 | 2033-08-03 | 2014-04-03 11:00 | 2.5 | 0.16674 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-WC-40052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.2 | 5.5 | 6.1 | 0.40825
PG05 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2095 |  | 2014-03-28 11:30 | 2014-03-28 12:00 | [36 empty] | 5.8 | CML-4 | CML: type TBC | 3 | 2031-04-12 | 2033-03-12 | 2014-03-28 11:30 | 2.5 | 0.17006 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 6 O'Clock | 50 | 5.54 | 50-WC-40054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.2 | 5.5 | 5.4 | 6.1 | 0.40825
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-20 | 300-WS-50806-1LC CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 10759 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.175 | CML-20 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 16.8 | 9 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.3 |  | 16.9 | 17.4 | 17.6 | 16.8 | 0.38622
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-19 | 300-WS-50806-1LC CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 10758 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.125 | CML-19 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A3: Inside Quadrant |  | 7.31 | 2.5 | 4.905 | 16.8 | 6 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.3 |  | 16.9 | 17.2 | 16.8 | 17.6 | 0.3594
CG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-CG-38459-09C02-P | CML-21 | 80-CG-38459-09C02-P CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 10971 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 18.1 | CML-21 | CML: Elbow | 6 | 2103-11-30 | 2088-08-29 | 2014-01-09 | 5.22 | 0 | A1: Outside Quadrant |  | 8.27 | 5.22 | 6.745 | 17.5 | 12 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.28 |  | 17.5 | 18.3 | 18.2 | 18.4 | 0.40825
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20048-03C03-P | CML-15 | 300-PG-20048-03C03-P CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21485 | Protective mesh removed | 2014-06-28 09:30 | 2014-06-28 10:45 | [36 empty] | 17.9 | CML-15 | CML: Reducer | 6 | 2107-02-11 | 2090-04-05 | 2014-06-28 09:30 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 17.6 | 12 O'Clock | 300 | 14.27 | 300-PG-20048-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.7 |  | 17.6 | 17.8 | 18.5 | 17.7 | 0.40825
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-14 | 300-WS-50806-1LC CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 10753 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.2 | CML-14 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A4: Left Quadrant |  | 7.31 | 2.5 | 4.905 | 16.8 | 9 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.3 |  | 17.7 | 17.2 | 17.1 | 16.8 | 0.37417
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20061-01C03-P | CML-2 | 80-PG-20061-01C03-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21674 | Protective mesh removed | 2014-06-26 11:00 | 2014-06-26 12:00 | [36 empty] | 20.6 | CML-2 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-06-26 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 20.2 | 6 O'Clock | 80 | 11.13 | 80-PG-20061-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 |  | 20.3 | 20.9 | 20.2 | 21 | 0.40825
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-1 | 300-WS-50806-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10740 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.2 | CML-1 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 16.8 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.3 |  | 17.5 | 16.8 | 17.4 | 17.1 | 0.31623
AD02 | Montara_Topside | No | Compressed Air (63) | Pipework | 0100-AI-63L9004-AS20-00 | CML-3 | 0100-AI-63L9004-AS20-00 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24279 | No pipe material class specified, elbow is a cast fitting, reading taken adjacent on pipe | 2016-02-24 07:00 | 2016-02-24 15:00 | [36 empty] | 6.625 | CML-3 |  | 0 | 2021-10-25 |  | 2016-02-24 07:00 |  | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.6 | 9 O'Clock | 25 | 3.38 | 0100-AI-63L9004-AS20-00 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.6 | 6.6 | 6.6 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-6 | 100-WC-40027-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 838 |  | 2014-04-02 09:00 | 2014-04-02 10:00 | Check Corrosion Rate of 0.622mm/ yr |  | Nestor | 2016-04-01 | [32 empty] | 5.8 | CML-6 | CML: Pipe Length | 3 | 2019-01-28 | 2019-04-06 | 2014-04-02 09:00 | 2.5 | 0.62153 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.5 | 6 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6 | 6 | 5.5 | 5.7 | 0.24495
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23002-03C03-A | CML-5 | 300-PG-23002-03C03-A CML-5 |  | FPSO 2013 | Pipe Wall Thickness | 10101 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 13.8 | CML-5 | CML: Elbow | 6 | 2017-12-10 | 2017-03-07 | 2013-11-07 | 5.22 | 1.9972 | A4: Left Quadrant |  | 8.27 | 5.22 | 6.745 | 13.4 | 9 O'Clock | 40 | 14.27 | 300-PG-23002-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.18 |  | 14.2 | 14.1 | 13.5 | 13.4 | 0.40825
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 300-WS-50806-1LC | CML-15 | 300-WS-50806-1LC CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 10754 | Rope Access | 2014-01-03 | 2014-01-03 | [36 empty] | 17.125 | CML-15 | CML: type TBC | 3 | 2091-07-06 | 2067-06-18 | 2014-01-03 | 2.5 | 0 | A2: Right Quadrant |  | 7.31 | 2.5 | 4.905 | 17 | 3 O'Clock | 300 | 10.31 | 300-WS-50806-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.5 |  | 17.3 | 17 | 17.1 | 17.1 | 0.12583
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50801-1LC | CML-1 | 500-WS-50801-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10775 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 11.675 | CML-1 | CML: type TBC | 3 | 2015-03-27 | 2014-07-17 | 2014-01-03 | 2.5 | 6.9113 | A2: Right Quadrant |  | 12.09 | 2.5 | 7.295 | 11 | 3 O'Clock | 500 | 15.09 | 500-WS-50801-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.5 |  | 11.3 | 11 | 12.3 | 12.1 | 0.62383
FH01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-FH-43507-01C02 | CML-15 | 100-FH-43507-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21612 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 10.1 | CML-15 | CML: Reducing Tee | 3 | 2059-02-11 | 2051-04-06 | 2014-06-28 13:00 | 3.61 | 0 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 9.8 | 12 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.19 |  | 9.8 | 10 | 10.7 | 9.9 | 0.40825
DH01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-DH-56137-01C02 | CML-21 | 50-DH-56137-01C02 CML-21 |  | FPSO 2015 | Pipe Wall Thickness | 23449 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 | [35 empty] | Low alarm breach | 18.05 | CML-21 | CML: Pipe Length | 3 | 2024-04-05 | 2019-09-12 | 2015-07-23 07:00 | 2.5 | 1.745 | A1: Outside Quadrant |  | 18.44 | 2.5 | 10.47 | 17.7 | 12 O'Clock | 300 | 21.44 | 400-WC-40500-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.2 | 3.4043 | 17.7 | 18.1 | 18.6 | 17.8 | 0.40415
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42313-01S01 | CML-3 | 40-CI-42313-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7518 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 8.075 | CML-3 | CML: type TBC | 1 | 2029-06-11 | 2024-09-11 | 2015-04-13 07:00 | 2.5 | 0.2893 | A3: Inside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.6 | 6 O'Clock | 40 | 7.14 | 40-CI-42313-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 9 | 8.4 | 6.6 | 8.3 | 1.0308
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42313-01S01 | CML-2 | 40-CI-42313-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7517 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.9 | CML-2 | CML: type TBC | 1 | 2029-06-11 | 2024-09-11 | 2015-04-13 07:00 | 2.5 | 0.2893 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.6 | 12 O'Clock | 40 | 7.14 | 40-CI-42313-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 8.4 | 8.7 | 7.9 | 0.92736
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42313-01S01 | CML-1 | 40-CI-42313-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7516 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.6 | CML-1 | CML: type TBC | 1 | 2029-06-11 | 2024-09-11 | 2015-04-13 07:00 | 2.5 | 0.2893 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.6 | 12 O'Clock | 40 | 7.14 | 40-CI-42313-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.6 | 8.6 | 7.6 | 0.8165
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42312-01S01 | CML-3 | 40-CI-42312-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7512 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 8.05 | CML-3 | CML: type TBC | 1 | 2029-06-11 | 2024-09-11 | 2015-04-13 07:00 | 2.5 | 0.2893 | A3: Inside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.6 | 6 O'Clock | 40 | 7.14 | 40-CI-42312-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 9 | 8.4 | 6.6 | 8.2 | 1.0247
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42312-01S01 | CML-2 | 40-CI-42312-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7511 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 8.15 | CML-2 | CML: type TBC | 1 | 2029-06-11 | 2024-09-11 | 2015-04-13 07:00 | 2.5 | 0.2893 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.6 | 12 O'Clock | 40 | 7.14 | 40-CI-42312-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 8.4 | 9.2 | 8.4 | 1.1
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-5 | 250-PG-23003-06C02-PA CML-5 | Yes | FPSO 2014 | Pipe Wall Thickness | 24243 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.4667 | CML-5 | CML: Pipe Length | 3 | 2085-04-24 | 2073-10-17 | 2014-09-24 07:00 | 7.9 | 0 | A3: Inside Quadrant |  | 12.09 | 7.9 | 9.0519 | 15.1 | 6 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 15.9 | 15.4 | 15.1 |  | 0.40415
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43453-01C02 | CML-15 | 150-FL-43453-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2259 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 6.65 | CML-15 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.1 | 9 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.9 | 6.6 | 7 | 6.1 | 0.40415
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-12 | 400-FH-43500-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 5648 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 7.85 | CML-12 | CML: type TBC | 3 | 2027-01-11 | 2025-03-26 | 2014-06-21 07:00 | 2.5 | 0.39788 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7.5 | 12 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8.4 | 7.6 | 7.9 | 0.40415
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50801-1LC | CML-5 | 500-WS-50801-1LC CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10779 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 11.9 | CML-5 | CML: type TBC | 3 | 2015-06-07 | 2014-08-31 | 2014-01-03 | 2.5 | 6.2354 | A2: Right Quadrant |  | 12.09 | 2.5 | 7.295 | 11.4 | 3 O'Clock | 500 | 15.09 | 500-WS-50801-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.6 | 11.4 | 12.5 | 12.1 | 0.49666
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50801-1LC | CML-3 | 500-WS-50801-1LC CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10777 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 11.925 | CML-3 | CML: type TBC | 3 | 2015-06-28 | 2014-09-13 | 2014-01-03 | 2.5 | 6.0664 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 11.5 | 9 O'Clock | 500 | 15.09 | 500-WS-50801-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 12.2 | 12.2 | 11.8 | 11.5 | 0.34034
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50801-1LC | CML-4 | 500-WS-50801-1LC CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10778 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 12 | CML-4 | CML: type TBC | 3 | 2015-07-20 | 2014-09-26 | 2014-01-03 | 2.5 | 5.8975 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 11.6 | 9 O'Clock | 500 | 15.09 | 500-WS-50801-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  |  | 11.7 | 12.7 | 11.6 | 0.60828
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63032-01E01 | CML-2 | 25-AI-63032-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8404 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.825 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-01-30 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 25 | 6.35 | 25-AI-63032-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 7.4 | 6.6 | 6.6 | 0.38622
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63032-01E01 | CML-1 | 25-AI-63032-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8403 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.6 | CML-1 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 25 | 6.35 | 25-AI-63032-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.6 | 6.6 | 6.6 | 0
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63037-01E01 | CML-6 | 50-AI-63037-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8402 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 6.925 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-30 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 3 O'Clock | 50 | 5.54 | 50-AI-63037-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.6 | 7.2 | 7.3 | 0.37749
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-18 | 50-AI-63450-01E01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8337 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.75 | CML-18 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 3 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.6 | 6.9 | 6.8 | 0.1291
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53003-01E01 | CML-3 | 50-WD-53003-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8293 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.75 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 3 O'Clock | 50 | 5.54 | 50-WD-53003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.6 | 6.7 | 6.9 | 0.1291
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-11 | 50-WD-53010-01E01 CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 8254 |  | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.875 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 12 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7 | 7.2 | 6.7 | 0.27538
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-1 | 50-WD-53014-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8216 | Reducing Hose Coupling | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.7 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.7 | 6.8 | 6.6 | 0.08165
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 50-OL-69006-01S01 | CML-2 | 50-OL-69006-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8191 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.775 | CML-2 | CML: type TBC | 1 | 2043-10-24 | 2037-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 4.54 | 2.5 | 3.1738 | 6.6 | 6 O'Clock | 50 | 5.54 | 50-OL-69006-01S01 | 80S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.2 | 6.6 | 6.7 | 0.28723
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50801-1LC | CML-2 | 500-WS-50801-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10776 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 12.175 | CML-2 | CML: type TBC | 3 | 2015-09-05 | 2014-10-25 | 2014-01-03 | 2.5 | 5.5595 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 11.8 | 9 O'Clock | 500 | 15.09 | 500-WS-50801-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.3 | 12.2 | 12.4 | 11.8 | 0.263
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-16 | 50-WD-53007-01E01 CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 8155 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.75 | CML-16 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 3 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.6 | 6.8 | 7 | 0.19149
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-14 | 50-WD-53007-01E01 CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8153 | Reducing Hose Coupling | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.625 | CML-14 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.7 | 6.6 | 6.6 | 0.05
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-8 | 50-WD-53007-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8147 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.75 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 6.6 | 6.8 | 6.6 | 0.19149
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-6 | 50-WD-53007-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8145 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.825 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.4 | 6.7 | 6.6 | 0.38622
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-5 | 50-WD-53007-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8144 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.975 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.3 | 6.7 | 6.6 | 7.3 | 0.37749
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-2 | 50-WD-53007-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8141 |  | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.8 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.9 | 6.9 | 6.6 | 6.8 | 0.14142
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50801-1LC | CML-7 | 500-WS-50801-1LC CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10781 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 13.25 | CML-7 | CML: type TBC | 3 | 2015-10-29 | 2014-11-27 | 2014-01-03 | 2.5 | 5.2215 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 12 | 9 O'Clock | 500 | 15.09 | 500-WS-50801-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.8 | 13.9 | 14.3 | 12 | 1.0472
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43004-01C02 | CML-6 | 200-FH-43004-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12546 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 7.85 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.5 | 12 O'Clock | 200 | 6.35 | 200-FH-43004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 7.6 | 8.4 | 7.9 | 0.40415
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43125-01C02 | CML-7 | 200-FH-43125-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2761 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 7.35 | CML-7 | CML: Elbow | 3 | 2063-07-07 | 2057-06-06 | 2014-03-13 09:00 | 1.34 | 0 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 7 | 3 O'Clock | 200 | 6.35 | 200-FH-43125-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.66 |  | 7.9 | 7 | 7.1 | 7.4 | 0.40415
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-25 | 100-FG-45001-09C02 CML-25 | Yes | FPSO 2015 | Pipe Wall Thickness | 23330 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 10.95 | CML-25 | CML: type TBC | 3 | 2039-01-01 | 2032-03-05 | 2015-07-11 07:00 | 4.7 | 0.25114 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.6 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 | -0.36181 | 11.5 | 10.6 | 11 | 10.7 | 0.40415
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-5 | 250-PW-20041-03C03-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21414 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.55 | CML-5 | CML: Fitting | 6 | 2022-12-25 | 2021-07-15 | 2014-07-12 07:30 | 4.1 | 0.89832 | A4: Left Quadrant |  | 6.7 | 4.1 | 5.4 | 11.7 | 9 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 13.3 | 12.6 | 12.6 | 11.7 | 0.65574
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 150-WC-40503-1CG | CML-1 | 150-WC-40503-1CG CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8630 | Rope Access / Material Class Not Selectable. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-02-10 09:30 | 2015-02-10 10:30 |  |  | Administrator | 2015-09-08 12:45 | [32 empty] | 11.5 | CML-1 | CML: Pipe Length | 3 | 2098-02-09 | 2070-10-05 | 2015-02-10 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 7.97 | 2.5 | 5.235 | 11.3 | 6 O'Clock | 150 | 10.97 | 150-WC-40503-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 11.6 | 11.4 | 11.3 | 11.7 | 0.18257
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-14 | 300-PG-20506-03C03-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 13228 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.05 | CML-14 | CML: type TBC | 6 | 2021-09-12 | 2020-03-17 | 2014-02-04 15:00 | 4.9 | 1.1304 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.5 | 3 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 |  | 14 | 13.5 | 14.3 | 14.4 | 0.40415
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-1 | 300-PF-20500-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21621 | Protective mesh removed | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 16.25 | CML-1 | CML: Equal Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-09-27 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 15.9 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11 |  | 15.9 | 16 | 16.8 | 16.3 | 0.40415
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML - 1 | 80-DH-56004-01C02 CML - 1 | yes | FPSO 2015 | Pipe Wall Thickness | 22610 | Rope Access | 2015-04-26 07:00 | 2015-04-26 15:00 | [36 empty] | 3.65 | CML - 1 | CML: Equal Tee | 0.5 | 2008-01-06 | 2014-04-07 | 2015-04-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 1.5 | 2.5 | 1.875 | 3.3 | 6 O'Clock | 80 | 2 | 0300-WF-71L9003-AK11-00 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.4 | 4.2 | 3.3 | 3.7 | 0.40415
FG02 | Montara_Topside | Yes | Separation (20) | Pipework | 25-FG-45455-01C02-E | CML-12 | 25-FG-45455-01C02-E CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 21815 |  | 2014-10-11 07:00 | 2014-10-11 15:00 | [36 empty] | 6.35 | CML-12 | CML: Pipe Length | 3 | 2253-01-17 | 2260-12-16 | 2014-10-11 07:00 | 2.5 | 0.01468 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6 | 3 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.7 | 6.7 | 0.40415
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45051-03C02 | CML-6 | 150-FG-45051-03C02 CML-6 | yes | FPSO 2016 | Pipe Wall Thickness | 24380 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.85 | CML-6 | CML: Elbow | 3 | 2030-07-29 | 2027-07-31 | 2016-06-06 07:00 | 2.5 | 0.26846 | A1: Outside Quadrant |  | 4.11 | 2.5 | 3.305 | 6.3 | 12 O'Clock | 150 | 7.11 | 150-FG-45051-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7.1 | 6.8 | 7.2 | 0.40415
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50801-1LC | CML-8 | 500-WS-50801-1LC CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10782 | Deck Level | 2014-01-03 | 2014-01-03 | [36 empty] | 13.35 | CML-8 | CML: type TBC | 3 | 2016-08-31 | 2015-06-06 | 2014-01-03 | 2.5 | 3.8697 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 12.8 | 12 O'Clock | 500 | 15.09 | 500-WS-50801-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.3 |  | 12.8 | 13.3 | 13.4 | 13.9 | 0.45092
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44036-01C02-P | CML-2 | 80-PW-44036-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21954 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.525 | CML-2 | CML: Reducing Tee | 3 | 2034-10-19 | 2037-04-15 | 2014-10-10 07:00 | 2.5 | 0.13974 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 80 | 5.49 | 80-PW-44036-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.3 | 6 | 5.5 | 0.3304
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43037-01C02 | CML-4 | 200-FH-43037-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12673 |  | 2014-02-06 11:00 | 2014-02-06 13:00 | [36 empty] | 6.7667 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 3 O'Clock | 200 | 6.35 | 200-FH-43037-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 7.2 | 6.4 |  | 6.7 | 0.40415
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-22 | 50-PF-20301-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 3020 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.45 | CML-22 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.9 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.29 | 0 | 9.8 | 9.7 | 8.9 | 9.4 | 0.40415
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20301-03C03-P | CML-22 | 50-PF-20301-03C03-P CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 22299 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 9.45 | CML-22 | CML: Elbow | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.9 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.29 |  | 9.8 | 9.7 | 8.9 | 9.4 | 0.40415
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-23 | 250-PW-20041-03C03-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21432 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.225 | CML-23 | CML: Fitting | 6 | 2022-12-25 | 2021-07-15 | 2014-07-12 07:30 | 4.1 | 0.89832 | A3: Inside Quadrant |  | 6.7 | 4.1 | 5.4 | 11.7 | 6 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 12.3 | 11.8 | 11.7 | 13.1 | 0.63966
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43136-01C02 | CML-6 | 150-FH-43136-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2767 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 6.55 | CML-6 | CML: Elbow | 3 | 2018-08-20 | 2017-09-11 | 2014-03-13 09:00 | 1.03 | 1.1639 | A3: Inside Quadrant |  | 4.11 | 1.03 | 2.1256 | 6.2 | 6 O'Clock | 150 | 7.11 | 150-FH-43136-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.17 |  | 7.1 | 6.6 | 6.2 | 6.3 | 0.40415
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50801-1LC | CML-6 | 500-WS-50801-1LC CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10780 | Deck Level | 2014-01-03 | 2014-01-03 | [36 empty] | 13.675 | CML-6 | CML: type TBC | 3 | 2016-12-23 | 2015-08-15 | 2014-01-03 | 2.5 | 3.5317 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 13 | 9 O'Clock | 500 | 15.09 | 500-WS-50801-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.5 |  | 13.6 | 14.1 | 14 | 13 | 0.49917
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50802-1LC | CML-3 | 500-WS-50802-1LC CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10828 | Deck Level | 2014-01-04 | 2014-01-04 | [35 empty] | Low alarm breach | 12.3 | CML-3 | CML: type TBC | 3 | 2015-09-08 | 2014-10-30 | 2014-01-04 | 2.9 | 5.3657 | A2: Right Quadrant |  | 12.09 | 2.9 | 7.495 | 11.9 | 3 O'Clock | 500 | 15.09 | 500-WS-50802-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 12.4 | 11.9 | 12.7 | 12.2 | 0.33665
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50802-1LC | CML-4 | 500-WS-50802-1LC CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10829 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 12.325 | CML-4 | CML: type TBC | 3 | 2015-12-03 | 2014-12-23 | 2014-01-04 | 2.9 | 4.8611 | A4: Left Quadrant |  | 12.09 | 2.9 | 7.495 | 12.2 | 9 O'Clock | 500 | 15.09 | 500-WS-50802-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.5 | 12.3 | 12.3 | 12.2 | 0.12583
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-8 | 100-FG-45001-09C02 CML-8 | Yes | FPSO 2015 | Pipe Wall Thickness | 23313 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 18.05 | CML-8 | CML: type TBC | 3 | 2077-09-17 | 2060-07-24 | 2015-07-11 07:00 | 4.7 | 0 | A1: Outside Quadrant |  | 8.13 | 4.7 | 6.415 | 17.5 | 12 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.8 | -0.72362 | 17.5 | 18.3 | 18 | 18.4 | 0.40415
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-22 | 200-PW-44018-01X01 CML-22 |  | FPSO 2015 | Pipe Wall Thickness | 23257 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.35 | CML-22 | CML: Pipe Length | 3 | 2030-10-11 | 2032-08-22 | 2015-05-11 07:00 | 2.5 | 0.17496 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0.089024 | 5.4 | 5.4 | 5.2 | 5.4 | 0.1
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23402-01C02-PA | CML-7 | 150-PG-23402-01C02-PA CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5615 |  | 2014-06-20 09:30 | 2014-06-20 11:00 | [36 empty] | 6.975 | CML-7 | CML: Fitting | 3 |  |  | 2014-06-20 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.6 | 3 O'Clock | 150 |  | 150-PG-23402-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.9 | 6.6 | 7.2 | 7.2 | 0.28723
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-31 | 200-PG-23007-09C03-PA CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 20718 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 |  |  | John Wilson | 2017-03-23 09:53 | [32 empty] | 20.65 | CML-31 | CML: Equal Tee | 6 | 2048-07-09 | 2041-02-04 | 2014-06-30 13:00 | 10.22 | 0.29604 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 20.3 | 3 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.08 |  | 20.3 | 20.3 | 21 | 21 | 0.40415
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PG-20044-03C03-P | CML-1 | 80-PG-20044-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21449 | Protective mesh removed | 2014-06-29 09:30 | 2014-06-29 11:00 | [36 empty] | 11.25 | CML-1 | CML: Elbow | 6 | 2053-10-29 | 2047-09-02 | 2014-06-29 09:30 | 2.5 | 0.2134 | A1: Outside Quadrant |  | 5.13 | 2.5 | 3.815 | 10.9 | 6 O'Clock | 80 | 11.13 | 80-PG-20044-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 |  | 10.9 | 11.6 | 10.9 | 11.6 | 0.40415
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-19 | 50-CG-38452-09C02-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21351 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 8.7333 | CML-19 | CML: Pipe Length | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A4: Left Quadrant |  | 5.18 | 3.61 | 4.395 | 8.3 | 9 O'Clock | 200 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.69 |  | 9.1 | 8.8 |  | 8.3 | 0.40415
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-17 | 250-WC-40017-01C02 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 2080 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | Check Corrosion Rate of 0.911mm/ yr | [35 empty] | 6.55 | CML-17 | CML: type TBC | 3 | 2017-08-21 | 2017-08-09 | 2014-03-28 09:30 | 2.5 | 0.9113 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.8 | 7.1 | 5.6 | 6.7 | 0.65574
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43114-01C02 | CML-4 | 200-FH-43114-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12812 |  | 2014-02-01 12:00 | 2014-02-01 14:00 | [36 empty] | 9.2667 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-01 12:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.9 | 6 O'Clock | 200 | 6.35 | 200-FH-43114-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 9.2 | 9.7 | 8.9 |  | 0.40415
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-39 | 200-PW-44018-01X01 CML-39 |  | FPSO 2015 | Pipe Wall Thickness | 8963 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.35 | CML-39 | CML: type TBC | 3 | 2028-12-20 | 2030-08-21 | 2015-02-26 09:00 | 2.5 | 0.19532 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.4 | 5.4 | 5.2 | 0.1
VA01 | Montara_Topside | Yes | Main Power (80) | Pipework | 100-VA-80006-01C02 | CML-3 | 100-VA-80006-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2172 | Rope Access | 2014-03-30 13:00 | 2014-03-30 14:00 | [36 empty] | 5.725 | CML-3 | CML: type TBC | 3 | 2017-06-19 | 2017-08-06 | 2014-03-30 13:00 | 2.5 | 0.86864 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 9 O'Clock | 100 | 6.02 | 100-VA-80006-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.9 | 5.5 | 6.2 | 5.3 | 0.40311
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50802-1LC | CML-1 | 500-WS-50802-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10826 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 12.525 | CML-1 | CML: type TBC | 3 | 2015-12-03 | 2014-12-23 | 2014-01-04 | 2.9 | 4.8611 | A2: Right Quadrant |  | 12.09 | 2.9 | 7.495 | 12.2 | 3 O'Clock | 500 | 15.09 | 500-WS-50802-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.5 | 12.2 | 12.7 | 12.7 | 0.23629
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56054-01C02 | CML-1 | 80-DH-56054-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20943 | Rope Access | 2014-05-17 08:00 | 2014-05-17 09:00 | [36 empty] | 5.825 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-17 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 9 O'Clock | 80 | 5.49 | 80-DH-56054-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.6 | 5.8 | 6.4 | 5.5 | 0.40311
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-15 | 50-DH-56137-01C02 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21099 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.025 | CML-15 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 5.6 | 12 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.8 | 6.2 | 6.5 | 0.40311
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23064-09C02 | CML-1 | 50-PG-23064-09C02 CML-1 | Yes | FPSO 2013 | Pipe Wall Thickness | 10724 | Deck Level | 2013-11-19 | 2013-11-19 | [36 empty] | 8.425 | CML-1 | CML: type TBC | 3 | 2017-12-24 | 2016-10-17 | 2013-11-19 | 2.5 | 1.3661 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.1 | 3 O'Clock | 50 | 8.74 | 50-PG-23064-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.6 |  | 9 | 8.1 | 8.2 | 8.4 | 0.40311
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-9 | 300-PF-20001-03C03-P CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 21147 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 9.175 | CML-9 | CML: Elbow | 6 | 2015-09-30 | 2015-03-05 | 2014-07-16 07:30 | 2.5 | 5.0438 | A4: Left Quadrant |  | 8.27 | 2.5 | 5.385 | 8.6 | 9 O'Clock | 50 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.5 | 9.2 | 9.4 | 8.6 | 0.40311
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38008-01C02 | CML-1 | 50-CG-38008-01C02 CML-1 | Yes | FPSO 2015 | Pipe Wall Thickness | 8429 | Pipe schedule estimated due to no isometric drawings | 2015-01-31 10:00 | 2015-01-31 15:00 | [36 empty] | 10.425 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-31 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.1 | 12 O'Clock | 15 | 5.54 | 50-CG-38008-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.1 | 11 | 10.2 | 10.4 | 0.40311
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38472-01C02 | CML-8 | 50-CG-38472-01C02 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 23663 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 11.175 | CML-8 | CML: Reducing Tee | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 10.7 | 9 O'Clock | 50 | 5.54 | 50-CG-38472-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11 | 11.4 | 11.6 | 10.7 | 0.40311
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20301-03C03-P | CML-4 | 200-PG-20301-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5883 |  | 2014-06-25 14:00 | 2014-06-25 15:00 | [36 empty] | 13.175 | CML-4 | CML: Fitting | 6 | 2113-09-05 | 2095-07-18 | 2014-06-25 14:00 | 3.3 | 0.09369 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 12.6 | 9 O'Clock | 200 | 12.7 | 200-PG-20301-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 13.5 | 13.2 | 13.4 | 12.6 | 0.40311
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20301-03C03-P | CML-4 | 200-PG-20301-03C03-P CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21663 |  | 2014-06-25 14:00 | 2014-06-25 15:00 | [36 empty] | 13.175 | CML-4 | CML: Fitting | 6 | 2113-09-05 | 2095-07-18 | 2014-06-25 14:00 | 3.3 | 0.09369 | A4: Left Quadrant |  | 6.7 | 3.3 | 5 | 12.6 | 9 O'Clock | 200 | 12.7 | 200-PG-20301-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 13.5 | 13.2 | 13.4 | 12.6 | 0.40311
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57027-01C02 | CML-6 | 50-DC-57027-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1405 | Rope access | 2014-04-05 15:00 | 2014-04-05 16:00 | [36 empty] | 6.95 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 15:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 9 O'Clock | 50 | 5.54 | 50-DC-57027-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.2 | 7.2 | 6.8 | 6.6 | 0.3
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50802-1LC | CML-2 | 500-WS-50802-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10827 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 12.575 | CML-2 | CML: type TBC | 3 | 2016-02-09 | 2015-02-03 | 2014-01-04 | 2.9 | 4.5247 | A2: Right Quadrant |  | 12.09 | 2.9 | 7.495 | 12.4 | 3 O'Clock | 500 | 15.09 | 500-WS-50802-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.7 | 12.4 | 12.6 | 12.6 | 0.12583
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PL-20011-01C02-P | CML-7 | 300-PL-20011-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 23792 | Protective mesh removed | 2014-09-25 07:00 | 2014-09-25 15:00 | [36 empty] | 6.8 | CML-7 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2014-09-25 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.7 | 9 O'Clock | 40 | 6.35 | 300-PL-20011-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.8 | 6.9 | 6.8 | 6.7 | 0.08165
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43038-01C02 | CML-3 | 200-FH-43038-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12684 |  | 2014-02-06 09:00 | 2014-02-06 11:00 | [36 empty] | 8.375 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 09:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.9 | 12 O'Clock | 200 | 6.35 | 200-FH-43038-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 7.9 | 8.6 | 8.8 | 8.2 | 0.40311
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 80-PW-20024-01C03-P | CML-18 | 80-PW-20024-01C03-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23062 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 16.725 | CML-18 | CML: Elbow | 6 | 2099-09-17 | 2086-07-24 | 2015-05-06 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 16 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.5 |  | 17.7 | 16.7 | 16 | 16.5 | 0.71356
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-2 | 500-WS-50803-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10853 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 12.95 | CML-2 | CML: type TBC | 3 | 2015-11-02 | 2014-12-04 | 2014-01-04 | 2.9 | 5.0293 | A3: Inside Quadrant |  | 12.09 | 2.9 | 7.495 | 12.1 | 6 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 12.5 | 14 | 12.1 | 13.2 | 0.83467
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-1 | 500-WS-50803-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10852 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 12.45 | CML-1 | CML: type TBC | 3 | 2015-11-02 | 2014-12-04 | 2014-01-04 | 2.9 | 5.0293 | A3: Inside Quadrant |  | 12.09 | 2.9 | 7.495 | 12.1 | 6 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 12.3 | 12.9 | 12.1 | 12.5 | 0.34157
FL01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 150-FL-43174-01C02 | CML-3 | 150-FL-43174-01C02 CML-3 | yes | FPSO 2015 | Pipe Wall Thickness | 9090 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 4.075 | CML-3 | CML: type TBC | 3 | 2016-01-09 | 2016-04-20 | 2015-03-02 07:00 | 2.5 | 1.1647 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.5 | 3 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1 |  | 4.4 | 3.5 | 4.3 | 4.1 | 0.40311
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43140-01C02 | CML-3 | 50-FH-43140-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12870 |  | 2014-01-21 10:00 | 2014-01-21 10:30 | [36 empty] | 5.375 | CML-3 | CML: Reducing Tee | 3 | 2016-01-20 | 2016-05-02 | 2014-01-21 10:00 | 2.5 | 1.1522 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-FH-43140-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.7 | 5.6 | 4.8 | 5.4 | 0.40311
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-28 | 50-DH-56062-01C02 CML-28 |  | FPSO 2015 | Pipe Wall Thickness | 9115 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 6.075 | CML-28 | CML: type TBC | 3 | 2146-06-10 | 2160-09-18 | 2015-03-02 07:00 | 2.5 | 0.02284 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 6 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 6.3 | 6.4 | 5.5 | 6.1 | 0.40311
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2893 | Rope Access | 2014-04-25 08:00 | 2014-04-25 09:00 | [36 empty] | 6.575 | CML-3 | CML: Elbow | 3 | 2023-04-21 | 2023-03-26 | 2014-04-25 08:00 | 2.5 | 0.38909 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 6 O'Clock | 250 | 6.35 | 250-FL-43014-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 6.8 | 6 | 6.6 | 0.40311
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-21 | 250-FH-43303-01C02 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 12959 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.875 | CML-21 | CML: type TBC | 3 | 2064-02-06 | 2063-09-23 | 2014-01-27 10:00 | 2.5 | 0.07591 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 3 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 7.2 | 6.3 | 7.1 | 6.9 | 0.40311
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40045-01C02 | CML-7 | 300-WC-40045-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1068 |  | 2014-03-20 14:30 | 2014-03-20 15:00 | Check Corrosion Rate of 0.936mm/ yr | [35 empty] | 6.325 | CML-7 | CML: type TBC | 3 | 2017-07-12 | 2017-07-01 | 2014-03-20 14:30 | 2.5 | 0.93556 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 9 O'Clock | 300 | 6.35 | 300-WC-40045-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.4 | 6.2 | 7.1 | 5.6 | 0.61847
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57056-03C02 | CML-2 | 50-DC-57056-03C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1134 | Rope Access | 2014-03-21 07:00 | 2014-03-21 08:30 | [36 empty] | 6.625 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-03-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 6.6 | 6 O'Clock | 50 | 5.54 | 50-DC-57056-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.6 | 6.6 | 6.7 | 0.05
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-14 | 100-DC-57038-01C02 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2377 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 6.75 | CML-14 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 9 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.8 | 6.9 | 6.6 | 0.1291
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-1 | 100-DC-57038-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2364 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 6.7 | CML-1 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 3 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.8 | 6.6 | 6.7 | 6.7 | 0.08165
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57037-01C02 | CML-5 | 100-DC-57037-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2356 | Rope Access | 2014-03-18 13:00 | 2014-03-18 14:00 | [36 empty] | 6.775 | CML-5 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.6 | 6 O'Clock | 100 | 6.02 | 100-DC-57037-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 6.7 | 6.6 | 6.8 | 0.17078
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-22 | 100-DC-57307-01C03 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 2330 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.471mm/ yr | [35 empty] | 6.75 | CML-22 | CML: type TBC | 6 | 2015-11-13 | 2015-11-08 | 2014-03-17 13:00 | 2.5 | 2.4708 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 6.6 | 9 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 7 | 6.7 | 6.6 | 0.17321
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-19 | 100-DC-57307-01C03 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2327 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.471mm/ yr | [35 empty] | 6.8 | CML-19 | CML: type TBC | 6 | 2015-11-13 | 2015-11-08 | 2014-03-17 13:00 | 2.5 | 2.4708 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 6.6 | 3 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.7 | 6.6 | 6.8 | 7.1 | 0.21602
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-15 | 100-DC-57307-01C03 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 2323 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.471mm/ yr | [35 empty] | 6.725 | CML-15 | CML: type TBC | 6 | 2015-11-13 | 2015-11-08 | 2014-03-17 13:00 | 2.5 | 2.4708 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.6 | 9 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 6.7 | 6.6 | 6.6 | 0.1893
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-12 | 100-DC-57307-01C03 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2320 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.471mm/ yr | [35 empty] | 6.975 | CML-12 | CML: type TBC | 6 | 2015-11-13 | 2015-11-08 | 2014-03-17 13:00 | 2.5 | 2.4708 | A4: Left Quadrant |  | 2.56 | 2.5 | 2.53 | 6.6 | 9 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7 | 7 | 7.3 | 6.6 | 0.28723
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-9 | 100-DC-57307-01C03 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 2317 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.471mm/ yr | [35 empty] | 6.925 | CML-9 | CML: type TBC | 6 | 2015-11-13 | 2015-11-08 | 2014-03-17 13:00 | 2.5 | 2.4708 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.6 | 6 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.1 | 6.8 | 6.6 | 7.2 | 0.27538
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-4 | 100-DC-57307-01C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2312 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.471mm/ yr | [35 empty] | 6.975 | CML-4 | CML: type TBC | 6 | 2015-11-13 | 2015-11-08 | 2014-03-17 13:00 | 2.5 | 2.4708 | A3: Inside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.6 | 6 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.2 | 7 | 6.6 | 7.1 | 0.263
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-26 | 100-DC-57307-01C03 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 2334 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.471mm/ yr | [35 empty] | 6.8 | CML-26 | CML: type TBC | 6 | 2015-11-13 | 2015-11-08 | 2014-03-17 13:00 | 2.5 | 2.4708 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.6 | 12 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.8 | 6.8 | 7 | 0.1633
PW03 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22930 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.325 | CML-6 | CML: Elbow | 3 | 2030-07-23 | 2032-05-25 | 2015-05-02 07:00 | 2.5 | 0.17721 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-DC-57013-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | -1.6023 | 5.2 | 5.4 | 5.3 | 5.4 | 0.095743
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23029-25C02-P | CML-9 | 80-PG-23029-25C02-P CML-9 | Yes | FPSO 2014 | Pipe Wall Thickness | 20567 | Protective mesh removed/Rope access | 2014-07-02 07:00 | 2014-07-02 09:00 | [35 empty] | Low alarm breach | 10.625 | CML-9 | CML: Pipe Length | 3 | 2015-09-07 | 2015-01-29 | 2014-07-02 07:00 | 4.7 | 4.642 | A2: Right Quadrant |  | 12.24 | 4.7 | 7.5175 | 10.2 | 3 O'Clock | 50 | 15.24 | 80-PG-23029-25C02-P | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.5 |  | 10.8 | 10.2 | 10.4 | 11.1 | 0.40311
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20506-03C03-P | CML-7 | 300-PG-20506-03C03-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 13221 |  | 2014-02-04 15:00 | 2014-02-04 18:00 | [36 empty] | 14.125 | CML-7 | CML: type TBC | 6 | 2024-08-09 | 2022-08-05 | 2014-02-04 15:00 | 4.9 | 0.8368 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.7 | 12 O'Clock | 300 | 14.27 | 300-PG-20506-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 13.7 | 14.3 | 14.6 | 13.9 | 0.40311
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45505-01C02 | CML-10 | 150-FG-45505-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 22350 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 26.425 | CML-10 |  | 3 | 2059-07-07 | 2055-11-27 | 2014-04-30 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.5 | 12 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5 |  | 7.5 | 8.2 | 7.8 | 8.4 | 0.40311
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56115-01C02 | CML-7 | 50-DH-56115-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 5238 | Rope Access | 2014-05-20 13:00 | 2014-05-20 14:00 | [36 empty] | 5.575 | CML-7 | CML: Elbow | 3 | 2018-11-12 | 2019-06-13 | 2014-05-20 13:00 | 2.5 | 0.5575 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 12 O'Clock | 50 | 5.54 | 50-DH-56115-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5 | 5.8 | 5.9 | 5.6 | 0.40311
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 100-FH-43102-01C02 | CML-4 | 100-FH-43102-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12749 |  | 2014-01-24 08:00 | 2014-01-24 09:00 | [36 empty] | 5.575 | CML-4 | CML: type TBC | 3 | 2015-08-29 | 2015-09-25 | 2014-01-24 08:00 | 2.5 | 1.5687 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5 | 3 O'Clock | 100 | 6.02 | 100-FH-43102-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5 | 5.9 | 5.6 | 0.40311
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38475-01C02-P | CML-1 | 50-CG-38475-01C02-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23624 |  | 2015-10-28 07:00 | 2015-10-28 15:00 | [36 empty] | 5.175 | CML-1 | CML: Pipe Length | 3 | 2022-02-16 | 2023-01-23 | 2015-10-28 07:00 | 2.5 | 0.34869 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38475-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5 | 4.7 | 5.4 | 5.6 | 0.40311
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-35 | 50-DH-56070-01C02 CML-35 |  | FPSO 2014 | Pipe Wall Thickness | 3251 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 6.675 | CML-35 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 3 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.9 | 6.2 | 6.5 | 7.1 | 0.40311
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-3 | 400-FH-43500-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5639 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 9.525 | CML-3 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 9.2 | 9 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10.1 | 9.3 | 9.5 | 9.2 | 0.40311
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-7 | 80-PW-44016-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21939 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.5 | CML-7 | CML: Elbow | 3 | 2034-10-19 | 2037-04-15 | 2014-10-10 07:00 | 2.5 | 0.13974 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.9 | 5.5 | 5.3 | 0.28284
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20501-03C03-P | CML-3 | 300-PF-20501-03C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21679 | Protective mesh removed | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 14.475 | CML-3 | CML: Pipe Length | 6 | 2059-06-06 | 2051-02-26 | 2014-09-28 07:00 | 4.9 | 0.20349 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14 | 12 O'Clock | 300 | 14.27 | 300-PF-20501-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 14 | 14.3 | 14.7 | 14.9 | 0.40311
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-10 | 500-WS-50803-1LC CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10861 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 12.95 | CML-10 | CML: type TBC | 3 | 2016-01-05 | 2015-01-12 | 2014-01-04 | 2.9 | 4.6929 | A2: Right Quadrant |  | 12.09 | 2.9 | 7.495 | 12.3 | 3 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 |  | 13 | 12.3 | 13.3 | 13.2 | 0.45092
PW03 | Montara_Topside | Yes | Fire Water (71) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 5130 | Pipe Schedule Estimated. All fittings CAST. Readings taken on piping adjacent to fitting. Rope Access | 2015-03-11 07:00 | 2015-03-11 15:00 | [36 empty] | 5.325 | CML-1 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-11 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.5 | 2.5 | 2.5 | 5.2 | 12 O'Clock | 150 | 3 | 150-WF-71315-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.4 | 5.3 | 5.4 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FL-43301-01C02 | CML-3 | 50-FL-43301-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20453 | Reviewed on 24/11/14. FFS. Repeat on Oct. 18 | 2014-10-05 07:00 | 2014-10-05 15:00 |  |  | Nestor | 2014-11-24 11:16 | [32 empty] | 5.475 | CML-3 | CML: Elbow | 3 | 2019-10-21 | 2020-06-28 | 2014-10-05 07:00 | 2.5 | 0.47548 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 9 O'Clock | 50 | 5.54 | 50-FL-43301-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.8 | 5.7 | 5.5 | 4.9 | 0.40311
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-9 | 80-DH-56074-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20954 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 5.775 | CML-9 | CML: Equal Tee | 3 | 2023-07-02 | 2024-09-03 | 2014-05-24 07:00 | 2.5 | 0.29626 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 6 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.8 | 6 | 5.2 | 6.1 | 0.40311
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-11 | 150-FG-45002-03C02 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10414 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.925 | CML-11 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.6 | 9 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.2 | 6.9 | 7 | 6.6 | 0.25
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 150-FG-45002-03C02 | CML-10 | 150-FG-45002-03C02 CML-10 |  | FPSO 2013 | Pipe Wall Thickness | 10413 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 6.975 | CML-10 | CML: type TBC | 3 |  |  | 2013-11-12 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.6 | 9 O'Clock | 150 |  | 150-FG-45002-03C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.3 | 6.9 | 7.1 | 6.6 | 0.29861
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56086-01C02 | CML-4 | 100-DH-56086-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20963 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 6.475 | CML-4 | CML: type TBC | 3 | 2041-06-27 | 2042-05-31 | 2014-05-16 13:00 | 2.5 | 0.12531 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.9 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.8 | 6.5 | 6.7 | 5.9 | 0.40311
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-3 | 25-FG-45455-01C02-E CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24348 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.475 | CML-3 | CML: Elbow | 3 | 2039-03-19 | 2039-01-09 | 2016-06-06 07:00 | 2.5 | 0.14914 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 3 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.8 | 5.9 | 6.7 | 6.5 | 0.40311
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-3 | 250-FH-43303-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12941 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 7.475 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 12 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.5 | 7.7 | 7.8 | 0.40311
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57012-01C02 | CML-6 | 50-DC-57012-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2885 | Rope Access | 2014-04-24 14:00 | 2014-04-24 15:00 | Check Corrosion Rate of 1.159mm/ yr | [35 empty] | 5 | CML-6 | CML: type TBC | 3 | 2017-11-15 | 2017-03-27 | 2014-04-24 14:00 | 0.37 | 1.1588 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-DC-57012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.13 |  | 4.5 | 5.1 | 5.4 | 5 | 0.37417
DH01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-DH-56137-01C02 | CML-6 | 50-DH-56137-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23028 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 16.925 | CML-6 | CML: Reducer | 6 | 2081-02-10 | 2077-04-05 | 2015-05-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.27 | 2.5 | 2.885 | 16.6 | 12 O'Clock | 250 | 9.27 | 250-PW-44010-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 14.1 | 1.6176 | 16.6 | 16.7 | 16.9 | 17.5 | 0.40311
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-21 | 200-PG-23065-09C02-A CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 435 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.175 | CML-21 | CML: Pipe Length | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A1: Outside Quadrant |  | 15.26 | 10.17 | 12.715 | 18.8 | 6 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.63 |  | 18.8 | 19.1 | 18.8 | 20 | 0.56789
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-7 | 200-PG-23065-09C02-A CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 619 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.125 | CML-7 | CML: Elbow | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 18.8 | 6 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.63 |  | 19.6 | 18.8 | 18.8 | 19.3 | 0.39476
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-29 | 150-PG-23506-25C02 CML-29 |  | FPSO 2014 | Pipe Wall Thickness | 2803 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 23.625 | CML-29 | CML: Pipe Length | 3 | 2074-02-10 | 2058-10-06 | 2014-03-15 09:00 | 15.88 | 0 | A2: Right Quadrant |  | 18.95 | 15.88 | 17.415 | 23.3 | 3 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.42 |  | 23.6 | 23.3 | 24.2 | 23.4 | 0.40311
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-4 | 500-WS-50803-1LC CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10855 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 13.9 | CML-4 | CML: type TBC | 3 | 2017-06-17 | 2015-12-08 | 2014-01-04 | 2.9 | 3.0108 | A1: Outside Quadrant |  | 12.09 | 2.9 | 7.495 | 13.3 | 12 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.4 |  | 13.3 | 13.6 | 14.7 | 14 | 0.60553
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-6 | 500-WS-50803-1LC CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10857 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 13.5 | CML-6 | CML: type TBC | 3 | 2017-12-20 | 2016-04-02 | 2014-01-04 | 2.9 | 2.6744 | A1: Outside Quadrant |  | 12.09 | 2.9 | 7.495 | 13.5 | 9 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.6 |  | 13.5 | 13.5 | 13.5 | 13.5 | 0
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-5 | 200-PG-23013-09C03-A CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10989 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 20.625 | CML-5 | CML: Elbow | 6 | 2033-04-04 | 2029-01-22 | 2014-01-10 | 10.22 | 0.52377 | A2: Right Quadrant |  | 14.62 | 10.22 | 12.42 | 20.3 | 3 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.08 |  | 20.6 | 20.3 | 20.4 | 21.2 | 0.40311
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-3 | 150-PG-23043-06C02-P CML-3 | yes | FPSO 2016 | Pipe Wall Thickness | 23765 | re-check line | 2016-02-13 07:00 | 2016-02-13 15:00 | [36 empty] | 11.275 | CML-3 | CML: Equal Tee | 3 | 2113-02-10 | 2098-01-06 | 2016-02-13 07:00 | 4.7 | 0.06285 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 10.8 | 3 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 0 | 11.7 | 10.8 | 11.1 | 11.5 | 0.40311
PG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23043-06C02-P | CML-3 | 150-PG-23043-06C02-P CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24154 | re-check line | 2016-02-13 | 2016-02-13 | [36 empty] | 11.275 | CML-3 | CML: Equal Tee | 3 | 2113-01-30 | 2097-12-27 | 2016-02-13 | 4.7 | 0.06287 | A2: Right Quadrant |  | 7.97 | 4.7 | 5.6494 | 10.8 | 3 O'Clock | 150 | 10.97 | 150-PG-23043-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 | 2.3293 | 11.7 | 10.8 | 11.1 | 11.5 | 0.40311
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44037-01C03 | CML-3 | 300-PW-44037-01C03 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21913 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 10.15 | CML-3 | CML: Elbow | 6 | 2048-01-23 | 2044-01-18 | 2014-10-16 07:00 | 2.5 | 0.22527 | A2: Right Quadrant |  | 4.31 | 2.5 | 3.405 | 10 | 6 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 10.5 | 10 | 10 | 10.1 | 0.23805
CG03 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-CG-38459-09C02-P | CML-3 | 80-CG-38459-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 5619 | Material typre 1CG (no option in drop down box) | 2014-06-20 11:00 | 2014-06-20 12:00 | [36 empty] | 15.375 | CML-3 | CML: Elbow | 3 | 2059-02-10 | 2041-09-15 | 2014-06-20 11:00 | 2.5 | 0.27532 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 14.8 | 9 O'Clock | 250 | 15.09 | 250-WC-40502-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.3 |  | 15.4 | 15.6 | 15.7 | 14.8 | 0.40311
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40016-01C02 | CML-1 | 250-WC-40016-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20363 | Reviewed 24/11/14. FFS. repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 | Check Corrosion Rate of 0.556mm/ yr |  | Nestor | 2014-11-24 10:37 | [32 empty] | 6.3 | CML-1 | CML: Pipe Length | 3 | 2020-05-02 | 2020-04-13 | 2014-10-06 07:00 | 2.5 | 0.55607 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 3 O'Clock | 250 | 6.35 | 250-WC-40016-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.7 | 5.6 | 6.4 | 6.5 | 0.48305
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-8 | 500-WS-50803-1LC CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10859 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 15.275 | CML-8 | CML: type TBC | 3 | 2019-01-11 | 2016-11-29 | 2014-01-04 | 2.9 | 2.1698 | A4: Left Quadrant |  | 12.09 | 2.9 | 7.495 | 13.8 | 9 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 |  | 15.5 | 16.3 | 15.5 | 13.8 | 1.0532
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 100-PG-23503-03C03-A | CML-8 | 100-PG-23503-03C03-A CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2724 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 11.3 | CML-8 | CML: Elbow | 6 | 2023-05-10 | 2023-11-02 | 2014-03-13 09:00 | 5.66 | 0.54998 | A1: Outside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.7 | 12 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.04 |  | 10.7 | 11.5 | 11.5 | 11.5 | 0.4
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-12 | 500-WS-50803-1LC CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10863 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 14.325 | CML-12 | CML: type TBC | 3 | 2020-01-22 | 2017-07-22 | 2014-01-04 | 2.9 | 1.8334 | A3: Inside Quadrant |  | 12.09 | 2.9 | 7.495 | 14 | 6 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 14.2 | 14.3 | 14 | 14.8 | 0.34034
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-41 | 150-PG-23506-25C02 CML-41 |  | FPSO 2014 | Pipe Wall Thickness | 20666 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | [36 empty] | 21.2 | CML-41 | CML: Pipe Length | 3 | 2019-09-26 | 2018-02-19 | 2014-05-28 07:00 | 15.88 | 0.95975 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.12 | -0.4938 | 21 | 21 | 21.8 | 21 | 0.4
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-11 | 500-WS-50803-1LC CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10862 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 14.275 | CML-11 | CML: type TBC | 3 | 2020-01-22 | 2017-07-22 | 2014-01-04 | 2.9 | 1.8334 | A1: Outside Quadrant |  | 12.09 | 2.9 | 7.495 | 14 | 6 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 14 | 14.5 | 14 | 14.6 | 0.32016
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-5 | 500-WS-50803-1LC CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10856 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 14.125 | CML-5 | CML: type TBC | 3 | 2020-01-22 | 2017-07-22 | 2014-01-04 | 2.9 | 1.8334 | A1: Outside Quadrant |  | 12.09 | 2.9 | 7.495 | 14 | 3 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 14 | 14 | 14.2 | 14.3 | 0.15
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-3 | 500-WS-50803-1LC CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10854 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 14.9 | CML-3 | CML: type TBC | 3 | 2020-01-22 | 2017-07-22 | 2014-01-04 | 2.9 | 1.8334 | A3: Inside Quadrant |  | 12.09 | 2.9 | 7.495 | 14 | 6 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.1 |  | 15.2 | 15.5 | 14 |  | 0.79373
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42312-01S01 | CML-6 | 40-CI-42312-01S01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7515 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.9 | CML-6 | CML: type TBC | 1 | 2033-01-31 | 2027-04-06 | 2015-04-13 07:00 | 2.5 | 0.23573 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.7 | 12 O'Clock | 40 | 7.14 | 40-CI-42312-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.7 | 9.2 | 8 | 1.0296
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42312-01S01 | CML-1 | 40-CI-42312-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7510 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 8.125 | CML-1 | CML: type TBC | 1 | 2033-01-31 | 2027-04-06 | 2015-04-13 07:00 | 2.5 | 0.23573 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.7 | 12 O'Clock | 40 | 7.14 | 40-CI-42312-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 8.2 | 9.1 | 8.5 | 1.021
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42311-01S01 | CML-5 | 40-CI-42311-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7508 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 8.075 | CML-5 | CML: type TBC | 1 | 2033-01-31 | 2027-04-06 | 2015-04-13 07:00 | 2.5 | 0.23573 | A4: Left Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.7 | 9 O'Clock | 40 | 7.14 | 40-CI-42311-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 8.2 | 9.4 | 8 | 6.7 | 1.1057
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42311-01S01 | CML-3 | 40-CI-42311-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7506 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 8.05 | CML-3 | CML: type TBC | 1 | 2033-01-31 | 2027-04-06 | 2015-04-13 07:00 | 2.5 | 0.23573 | A3: Inside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.7 | 6 O'Clock | 40 | 7.14 | 40-CI-42311-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 9.2 | 8 | 6.7 | 8.3 | 1.0344
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42311-01S01 | CML-1 | 40-CI-42311-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7504 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.85 | CML-1 | CML: type TBC | 1 | 2033-01-31 | 2027-04-06 | 2015-04-13 07:00 | 2.5 | 0.23573 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.7 | 12 O'Clock | 40 | 7.14 | 40-CI-42311-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 8 | 8.6 | 8.1 | 0.81035
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42309-01S01 | CML-3 | 40-CI-42309-01S01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7499 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.775 | CML-3 | CML: type TBC | 1 | 2033-01-31 | 2027-04-06 | 2015-04-13 07:00 | 2.5 | 0.23573 | A3: Inside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.7 | 6 O'Clock | 40 | 7.14 | 40-CI-42309-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 9 | 7.5 | 6.7 | 7.9 | 0.95699
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42310-01S01 | CML-4 | 40-CI-42310-01S01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7493 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.65 | CML-4 | CML: type TBC | 1 | 2033-01-31 | 2027-04-06 | 2015-04-13 07:00 | 2.5 | 0.23573 | A3: Inside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.7 | 6 O'Clock | 40 | 7.14 | 40-CI-42310-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 9.4 | 7.5 | 6.7 | 7 | 1.2124
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42310-01S01 | CML-1 | 40-CI-42310-01S01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7490 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.55 | CML-1 | CML: type TBC | 1 | 2033-01-31 | 2027-04-06 | 2015-04-13 07:00 | 2.5 | 0.23573 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.7 | 12 O'Clock | 40 | 7.14 | 40-CI-42310-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.1 | 8.8 | 7.6 | 0.91104
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 150-PG-23506-25C02 | CML-40 | 150-PG-23506-25C02 CML-40 |  | FPSO 2014 | Pipe Wall Thickness | 20665 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | [36 empty] | 21.2 | CML-40 | CML: Pipe Length | 3 | 2019-09-26 | 2018-02-19 | 2014-05-28 07:00 | 15.88 | 0.95975 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 21 | 6 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.12 | -1.9752 | 21 | 21 | 21 | 21.8 | 0.4
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-9 | 500-WS-50803-1LC CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10860 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 14.825 | CML-9 | CML: type TBC | 3 | 2022-08-01 | 2019-02-16 | 2014-01-04 | 2.9 | 1.3288 | A3: Inside Quadrant |  | 12.09 | 2.9 | 7.495 | 14.3 | 6 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.4 |  | 15.1 | 14.8 | 14.3 | 15.1 | 0.37749
SD02 | Montara_Topside | No | Steam (55) | Pipework | 80-SC-55002-01C02-P | CML-14 | 80-SC-55002-01C02-P CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 8844 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 6.975 | CML-14 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2015-02-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.7 | 3 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.9 | 6.7 | 7.1 | 7.2 | 0.22174
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 | Yes | FPSO 2014 | Pipe Wall Thickness | 24242 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.5 | CML-4 | CML: Pipe Length | 3 | 2085-04-24 | 2073-10-17 | 2014-09-24 07:00 | 7.9 | 0 | A3: Inside Quadrant |  | 12.09 | 7.9 | 9.0519 | 15.1 | 6 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 15.5 | 15.9 | 15.1 |  | 0.4
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23018-09C03-A | CML-10 | 200-PG-23018-09C03-A CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 13071 |  | 2014-01-10 07:00 | 2014-01-10 09:00 | [36 empty] | 20.1 | CML-10 | CML: type TBC | 6 | 2019-02-13 | 2017-11-26 | 2014-01-10 07:00 | 10.17 | 1.8308 | A2: Right Quadrant |  | 14.62 | 10.17 | 12.395 | 19.5 | 3 O'Clock | 200 | 20.62 | 200-PG-23018-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.33 |  | 20.3 | 19.5 | 20.3 | 20.3 | 0.4
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63009-01E01 | CML-8 | 50-AI-63009-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8530 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.825 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 9 O'Clock | 50 | 5.54 | 50-AI-63009-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7 | 6.8 | 6.8 | 6.7 | 0.12583
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC | CML-7 | 500-WS-50803-1LC CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10858 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 15.15 | CML-7 | CML: type TBC | 3 | 2051-07-14 | 2037-03-01 | 2014-01-04 | 2.9 | 0.31959 | A4: Left Quadrant |  | 12.09 | 2.9 | 7.495 | 14.9 | 9 O'Clock | 500 | 15.09 | 500-WS-50803-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12 |  | 15.4 | 15.1 | 15.2 | 14.9 | 0.20817
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50803-1LC |  | 500-WS-50803-1LC |  | FPSO 2015 | Pipe Wall Thickness | 1519 | SPOOL REMOVED | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | No Readings to Review | [32 empty] | 500-WS-50803-1LC | Piping | 3 | 2135-04-24 |  | 2015-06-12 |  | 0 |  |  |  | 2.9 |  |  | 9 O'Clock | 500 | 15.09 | Pipework | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-27 | 50-WD-53010-01E01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 8270 | Reducing Hose Coupling | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.875 | CML-27 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.4 | 6.7 | 6.7 | 6.7 | 0.35
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53010-01E01 | CML-18 | 50-WD-53010-01E01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 8261 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 6.75 | CML-18 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 9 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.9 | 6.7 | 6.7 | 6.7 | 0.1
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53014-01E01 | CML-3 | 50-WD-53014-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8218 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 6.8 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 12 O'Clock | 50 | 5.54 | 50-WD-53014-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 6.9 | 6.8 | 6.8 | 0.08165
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53008-01E01 | CML-1 | 50-WD-53008-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8166 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 6.925 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 12 O'Clock | 50 | 5.54 | 50-WD-53008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.4 | 6.8 | 6.8 | 0.32016
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50812-1LC | CML-2 | 500-WS-50812-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10825 | Deck Level | 2014-01-04 | 2014-01-04 | [35 empty] | Low alarm breach | 12.375 | CML-2 | CML: type TBC | 3 | 2015-07-23 | 2014-09-28 | 2014-01-04 | 2.5 | 5.8703 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.6 | 6 O'Clock | 500 | 15.09 | 500-WS-50812-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 12.8 | 12.2 | 11.6 | 12.9 | 0.60208
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-9 | 250-PG-23003-06C02-PA CML-9 | yes | FPSO 2013 | Pipe Wall Thickness | 10676 | Deck Level. | 2013-11-17 | 2013-11-17 |  |  | Administrator | 2015-09-06 15:58 | [32 empty] | 4.4 | CML-9 | CML: Pipe Length | 3 | 2014-03-23 | 2014-04-23 | 2013-11-17 | 2.5 | 3.758 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 3.8 | 3 O'Clock | 50 | 5.54 | 50-FH-43450-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.3 |  | 4.6 | 3.8 | 4.6 | 4.6 | 0.4
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56028-01C02 | CML-6 | 80-DH-56028-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20903 | Rope Access | 2014-05-22 07:00 | 2014-05-22 08:00 | [36 empty] | 5.6 | CML-6 | CML: Elbow | 3 | 2019-05-09 | 2020-01-16 | 2014-05-22 07:00 | 2.5 | 0.50339 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5 | 9 O'Clock | 80 | 5.49 | 80-DH-56028-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5.8 | 5.8 | 5 | 0.4
FH01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PG-23074-01C02-P | CML-7 | 50-PG-23074-01C02-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20629 | Protective mesh removed/Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 5.6 | CML-7 | CML: Elbow | 3 | 2019-11-23 | 2020-08-03 | 2014-07-26 07:00 | 2.5 | 0.46896 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-PG-23074-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.8 | 5.8 | 5.8 | 5 | 0.4
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FH-43001-01C02 | CML-9 | 300-FH-43001-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12521 |  | 2014-01-24 13:00 | 2014-01-24 15:00 | [36 empty] | 6.2 | CML-9 | CML: type TBC | 3 | 2020-07-26 | 2020-07-07 | 2014-01-24 13:00 | 2.5 | 0.5378 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6 | 9 O'Clock | 300 | 6.35 | 300-FH-43001-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.8 | 6 | 6 | 0.4
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23021-03C03 | CML-15 | 50-PL-23021-03C03 CML-15 |  | FPSO 2013 | Pipe Wall Thickness | 10247 | Deck Level | 2013-11-08 | 2013-11-08 | [36 empty] | 8 | CML-15 | CML: type TBC | 6 | 2015-06-16 | 2015-06-01 | 2013-11-08 | 2.5 | 3.0569 | A3: Inside Quadrant |  | 2.74 | 2.5 | 2.62 | 7.4 | 6 O'Clock | 50 | 8.74 | 50-PL-23021-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.9 |  | 8.2 | 8.2 | 7.4 | 8.2 | 0.4
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-11 | 50-PL-45016-03C03 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10451 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 8 | CML-11 | CML: type TBC | 6 | 2016-01-11 | 2015-09-25 | 2013-11-13 | 0.99 | 2.9642 | A1: Outside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.4 | 12 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.41 |  | 7.4 | 8.2 | 8.2 | 8.2 | 0.4
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50812-1LC | CML-1 | 500-WS-50812-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10824 | Deck Level | 2014-01-04 | 2014-01-04 | [36 empty] | 12.475 | CML-1 | CML: type TBC | 3 | 2015-12-01 | 2014-12-18 | 2014-01-04 | 2.5 | 5.0293 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 12.1 | 12 O'Clock | 500 | 15.09 | 500-WS-50812-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 12.1 | 12.6 | 13 | 12.2 | 0.4113
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-1 | 500-WS-50813-1LC CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 10783 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Medium alarm breach | 6.25 | CML-1 | CML: type TBC | 3 | 2014-03-30 | 2013-12-05 | 2014-01-03 | 2.5 | 15.1914 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 6.1 | 9 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.4 | 6.2 | 6.3 | 6.1 | 0.1291
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-13 | 80-DC-57002-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20242 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.7 | CML-13 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.7 | 12 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7.6 | 8.4 | 8.1 | 0.74386
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-29 | 200-PG-23007-09C03-PA CML-29 |  | FPSO 2016 | Pipe Wall Thickness | 24452 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | Check Corrosion Rate of 0.33mm/ yr |  | John Wilson | 2017-03-23 09:51 | Loss within CA no further action required. | [31 empty] | 20.2 | CML-29 | CML: Fitting | 6 | 2044-11-29 | 2038-04-01 | 2016-07-03 07:00 | 10.22 | 0.32997 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 19.6 | 12 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.38 | 0 | 19.6 | 20.4 | 20.4 | 20.4 | 0.4
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-12 | 200-PG-23007-09C03-PA CML-12 |  | FPSO 2016 | Pipe Wall Thickness | 24448 | Re-check as requested by N.Sequera | 2016-07-03 07:00 | 2016-07-03 15:00 | Check Corrosion Rate of 0.33mm/ yr |  | John Wilson | 2017-03-23 09:43 | Loss within CA no further action required. | [31 empty] | 20.2 | CML-12 | CML: Fitting | 6 | 2044-11-29 | 2038-04-01 | 2016-07-03 07:00 | 10.22 | 0.32997 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 19.6 | 12 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.38 | 0 | 19.6 | 20.4 | 20.4 | 20.4 | 0.4
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56118-01C02 | CML-6 | 50-DH-56118-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21025 | Rope Access | 2014-05-19 11:00 | 2014-05-19 12:00 | [36 empty] | 5.075 | CML-6 | CML: type TBC | 3 | 2016-07-14 | 2016-11-14 | 2014-05-19 11:00 | 2.5 | 0.97345 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 6 O'Clock | 50 | 5.54 | 50-DH-56118-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.4 | 5.4 | 4.6 | 4.9 | 0.39476
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56082-01C02 | CML-26 | 100-DH-56082-01C02 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 3394 | Rope Access | 2014-05-10 09:30 | 2014-05-10 12:00 | [36 empty] | 8.225 | CML-26 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-10 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.9 | 6 O'Clock | 100 | 6.02 | 100-DH-56082-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.1 | 8.1 | 7.9 | 8.8 | 0.39476
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57450-01C02-P | CML-2 | 50-DC-57450-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20318 |  | 2014-10-05 07:00 | 2014-10-05 15:00 | Check Corrosion Rate of 0.327mm/ yr | [35 empty] | 8.1 | CML-2 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-10-05 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 9 O'Clock | 40 | 5.54 | 50-DC-57450-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 8.8 | 9.1 | 7.8 | 6.7 | 1.0863
FH01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FH-43507-01C02 | CML-27 | 100-FH-43507-01C02 CML-27 | Yes | FPSO 2015 | Pipe Wall Thickness | 23332 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.225 | CML-27 |  | 3 | 2072-05-16 | 2056-08-24 | 2015-07-11 07:00 | 4.7 | 0.10898 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 10.9 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 11.1 | 10.9 | 11.1 | 11.8 | 0.39476
DC01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 50-CG-38465-01C02 | CML-16 | 50-CG-38465-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20879 |  | 2014-10-04 07:00 | 2014-10-04 15:00 | [36 empty] | 7.8 | CML-16 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-10-04 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 9 O'Clock | 80 | 5.54 | 50-CG-38465-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 9.3 | 8.5 | 6.7 | 6.7 | 1.3115
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-24 | 100-FG-45001-09C02 CML-24 | Yes | FPSO 2015 | Pipe Wall Thickness | 23329 | Re-check on line | 2015-07-11 07:00 | 2015-07-11 10:00 | [36 empty] | 11.675 | CML-24 | CML: type TBC | 3 | 206525 | 2344-11-17 | 2015-07-11 07:00 | 4.7 | 0.01422 | A2: Right Quadrant |  | 8.13 | 4.7 | 6.415 | 11.1 | 3 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 | -0.1206 | 11.8 | 11.1 | 11.8 | 12 | 0.39476
FG01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-FG-45024-01C02 | CML-1 | 50-FG-45024-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2092 |  | 2014-03-28 11:30 | 2014-03-28 12:00 | [36 empty] | 9.525 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-28 11:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.2 | 9 O'Clock | 50 | 5.54 | 50-WC-40054-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.7 | 10 | 9.2 | 0.39476
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44003-01C03 | CML-27 | 300-PW-44003-01C03 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 21869 | Reviewed 21/11/14. FFS. Recheck in Oct. 19. | 2014-10-19 07:00 | 2014-10-19 15:00 |  |  | Nestor | 2014-11-21 17:09 | [32 empty] | 10.75 | CML-27 | CML: Pipe Length | 6 | 2111-08-22 | 2100-04-04 | 2014-10-19 07:00 | 2.5 | 0.07946 | A1: Outside Quadrant |  | 4.31 | 2.5 | 3.405 | 10.2 | 12 O'Clock | 300 | 10.31 | 300-PW-44003-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 10.2 | 10.3 | 11.5 | 11 | 0.61373
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23046-06C03 | CML-4 | 80-PG-23046-06C03 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20581 | Rope Access | 2014-05-27 07:00 | 2014-05-27 08:00 | [36 empty] | 11.475 | CML-4 | CML: type TBC | 6 | 2076-08-15 | 2067-10-13 | 2014-05-27 07:00 | 2.8 | 0.1317 | A4: Left Quadrant |  | 5.13 | 2.8 | 3.965 | 11 | 9 O'Clock | 80 | 11.13 | 80-PG-23046-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.2 |  | 11.8 | 11.8 | 11.3 | 11 | 0.39476
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-24 | 250-PW-20040-03C03-P CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 23468 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 12.3 | CML-24 | CML: Fitting | 6 | 2033-11-27 | 2030-10-23 | 2015-07-24 07:00 | 4.1 | 0.41938 | A1: Outside Quadrant |  | 6.7 | 4.1 | 5.4 | 11.8 | 12 O'Clock | 250 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 | 0.096822 | 11.8 | 12.8 | 12.6 | 12 | 0.4761
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38459-09C02-P | CML-16 | 80-CG-38459-09C02-P CML-16 |  | FPSO 2015 | Pipe Wall Thickness | 23114 |  | 2015-05-10 07:00 | 2015-05-10 15:00 | [36 empty] | 14.675 | CML-16 | CML: Elbow | 6 | 2081-02-10 | 2077-04-05 | 2015-05-10 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.27 | 2.5 | 2.885 | 14.1 | 6 O'Clock | 250 | 9.27 | 250-PW-20022-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.6 | 1.2525 | 14.8 | 14.8 | 14.1 | 15 | 0.39476
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40401-01C02 | CML-5 | 200-WC-40401-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7921 | Line is FFS. Current RBI frequency is 48m. Rest of CML’s have low CR’s Action: Recheck CML-5 & 6 in two years (Jan. 2017) to confirm CR | 2015-01-17 08:00 | 2015-01-17 09:00 | Check Corrosion Rate of 0.46mm/ yr |  | Administrator | 2015-09-08 11:21 | [32 empty] | 5.95 | CML-5 | CML: Elbow | 3 | 2021-10-13 | 2021-09-20 | 2015-01-17 08:00 | 2.5 | 0.45983 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 200 | 6.35 | 200-WC-40401-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.6 | 5.6 | 5.6 | 6 | 0.47258
FG01 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-FG-45024-01C02 | CML-5 | 50-FG-45024-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20302 | Reviewed 24/11/14. FFS. CML to be checked in Oct.16 | 2014-10-02 07:00 | 2014-10-02 15:00 | Check Corrosion Rate of 1.323mm/ yr |  | Nestor | 2014-11-24 08:45 | [32 empty] | 9.525 | CML-5 | CML: Reducing Tee | 6 | 2019-10-24 | 2018-11-17 | 2014-10-02 07:00 | 2.5 | 1.3231 | A2: Right Quadrant |  | 4.97 | 2.5 | 3.735 | 9.2 | 9 O'Clock | 150 | 10.97 | 150-DC-57308-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 10 | 9.2 | 9.7 | 9.2 | 0.39476
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 300-PG-23001-03C03 | CML-24 | 300-PG-23001-03C03 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 10974 | Rope Access | 2014-01-09 | 2014-01-09 | [36 empty] | 14.175 | CML-24 | CML: Elbow | 6 | 2023-01-24 | 2021-06-09 | 2014-01-09 | 5.22 | 0.93716 | A2: Right Quadrant |  | 8.27 | 5.22 | 6.745 | 13.7 | 3 O'Clock | 300 | 14.27 | 300-PG-23001-03C03 | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.48 |  | 14.5 | 13.7 | 14 | 14.5 | 0.39476
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-2 | 500-WS-50813-1LC CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 10784 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Medium alarm breach | 6.2 | CML-2 | CML: type TBC | 3 | 2014-04-02 | 2013-12-07 | 2014-01-03 | 2.5 | 15.0224 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 6.2 | 9 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.2 | 6.2 | 6.2 | 0
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-3 | 500-WS-50813-1LC CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 10785 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 10.175 | CML-3 | CML: type TBC | 3 | 2014-11-27 | 2014-05-04 | 2014-01-03 | 2.5 | 8.4322 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 10.1 | 6 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.6 |  | 10.2 | 10.2 | 10.1 | 10.2 | 0.05
PG02 | Montara_Topside | No | Separation (20) | Pipework | 250-PG-20042-01D01-P | CML-8 | 250-PG-20042-01D01-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21441 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 6.9 | CML-8 | CML: Elbow | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.35 | 2.5 | 3.925 | 6.7 | 12 O'Clock | 350 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 6.9 | 7 | 7 | 0.14142
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23402-01C02-PA | CML-8 | 150-PG-23402-01C02-PA CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 5616 |  | 2014-06-20 09:30 | 2014-06-20 11:00 | [36 empty] | 7.3 | CML-8 | CML: Fitting | 3 |  |  | 2014-06-20 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.7 | 9 O'Clock | 150 |  | 150-PG-23402-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 7.5 | 7.5 | 7.5 | 6.7 | 0.4
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 150-PG-23402-01C02-PA | CML-5 | 150-PG-23402-01C02-PA CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 5613 |  | 2014-06-20 09:30 | 2014-06-20 11:00 | [36 empty] | 7 | CML-5 | CML: Fitting | 3 |  |  | 2014-06-20 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.7 | 9 O'Clock | 150 |  | 150-PG-23402-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.9 | 7.1 | 7.3 | 6.7 | 0.2582
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-12 | 500-WS-50813-1LC CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 10794 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 11.525 | CML-12 | CML: type TBC | 3 | 2014-12-20 | 2014-05-18 | 2014-01-03 | 2.5 | 8.0942 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 10.3 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.8 |  | 10.3 | 12.3 | 12.6 | 10.9 | 1.1026
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-23 | 200-PG-23065-09C02-A CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 437 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.2 | CML-23 | CML: Pipe Length | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A1: Outside Quadrant |  | 15.26 | 10.17 | 12.715 | 18.8 | 12 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.63 |  | 18.8 | 19.5 | 19 | 19.5 | 0.3559
PG09 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23065-09C02-A | CML-17 | 200-PG-23065-09C02-A CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 431 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 19.175 | CML-17 | CML: Pipe Length | 3 | 2094-04-24 | 2068-11-11 | 2014-03-12 09:00 | 10.17 | 0 | A2: Right Quadrant |  | 15.26 | 10.17 | 12.715 | 18.8 | 3 O'Clock | 200 | 18.26 | 200-PG-23065-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.63 |  | 19.1 | 18.8 | 19.4 | 19.4 | 0.28723
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML46 | 80-DH-56004-01C02 CML46 | yes | FPSO 2015 | Pipe Wall Thickness | 7578 |  | 2015-04-14 07:00 | 2015-04-14 15:00 | [36 empty] | 3.875 | CML46 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 6 O'Clock | 100 | 3 | 100-WF-71326-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 4 | 4 | 3.3 | 4.2 | 0.39476
PG06 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20836 | Reviewed on 20/11/14. FFS. This line has not been RBI assessed. CML to be rechecked Oct. 18 based on other line on this circuit which are a 48m interval | 2014-10-04 07:00 | 2014-10-04 15:00 |  |  | Nestor | 2014-11-20 16:11 | [32 empty] | 5.425 | CML-2 | CML: Elbow | 3 | 2022-09-09 | 2023-09-08 | 2014-10-04 07:00 | 2.5 | 0.32756 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-CG-38464-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.1 | 6 | 5.3 | 0.39476
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-17 | 25-FG-45455-01C02-E CML-17 | yes | FPSO 2014 | Pipe Wall Thickness | 2325 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 3.227mm/ yr | [35 empty] | 6.575 | CML-17 | CML: type TBC | 6 | 2015-04-17 | 2015-04-14 | 2014-03-17 13:00 | 2.5 | 3.2272 | A2: Right Quadrant |  | 2.56 | 2.5 | 2.53 | 6 | 3 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.9 | 6 | 6.7 | 6.7 | 0.39476
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-53 | 200-PW-44018-01X01 CML-53 |  | FPSO 2015 | Pipe Wall Thickness | 8977 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.325 | CML-53 | CML: type TBC | 3 | 2028-12-20 | 2030-08-21 | 2015-02-26 09:00 | 2.5 | 0.19532 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.3 | 5.2 | 5.4 | 0.095743
PW03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PW-44018-01X01 | CML-9 | 200-PW-44018-01X01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8393 |  | 2015-01-30 07:30 | 2015-01-30 15:00 | [36 empty] | 5.325 | CML-9 | CML: type TBC | 3 | 2028-04-22 | 2028-03-17 | 2015-01-30 07:30 | 2.5 | 0.20401 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PG-23411-03C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.3 | 5.2 | 5.4 | 0.095743
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56042-01C02 | CML-3 | 80-DH-56042-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20928 | Rope Access | 2014-05-18 08:00 | 2014-05-18 09:00 | [36 empty] | 5.225 | CML-3 | CML: type TBC | 3 | 2018-04-16 | 2018-11-09 | 2014-05-18 08:00 | 2.5 | 0.61295 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 9 O'Clock | 80 | 5.49 | 80-DH-56042-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.4 | 5.7 | 4.9 | 0.39476
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12625 |  | 2014-01-23 10:00 | 2014-01-23 13:00 | [36 empty] | 5.225 | CML-6 | CML: type TBC | 3 | 2016-06-27 | 2016-10-26 | 2014-01-23 10:00 | 2.5 | 0.98809 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FH-43023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 4.9 | 5.7 | 4.9 | 5.4 | 0.39476
PG05 | Montara_Topside | Yes | Open Drain (56) | Pipework | 250-PG-23003-06C02-PA | CML-18 | 250-PG-23003-06C02-PA CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 858 | Rope Access | 2014-04-02 14:00 | 2014-04-02 15:00 | [36 empty] | 5.875 | CML-18 | CML: Pipe Length | 3 | 2031-08-01 | 2033-07-13 | 2014-04-02 14:00 | 2.5 | 0.16722 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 12 O'Clock | 50 | 5.54 | 50-DN-56101-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.2 | 5.7 | 6.2 | 0.39476
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 80-CG-38459-09C02-P | CML-7 | 80-CG-38459-09C02-P CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 23704 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.725 | CML-7 | CML: Elbow | 3 | 2093-07-29 | 2102-11-29 | 2015-10-30 07:00 | 2.5 | 0.03727 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-CG-38459-01C02-H | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.2 | 5.4 | 5.9 | 5.4 | 0.39476
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 300-WC-40043-01C02 | CML-4 | 300-WC-40043-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1045 |  | 2014-03-20 13:00 | 2014-03-20 14:00 | Check Corrosion Rate of 0.936mm/ yr | [35 empty] | 6.075 | CML-4 | CML: type TBC | 3 | 2017-07-11 | 2017-06-30 | 2014-03-20 13:00 | 2.5 | 0.93576 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 6 O'Clock | 300 | 6.35 | 300-WC-40043-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.1 | 6.5 | 5.6 | 6.1 | 0.36856
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-1 | 50-DH-56137-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21085 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.275 | CML-1 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 5.8 | 3 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.6 | 5.8 | 6.1 | 6.6 | 0.39476
FG02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 25-FG-45455-01C02-E | CML-6 | 25-FG-45455-01C02-E CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2414 |  | 2014-03-19 14:00 | 2014-03-19 15:00 | [36 empty] | 6.325 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-19 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-DC-57019-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.8 | 6 | 6.5 | 0.39476
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56070-01C02 | CML-51 | 50-DH-56070-01C02 CML-51 |  | FPSO 2014 | Pipe Wall Thickness | 3267 | Rope Access | 2014-05-09 07:00 | 2014-05-09 11:00 | [36 empty] | 7.125 | CML-51 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 50 | 5.54 | 50-DH-56070-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.6 | 6.8 | 7.3 | 6.8 | 0.39476
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57451-01C02-P | CML-2 | 50-DC-57451-01C02-P CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1373 | Rope access | 2014-04-05 10:30 | 2014-04-05 11:30 | [36 empty] | 6.875 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57451-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 6.7 | 7 | 6.9 | 6.9 | 0.12583
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43510-01C02 | CML-1 | 300-FL-43510-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20472 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 7.775 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.3 | 12 O'Clock | 300 | 6.35 | 300-FL-43510-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.8 |  | 7.3 | 7.6 | 8.1 | 8.1 | 0.39476
PW02 | Montara_Topside | Yes | Produced Water (44) | Pipework | 300-PW-44037-01C03 | CML-4 | 300-PW-44037-01C03 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 22957 |  | 2015-05-04 07:00 | 2015-05-04 15:00 | [36 empty] | 11.9 | CML-4 | CML: Elbow | 6 | 2091-07-06 | 2082-06-18 | 2015-05-04 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 4.31 | 2.5 | 3.405 | 11.4 | 9 O'Clock | 300 | 10.31 | 300-PW-44037-01C03 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 | 1.6425 | 11.8 | 12.7 | 11.7 | 11.4 | 0.55976
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43500-01C02 | CML-2 | 400-FH-43500-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 5638 | Rope access | 2014-06-21 07:00 | 2014-06-21 10:00 | [36 empty] | 10.025 | CML-2 | CML: type TBC | 3 | 2067-08-12 | 2060-06-18 | 2014-06-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 9.7 | 6 O'Clock | 400 | 7.92 | 400-FH-43500-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.2 |  | 9.9 | 10.6 | 9.7 | 9.9 | 0.39476
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20003-03C03-P | CML-36 | 300-PF-20003-03C03-P CML-36 |  | FPSO 2014 | Pipe Wall Thickness | 21774 | Rope Access - Covers Removed | 2014-10-01 07:00 | 2014-10-01 15:00 | [36 empty] | 14.475 | CML-36 | CML: Fitting | 6 | 2047-03-15 | 2041-02-15 | 2014-10-01 07:00 | 4.9 | 0.27714 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 6 O'Clock | 300 | 14.27 | 300-PF-20003-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.6 | 14.6 | 13.9 | 14.8 | 0.39476
DH01 | Montara_Topside | Yes | Fire Water (71) | Pipework | 80-DH-56004-01C02 | CML54 | 80-DH-56004-01C02 CML54 | yes | FPSO 2015 | Pipe Wall Thickness | 7393 |  | 2015-04-11 07:00 | 2015-04-11 15:00 | [36 empty] | 3.775 | CML54 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-04-11 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.5 | 2.5 | 2.5 | 3.3 | 9 O'Clock | 100 | 3 | 100-WF-71309-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 0.8 |  | 3.6 | 4.1 | 4.1 | 3.3 | 0.39476
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-41 | 50-DH-56062-01C02 CML-41 |  | FPSO 2015 | Pipe Wall Thickness | 9128 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 8.025 | CML-41 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.7 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 7.7 | 8.2 | 8.5 | 7.7 | 0.39476
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56051-01C02 | CML-1 | 80-DH-56051-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20938 | Rope Access | 2014-05-16 08:00 | 2014-05-16 09:00 | [36 empty] | 5.475 | CML-1 | CML: type TBC | 3 | 2018-04-06 | 2018-10-29 | 2014-05-16 08:00 | 2.5 | 0.61646 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 4.9 | 3 O'Clock | 80 | 5.49 | 80-DH-56051-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.6 | 4.9 | 5.8 | 5.6 | 0.39476
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43111-01C02 | CML-3 | 80-FH-43111-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12801 |  | 2014-02-01 07:00 | 2014-02-01 09:00 | [36 empty] | 5.525 | CML-3 | CML: type TBC | 3 | 2020-05-04 | 2021-02-22 | 2014-02-01 07:00 | 2.5 | 0.43153 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 3 O'Clock | 80 | 5.49 | 80-FH-43111-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.4 | 6.1 | 0.39476
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40052-01C02 | CML-3 | 50-WC-40052-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1526 |  | 2014-04-03 11:00 | 2014-04-03 12:00 | [36 empty] | 5.95 | CML-3 | CML: Pipe Length | 3 | 2043-10-24 | 2047-01-28 | 2014-04-03 11:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-WC-40052-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 5.7 | 6.3 | 5.6 | 0.35119
PG08 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 100-FG-45001-09C02 | CML-13 | 100-FG-45001-09C02 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10428 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 10.375 | CML-13 | CML: type TBC | 3 | 2015-08-07 | 2015-01-06 | 2013-11-13 | 4.7 | 2.9421 | A3: Inside Quadrant |  | 8.13 | 4.7 | 6.415 | 9.8 | 6 O'Clock | 100 | 11.13 | 100-FG-45001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.1 |  | 10.5 | 10.5 | 9.8 | 10.7 | 0.39476
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23013-09C03-A | CML-22 | 200-PG-23013-09C03-A CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 20006 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 20.625 | CML-22 | CML: type TBC | 6 | 2033-04-04 | 2029-01-22 | 2014-01-10 | 10.22 | 0.52377 | A4: Left Quadrant |  | 14.62 | 10.22 | 12.42 | 20.3 | 9 O'Clock | 200 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.08 |  | 20.5 | 21.2 | 20.5 | 20.3 | 0.39476
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40021-01C02 | CML-2 | 50-WC-40021-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2097 | Rope Access | 2014-03-28 13:00 | 2014-03-28 14:00 | [36 empty] | 5.925 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-28 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 6 O'Clock | 50 | 5.54 | 50-WC-40021-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 6.2 | 5.6 | 6.2 | 0.32016
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20001-03C03-P | CML-39 | 300-PF-20001-03C03-P CML-39 |  | FPSO 2014 | Pipe Wall Thickness | 21177 | Protective mesh removed/ Rope access | 2014-07-16 07:30 | 2014-07-16 15:00 | [36 empty] | 14.9 | CML-39 | CML: Fitting | 6 | 2107-02-11 | 2090-04-05 | 2014-07-16 07:30 | 4.9 | 0 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 14.5 | 9 O'Clock | 300 | 14.27 | 300-PF-20001-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 14.7 | 15 | 15.4 | 14.5 | 0.39158
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45302-01C02 | CML-2 | 50-FG-45302-01C02 CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 5770 | Rope access | 2014-06-23 11:00 | 2014-06-23 12:00 | [36 empty] | 5.3 | CML-2 | CML: Elbow | 3 | 2017-10-09 | 2018-03-29 | 2014-06-23 11:00 | 2.5 | 0.69711 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 9 O'Clock | 50 | 5.54 | 50-FG-45302-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.5 | 5.2 | 5.7 | 4.8 | 0.39158
PG06 | Montara_Topside | Yes | Open Drain (56) | Pipework | 200-PG-23008-15S01-A | CML-2 | 200-PG-23008-15S01-A CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21137 | Reviewed on 21/11/14. FFS. Recheck in Oct. 18. This line has not been RBI assessed. It is assumed 48m based on other lines on this circuit. | 2014-10-08 07:00 | 2014-10-08 15:00 |  |  | Nestor | 2014-11-21 09:11 | [32 empty] | 5.5 | CML-2 | CML: Elbow | 3 | 2022-10-07 | 2023-10-08 | 2014-10-08 07:00 | 2.5 | 0.32491 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 3 O'Clock | 50 | 5.54 | 50-DH-56559-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.3 | 5.1 | 6 | 5.6 | 0.39158
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-1 | 80-DH-56074-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20946 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 6 | CML-1 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-05-24 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.6 | 6 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.1 | 5.8 | 5.6 | 6.5 | 0.39158
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45023-01C02 | CML-1 | 50-FG-45023-01C02 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1149 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.3 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.8 | 12 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 | -2.9867 | 5.8 | 6.7 | 6.5 | 6.2 | 0.39158
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-15 | 500-WS-50813-1LC CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 1529 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | Reviewed & Accepted - Alarm not deemed critical and line FFS (Loss within manufacturing tolerance). | [30 empty] | Low alarm breach | 11.575 | CML-15 | CML: type TBC | 3 | 2019-07-06 | 2017-03-10 | 2015-06-12 | 2.5 | 2.0639 | A2: Right Quadrant |  | 12.09 | 2.5 | 7.295 | 10.9 | 3 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.4 | 0.34762 | 11.4 | 10.9 | 12.4 | 11.6 | 0.62383
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 25-DH-56142-01C02 | CML-5 | 25-DH-56142-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7526 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 |  |  | Nestor | 2014-11-24 09:40 | [32 empty] | 6.6 | CML-5 | CML: Elbow | 3 | 2042-02-20 | 2041-12-06 | 2015-04-13 07:00 | 2.5 | 0.13394 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 3 O'Clock | 25 | 6.35 | 25-DH-56142-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 7 | 6.1 | 6.5 | 6.8 | 0.39158
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-11 | 500-WS-50813-1LC CML-11 |  | FPSO 2015 | Pipe Wall Thickness | 1526 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | Reviewed & Accepted - Alarm not deemed critical and line FFS (Loss within manufacturing tolerance). | [30 empty] | Low alarm breach | 11.45 | CML-11 | CML: type TBC | 3 | 2019-10-26 | 2017-05-18 | 2015-06-12 | 2.5 | 1.9654 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.1 | 6 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.6 | 0.069524 | 11.9 | 11.4 | 11.1 | 11.4 | 0.33166
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-11 | 500-WS-50813-1LC CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 10793 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 11.575 | CML-11 | CML: type TBC | 3 | 2015-05-01 | 2014-08-07 | 2014-01-03 | 2.5 | 6.5734 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.2 | 9 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.2 | 11.7 | 12.2 | 11.2 | 0.47871
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-4 | 500-WS-50813-1LC CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 10786 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 11.775 | CML-4 | CML: type TBC | 3 | 2015-05-01 | 2014-08-07 | 2014-01-03 | 2.5 | 6.5734 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.2 | 3 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.7 |  | 11.2 | 11.2 | 12.8 | 11.9 | 0.75884
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43157-01C02 | CML-11 | 150-FH-43157-01C02 CML-11 |  | FPSO 2013 | Pipe Wall Thickness | 10667 | Deck Level | 2013-11-18 | 2013-11-18 | [36 empty] | 6.8 | CML-11 | CML: type TBC | 3 | 2016-01-24 | 2015-11-09 | 2013-11-18 | 2.5 | 1.7391 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.3 | 12 O'Clock | 150 | 7.11 | 150-FH-43157-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.7 | 7 | 7.2 | 0.39158
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45003-03C02 | CML-3 | 150-FG-45003-03C02 CML-3 |  | FPSO 2016 | Pipe Wall Thickness | 24369 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.9 | CML-3 | CML: Elbow | 3 | 2036-03-14 | 2032-03-22 | 2016-06-06 07:00 | 2.5 | 0.20217 | A3: Inside Quadrant |  | 4.11 | 2.5 | 3.305 | 6.5 | 6 O'Clock | 150 | 7.11 | 150-FG-45003-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7 | 6.7 | 6.5 | 7.4 | 0.39158
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-14 | 500-WS-50813-1LC CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 10796 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 11.825 | CML-14 | CML: type TBC | 3 | 2015-05-19 | 2014-08-19 | 2014-01-03 | 2.5 | 6.4044 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 11.3 | 9 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.8 |  | 12.1 | 11.8 | 12.1 | 11.3 | 0.37749
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43460-01C02 | CML-4 | 80-FL-43460-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2969 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 6.5 | CML-4 | CML: Equal Tee | 3 | 2062-11-29 | 2056-08-05 | 2014-05-01 14:00 | 0.54 | 0 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 6 | 9 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.46 | 0 | 6.7 | 6.4 | 6.9 | 6 | 0.39158
PG02 | Montara_Topside | No | Gas Compression (23) | Pipework | 250-PG-23039-06D01 | CML-3 | 250-PG-23039-06D01 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10705 | Deck Level | 2013-11-07 | 2013-11-07 | [36 empty] | 10.05 | CML-3 | CML: type TBC | 1 | 2035-06-01 | 2034-04-16 | 2013-11-07 | 5.6 | 0 | A4: Left Quadrant |  | 6.8 | 5.6 | 5.7125 | 9.8 | 9 O'Clock | 250 | 7.8 | 250-PG-23039-06D01 | 30 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.2 |  | 10.3 | 10.1 | 10 | 9.8 | 0.20817
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43460-01C02 | CML-4 | 80-FL-43460-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22248 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 6.5 | CML-4 | CML: Equal Tee | 3 | 2062-11-29 | 2056-08-05 | 2014-05-01 14:00 | 0.54 | 0 | A4: Left Quadrant |  | 2.49 | 0.54 | 1.1719 | 6 | 9 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.46 |  | 6.7 | 6.4 | 6.9 | 6 | 0.39158
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-5 | 150-FH-43518-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2705 | Rope Access | 2014-03-12 09:00 | 2014-03-12 15:00 | [36 empty] | 7.6 | CML-5 | CML: Elbow | 3 | 208638 | 2393-09-16 | 2014-03-12 09:00 | 1.23 | 0.01284 | A2: Right Quadrant |  | 4.11 | 1.23 | 2.2256 | 7.1 | 3 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.87 | 0 | 8 | 7.1 | 7.5 | 7.8 | 0.39158
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FH-43518-01C02 | CML-5 | 150-FH-43518-01C02 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 344 | Rope Access | 2014-03-12 | 2014-03-12 | [36 empty] | 7.6 | CML-5 | CML: Elbow | 3 | 208418 | 2393-03-17 | 2014-03-12 | 1.23 | 0.01285 | A2: Right Quadrant |  | 4.11 | 1.23 | 2.2256 | 7.1 | 3 O'Clock | 150 | 7.11 | 150-FH-43518-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.87 |  | 8 | 7.1 | 7.5 | 7.8 | 0.39158
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43012-01C02 | CML-6 | 200-FH-43012-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2836 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.9 | CML-6 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 7.5 | 9 O'Clock | 200 | 6.35 | 200-FH-43012-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.16 |  | 8 | 7.7 | 8.4 | 7.5 | 0.39158
FL02 | Montara_Topside | Yes | Potable Water (53) | Pipework | 50-FL-43454-01C02-P | CML-2 | 50-FL-43454-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8203 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 9.5 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.1 | 9 O'Clock | 50 | 5.54 | 50-WD-53016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.3 | 9.6 | 10 | 9.1 | 0.39158
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8992 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.325 | CML-1 | CML: type TBC | 3 | 2029-01-06 | 2030-09-09 | 2015-02-28 07:00 | 2.5 | 0.19473 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 5.4 | 5.4 | 0.095743
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-3 | 300-PG-23400-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20037 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 10.075 | CML-3 | CML: Pipe Length | 6 | 2019-08-25 | 2020-03-16 | 2014-05-29 07:00 | 5.22 | 0.81606 | A4: Left Quadrant |  | 4.31 | 5.22 | 4.765 | 9.5 | 9 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.28 | 0 | 10.1 | 10.1 | 10.6 | 9.5 | 0.45
RP01 | Montara_Topside | No | Gas Compression (23) | Pipework | 300-PG-23400-01C03-P | CML-3 | 300-PG-23400-01C03-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 520 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 10 | CML-3 | CML: Pipe Length | 6 | 2018-04-29 | 2018-10-06 | 2014-03-13 09:00 | 5.22 | 1.036 | A3: Inside Quadrant |  | 4.31 | 5.22 | 4.765 | 9.5 | 6 O'Clock | 300 | 10.31 | 300-PG-23400-01C03-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.28 |  | 9.9 | 10.6 | 9.5 | 10 | 0.45461
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-3 | 50-WC-40451-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10143 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 5.9 | CML-3 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2013-11-09 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 6.2 | 5.6 |  | 5.9 | 0.3
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56074-01C02 | CML-6 | 80-DH-56074-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20951 | Rope Access | 2014-05-24 07:00 | 2014-05-24 09:00 | [36 empty] | 6.3 | CML-6 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.9 | 3 O'Clock | 80 | 5.49 | 80-DH-56074-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.8 | 5.9 | 6.1 | 6.4 | 0.39158
CG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38500-01C02 | CML-1 | 50-CG-38500-01C02 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23288 | Re-check on line | 2015-07-04 09:30 | 2015-07-04 12:00 | [36 empty] | 5.1 | CML-1 | CML: Elbow | 3 | 2020-12-23 | 2021-10-16 | 2015-07-04 09:30 | 2.5 | 0.40163 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38500-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 | 0.427 | 5.6 | 4.7 | 4.9 | 5.2 | 0.39158
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-15 | 500-WS-50813-1LC CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 10797 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 11.5333 | CML-15 | CML: type TBC | 3 | 2015-06-07 | 2014-08-31 | 2014-01-03 | 2.5 | 6.2354 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.4 | 6 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.4 | 11.8 | 11.4 |  | 0.23094
PG05 | Montara_Topside | Yes | Flare (43) | Pipework | 250-PG-23003-06C02-PA | CML-10 | 250-PG-23003-06C02-PA CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12880 |  | 2014-02-03 08:00 | 2014-02-03 10:00 | [36 empty] | 5.9 | CML-10 | CML: type TBC | 3 | 2017-04-05 | 2017-05-21 | 2014-02-03 08:00 | 2.5 | 0.91496 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 9 O'Clock | 100 | 6.02 | 100-FL-43154-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.8 | 6.1 | 6.3 | 5.4 | 0.39158
CG05 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38454-01C02-H | CML-10 | 50-CG-38454-01C02-H CML-10 | yes | FPSO 2015 | Pipe Wall Thickness | 23674 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.1 | CML-10 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.2 |  | 8.2 | 7.7 | 7.9 | 8.6 | 0.39158
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-18 | 200-PW-44018-01X01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 9049 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 5.275 | CML-18 | CML: type TBC | 3 | 2029-01-15 | 2030-09-19 | 2015-03-01 07:00 | 2.5 | 0.19443 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.2 | 5.4 | 5.3 | 0.095743
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43508-01C02 | CML-25 | 400-FH-43508-01C02 CML-25 |  | FPSO 2015 | Pipe Wall Thickness | 6574 | Rope Access | 2015-03-30 07:00 | 2015-03-30 15:00 | [36 empty] | 9.3 | CML-25 | CML: Pipe Length | 3 | 2067-08-12 | 2060-06-18 | 2015-03-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 4.92 | 2.5 | 3.215 | 8.8 | 6 O'Clock | 400 | 7.92 | 400-FH-43508-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.3 |  | 9.7 | 9.2 | 8.8 | 9.5 | 0.39158
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20004-03C03-P | CML-28 | 300-PG-20004-03C03-P CML-28 |  | FPSO 2014 | Pipe Wall Thickness | 6151 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.3 | CML-28 | CML: Fitting | 6 | 2035-07-16 | 2031-07-24 | 2014-07-11 07:30 | 4.9 | 0.42325 | A2: Right Quadrant |  | 8.27 | 4.9 | 6.585 | 13.8 | 3 O'Clock | 300 | 14.27 | 300-PG-20004-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 14.7 | 13.8 | 14.5 | 14.2 | 0.39158
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38477-01C02-P | CML-13 | 50-CG-38477-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 5510 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 17.95 | CML-13 | CML: Pipe Length | 3 | 2018-04-15 | 2017-08-03 | 2014-05-31 07:00 | 14.06 | 0.86167 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 17.4 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.34 |  | 18 | 17.4 | 18.1 | 18.3 | 0.3873
CG04 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-CG-38477-01C02-P | CML-13 | 50-CG-38477-01C02-P CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20658 | Rope access (Re-checking line) | 2014-05-31 07:00 | 2014-05-31 09:00 | [36 empty] | 17.95 | CML-13 | CML: Pipe Length | 3 | 2018-04-15 | 2017-08-03 | 2014-05-31 07:00 | 14.06 | 0.86167 | A2: Right Quadrant |  | 15.26 | 14.06 | 14.66 | 17.4 | 3 O'Clock | 200 | 18.26 | 200-PG-23505-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.34 | -0.91345 | 18 | 17.4 | 18.1 | 18.3 | 0.3873
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-5 | 500-WS-50813-1LC CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 10787 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 12.075 | CML-5 | CML: type TBC | 3 | 2015-06-07 | 2014-08-31 | 2014-01-03 | 2.5 | 6.2354 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.4 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.9 |  | 11.4 | 12.6 | 12.2 | 12.1 | 0.49917
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-14 | 500-WS-50813-1LC CML-14 |  | FPSO 2015 | Pipe Wall Thickness | 1528 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | [31 empty] | Low alarm breach | 12 | CML-14 | CML: type TBC | 3 | 2020-09-25 | 2017-12-12 | 2015-06-12 | 2.5 | 1.7191 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 11.6 | 9 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 | -0.20857 | 12 | 12.2 | 12.2 | 11.6 | 0.28284
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-18 | 500-WS-50813-1LC CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 10800 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 12.125 | CML-18 | CML: type TBC | 3 | 2015-07-20 | 2014-09-26 | 2014-01-03 | 2.5 | 5.8975 | A2: Right Quadrant |  | 12.09 | 2.5 | 7.295 | 11.6 | 3 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 12.3 | 11.6 | 12.3 | 12.3 | 0.35
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-25 | 200-FH-43025-01C02 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 2498 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 10.75 | CML-25 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 10.2 | 3 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 11.1 | 10.2 | 10.8 | 10.9 | 0.3873
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40011-01C02 | CML-9 | 50-WC-40011-01C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1894 | Rope Access | 2014-03-25 13:00 | 2014-03-25 14:00 | [36 empty] | 5.825 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-25 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 12 O'Clock | 50 | 5.54 | 50-WC-40011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.9 | 5.7 | 6.1 | 0.22174
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45020-03C02 | CML-23 | 50-FG-45020-03C02 CML-23 | yes | FPSO 2013 | Pipe Wall Thickness | 10595 | Deck Level | 2013-11-17 | 2013-11-17 | [36 empty] | 4.85 | CML-23 | CML: type TBC | 3 | 2014-07-20 | 2014-07-17 | 2013-11-17 | 2.5 | 2.6781 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.3 | 6 O'Clock | 50 | 5.54 | 50-FG-45020-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 1.8 |  | 5.2 | 5 | 4.3 | 4.9 | 0.3873
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-9 | 500-WS-50813-1LC CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 10791 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 12.225 | CML-9 | CML: type TBC | 3 | 2015-07-20 | 2014-09-26 | 2014-01-03 | 2.5 | 5.8975 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.6 | 6 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.1 |  | 12.9 | 12.3 | 11.6 | 12.1 | 0.53774
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42313-01S01 | CML-5 | 40-CI-42313-01S01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7520 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.775 | CML-5 | CML: type TBC | 1 | 2038-11-14 | 2031-05-02 | 2015-04-13 07:00 | 2.5 | 0.18215 | A4: Left Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.8 | 9 O'Clock | 40 | 7.14 | 40-CI-42313-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.7 | 8.6 | 8 | 6.8 | 0.75
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42310-01S01 | CML-7 | 40-CI-42310-01S01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 7496 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 8.125 | CML-7 | CML: type TBC | 1 | 2038-11-14 | 2031-05-02 | 2015-04-13 07:00 | 2.5 | 0.18215 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.8 | 12 O'Clock | 40 | 7.14 | 40-CI-42310-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.9 | 9.3 | 8.5 | 1.0532
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56121-01C02 | CML-3 | 50-DH-56121-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21041 | Rope Access | 2014-05-19 07:00 | 2014-05-19 08:00 | [36 empty] | 5.15 | CML-3 | CML: type TBC | 3 | 2016-07-14 | 2016-11-13 | 2014-05-19 07:00 | 2.5 | 0.97391 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-DH-56121-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 5.3 | 4.6 | 5.5 | 5.2 | 0.3873
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-5 | 50-FH-43011-01C02 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7955 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 6.25 | CML-5 | CML: Elbow | 3 | 2017-08-03 | 2017-01-14 | 2015-01-18 08:00 | 2.5 | 1.2976 | A4: Left Quadrant |  | 4.92 | 2.5 | 3.215 | 5.8 | 9 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.3 |  | 6.7 | 6.1 | 6.4 | 5.8 | 0.3873
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63015-01E01 | CML-5 | 50-AU-63015-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 9036 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-03-01 07:00 | 2015-03-01 09:00 | [36 empty] | 6.85 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-01 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 50 | 5.54 | 50-AU-63015-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7 | 6.8 | 6.8 | 0.1
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-40 | 50-AI-63004-01E01 CML-40 |  | FPSO 2015 | Pipe Wall Thickness | 9031 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.8 | CML-40 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.8 | 6.8 | 6.8 | 0
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63004-01E01 | CML-34 | 50-AI-63004-01E01 CML-34 |  | FPSO 2015 | Pipe Wall Thickness | 9025 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 6.8 | CML-34 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-28 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.8 | 6.8 | 6.8 | 0
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67003-01E01 | CML-7 | 50-GN-67003-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8502 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-02 07:30 | 2015-02-02 15:00 | [36 empty] | 7.05 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-02 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 6 O'Clock | 50 | 5.54 | 50-GN-67003-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.3 | 7.2 | 6.8 | 6.9 | 0.23805
GN01 | Montara_Topside | No | Nitrogen (67) | Pipework | 50-GN-67008-01E01 | CML-1 | 50-GN-67008-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8463 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.8 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 50 | 5.54 | 50-GN-67008-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.8 | 6.8 | 6.8 | 0
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AU-63022-01E01 | CML-1 | 50-AU-63022-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8439 |  | 2015-02-01 07:30 | 2015-02-01 15:00 | [36 empty] | 6.95 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-01 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 50 | 5.54 | 50-AU-63022-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.4 | 6.8 | 6.8 | 6.8 | 0.3
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 50-AI-63450-01E01 | CML-1 | 50-AI-63450-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8320 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-28 07:30 | 2015-01-28 15:00 | [36 empty] | 6.825 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-28 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 9 O'Clock | 50 | 5.54 | 50-AI-63450-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.8 | 6.9 | 6.8 | 0.05
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53016-01E01 | CML-1 | 50-WD-53016-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8202 | Reducing Hose Coupling | 2015-01-25 07:30 | 2015-01-25 15:00 | [36 empty] | 7.3 | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-25 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 3 O'Clock | 50 | 5.54 | 50-WD-53016-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.5 | 6.8 | 7.4 | 7.5 | 0.33665
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-26 | 50-WD-53007-01E01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 8165 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 7.1 | CML-26 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 3 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.4 | 6.8 | 6.9 | 7.3 | 0.29439
WD01 | Montara_Topside | No | Potable Water (53) | Pipework | 50-WD-53007-01E01 | CML-4 | 50-WD-53007-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8143 | Reducing Hose Coupling | 2015-01-24 07:30 | 2015-01-24 15:00 | [36 empty] | 7.05 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-24 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.8 | 6 O'Clock | 50 | 5.54 | 50-WD-53007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.7 | 6.8 | 6.9 | 0.43589
OL01 | Montara_Topside | No | Lube Oil (69) | Pipework | 100-OL-69001-01S01 | CML-17 | 100-OL-69001-01S01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 8119 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 7.025 | CML-17 | CML: type TBC | 1 | 2048-08-12 | 2039-10-11 | 2015-01-23 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.02 | 2.5 | 3.3838 | 6.8 | 9 O'Clock | 100 | 6.02 | 100-OL-69001-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7 | 7.5 | 6.8 | 0.3304
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 100-DH-56087-01C02 | CML-10 | 100-DH-56087-01C02 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8040 | Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Jan. 2020). RBI to be updated | 2015-01-20 14:30 | 2015-01-20 15:00 |  |  | Administrator | 2015-09-08 16:32 | [32 empty] | 6.85 | CML-10 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2015-01-20 14:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.3 | 3 O'Clock | 100 | 6.02 | 100-DH-56087-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.9 | 6.3 | 7.2 | 7 | 0.3873
CG04 | Montara_Topside | Yes | Separation (20) | Pipework | 50-CG-38452-09C02-P | CML-24 | 50-CG-38452-09C02-P CML-24 |  | FPSO 2015 | Pipe Wall Thickness | 8821 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.15 | CML-24 | CML: Pipe Length | 3 | 2029-11-20 | 2027-08-09 | 2015-02-21 07:00 | 1.1 | 0.3185 | A3: Inside Quadrant |  | 3.35 | 1.1 | 1.8281 | 5.8 | 6 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 6.7 | 6 | 5.8 | 6.1 | 0.3873
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57303-03C03 | CML-1 | 20-DC-57303-03C03 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 7926 |  | 2015-01-17 10:30 | 2015-01-17 12:00 | [36 empty] | 7 | CML-1 | CML: type TBC | 6 | 2044-01-06 | 2058-09-17 | 2015-01-17 10:30 | 2.5 | 0 | A2: Right Quadrant |  | -0.44 | 2.5 | 1.03 | 6.8 | 6 O'Clock | 20 | 5.56 | 20-DC-57303-03C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.3 | 6.8 | 6.8 | 7.1 | 0.24495
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-5 | 500-WS-50813-1LC CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 1521 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | [31 empty] | Low alarm breach | 12.25 | CML-5 | CML: type TBC | 3 | 2020-12-12 | 2018-01-29 | 2015-06-12 | 2.5 | 1.6698 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.7 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 | -0.20857 | 11.7 | 12.8 | 12.5 | 12 | 0.49329
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-17 | 500-WS-50813-1LC CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 1530 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | [31 empty] | Low alarm breach | 14.3 | CML-17 | CML: type TBC | 3 | 2021-03-06 | 2018-03-22 | 2015-06-12 | 2.5 | 1.6206 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.8 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 | 1.3905 | 11.8 | 16.7 | 15.3 | 13.4 | 2.1463
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-7 | 500-WS-50813-1LC CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 1523 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | [31 empty] | Low alarm breach | 12.4 | CML-7 | CML: type TBC | 3 | 2021-03-06 | 2018-03-22 | 2015-06-12 | 2.5 | 1.6206 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.8 | 6 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 | 0.41714 | 12.6 | 12.7 | 11.8 | 12.5 | 0.40825
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45019-03C02 | CML-8 | 50-FG-45019-03C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2599 | Rope Access | 2014-04-26 08:00 | 2014-04-26 09:00 | [36 empty] | 10.35 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-04-26 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 9.9 | 3 O'Clock | 50 | 5.54 | 50-FG-45019-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.4 | -12.3665 | 10.8 | 9.9 | 10.5 | 10.2 | 0.3873
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40401-01C02 | CML-6 | 200-WC-40401-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 7922 | Line is FFS. Current RBI frequency is 48m. Rest of CML’s have low CR’s Action: Recheck CML-5 & 6 in two years (Jan. 2017) to confirm CR | 2015-01-17 08:00 | 2015-01-17 09:00 | Check Corrosion Rate of 0.46mm/ yr |  | Administrator | 2015-09-08 11:21 | [32 empty] | 5.7 | CML-6 | CML: Elbow | 3 | 2021-10-13 | 2021-09-20 | 2015-01-17 08:00 | 2.5 | 0.45983 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.6 | 3 O'Clock | 200 | 6.35 | 200-WC-40401-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 5.9 | 5.7 | 0.14142
PG03 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20037-03C03-PA | CML-1 | 300-PG-20037-03C03-PA CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 21376 | Protective mesh removed/Rope access | 2014-06-29 13:00 | 2014-06-29 15:00 | Check Corrosion Rate of 0.714mm/ yr | [35 empty] | 13.85 | CML-1 | CML: Pipe Length | 6 | 2025-12-04 | 2023-11-13 | 2014-06-29 13:00 | 5.33 | 0.71416 | A3: Inside Quadrant |  | 8.27 | 5.33 | 6.8 | 13.5 | 6 O'Clock | 300 | 14.27 | 300-PG-20037-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.17 |  | 13.7 | 14.4 | 13.5 | 13.8 | 0.3873
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-31 | 300-PF-20500-03C03-P CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 21651 |  | 2014-09-27 07:00 | 2014-09-27 15:00 | [36 empty] | 14.65 | CML-31 | CML: Pipe Length | 6 | 2190-07-15 | 2158-09-07 | 2014-09-27 07:00 | 4.9 | 0.05287 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.2 | 6 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 14.8 | 15.1 | 14.2 | 14.5 | 0.3873
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-1 | 25-FG-45455-01C02-E CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1750 | Rope access | 2014-04-27 07:00 | 2014-04-27 08:00 | [36 empty] | 5.55 | CML-1 | CML: Fitting | 3 | 2019-08-31 | 2020-05-01 | 2014-04-27 07:00 | 2.5 | 0.48624 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.1 | 6 O'Clock | 50 | 5.54 | 50-FH-43117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.6 |  | 5.4 | 5.7 | 5.1 | 6 | 0.3873
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-1 | 200-PW-44018-01X01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8877 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.275 | CML-1 | CML: type TBC | 3 | 2028-12-11 | 2030-08-11 | 2015-02-25 09:30 | 2.5 | 0.19562 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.4 | 5.2 | 5.2 | 0.095743
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FL-43015-01C02 | CML-4 | 80-FL-43015-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20409 | Reviewed on 20/11/14. Line is FFS. Repeat on Oct. 19 | 2014-10-06 07:00 | 2014-10-06 15:00 |  |  | Nestor | 2014-11-20 11:26 | [32 empty] | 5.95 | CML-4 | CML: Equal Tee | 3 | 2043-04-25 | 2046-10-17 | 2014-10-06 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-FL-43015-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.1 | 6.4 | 5.8 | 0.3873
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43080-01C02 | CML-2 | 300-FL-43080-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2381 | Rope Access | 2014-03-19 07:00 | 2014-03-19 09:00 | [36 empty] | 7.05 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 300 | 6.35 | 300-FL-43080-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.2 | 7.1 | 6.5 | 7.4 | 0.3873
PG08 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-PG-23300-25C02 | CML-6 | 25-PG-23300-25C02 CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 20673 | Rope Access | 2014-05-27 09:30 | 2014-05-27 12:00 | [36 empty] | 8.55 | CML-6 | CML: Elbow | 3 | 2018-08-13 | 2017-09-04 | 2014-05-27 09:30 | 4.4 | 0.90137 | A4: Left Quadrant |  | 6.09 | 4.4 | 5.245 | 8.2 | 9 O'Clock | 25 | 9.09 | 25-PG-23300-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 8.4 | 8.5 | 9.1 | 8.2 | 0.3873
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-19 | 50-PF-20300-03C03-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21585 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.45 | CML-19 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 8.9 | 12 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.4 |  | 8.9 | 9.6 | 9.8 | 9.5 | 0.3873
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-16 | 500-WS-50813-1LC CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 10798 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 12.1 | CML-16 | CML: type TBC | 3 | 2015-09-05 | 2014-10-25 | 2014-01-03 | 2.5 | 5.5595 | A2: Right Quadrant |  | 12.09 | 2.5 | 7.295 | 11.8 | 3 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.6 | 11.8 | 11.9 | 12.1 | 0.3559
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-6 | 500-WS-50813-1LC CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 10788 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 12.25 | CML-6 | CML: type TBC | 3 | 2015-09-05 | 2014-10-25 | 2014-01-03 | 2.5 | 5.5595 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 11.8 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 11.8 | 12 | 12.4 | 12.8 | 0.44347
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-6 | 500-WS-50813-1LC CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 1522 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | [31 empty] | Low alarm breach | 12.45 | CML-6 | CML: type TBC | 3 | 2021-06-03 | 2018-05-16 | 2015-06-12 | 2.5 | 1.5713 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 11.9 | 9 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 | -0.069524 | 12.7 | 12.8 | 12.4 | 11.9 | 0.40415
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-4 | 500-WS-50813-1LC CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 1520 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | [31 empty] | Low alarm breach | 12.175 | CML-4 | CML: type TBC | 3 | 2021-06-03 | 2018-05-16 | 2015-06-12 | 2.5 | 1.5713 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 11.9 | 9 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.4 | -0.48667 | 12.1 | 12.6 | 12.1 | 11.9 | 0.29861
PG05 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 250-PG-23003-06C02-PA | CML-14 | 250-PG-23003-06C02-PA CML-14 | Yes | FPSO 2014 | Pipe Wall Thickness | 24252 | Protective mesh removed/Rope Access | 2014-09-24 07:00 | 2014-09-24 15:00 | [36 empty] | 15.05 | CML-14 | CML: Elbow | 3 | 2032-09-16 | 2029-08-14 | 2014-09-24 07:00 | 7.9 | 0.37238 | A3: Inside Quadrant |  | 12.09 | 7.9 | 9.0519 | 14.6 | 6 O'Clock | 250 | 15.09 | 250-PG-23003-06C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 15.5 | 15.2 | 14.6 | 14.9 | 0.3873
FG01 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45024-01C02 | CML-18 | 50-FG-45024-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1201 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 9.95 | CML-18 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.4 | 6 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.9 |  | 10.3 | 10 | 9.4 | 10.1 | 0.3873
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-31 | 300-PG-20005-03C03-P CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 22793 | New location | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 14.45 | CML-31 | CML: Reducing Tee | 6 | 2061-10-05 | 2053-01-24 | 2015-04-29 07:00 | 4.9 | 0.19368 | A4: Left Quadrant |  | 8.27 | 4.9 | 6.585 | 13.9 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 14.8 | 14.5 | 14.6 | 13.9 | 0.3873
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-8 | 500-WS-50813-1LC CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 10790 | Deck Level | 2014-01-03 | 2014-01-03 | [35 empty] | Low alarm breach | 12.375 | CML-8 | CML: type TBC | 3 | 2015-10-29 | 2014-11-27 | 2014-01-03 | 2.5 | 5.2215 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 12 | 6 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.5 |  | 12.3 | 13.1 | 12 | 12.1 | 0.49917
PG02 | Montara_Topside | No | Separation (20) | Pipework | 250-PG-20042-01D01-P | CML-6 | 250-PG-20042-01D01-P CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 21439 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 7 | CML-6 | CML: Elbow | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 5.35 | 2.5 | 3.925 | 6.8 | 6 O'Clock | 250 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7 | 7.2 | 6.8 | 7 | 0.1633
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-9 | 50-DH-56062-01C02 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 9096 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.25 | CML-9 | CML: type TBC | 3 | 2019-10-01 | 2020-06-05 | 2015-03-02 07:00 | 2.5 | 0.47959 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 4.7 | 5.6 | 5.4 | 5.3 | 0.3873
FG02 | Montara_Topside | Yes | Flare (43) | Pipework | 25-FG-45455-01C02-E | CML-2 | 25-FG-45455-01C02-E CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1751 | Rope access | 2014-04-27 07:00 | 2014-04-27 08:00 | [36 empty] | 5.25 | CML-2 | CML: Elbow | 3 | 2017-09-16 | 2018-03-04 | 2014-04-27 07:00 | 2.5 | 0.70725 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.9 | 6 O'Clock | 50 | 5.54 | 50-FH-43117-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.4 |  | 5.8 | 5.2 | 4.9 | 5.1 | 0.3873
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-7 | 500-WS-50813-1LC CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 10789 | Deck Level | 2014-01-03 | 2014-01-03 | [36 empty] | 12.5667 | CML-7 | CML: type TBC | 3 | 2016-03-07 | 2015-02-16 | 2014-01-03 | 2.5 | 4.5456 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 12.4 | 9 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.9 |  |  | 12.9 | 12.4 | 12.4 | 0.28868
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43308-01C02-E | CML-4 | 200-PL-43308-01C02-E CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 8797 | LAGGING REMOVAL REQUIRED | 2015-02-15 13:00 | 2015-02-15 15:00 | [36 empty] | 6.575 | CML-4 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-02-15 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-PL-43308-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.5 | 6.9 | 6.4 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43303-01C02 | CML-2 | 250-FH-43303-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12940 |  | 2014-01-27 10:00 | 2014-01-27 12:00 | [36 empty] | 6.75 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-27 10:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 6 O'Clock | 250 | 6.35 | 250-FH-43303-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 7.3 | 6.4 | 6.6 | 0.3873
CG04 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-CG-38452-09C02-P | CML-19 | 50-CG-38452-09C02-P CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 20358 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.75 | CML-19 | CML: Elbow | 3 | 2059-07-07 | 2055-11-27 | 2014-10-09 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.2 | 3 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.7 |  | 7.9 | 7.2 | 8.1 | 7.8 | 0.3873
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-13 | 500-WS-50813-1LC CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 1527 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | [32 empty] | 13.1 | CML-13 | CML: type TBC | 3 | 2023-09-03 | 2019-10-07 | 2015-06-12 | 2.5 | 1.2265 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 12.6 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.1 | 0.2781 | 12.6 | 13.1 | 14 | 12.7 | 0.6377
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 50-FH-43011-01C02 | CML-12 | 50-FH-43011-01C02 CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 7962 |  | 2015-01-18 08:00 | 2015-01-18 10:30 | [36 empty] | 5.65 | CML-12 | CML: Elbow | 3 | 2016-09-01 | 2016-03-28 | 2015-01-18 08:00 | 2.5 | 1.6648 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 5.2 | 12 O'Clock | 50 | 7.92 | 50-FH-43011-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 6.1 | 5.5 | 5.8 | 0.3873
PW03 | Montara_Topside | Yes | Steam (55) | Pipework | 200-PW-44018-01X01 | CML-13 | 200-PW-44018-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 8843 |  | 2015-02-24 07:00 | 2015-02-24 11:00 | [36 empty] | 5.275 | CML-13 | CML: type TBC | 3 | 2031-04-17 | 2033-05-16 | 2015-02-24 07:00 | 2.5 | 0.16714 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.2 | 9 O'Clock | 80 | 5.49 | 80-SC-55002-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.2 | 5.3 | 5.2 | 0.095743
PW03 | Montara_Topside | Yes | Fire Water (71) | Pipework | 200-PW-44018-01X01 | CML-6 | 200-PW-44018-01X01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 6415 | Rope Access | 2015-03-21 07:00 | 2015-03-21 15:00 | [36 empty] | 5.3 | CML-6 | CML: type TBC | 0.5 | 2018-06-01 | 2018-06-01 | 2015-03-21 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.5 | 2.5 | 2.5 | 5.2 | 3 O'Clock | 100 | 3 | 100-WF-71336-01K01 | 01K01 - SPECIAL | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.2 | 5.4 | 5.3 | 0.08165
PW01 | Montara_Topside | Yes | Separation (20) | Pipework | 100-PW-20021-01C02-P | CML-15 | 100-PW-20021-01C02-P CML-15 |  | FPSO 2015 | Pipe Wall Thickness | 22833 | Rope Access | 2015-04-30 07:00 | 2015-04-30 15:00 | [36 empty] | 5.6 | CML-15 | CML: Elbow | 3 | 2022-10-05 | 2023-01-26 | 2015-04-30 07:00 | 2.5 | 0.37635 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.3 | 12 O'Clock | 100 | 6.02 | 100-PW-20021-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 1.2711 | 5.3 | 5.5 | 5.8 | 5.8 | 0.24495
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-17 | 200-PW-44018-01X01 CML-17 |  | FPSO 2015 | Pipe Wall Thickness | 9008 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-28 07:00 | 2015-02-28 09:00 | [36 empty] | 5.3 | CML-17 | CML: type TBC | 3 | 2029-01-06 | 2030-09-09 | 2015-02-28 07:00 | 2.5 | 0.19473 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63004-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.3 | 5.4 | 5.2 | 0.08165
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-23 | 200-PL-20034-03C02-P CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 21620 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.55 | CML-23 | CML: Fitting | 3 | 2030-12-15 | 2027-12-11 | 2014-06-28 13:00 | 3.61 | 0.26035 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.9 | 6 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.29 |  | 9.2 | 8.7 | 7.9 | 8.4 | 0.54467
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-5 | 250-PW-20041-03C03-P CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 23491 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 12.375 | CML-5 | CML: Fitting | 6 | 2033-12-26 | 2030-11-16 | 2015-07-27 07:00 | 4.1 | 0.41778 | A1: Outside Quadrant |  | 6.7 | 4.1 | 5.4 | 11.8 | 12 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 | -0.096058 | 11.8 | 12.2 | 12.8 | 12.7 | 0.46458
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43025-01C02 | CML-16 | 200-FH-43025-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2489 | Rope Access | 2014-03-24 07:00 | 2014-03-24 12:00 | [36 empty] | 8.65 | CML-16 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-24 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.3 | 12 O'Clock | 200 | 6.35 | 200-FH-43025-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.5 | 8.6 | 9.2 | 0.3873
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57036-01C02 | CML-7 | 100-DC-57036-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1413 | Rope access | 2014-04-07 07:00 | 2014-04-07 12:00 | [36 empty] | 7.1 | CML-7 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-04-07 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.8 | 12 O'Clock | 100 | 6.02 | 100-DC-57036-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.1 | 7.2 | 7.3 | 0.21602
CG03 | Montara_Topside | Yes | Separation (20) | Pipework | 80-CG-38486-09C02-P | CML-3 | 80-CG-38486-09C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21470 | Protective mesh removed | 2014-06-28 07:00 | 2014-06-28 08:00 | [36 empty] | 16.225 | CML-3 | CML: Reducer | 6 | 2099-09-17 | 2086-07-24 | 2014-06-28 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 15.7 | 6 O'Clock | 80 | 11.13 | 80-PG-20047-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 13.2 |  | 16.2 | 16.4 | 15.7 | 16.6 | 0.38622
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 400-FH-43029-01C02 | CML-3 | 400-FH-43029-01C02 CML-3 |  | FPSO 2013 | Pipe Wall Thickness | 10019 | Deck Level | 2013-11-04 | 2013-11-04 | [36 empty] | 7.725 | CML-3 | CML: Elbow | 3 | 2018-12-12 | 2018-03-18 | 2013-11-04 | 2.48 | 0.98269 | A2: Right Quadrant |  | 4.92 | 2.48 | 3.205 | 7.5 | 6 O'Clock | 400 | 7.92 | 400-FH-43029-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.02 |  | 7.6 | 7.5 | 7.5 | 8.3 | 0.38622
PG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 80-PG-23046-06C03 | CML-2 | 80-PG-23046-06C03 CML-2 | Yes | FPSO 2014 | Pipe Wall Thickness | 20579 | Rope Access | 2014-05-27 07:00 | 2014-05-27 08:00 | [36 empty] | 8.775 | CML-2 | CML: Pipe Length | 6 | 2016-03-21 | 2015-10-30 | 2014-05-27 07:00 | 2.8 | 2.9683 | A2: Right Quadrant |  | 5.13 | 2.8 | 3.965 | 8.2 | 3 O'Clock | 80 | 11.13 | 80-PG-23046-06C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 9 | 8.2 | 8.9 | 9 | 0.38622
FG01 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-FG-45044-03C02 | CML-16 | 50-FG-45044-03C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 20816 | Protective mesh removed | 2014-07-18 11:00 | 2014-07-18 16:00 | [36 empty] | 9.175 | CML-16 | CML: Fitting | 3 | 2063-09-30 | 2050-09-06 | 2014-07-18 11:00 | 2.5 | 0.12389 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 8.6 | 3 O'Clock | 50 | 8.74 | 50-CG-38487-09C02-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.1 |  | 9.3 | 8.6 | 9.4 | 9.4 | 0.38622
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-31 | 200-PW-44018-01X01 CML-31 |  | FPSO 2015 | Pipe Wall Thickness | 8955 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.3 | CML-31 | CML: type TBC | 3 | 2028-12-20 | 2030-08-21 | 2015-02-26 09:00 | 2.5 | 0.19532 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.2 | 5.3 | 5.4 | 0.08165
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45036-03C02 | CML-4 | 50-FG-45036-03C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2576 |  | 2014-04-26 13:00 | 2014-04-26 14:00 | [36 empty] | 5.825 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2043-08-12 | 2014-04-26 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-FG-45036-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.6 | 5.6 | 5.7 | 6.4 | 0.38622
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-5 | 200-PL-20034-03C02-P CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 21602 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.2 | CML-5 | CML: Pipe Length | 3 | 2030-12-15 | 2027-12-11 | 2014-06-28 13:00 | 3.61 | 0.26035 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.9 | 12 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.29 |  | 7.9 | 8.3 | 8.1 | 8.5 | 0.2582
FL02 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 50-FL-43454-01C02-P | CML-16 | 50-FL-43454-01C02-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 2562 | Rope Access | 2014-04-03 13:00 | 2014-04-03 15:00 | [36 empty] | 9.625 | CML-16 | CML: type TBC | 3 | 2075-10-24 | 2059-08-12 | 2014-04-03 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 5.74 | 2.5 | 4.12 | 9.1 | 3 O'Clock | 50 | 8.74 | 50-CG-24002-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.6 | 9.1 | 10 | 9.8 | 0.38622
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-12 | 300-PG-20005-03C03-P CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 6168 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 12.775 | CML-12 | CML: Pipe Length | 6 | 2018-12-22 | 2017-12-22 | 2014-07-11 07:30 | 4.9 | 1.684 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 12.4 | 6 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.5 |  | 12.8 | 13.3 | 12.4 | 12.6 | 0.38622
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20041-03C03-P | CML-8 | 250-PW-20041-03C03-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 21417 | Protective mesh removed | 2014-07-12 07:30 | 2014-07-12 15:00 | [36 empty] | 12.225 | CML-8 | CML: Fitting | 6 | 2024-01-17 | 2022-06-09 | 2014-07-12 07:30 | 4.1 | 0.80849 | A2: Right Quadrant |  | 6.7 | 4.1 | 5.4 | 11.8 | 3 O'Clock | 250 | 12.7 | 250-PW-20041-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 |  | 12.4 | 11.8 | 12.5 | 12.2 | 0.30957
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40451-01C02 | CML-7 | 50-WC-40451-01C02 CML-7 |  | FPSO 2013 | Pipe Wall Thickness | 10147 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 5.675 | CML-7 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2013-11-09 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 3 O'Clock | 50 | 5.54 | 50-WC-40451-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.7 | 5.6 | 5.7 | 5.7 | 0.05
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-9 | 50-FG-45021-03C02 CML-9 | yes | FPSO 2013 | Pipe Wall Thickness | 10537 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.025 | CML-9 | CML: type TBC | 3 | 2014-10-05 | 2014-10-01 | 2013-11-16 | 2.5 | 2.2595 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.5 | 12 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2 |  | 4.5 | 5.4 | 5 | 5.2 | 0.38622
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57038-01C02 | CML-12 | 100-DC-57038-01C02 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 2375 | Rope Access | 2014-03-18 14:00 | 2014-03-18 15:00 | [36 empty] | 6.975 | CML-12 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-03-18 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.8 | 3 O'Clock | 100 | 6.02 | 100-DC-57038-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 6.8 | 7.3 | 7 | 0.23629
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-13 | 100-DC-57307-01C03 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 2321 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.219mm/ yr | [35 empty] | 7.95 | CML-13 | CML: type TBC | 6 | 2016-02-22 | 2016-02-18 | 2014-03-17 13:00 | 2.5 | 2.2187 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.8 | 6 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7 | 6.8 | 11.2 | 2.1687
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-11 | 100-DC-57307-01C03 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 2319 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.219mm/ yr | [35 empty] | 6.95 | CML-11 | CML: type TBC | 6 | 2016-02-22 | 2016-02-18 | 2014-03-17 13:00 | 2.5 | 2.2187 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.8 | 12 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7 | 7 | 7 | 0.1
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 100-DC-57307-01C03 | CML-1 | 100-DC-57307-01C03 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 2309 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.219mm/ yr | [35 empty] | 7.025 | CML-1 | CML: type TBC | 6 | 2016-02-22 | 2016-02-18 | 2014-03-17 13:00 | 2.5 | 2.2187 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.8 | 9 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.8 | 7.1 | 7.4 | 6.8 | 0.28723
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-13 | 500-WS-50813-1LC CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10795 | Deck Level | 2014-01-03 | 2014-01-03 | [36 empty] | 13.575 | CML-13 | CML: type TBC | 3 | 2016-12-23 | 2015-08-15 | 2014-01-03 | 2.5 | 3.5317 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 13 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.5 |  | 13 | 13.4 | 14.2 | 13.7 | 0.5058
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43146-01C02 | CML-1 | 80-FH-43146-01C02 CML-1 |  | FPSO 2013 | Pipe Wall Thickness | 10554 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 6.975 | CML-1 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2013-11-16 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.6 | 12 O'Clock | 80 | 5.49 | 80-FH-43146-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 7.5 | 6.8 | 7 | 0.38622
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-14 | 200-PL-20034-03C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21611 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.2 | CML-14 | CML: Fitting | 3 | 2030-12-15 | 2027-12-11 | 2014-06-28 13:00 | 3.61 | 0.26035 | A3: Inside Quadrant |  | 5.18 | 3.61 | 4.395 | 7.9 | 6 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.29 |  | 8.4 | 8.3 | 7.9 | 8.2 | 0.21602
FG01 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-FG-45024-01C02 | CML-10 | 50-FG-45024-01C02 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1882 | Rope Access | 2014-03-25 07:00 | 2014-03-25 08:30 | [36 empty] | 9.425 | CML-10 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-03-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9.2 | 6 O'Clock | 50 | 8.74 | 50-PL-23033-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.7 |  | 9.2 | 9.3 | 9.2 | 10 | 0.38622
PG08 | Montara_Topside | Yes | Gas Treatment (24) | Pipework | 200-PG-24001-09C02 | CML-9 | 200-PG-24001-09C02 CML-9 |  | FPSO 2013 | Pipe Wall Thickness | 10265 | Deck Level | 2013-11-09 | 2013-11-09 | Check Corrosion Rate of %vmm/ yr | [35 empty] | 17.725 | CML-9 | CML: Pipe Length | 3 | 2018-09-02 | 2016-11-29 | 2013-11-09 | 9.2 | 1.723 | A2: Right Quadrant |  | 15.26 | 9.2 | 12.23 | 17.5 | 9 O'Clock | 200 | 18.26 | 200-PG-24001-09C02 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 8.3 |  | 17.6 | 17.5 | 18.3 | 17.5 | 0.38622
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-26 | 200-PW-44018-01X01 CML-26 |  | FPSO 2015 | Pipe Wall Thickness | 8950 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-26 09:00 | 2015-02-26 15:00 | [36 empty] | 5.3 | CML-26 | CML: type TBC | 3 | 2028-12-20 | 2030-08-21 | 2015-02-26 09:00 | 2.5 | 0.19532 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-AI-63007-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.4 | 5.3 | 5.2 | 5.3 | 0.08165
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 150-FG-45005-03C02-E | CML-4 | 150-FG-45005-03C02-E CML-4 |  | FPSO 2016 | Pipe Wall Thickness | 24322 | Lagging removed | 2016-06-01 07:00 | 2016-06-01 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.675 | CML-4 | CML: Fitting | 3 | 2029-06-30 | 2027-01-06 | 2016-06-01 07:00 | 2.77 | 0.26968 | A2: Right Quadrant |  | 4.11 | 2.77 | 3.44 | 6.3 | 3 O'Clock | 150 | 7.11 | 150-FG-45005-03C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.53 |  | 6.5 | 6.3 | 6.7 | 7.2 | 0.38622
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-14 | 80-PW-44016-01C02-P CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21946 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.475 | CML-14 | CML: Elbow | 3 | 2034-10-19 | 2037-04-15 | 2014-10-10 07:00 | 2.5 | 0.13974 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 6 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.7 | 5.3 | 5.6 | 0.20616
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57012-01C02 | CML-3 | 50-DC-57012-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2882 | Rope Access | 2014-04-24 14:00 | 2014-04-24 15:00 | Check Corrosion Rate of 0.936mm/ yr | [35 empty] | 4.95 | CML-3 | CML: type TBC | 3 | 2018-12-08 | 2018-02-23 | 2014-04-24 14:00 | 0.37 | 0.93595 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.33 |  | 4.7 | 5 | 4.9 | 5.2 | 0.20817
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 50-DC-57024-01C02 | CML-7 | 50-DC-57024-01C02 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2879 | Rope Access | 2014-04-24 13:00 | 2014-04-24 14:00 | Check Corrosion Rate of 0.936mm/ yr | [35 empty] | 4.975 | CML-7 | CML: type TBC | 3 | 2018-12-07 | 2018-02-22 | 2014-04-24 13:00 | 0.37 | 0.93606 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 4.7 | 12 O'Clock | 50 | 5.54 | 50-DC-57024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.33 |  | 4.7 | 5.1 | 5.2 | 4.9 | 0.22174
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 200-FH-43131-01C02 | CML-6 | 200-FH-43131-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2827 | Rope Access | 2014-03-15 09:00 | 2014-03-15 15:00 | [36 empty] | 7.525 | CML-6 | CML: Pipe Length | 3 | 2063-07-07 | 2057-06-06 | 2014-03-15 09:00 | 1.34 | 0 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 7 | 9 O'Clock | 200 | 6.35 | 200-FH-43131-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.66 |  | 7.7 | 7.9 | 7.5 | 7 | 0.38622
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20034-03C02-P | CML-17 | 200-PL-20034-03C02-P CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 21614 | Protective mesh removed | 2014-06-28 13:00 | 2014-06-28 15:00 | [36 empty] | 8.1 | CML-17 | CML: Reducer | 3 | 2030-12-15 | 2027-12-11 | 2014-06-28 13:00 | 3.61 | 0.26035 | A2: Right Quadrant |  | 5.18 | 3.61 | 4.395 | 7.9 | 3 O'Clock | 200 | 8.18 | 200-PL-20034-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.29 |  | 8.2 | 7.9 | 8.3 | 8 | 0.18257
PW02 | Montara_Topside | Yes | Separation (20) | Pipework | 250-PW-20040-03C03-P | CML-9 | 250-PW-20040-03C03-P CML-9 | yes | FPSO 2015 | Pipe Wall Thickness | 23466 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-24 07:00 | 2015-07-24 15:00 | [36 empty] | 10.225 | CML-9 | CML: Reducer | 6 | 2022-03-01 | 2020-05-12 | 2015-07-24 07:00 | 2.5 | 1.165 | A1: Outside Quadrant |  | 6.7 | 2.5 | 4.6 | 10.2 | 9 O'Clock | 20 | 12.7 | 250-PW-20040-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.7 | -3.292 | 10.2 | 10.2 | 10.3 | 10.2 | 0.05
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56110-01C02 | CML-2 | 50-DH-56110-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21009 | Rope Access | 2014-05-24 13:00 | 2014-05-24 14:00 | [36 empty] | 8.925 | CML-2 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-24 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 6 O'Clock | 50 | 5.54 | 50-DH-56110-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 9.1 | 9.3 | 8.4 | 8.9 | 0.38622
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44040-01C02 | CML-27 | 50-PW-44040-01C02 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 23262 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.55 | CML-27 | CML: Fitting | 3 | 2038-01-05 | 2040-08-26 | 2015-05-11 07:00 | 2.5 | 0.1235 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | -0.089024 | 5.7 | 5.3 | 5.6 | 5.6 | 0.17321
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56062-01C02 | CML-13 | 50-DH-56062-01C02 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 9100 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 5.375 | CML-13 | CML: type TBC | 3 | 2023-04-08 | 2024-04-29 | 2015-03-02 07:00 | 2.5 | 0.30831 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5 | 9 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.5 |  | 5.1 | 5.8 | 5.6 | 5 | 0.38622
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-10 | 500-WS-50813-1LC CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 10792 | Deck Level | 2014-01-03 | 2014-01-03 | [36 empty] | 14.2333 | CML-10 | CML: type TBC | 3 | 2017-07-29 | 2015-12-28 | 2014-01-03 | 2.5 | 3.0248 | A3: Inside Quadrant |  | 12.09 | 2.5 | 7.295 | 13.3 | 6 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.8 |  | 14.8 |  | 13.3 | 14.6 | 0.81445
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-4 | 50-WC-40032-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1238 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 6.7 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 7.4 | 7.3 | 5.7 | 6.4 | 0.80416
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 80-DH-56023-01C02 | CML-2 | 80-DH-56023-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3481 | Rope Access | 2014-05-14 08:00 | 2014-05-14 09:00 | [36 empty] | 6.075 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-14 08:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.5 | 12 O'Clock | 80 | 5.49 | 80-DH-56023-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 6.3 | 6.3 | 6.2 | 0.38622
FG02 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 25-FG-45455-01C02-E | CML-5 | 25-FG-45455-01C02-E CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8383 | Pipe schedule estimated due to no isometric drawings | 2015-01-29 07:30 | 2015-01-29 15:00 | [36 empty] | 6.225 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-29 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 3 O'Clock | 50 | 5.54 | 50-PG-23408-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6 | 6.1 | 6.8 | 0.38622
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-20 | 25-FG-45455-01C02-E CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 1168 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 6.425 | CML-20 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.7 | 6 | 6.8 | 0.38622
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-16 | 80-FH-43158-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12897 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 6.425 | CML-16 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-01-22 11:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.2 | 9 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.3 | 7 | 6.2 | 0.38622
PL02 | Montara_Topside | Yes | Flare (43) | Pipework | 200-PL-43301-01C02-E | CML-1 | 200-PL-43301-01C02-E CML-1 | yes | FPSO 2015 | Pipe Wall Thickness | 8598 | Line is FFS. Action: to recheck in a year (Feb. 2016) to confirm CR. | 2015-02-09 07:30 | 2015-02-09 15:00 |  |  | Administrator | 2015-09-07 16:33 | [32 empty] | 6.475 | CML-1 | CML: Elbow | 3 | 2021-06-29 | 2020-07-06 | 2015-02-09 07:30 | 1.34 | 0.61983 | A2: Right Quadrant |  | 3.35 | 1.34 | 1.9481 | 5.3 | 3 O'Clock | 200 | 6.35 | 200-PL-43301-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.96 |  | 6.1 | 5.3 | 7 | 7.5 | 0.97425
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-8 | 200-PW-44018-01X01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8884 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.3 | CML-8 | CML: type TBC | 3 | 2028-12-11 | 2030-08-11 | 2015-02-25 09:30 | 2.5 | 0.19562 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 9 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.3 | 5.4 | 5.2 | 0.08165
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-9 | 500-WS-50813-1LC CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 1524 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | [32 empty] | 13.95 | CML-9 | CML: type TBC | 3 | 2028-07-12 | 2022-10-09 | 2015-06-12 | 2.5 | 0.83246 | A4: Left Quadrant |  | 12.09 | 2.5 | 7.295 | 13.4 | 9 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 10.9 | -1.2514 | 14.6 | 14.1 | 13.7 | 13.4 | 0.51962
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-A | 500-WS-50813-1LC CML-A |  | FPSO 2016 | Pipe Wall Thickness | 24291 | Material Class 1LC not in drop down list - pipe class incorrect? | 2016-05-03 07:00 | 2016-05-03 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 14.2 | CML-A |  | 3 | 2041-12-07 |  | 2016-05-03 07:00 |  | 0.44116 | A3: Inside Quadrant |  |  | 2.5 |  | 13.8 | 6 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 14.7 | 14.2 | 13.8 | 14.1 | 0.37417
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-17 | 500-WS-50813-1LC CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 10799 | Deck Level | 2014-01-03 | 2014-01-03 | [36 empty] | 14.1667 | CML-17 | CML: type TBC | 3 | 2019-03-10 | 2016-12-27 | 2014-01-03 | 2.5 | 2.1799 | A2: Right Quadrant |  | 12.09 | 2.5 | 7.295 | 13.8 | 3 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 11.3 |  | 13.9 | 13.8 | 14.8 |  | 0.55076
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-C | 500-WS-50813-1LC CML-C |  | FPSO 2016 | Pipe Wall Thickness | 24293 | Material Class 1LC not in drop down list - pipe class incorrect? | 2016-05-03 07:00 | 2016-05-03 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 16.1 | CML-C |  | 3 | 2088-06-29 |  | 2016-05-03 07:00 |  | 0.16757 | A1: Outside Quadrant |  |  | 2.5 |  | 14.6 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 12.1 |  | 14.6 | 17.5 | 15.2 | 17.1 | 1.4166
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43158-01C02 | CML-11 | 80-FH-43158-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12892 |  | 2014-01-22 11:00 | 2014-01-22 13:00 | [36 empty] | 5.825 | CML-11 | CML: type TBC | 3 | 2034-10-31 | 2037-04-29 | 2014-01-22 11:00 | 2.5 | 0.13952 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 3 O'Clock | 80 | 5.49 | 80-FH-43158-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.1 | 5.4 | 5.6 | 6.2 | 0.38622
CI01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 40-CI-42311-01S01 | CML-2 | 40-CI-42311-01S01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7505 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.9 | CML-2 | CML: type TBC | 1 | 2049-06-23 | 2038-10-19 | 2015-04-13 07:00 | 2.5 | 0.12858 | A1: Outside Quadrant |  | 6.14 | 2.5 | 3.8737 | 6.9 | 12 O'Clock | 40 | 7.14 | 40-CI-42311-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 8.1 | 8.7 | 7.9 | 0.74833
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 80-WC-40059-01C02 | CML-2 | 80-WC-40059-01C02 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3151 |  | 2014-05-02 11:30 | 2014-05-02 12:00 | [36 empty] | 6.725 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-05-02 11:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.7 | 9 O'Clock | 80 | 5.49 | 80-WC-40059-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 7.4 | 7.2 | 6.6 | 5.7 | 0.76322
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 250-WC-40017-01C02 | CML-18 | 250-WC-40017-01C02 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2081 | Rope Access | 2014-03-28 09:30 | 2014-03-28 11:30 | Check Corrosion Rate of 0.79mm/ yr | [35 empty] | 6.45 | CML-18 | CML: type TBC | 3 | 2018-04-15 | 2018-04-02 | 2014-03-28 09:30 | 2.5 | 0.78979 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.7 | 6 O'Clock | 250 | 6.35 | 250-WC-40017-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.6 | 7 | 5.7 | 6.5 | 0.54467
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40403-01C02 | CML-6 | 100-WC-40403-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20386 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 6.025 | CML-6 | CML: Elbow | 3 | 2028-08-08 | 2029-02-07 | 2014-10-18 07:00 | 2.5 | 0.23161 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 9 O'Clock | 80 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.2 | 5.7 | 6.5 | 5.7 | 0.39476
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-D | 500-WS-50813-1LC CML-D |  | FPSO 2016 | Pipe Wall Thickness | 24294 | Material Class 1LC not in drop down list - pipe class incorrect? | 2016-05-03 07:00 | 2016-05-03 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 19.2 | CML-D |  | 3 | 2139-04-24 |  | 2016-05-03 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 17.9 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.4 |  | 17.9 | 20.5 | 18.8 | 19.6 | 1.1106
FG04 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FG-45021-03C02 | CML-13 | 50-FG-45021-03C02 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10541 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 5.225 | CML-13 | CML: type TBC | 3 | 2015-01-30 | 2015-01-26 | 2013-11-16 | 2.5 | 1.825 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.52 | 4.7 | 6 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.6 | 5.4 | 4.7 | 5.2 | 0.38622
DC02 | Montara_Topside | No | Closed Drain (57) | Pipework | 20-DC-57303-03C03 | CML-4 | 20-DC-57303-03C03 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 7929 |  | 2015-01-17 10:30 | 2015-01-17 12:00 | [36 empty] | 7.35 | CML-4 | CML: type TBC | 6 | 2044-01-06 | 2058-09-17 | 2015-01-17 10:30 | 2.5 | 0 | A2: Right Quadrant |  | -0.44 | 2.5 | 1.03 | 6.9 | 3 O'Clock | 20 | 5.56 | 20-DC-57303-03C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.8 | 6.9 | 7.6 | 7.1 | 0.42032
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-B | 500-WS-50813-1LC CML-B |  | FPSO 2016 | Pipe Wall Thickness | 24292 | Material Class 1LC not in drop down list - pipe class incorrect? | 2016-05-03 07:00 | 2016-05-03 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 18.75 | CML-B |  | 3 | 2139-04-24 |  | 2016-05-03 07:00 |  | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 18 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 15.5 |  | 18 | 18.4 | 18.2 | 20.4 | 1.1121
Marine | Montara_Topside | No | Sea Water (50) | Pipework | 500-WS-50813-1LC | CML-10 | 500-WS-50813-1LC CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 1525 |  | 2015-06-12 | 2015-06-12 |  |  | Justin Williams | 2016-05-19 | [32 empty] | 20.275 | CML-10 | CML: type TBC | 3 | 2139-04-24 | 2091-05-12 | 2015-06-12 | 2.5 | 0 | A1: Outside Quadrant |  | 12.09 | 2.5 | 7.295 | 20.2 | 12 O'Clock | 500 | 15.09 | 500-WS-50813-1LC | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 17.7 | -4.7971 | 20.2 | 20.3 | 20.3 | 20.3 | 0.05
CG03 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38458-01C02-P | CML-2 | 50-CG-38458-01C02-P CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23730 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 5.225 | CML-2 | CML: Elbow | 3 | 2022-02-23 | 2023-01-31 | 2015-10-30 07:00 | 2.5 | 0.3479 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.7 | 3 O'Clock | 50 | 5.54 | 50-CG-38458-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.2 |  | 5.4 | 4.7 | 5.2 | 5.6 | 0.38622
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-3 | 80-DC-57002-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20232 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.6 | CML-3 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.9 | 6 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 8.3 | 8 | 6.9 | 7.2 | 0.65828
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-4 | 80-DC-57002-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 20233 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.425 | CML-4 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.9 | 3 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.9 | 6.9 | 7.1 | 7.8 | 0.49917
DC01 | Montara_Topside | No | Closed Drain (57) | Pipework | 80-DC-57002-01C02 | CML-6 | 80-DC-57002-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20235 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.125 | CML-6 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.9 | 9 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.4 | 6.9 | 7.3 | 6.9 | 0.263
FG02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 25-FG-45455-01C02-E | CML-15 | 25-FG-45455-01C02-E CML-15 |  | FPSO 2016 | Pipe Wall Thickness | 24360 | Lagging removed | 2016-06-06 07:00 | 2016-06-06 15:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. | [31 empty] | 6.475 | CML-15 | CML: Equal Tee | 3 | 2039-03-19 | 2039-01-09 | 2016-06-06 07:00 | 2.5 | 0.14914 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 3 O'Clock | 25 | 6.35 | 25-FG-45455-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.7 | 5.9 | 6.6 | 6.7 | 0.38622
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 250-FH-43302-01C02 | CML-13 | 250-FH-43302-01C02 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 12929 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.475 | CML-13 | CML: type TBC | 3 | 2019-01-08 | 2018-12-24 | 2014-01-26 07:00 | 2.5 | 0.6864 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 12 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 5.9 | 6.6 | 6.7 | 6.7 | 0.38622
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-52 | 200-PL-20019-01C02 CML-52 |  | FPSO 2014 | Pipe Wall Thickness | 21303 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.875 | CML-52 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 6 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.9 | 9.1 | 6.8 | 7.7 | 0.94648
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43514-01C02 | CML-6 | 150-FL-43514-01C02 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20499 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.025 | CML-6 | CML: type TBC | 3 |  |  | 2014-10-03 07:00 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.8 | 9 O'Clock | 100 |  | 100-FL-43514-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 6.9 | 6.8 | 7.6 | 6.8 | 0.38622
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 25-CG-38495-01C02 | CML-6 | 25-CG-38495-01C02 CML-6 |  | FPSO 2013 | Pipe Wall Thickness | 10403 | Deck Level | 2013-11-12 | 2013-11-12 | [36 empty] | 8.325 | CML-6 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2013-11-12 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.8 | 9 O'Clock | 25 | 6.35 | 25-CG-38495-01C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.3 | 7.8 | 8.5 | 8.7 | 8.3 | 7.8 | 0.38622
PL03 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-PL-45016-03C03 | CML-13 | 50-PL-45016-03C03 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10453 | Deck Level | 2013-11-13 | 2013-11-13 | [36 empty] | 7.825 | CML-13 | CML: type TBC | 6 | 2015-11-06 | 2015-07-28 | 2013-11-13 | 0.99 | 3.1854 | A3: Inside Quadrant |  | 2.74 | 0.99 | 1.865 | 7.3 | 6 O'Clock | 50 | 8.74 | 50-PL-45016-03C03 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.31 |  | 7.8 | 8 | 7.3 | 8.2 | 0.38622
PW03 | Montara_Topside | Yes | Compressed Air (63) | Pipework | 200-PW-44018-01X01 | CML-7 | 200-PW-44018-01X01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8883 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-25 09:30 | 2015-02-25 12:00 | [36 empty] | 5.3 | CML-7 | CML: type TBC | 3 | 2028-12-11 | 2030-08-11 | 2015-02-25 09:30 | 2.5 | 0.19562 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 12 O'Clock | 50 | 5.54 | 50-AI-63005-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.2 | 5.3 | 5.3 | 5.4 | 0.08165
PG02 | Montara_Topside | No | Separation (20) | Pipework | 250-PG-20042-01D01-P | CML-10 | 250-PG-20042-01D01-P CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 21443 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 7.125 | CML-10 | CML: Elbow | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 5.35 | 2.5 | 3.925 | 6.9 | 3 O'Clock | 250 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7 | 6.9 | 7.2 | 7.4 | 0.22174
PG02 | Montara_Topside | No | Separation (20) | Pipework | 250-PG-20042-01D01-P | CML-7 | 250-PG-20042-01D01-P CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21440 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 7 | CML-7 | CML: Reducer | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.35 | 2.5 | 3.925 | 6.9 | 6 O'Clock | 350 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 6.9 | 6.9 | 7.3 | 0.2
PG02 | Montara_Topside | No | Separation (20) | Pipework | 250-PG-20042-01D01-P | CML-3 | 250-PG-20042-01D01-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21436 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 6.925 | CML-3 | CML: Reducer | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 5.35 | 2.5 | 3.925 | 6.9 | 9 O'Clock | 350 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7 | 6.9 | 6.9 | 6.9 | 0.05
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40032-01C02 | CML-11 | 50-WC-40032-01C02 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1245 | Rope Access | 2014-03-23 13:00 | 2014-03-23 14:00 | [36 empty] | 5.95 | CML-11 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-23 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 9 O'Clock | 50 | 5.54 | 50-WC-40032-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 5.7 | 6 | 6.4 | 5.7 | 0.33166
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-6 | 25-AI-63036-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8508 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | Check Corrosion Rate of 0.441mm/ yr | [35 empty] | 5.55 | CML-6 | CML: type TBC | 3 | 2020-04-20 | 2021-01-15 | 2015-02-03 07:30 | 2.5 | 0.44111 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 4.8 | 6 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.3 |  | 5.4 | 6.2 | 4.8 | 5.8 | 0.59722
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-10 | 25-AI-63036-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8512 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 5.425 | CML-10 | CML: type TBC | 3 | 2034-08-25 | 2036-12-05 | 2015-02-03 07:30 | 2.5 | 0.14306 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 6 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.7 | 5.3 | 5.4 | 0.1893
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-4 | 25-AI-63036-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 5612 |  | 2014-06-20 09:30 | 2014-06-20 11:00 | [36 empty] | 7.275 | CML-4 | CML: Fitting | 3 |  |  | 2014-06-20 09:30 | 2.5 | 0 | A4: Left Quadrant |  |  | 2.5 |  | 6.9 | 9 O'Clock | 150 |  | 150-PG-23402-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.4 | 7.5 | 7.3 | 6.9 | 0.263
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-1 | 25-AI-63036-01E01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 5609 |  | 2014-06-20 09:30 | 2014-06-20 11:00 | [36 empty] | 7.175 | CML-1 | CML: Elbow | 3 |  |  | 2014-06-20 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.9 | 3 O'Clock | 150 |  | 150-PG-23402-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7 | 6.9 | 7.6 | 7.2 | 0.30957
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-19 | 25-AI-63036-01E01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 12935 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.475 | CML-19 | CML: type TBC | 3 | 2030-03-25 | 2030-02-08 | 2014-01-26 07:00 | 2.5 | 0.2288 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 3 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.2 | 6.9 | 6.5 | 0.30957
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63036-01E01 | CML-14 | 25-AI-63036-01E01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20973 | Rope Access | 2014-05-16 13:00 | 2014-05-16 16:00 | [36 empty] | 7.325 | CML-14 | CML: type TBC | 3 | 2048-08-12 | 2049-10-10 | 2014-05-16 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.9 | 9 O'Clock | 100 | 6.02 | 100-DH-56086-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.7 | 7.2 | 7.5 | 6.9 | 0.35
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63036-01E01 | CML-6 | 25-AI-63036-01E01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 3472 | Rope Access | 2014-05-13 10:30 | 2014-05-13 12:00 | [36 empty] | 7.05 | CML-6 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-13 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 6.9 | 3 O'Clock | 80 | 5.49 | 80-DH-56012-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.2 | 6.9 | 7 | 7.1 | 0.1291
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63036-01E01 | CML-5 | 25-AI-63036-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3328 | Rope Access | 2014-05-08 07:00 | 2014-05-08 09:00 | [36 empty] | 7.05 | CML-5 | CML: type TBC | 3 | 2033-12-05 | 2032-04-28 | 2014-05-08 07:00 | 2.5 | 0.22459 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.9 | 6 O'Clock | 150 | 7.11 | 150-DH-56080-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.1 | 7.2 | 6.9 | 7 | 0.1291
AD01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 25-AI-63036-01E01 | CML-8 | 25-AI-63036-01E01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 22348 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.475 | CML-8 |  | 3 | 2033-06-18 | 2031-11-23 | 2014-04-30 13:00 | 2.5 | 0.22981 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 6.9 | 9 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.6 | 7.5 | 7.9 | 6.9 | 0.41932
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1716 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.1 | CML-2 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.9 | 9 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.5 | 7 | 7 | 6.9 | 0.2708
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1735 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.2 | CML-2 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 6.9 | 6 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.3 | 7.2 | 6.9 | 7.4 | 0.21602
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-4 | 25-AI-63036-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8506 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 5.55 | CML-4 | CML: type TBC | 3 | 2034-08-25 | 2036-12-05 | 2015-02-03 07:30 | 2.5 | 0.14306 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 12 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.3 | 5.4 | 5.5 | 6 | 0.31091
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-11 | 25-AI-63036-01E01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 12927 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.35 | CML-11 | CML: type TBC | 3 | 2030-03-25 | 2030-02-08 | 2014-01-26 07:00 | 2.5 | 0.2288 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.2 | 6.6 | 6.2 | 0.19149
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-6 | 25-AI-63036-01E01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 12922 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.5 | CML-6 | CML: type TBC | 3 | 2030-03-25 | 2030-02-08 | 2014-01-26 07:00 | 2.5 | 0.2288 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.7 | 6.5 | 6.6 | 0.21602
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1253 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7.175 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 6 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.2 | 7 | 6.9 | 7.6 | 0.30957
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-25 | 25-AI-63036-01E01 CML-25 |  | FPSO 2014 | Pipe Wall Thickness | 1301 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.375 | CML-25 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 12 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.6 | 7.5 | 7.5 | 0.32016
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-21 | 25-AI-63036-01E01 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 1297 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.175 | CML-21 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 3 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7 | 6.9 | 7.4 | 7.4 | 0.263
AD01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1185 | Rope Access | 2014-03-22 07:00 | 2014-03-22 08:30 | [36 empty] | 7.075 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.9 | 12 O'Clock | 50 | 5.54 | 50-FG-45024-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7.1 | 7.3 | 7 | 0.17078
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-8 | 25-AI-63036-01E01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1077 | Rope Access | 2014-03-21 13:00 | 2014-03-21 15:00 | Check Corrosion Rate of 1.144mm/ yr | [35 empty] | 8.5 | CML-8 | CML: type TBC | 3 | 2018-01-23 | 2017-06-25 | 2014-03-21 13:00 | 2.6 | 1.144 | A3: Inside Quadrant |  | 4.92 | 2.6 | 3.265 | 7 | 6 O'Clock | 400 | 7.92 | 400-WC-40024-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 9.7 | 9.7 | 7 | 7.6 | 1.4071
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 2396 | Rope Access | 2014-03-19 09:30 | 2014-03-19 11:00 | [36 empty] | 6.975 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-19 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.9 | 9 O'Clock | 300 | 6.35 | 300-FL-43509-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.2 | 6.9 | 6.9 | 6.9 | 0.15
AD01 | Montara_Topside | No | Closed Drain (57) | Pipework | 25-AI-63036-01E01 | CML-18 | 25-AI-63036-01E01 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 2326 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | Check Corrosion Rate of 2.093mm/ yr | [35 empty] | 22.675 | CML-18 | CML: type TBC | 6 | 2016-04-23 | 2016-04-17 | 2014-03-17 13:00 | 2.5 | 2.0926 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 6.9 | 6 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 6.9 | 6.9 | 70 | 31.55
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-19 | 25-AI-63036-01E01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 2263 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 7.05 | CML-19 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6.9 | 3 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.1 | 6.9 | 7 | 7.2 | 0.1291
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-14 | 25-AI-63036-01E01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 2258 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 7.125 | CML-14 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A3: Inside Quadrant |  |  | 2.5 |  | 6.9 | 6 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 7.3 | 7.1 | 6.9 | 7.2 | 0.17078
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-10 | 25-AI-63036-01E01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 2254 | Rope Access | 2014-03-16 09:30 | 2014-03-16 11:30 | [36 empty] | 7.05 | CML-10 | CML: type TBC | 3 |  |  | 2014-03-16 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 6.9 | 12 O'Clock | 150 |  | 150-FL-43453-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 6.9 | 7 | 7.1 | 7.2 | 0.1291
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-5 | 25-AI-63036-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12921 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.9 | CML-5 | CML: type TBC | 3 | 2030-03-25 | 2030-02-08 | 2014-01-26 07:00 | 2.5 | 0.2288 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 12 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 7 | 7 | 7.4 | 0.50332
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12918 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.25 | CML-2 | CML: type TBC | 3 | 2030-03-25 | 2030-02-08 | 2014-01-26 07:00 | 2.5 | 0.2288 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 9 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.2 | 6.4 | 6.2 | 6.2 | 0.1
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-15 | 25-AI-63036-01E01 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12931 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.825 | CML-15 | CML: type TBC | 3 | 2063-11-11 | 2063-06-29 | 2014-01-26 07:00 | 2.5 | 0.07627 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 3 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.7 | 6.3 | 7.2 | 7.1 | 0.4113
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-12 | 25-AI-63036-01E01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12928 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.775 | CML-12 | CML: type TBC | 3 | 2063-11-11 | 2063-06-29 | 2014-01-26 07:00 | 2.5 | 0.07627 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 7 | 6.9 | 6.9 | 0.32016
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-10 | 25-AI-63036-01E01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 12926 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.775 | CML-10 | CML: type TBC | 3 | 2063-11-11 | 2063-06-29 | 2014-01-26 07:00 | 2.5 | 0.07627 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 3 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.8 | 6.3 | 6.9 | 7.1 | 0.34034
AD01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 25-AI-63036-01E01 | CML-8 | 25-AI-63036-01E01 CML-8 | yes | FPSO 2013 | Pipe Wall Thickness | 10536 | Deck Level | 2013-11-16 | 2013-11-16 | [36 empty] | 4.975 | CML-8 | CML: type TBC | 3 | 2014-11-26 | 2014-11-22 | 2013-11-16 | 2.5 | 2.0423 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.52 | 4.6 | 3 O'Clock | 50 | 5.54 | 50-FG-45021-03C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.1 |  | 4.9 | 4.6 | 5.4 | 5 | 0.3304
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20537 | Rope access (Re-checking line) | 2014-05-30 09:30 | 2014-05-30 09:30 | [36 empty] | 21.975 | CML-3 | CML: Elbow | 3 | 2017-01-27 | 2016-02-24 | 2014-05-30 09:30 | 15.88 | 1.6573 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.3 | 6 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.42 | 0.26255 | 21.1 | 25.5 | 20.3 | 21 | 2.3768
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20041 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 22.05 | CML-3 | CML: Elbow | 3 | 2017-01-23 | 2016-02-21 | 2014-05-29 07:00 | 15.88 | 1.6623 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.3 | 6 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.42 | 0 | 23 | 23 | 20.3 | 21.9 | 1.2767
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-46 | 25-AI-63036-01E01 CML-46 |  | FPSO 2014 | Pipe Wall Thickness | 20667 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | [36 empty] | 20.825 | CML-46 | CML: Pipe Length | 3 | 2017-01-20 | 2016-02-19 | 2014-05-28 07:00 | 15.88 | 1.6669 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 20.3 | 9 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.42 | 1.9752 | 21 | 21 | 21 | 20.3 | 0.35
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-33 | 25-AI-63036-01E01 CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 20660 | Rope Access | 2014-05-28 07:00 | 2014-05-28 10:00 | [36 empty] | 20.375 | CML-33 | CML: Elbow | 3 | 2017-01-20 | 2016-02-19 | 2014-05-28 07:00 | 15.88 | 1.6669 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.3 | 12 O'Clock | 150 | 21.95 | 150-PG-23506-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.42 | -3.9504 | 20.3 | 20.4 | 20.4 | 20.4 | 0.05
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13093 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 22.425 | CML-3 | CML: Elbow | 3 | 2015-08-31 | 2015-02-04 | 2014-01-10 09:00 | 15.88 | 2.6961 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.3 | 6 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.42 |  | 24.5 | 22.8 | 20.3 | 22.1 | 1.7385
AD01 | Montara_Topside | No | Closed Drain (57) | Pipework | 25-AI-63036-01E01 | CML-5 | 25-AI-63036-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 2884 | Rope Access | 2014-04-24 14:00 | 2014-04-24 15:00 | Check Corrosion Rate of 0.825mm/ yr | [35 empty] | 5.1 | CML-5 | CML: type TBC | 3 | 2019-09-06 | 2018-10-14 | 2014-04-24 14:00 | 0.37 | 0.82452 | A1: Outside Quadrant |  | 2.54 | 0.37 | 1.1087 | 4.8 | 12 O'Clock | 50 | 5.54 | 50-DC-57012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.43 |  | 4.8 | 5.4 | 4.9 | 5.3 | 0.29439
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-6 | 25-AI-63036-01E01 CML-6 | Yes | FPSO 2014 | Pipe Wall Thickness | 5512 | Rope access (Re-checking line) | 2014-06-01 07:00 | 2014-06-01 15:00 | [36 empty] | 11.55 | CML-6 | CML: Pipe Length | 6 | 2018-09-22 | 2018-12-25 | 2014-06-01 07:00 | 5.66 | 1.0292 | A3: Inside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.1 | 6 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.44 | 0.45673 | 12 | 12.1 | 10.1 | 12 | 0.96782
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8604 |  | 2015-02-09 07:30 | 2015-02-09 15:00 | [36 empty] | 5.875 | CML-3 | CML: type TBC | 3 | 2028-11-01 | 2026-12-18 | 2015-02-09 07:30 | 1.34 | 0.32467 | A3: Inside Quadrant |  | 3.35 | 1.34 | 1.9481 | 5.8 | 6 O'Clock | 200 | 6.35 | 200-PL-43302-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.46 |  | 5.9 | 5.9 | 5.8 | 5.9 | 0.05
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-9 | 25-AI-63036-01E01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 12925 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.575 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 6 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 6.5 | 6.6 | 6.5 | 6.7 | 0.095743
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-7 | 25-AI-63036-01E01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2972 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.425 | CML-7 | CML: Elbow | 3 | 2022-09-01 | 2021-06-27 | 2014-05-01 14:00 | 0.54 | 0.53455 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5 | 12 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.46 |  | 5 | 5.5 | 5.8 | 5.4 | 0.3304
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-7 | 25-AI-63036-01E01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22251 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.425 | CML-7 | CML: Elbow | 3 | 2022-09-01 | 2021-06-27 | 2014-05-01 14:00 | 0.54 | 0.53455 | A1: Outside Quadrant |  | 2.49 | 0.54 | 1.1719 | 5 | 12 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.46 |  | 5 | 5.5 | 5.8 | 5.4 | 0.3304
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-4 | 25-AI-63036-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12920 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.85 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.5 | 3 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4 |  | 7.3 | 6.5 | 6.7 | 6.9 | 0.34157
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-14 | 25-AI-63036-01E01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12930 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 6.725 | CML-14 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.6 | 9 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 7.1 | 6.6 | 6.6 | 6.6 | 0.25
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 12919 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 7.6 | CML-3 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 6 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.7 | 8 | 6.8 | 7.9 | 0.54772
AD01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2016 | Pipe Wall Thickness | 24296 | Lagging removed | 2016-05-27 07:00 | 2016-05-27 09:00 |  |  | Nestor | 2016-11-08 | Reviewed. Line FFS. No internal damage in RBI | [31 empty] | 5.95 | CML-2 | CML: Fitting | 3 | 2024-09-12 | 2022-08-31 | 2016-05-27 07:00 | 1.03 | 0.53849 | A1: Outside Quadrant |  | 4.11 | 1.03 | 2.1256 | 5.5 | 12 O'Clock | 40 | 7.11 | 150-FG-45009-01C02-E | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.47 |  | 5.5 | 6.1 | 6.1 | 6.1 | 0.3
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-10 | 25-AI-63036-01E01 CML-10 | yes | FPSO 2014 | Pipe Wall Thickness | 10994 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 16.875 | CML-10 | CML: Elbow | 6 | 2014-06-27 | 2014-04-05 | 2014-01-10 | 10.22 | 9.6897 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 14.7 | 12 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.48 |  | 14.7 | 17 | 20.3 | 15.5 | 2.4744
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-5 | 25-AI-63036-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8507 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 5.775 | CML-5 | CML: type TBC | 3 | 2140-10-28 | 2154-07-01 | 2015-02-03 07:30 | 2.5 | 0.02384 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.5 | 12 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3 |  | 5.5 | 5.7 | 5.6 | 6.3 | 0.3594
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-7 | 25-AI-63036-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8509 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 5.95 | CML-7 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.6 | 9 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.1 |  | 5.9 | 6 | 6.3 | 5.6 | 0.28868
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-8 | 25-AI-63036-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8510 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.25 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 6 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.2 | 6.5 | 6 | 6.3 | 0.20817
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-9 | 25-AI-63036-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8511 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.3 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.4 | 6.3 | 6.2 | 6.3 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8504 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 6.825 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.6 | 12 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.1 |  | 6.6 | 6.9 | 6.8 | 7 | 0.17078
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 23046 |  | 2015-05-06 07:00 | 2015-05-06 15:00 | [36 empty] | 7.95 | CML-2 | CML: Elbow | 6 | 2017-06-11 | 2016-10-30 | 2015-05-06 07:00 | 2.5 | 2.1404 | A3: Inside Quadrant |  | 5.13 | 2.5 | 3.815 | 7 | 6 O'Clock | 80 | 11.13 | 80-PW-20024-01C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.5 | 7.6 | 7 | 8.7 | 0.79373
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8505 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [36 empty] | 8.5 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.9 | 3 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.4 |  | 8.8 | 6.9 | 8.8 | 9.5 | 1.1165
AD01 | Montara_Topside | No | Produced Water (44) | Pipework | 25-AI-63036-01E01 | CML-18 | 25-AI-63036-01E01 CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 22762 | Rope Access | 2015-04-29 07:00 | 2015-04-29 15:00 | [36 empty] | 7.525 | CML-18 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-04-29 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 12 O'Clock | 250 | 6.35 | 250-PW-44004-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.2 | 8.3 | 7.6 | 0.57373
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-18 | 25-AI-63036-01E01 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 12934 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 7.175 | CML-18 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.4 | 7.3 | 7 | 7 | 0.20616
AD01 | Montara_Topside | No | Nitrogen (67) | Pipework | 25-AI-63036-01E01 | CML-10 | 25-AI-63036-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 22494 |  | 2015-04-20 07:00 | 2015-04-20 15:00 | [36 empty] | 8.075 | CML-10 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-04-20 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 25 | 6.35 | 25-GN-67300-01E01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.9 | 8.6 | 7.8 | 7 | 0.85391
AD01 | Montara_Topside | No | Potable Water (53) | Pipework | 25-AI-63036-01E01 | CML-33 | 25-AI-63036-01E01 CML-33 |  | FPSO 2015 | Pipe Wall Thickness | 8276 | Reducing Hose Coupling | 2015-01-26 07:30 | 2015-01-26 15:00 | [36 empty] | 7.375 | CML-33 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-01-26 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 12 O'Clock | 50 | 5.54 | 50-WD-53010-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.6 | 7.5 | 7.4 | 0.263
AD01 | Montara_Topside | No | Lube Oil (69) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8081 |  | 2015-01-23 07:30 | 2015-01-23 15:00 | [36 empty] | 7.125 | CML-3 | CML: type TBC | 1 | 2043-04-25 | 2036-10-17 | 2015-01-23 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.49 | 2.5 | 3.1519 | 7 | 9 O'Clock | 80 | 5.49 | 80-OL-69003-01S01 | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7.3 | 7.1 | 7 | 0.12583
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-22 | 25-AI-63036-01E01 CML-22 |  | FPSO 2014 | Pipe Wall Thickness | 12938 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 7.375 | CML-22 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 9 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.7 | 7.4 | 7.3 | 7.1 | 0.25
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-16 | 25-AI-63036-01E01 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12932 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 7.25 | CML-16 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7.1 | 12 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.2 | 7.4 | 7.3 | 0.1291
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-13 | 25-AI-63036-01E01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 7819 |  | 2015-01-13 09:30 | 2015-01-13 12:00 | [36 empty] | 7.425 | CML-13 | CML: Reducer | 3 | 2051-11-30 | 2051-08-19 | 2015-01-13 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 12 O'Clock | 200 | 6.35 | 200-WC-40008-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.8 | 7.2 | 7.7 | 0.38622
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 7707 |  | 2015-01-09 07:00 | 2015-01-09 10:00 | [36 empty] | 7.25 | CML-3 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2015-01-09 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 200 | 6.35 | 200-WC-40036-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.4 | 7.5 | 7.1 | 7 | 0.23805
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20375 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 7.25 | CML-2 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 9 O'Clock | 100 | 6.02 | 100-WC-40402-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.5 | 7.4 | 7.1 | 7 | 0.23805
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-7 | 25-AI-63036-01E01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20401 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 7.425 | CML-7 | CML: type TBC | 3 | 2071-03-01 | 2066-08-24 | 2014-10-17 07:00 | 2.5 | 0.07977 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 6 O'Clock | 150 | 7.11 | 150-WC-40405-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.5 | 7.8 | 7 | 7.4 | 0.3304
AD01 | Montara_Topside | No | Closed Drain (57) | Pipework | 25-AI-63036-01E01 | CML-7 | 25-AI-63036-01E01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 20236 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.375 | CML-7 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7 | 6 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.8 | 7.5 | 7 | 7.2 | 0.35
AD01 | Montara_Topside | No | Closed Drain (57) | Pipework | 25-AI-63036-01E01 | CML-10 | 25-AI-63036-01E01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20239 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.65 | CML-10 | CML: Fitting | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7 | 12 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.7 | 7.8 | 8.1 | 0.46547
AD01 | Montara_Topside | No | Closed Drain (57) | Pipework | 25-AI-63036-01E01 | CML-14 | 25-AI-63036-01E01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 20243 |  | 2014-10-16 07:00 | 2014-10-14 15:00 | [36 empty] | 7.25 | CML-14 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-10-16 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7 | 6 O'Clock | 80 | 5.49 | 80-DC-57002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7.2 | 7 | 7.6 | 0.25166
AD01 | Montara_Topside | No | Produced Water (44) | Pipework | 25-AI-63036-01E01 | CML-24 | 25-AI-63036-01E01 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 22015 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.7 | CML-24 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7 | 6 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.8 | 7.2 | 7 | 7.8 | 0.80829
AD01 | Montara_Topside | No | Produced Water (44) | Pipework | 25-AI-63036-01E01 | CML-16 | 25-AI-63036-01E01 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 22007 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.525 | CML-16 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.6 | 8.4 | 7.1 | 0.63966
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63036-01E01 | CML-4 | 25-AI-63036-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21841 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.15 | CML-4 | CML: Reducing Tee | 3 | 2048-08-12 | 2049-10-10 | 2014-10-14 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 9 O'Clock | 100 | 6.02 | 100-PW-20057-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7.3 | 7.1 | 7 | 0.1291
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-5 | 25-AI-63036-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 20344 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.125 | CML-5 | CML: Fitting | 3 | 2070-03-31 | 2065-10-19 | 2014-10-09 07:00 | 2.5 | 0.08106 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 9 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.3 | 7.1 | 7.1 | 7 | 0.12583
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-10 | 25-AI-63036-01E01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 20339 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.925 | CML-10 | CML: Elbow | 3 | 2070-03-31 | 2065-10-19 | 2014-10-09 07:00 | 2.5 | 0.08106 | A3: Inside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 6 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.6 | 8.3 | 7 | 7.8 | 0.6994
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-9 | 25-AI-63036-01E01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 20338 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.025 | CML-9 | CML: Fitting | 3 | 2070-03-31 | 2065-10-19 | 2014-10-09 07:00 | 2.5 | 0.08106 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 9 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7 | 7.1 | 7 | 0.05
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-23 | 25-AI-63036-01E01 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 20362 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.125 | CML-23 | CML: Pipe Length | 3 | 2070-03-31 | 2065-10-19 | 2014-10-09 07:00 | 2.5 | 0.08106 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 9 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7.3 | 7.1 | 7 | 0.12583
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63036-01E01 | CML-20 | 25-AI-63036-01E01 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 20359 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.625 | CML-20 | CML: Elbow | 3 | 2070-03-31 | 2065-10-19 | 2014-10-09 07:00 | 2.5 | 0.08106 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 3 O'Clock | 150 | 7.11 | 150-WC-40002-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.4 | 7 | 7.5 | 7.6 | 0.57951
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-8 | 25-AI-63036-01E01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 20482 |  | 2014-10-03 07:00 | 2014-10-03 15:00 | [36 empty] | 7.35 | CML-8 | CML: Pipe Length | 1 | 2069-07-22 | 2052-12-26 | 2014-10-03 07:00 | 2.5 | 0.08206 | A4: Left Quadrant |  | 6.11 | 2.5 | 3.8606 | 7 | 9 O'Clock | 150 | 7.11 | 150-FH-43313-01S01-P | 40S | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.3 | 7.5 | 7.6 | 7 | 0.26458
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63036-01E01 | CML-19 | 25-AI-63036-01E01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 21270 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.275 | CML-19 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.6 | 7 | 7.1 | 7.4 | 0.27538
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63036-01E01 | CML-7 | 25-AI-63036-01E01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 21258 | Reviewed on 27/11/14. FFS. recheck on Sep.15 | 2014-09-30 07:00 | 2014-09-30 15:00 |  |  | Nestor | 2014-11-27 15:57 | [32 empty] | 7.25 | CML-7 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.7 | 7.3 | 7 | 7 | 0.33166
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63036-01E01 | CML-14 | 25-AI-63036-01E01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 21318 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 7.625 | CML-14 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-28 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 200 | 6.35 | 200-PL-20020-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.2 | 7.6 | 7.7 | 7 | 0.49244
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-3 | 25-AI-63036-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20445 | Rope Access | 2014-07-26 07:00 | 2014-07-26 15:00 | [36 empty] | 7.4 | CML-3 | CML: Equal Tee | 3 | 2043-10-24 | 2047-01-28 | 2014-07-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 12 O'Clock | 50 | 5.54 | 50-FH-43309-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.8 | 7.3 | 7.5 | 0.33665
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63036-01E01 | CML-4 | 25-AI-63036-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21243 | Protective mesh removed | 2014-07-14 07:30 | 2014-07-14 15:00 | [36 empty] | 9 | CML-4 | CML: Reducing Tee | 3 | 2051-11-30 | 2051-08-19 | 2014-07-14 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 150 | 6.35 | 200-PL-20017-01C02-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 9.8 | 9.4 | 9.8 | 7 | 1.3466
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63036-01E01 | CML-2 | 25-AI-63036-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21435 | Protective mesh removed | 2014-07-13 07:30 | 2014-07-13 15:00 | [36 empty] | 7 | CML-2 | CML: Elbow | 1 | 2051-11-30 | 2037-08-30 | 2014-07-13 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 5.35 | 2.5 | 3.925 | 7 | 9 O'Clock | 350 | 6.35 | 250-PG-20042-01D01-P | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7 | 7 | 7 | 0
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-1 | 25-AI-63036-01E01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 20431 | Protective mesh removed/Rope access | 2014-06-27 10:30 | 2014-06-27 12:00 | [36 empty] | 7.625 | CML-1 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-06-27 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 12 O'Clock | 200 | 6.35 | 300-FL-43176-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.5 | 8.2 | 7.8 | 0.5058
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63036-01E01 | CML-15 | 25-AI-63036-01E01 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 21526 | Protective mesh removed/Rope access | 2014-06-26 13:00 | 2014-06-26 15:00 | [36 empty] | 7.5 | CML-15 | CML: Elbow | 6 | 2015-09-12 | 2015-05-13 | 2014-06-26 13:00 | 2.5 | 3.7104 | A1: Outside Quadrant |  | 4.97 | 2.5 | 3.735 | 7 | 12 O'Clock | 100 | 10.97 | 150-PG-20054-01C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.1 | 8 | 7.9 | 0.52281
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63036-01E01 | CML-17 | 25-AI-63036-01E01 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12933 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 8.825 | CML-17 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 8.7 | 9 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.2 |  | 9.2 | 8.7 | 8.7 | 8.7 | 0.25
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63036-01E01 | CML-6 | 25-AI-63036-01E01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5614 |  | 2014-06-20 09:30 | 2014-06-20 11:00 | [36 empty] | 7.175 | CML-6 | CML: Fitting | 3 |  |  | 2014-06-20 09:30 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7 | 12 O'Clock | 150 |  | 150-PG-23402-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.3 | 7.1 | 7.3 | 0.15
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63036-01E01 | CML-1 | 25-AI-63036-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8503 | No Reducer on site. All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-03 07:30 | 2015-02-03 15:00 | [37 empty] | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-03 07:30 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-AI-63036-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
PG05 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 250-PG-23003-06C02-PA | CML-4 | 250-PG-23003-06C02-PA CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2423 | Rope Access | 2014-03-20 07:00 | 2014-03-20 09:00 | Check Corrosion Rate of 0.774mm/ yr | [35 empty] | 5.925 | CML-4 | CML: type TBC | 3 | 2017-12-16 | 2018-02-09 | 2014-03-20 07:00 | 2.5 | 0.77423 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.4 | 12 O'Clock | 100 | 6.02 | 100-DC-57075-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 5.4 | 6.3 | 5.9 | 6.1 | 0.38622
FG06 | Montara_Topside | No | Fuel Gas (45) | Pipework | 100-FG-45304-03C02 | CML-9 | 100-FG-45304-03C02 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 22065 | Rope Access | 2014-05-25 07:00 | 2014-05-25 09:00 | [36 empty] | 7.575 | CML-9 | CML: type TBC | 3 | 2048-08-12 | 2046-01-05 | 2014-05-25 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.76 | 7 | 12 O'Clock | 100 | 6.02 | 100-FG-45304-03C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 8 | 7.9 | 7.4 | 0.46458
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8560 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.775 | CML-4 | CML: type TBC | 3 | 2034-09-07 | 2036-12-19 | 2015-02-04 07:30 | 2.5 | 0.14283 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.3 | 3 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.3 | 5.9 | 6.2 | 0.37749
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-23 | 25-AI-63039-01E01 CML-23 |  | FPSO 2015 | Pipe Wall Thickness | 9110 |  | 2015-03-02 07:00 | 2015-03-02 12:00 | [36 empty] | 7.3 | CML-23 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-03-02 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 12 O'Clock | 50 | 5.54 | 50-DH-56062-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.2 | 7.2 | 7.8 | 0.34641
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 7937 |  | 2015-01-17 13:00 | 2015-01-17 15:00 | [36 empty] | 7.8 | CML-5 | CML: Equal Tee | 3 | 2048-08-12 | 2049-10-10 | 2015-01-17 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 12 O'Clock | 100 | 6.02 | 100-DH-56561-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.5 | 7.7 | 9 | 0.85245
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-6 | 25-AI-63039-01E01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 5237 | Rope Access | 2014-05-20 13:00 | 2014-05-20 14:00 | [36 empty] | 8.425 | CML-6 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-05-20 13:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 3 O'Clock | 50 | 5.54 | 50-DH-56115-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.7 | 7 | 9.2 | 8.8 | 0.97425
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3483 | Rope Access | 2014-05-14 09:30 | 2014-05-14 11:00 | [36 empty] | 7.425 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-14 09:30 | 2.5 | 0 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 7 | 9 O'Clock | 80 | 5.49 | 80-DH-56022-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.5 | 7.3 | 7.9 | 7 | 0.37749
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3462 | Rope Access | 2014-05-13 09:30 | 2014-05-13 10:30 | [36 empty] | 7.125 | CML-2 | CML: type TBC | 3 | 2043-04-25 | 2046-10-17 | 2014-05-13 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7 | 12 O'Clock | 80 | 5.49 | 80-DH-56019-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.2 | 7.2 | 7.1 | 0.095743
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 3426 | Rope Access | 2014-05-12 07:00 | 2014-05-12 09:00 | [36 empty] | 7.575 | CML-3 | CML: type TBC | 3 |  |  | 2014-05-12 07:00 | 2.5 | 0 | A1: Outside Quadrant |  |  | 2.5 |  | 7 | 12 O'Clock | 100 |  | 100-DH-56009-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.3 | 8.2 | 7.8 | 0.53151
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 3170 | Rope Access | 2014-05-07 08:00 | 2014-05-07 09:00 | [36 empty] | 7.55 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 9 O'Clock | 50 | 5.54 | 50-DH-56057-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.3 | 7.5 | 8.4 | 7 | 0.60277
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20122 | Rope Access | 2014-05-07 08:00 | 2014-05-07 09:00 | [36 empty] | 7.55 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-07 08:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 9 O'Clock | 50 | 5.54 | 50-DH-56056-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 | -13140.9235 | 7.3 | 7.5 | 8.4 | 7 | 0.60277
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 22321 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 7.25 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 6 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7.6 | 7 | 7.3 | 0.26458
AD01 | Montara_Topside | No | Open Drain (56) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1841 | Rope Access | 2014-05-06 10:30 | 2014-05-06 14:00 | [36 empty] | 7.25 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-05-06 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 6 O'Clock | 50 | 5.54 | 50-DH-56010-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7.6 | 7 | 7.3 | 0.26458
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-7 | 25-AI-63039-01E01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 2984 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | [36 empty] | 7.925 | CML-7 | CML: Elbow | 3 | 2051-10-14 | 2048-10-12 | 2014-05-01 09:30 | 2.5 | 0.12007 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 3 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8 | 7 | 8.2 | 8.5 | 0.65
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2980 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | [36 empty] | 7.675 | CML-3 | CML: Elbow | 3 | 2051-10-14 | 2048-10-12 | 2014-05-01 09:30 | 2.5 | 0.12007 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 3 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8 | 7 | 7.5 | 8.2 | 0.53774
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-7 | 25-AI-63039-01E01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 22263 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | [36 empty] | 7.925 | CML-7 | CML: Elbow | 3 | 2051-10-14 | 2048-10-12 | 2014-05-01 09:30 | 2.5 | 0.12007 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 3 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8 | 7 | 8.2 | 8.5 | 0.65
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22259 | Rope Access | 2014-05-01 09:30 | 2014-05-01 10:00 | [36 empty] | 7.675 | CML-3 | CML: Elbow | 3 | 2051-10-14 | 2048-10-12 | 2014-05-01 09:30 | 2.5 | 0.12007 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 3 O'Clock | 150 | 7.11 | 150-WC-40003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8 | 7 | 7.5 | 8.2 | 0.53774
AD01 | Montara_Topside | No | Fuel Gas (45) | Pipework | 25-AI-63039-01E01 | CML-11 | 25-AI-63039-01E01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 22351 | Rope Access | 2014-04-30 13:00 | 2014-04-30 15:00 | [36 empty] | 7.45 | CML-11 |  | 3 | 2051-09-08 | 2048-09-09 | 2014-04-30 13:00 | 2.5 | 0.12037 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 12 O'Clock | 150 | 7.11 | 150-FG-45505-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.7 | 7.2 | 7.9 | 0.42032
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1807 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 7.5 | CML-5 | CML: Elbow | 3 | 2051-07-25 | 2048-07-30 | 2014-04-29 11:00 | 2.5 | 0.12077 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 12 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 8.2 | 7.6 | 7.2 | 0.52915
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1805 | Rope access | 2014-04-29 11:00 | 2014-04-29 12:00 | [36 empty] | 7.175 | CML-3 | CML: Fitting | 3 | 2051-07-25 | 2048-07-30 | 2014-04-29 11:00 | 2.5 | 0.12077 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7 | 12 O'Clock | 150 | 7.11 | 150-WC-40004-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.4 | 7.2 | 7.1 | 0.17078
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-8 | 25-AI-63039-01E01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12924 |  | 2014-01-26 07:00 | 2014-01-26 10:00 | [36 empty] | 11.9667 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-01-26 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 11.7 | 12 O'Clock | 250 | 6.35 | 250-FH-43302-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.2 |  | 11.7 | 11.8 | 12.4 |  | 0.37859
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-15 | 25-AI-63039-01E01 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1729 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.35 | CML-15 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.3 | 8 | 7 | 7.1 | 0.45092
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-12 | 25-AI-63039-01E01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 1726 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.85 | CML-12 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.2 | 8.2 | 7 | 8 | 0.57446
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-11 | 25-AI-63039-01E01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1725 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.525 | CML-11 | CML: Fitting | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 12 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.4 | 8.2 | 7.5 | 0.49917
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-8 | 25-AI-63039-01E01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1722 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.325 | CML-8 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 12 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.4 | 7.4 | 7.5 | 0.22174
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-7 | 25-AI-63039-01E01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1721 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.85 | CML-7 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.8 | 8.8 | 7 | 7.8 | 0.73711
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1719 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.15 | CML-5 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.3 | 7 | 7 | 7.3 | 0.17321
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1718 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.375 | CML-4 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.6 | 7.8 | 7 | 7.1 | 0.38622
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-1 | 25-AI-63039-01E01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1715 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.425 | CML-1 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.9 | 7 | 7 | 7.8 | 0.49244
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-19 | 25-AI-63039-01E01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1733 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.65 | CML-19 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 12 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.5 | 8.1 | 8 | 0.50662
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-18 | 25-AI-63039-01E01 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 1732 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.675 | CML-18 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 3 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.6 | 7 | 8.4 | 7.7 | 0.57373
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-17 | 25-AI-63039-01E01 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1731 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.8 | CML-17 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.5 | 8 | 7 | 7.7 | 0.62716
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-16 | 25-AI-63039-01E01 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 1730 | Rope access | 2014-04-21 10:30 | 2014-04-21 12:00 | [36 empty] | 7.3 | CML-16 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 10:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 6 O'Clock | 100 | 6.02 | 100-WC-40034-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.4 | 7 | 7 | 7.8 | 0.38297
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-11 | 25-AI-63039-01E01 CML-11 |  | FPSO 2014 | Pipe Wall Thickness | 1744 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.475 | CML-11 | CML: Pipe Length | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 3 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.5 | 7 | 7.5 | 7.9 | 0.36856
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1737 | Rope access | 2014-04-21 08:00 | 2014-04-21 10:30 | [36 empty] | 7.1 | CML-4 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 08:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 9 O'Clock | 100 | 6.02 | 100-WC-40035-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.1 | 7 | 7.3 | 7 | 0.14142
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1714 | Rope access | 2014-04-21 07:00 | 2014-04-21 08:00 | [36 empty] | 7.15 | CML-5 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 9 O'Clock | 100 | 6.02 | 100-WC-40069-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7.3 | 7.1 | 7 | 0.1291
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1713 | Rope access | 2014-04-21 07:00 | 2014-04-21 08:00 | [36 empty] | 7.925 | CML-4 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 12 O'Clock | 100 | 6.02 | 100-WC-40069-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 8.5 | 7.5 | 8.7 | 0.80984
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1712 | Rope access | 2014-04-21 07:00 | 2014-04-21 08:00 | [36 empty] | 7.625 | CML-3 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-04-21 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 7 | 6 O'Clock | 100 | 6.02 | 100-WC-40069-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8.6 | 7.2 | 7 | 7.7 | 0.71356
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1708 | Rope Access | 2014-04-13 11:15 | 2014-04-13 12:15 | [36 empty] | 7.675 | CML-2 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 11:15 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 12 O'Clock | 50 | 5.54 | 50-WC-40055-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 8 | 8.4 | 7.3 | 0.63966
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 1709 | Rope Access | 2014-04-13 11:15 | 2014-04-13 12:15 | [36 empty] | 7.3 | CML-3 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 11:15 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 6 O'Clock | 50 | 5.54 | 50-WC-40055-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.5 | 7.2 | 7 | 7.5 | 0.24495
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-6 | 25-AI-63039-01E01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 1700 | Rope Access | 2014-04-13 09:15 | 2014-04-13 10:15 | [36 empty] | 7.425 | CML-6 | CML: Elbow | 3 | 2043-10-24 | 2047-01-28 | 2014-04-13 09:15 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 9 O'Clock | 50 | 5.54 | 50-WC-40018-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.7 | 7.7 | 7.3 | 7 | 0.34034
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-7 | 25-AI-63039-01E01 CML-7 |  | FPSO 2015 | Pipe Wall Thickness | 8563 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6 | CML-7 | CML: type TBC | 3 | 2049-11-16 | 2053-10-15 | 2015-02-04 07:30 | 2.5 | 0.08332 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.2 | 6.4 | 6 | 5.4 | 0.43205
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-1 | 25-AI-63039-01E01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 925 |  | 2014-04-10 11:00 | 2014-04-10 12:00 | [36 empty] | 7.825 | CML-1 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-04-10 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 7 | 3 O'Clock | 80 | 5.49 | 80-WC-40068-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8 | 7 | 7.4 | 8.9 | 0.82614
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-1 | 25-AI-63039-01E01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 1589 |  | 2014-04-10 11:00 | 2014-04-10 12:00 | [36 empty] | 7.825 | CML-1 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-04-10 11:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 7 | 3 O'Clock | 80 | 5.49 | 80-WC-40068-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8 | 7 | 7.4 | 8.9 | 0.82614
AD01 | Montara_Topside | No | Closed Drain (57) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1398 | Rope access | 2014-04-05 14:00 | 2014-04-05 15:00 | [36 empty] | 7.15 | CML-5 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 3 O'Clock | 50 | 5.54 | 50-DC-57051-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.3 | 7 | 7.1 | 7.2 | 0.1291
AD01 | Montara_Topside | No | Closed Drain (57) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1389 | Rope access | 2014-04-05 13:00 | 2014-04-05 14:00 | [36 empty] | 7.25 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-04-05 13:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 9 O'Clock | 50 | 5.54 | 50-DC-57063-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.4 | 7.4 | 7.2 | 7 | 0.19149
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-6 | 25-AI-63039-01E01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2101 | Rope Access | 2014-03-28 13:00 | 2014-03-28 14:00 | [36 empty] | 7.1667 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-28 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 12 O'Clock | 50 | 5.54 | 50-WC-40021-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.2 | 7.3 |  | 0.15275
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-21 | 25-AI-63039-01E01 CML-21 |  | FPSO 2014 | Pipe Wall Thickness | 1956 | Rope Access | 2014-03-26 09:30 | 2014-03-26 10:30 | [36 empty] | 7.15 | CML-21 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2014-03-26 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 7 | 6 O'Clock | 50 | 5.54 | 50-WC-40071-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.3 | 7 | 7 | 7.3 | 0.17321
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2015 | Pipe Wall Thickness | 8561 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 5.55 | CML-5 | CML: type TBC | 3 | 2049-11-16 | 2053-10-15 | 2015-02-04 07:30 | 2.5 | 0.08332 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.4 | 9 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6 | 5.4 | 5.4 | 5.4 | 0.3
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-12 | 25-AI-63039-01E01 CML-12 |  | FPSO 2014 | Pipe Wall Thickness | 12975 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.3 | CML-12 | CML: type TBC | 3 | 2019-04-10 | 2019-03-25 | 2014-02-06 01:00 | 2.5 | 0.65689 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 5.9 | 6 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.6 | 6.6 | 5.9 | 6.1 | 0.3559
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-1 | 25-AI-63039-01E01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 12964 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.55 | CML-1 | CML: type TBC | 3 | 2023-12-16 | 2023-11-18 | 2014-02-06 01:00 | 2.5 | 0.36494 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.1 | 6 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.5 | 7 | 6.1 | 6.6 | 0.36968
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-8 | 25-AI-63039-01E01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 12971 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.475 | CML-8 | CML: type TBC | 3 | 2066-02-16 | 2065-09-28 | 2014-02-06 01:00 | 2.5 | 0.07299 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 12 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.3 | 6.5 | 6.6 | 6.5 | 0.12583
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 12968 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.475 | CML-5 | CML: type TBC | 3 | 2066-02-16 | 2065-09-28 | 2014-02-06 01:00 | 2.5 | 0.07299 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.3 | 6 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.8 |  | 6.6 | 6.4 | 6.3 | 6.6 | 0.15
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-9 | 25-AI-63039-01E01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1259 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7.275 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 12 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.6 | 7.3 | 7.2 | 0.25
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-8 | 25-AI-63039-01E01 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 1258 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7.1 | CML-8 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7 | 7.2 | 7 | 0.11547
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1252 |  | 2014-03-23 14:00 | 2014-03-23 15:00 | [36 empty] | 7.175 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 14:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 6 O'Clock | 300 | 6.35 | 300-WC-40046-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7.3 | 7 | 7.2 | 0.12583
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-26 | 25-AI-63039-01E01 CML-26 |  | FPSO 2014 | Pipe Wall Thickness | 1302 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.375 | CML-26 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 8 | 7 | 7.4 | 7.1 | 0.45
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-19 | 25-AI-63039-01E01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 1295 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.375 | CML-19 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.4 | 7 | 7.7 | 7.4 | 0.28723
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-17 | 25-AI-63039-01E01 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 1293 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.1 | CML-17 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7 |  | 7.3 | 0.17321
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-15 | 25-AI-63039-01E01 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 1291 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.025 | CML-15 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 6 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7 | 7 | 7.1 | 0.05
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-10 | 25-AI-63039-01E01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 1286 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.375 | CML-10 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 12 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.6 | 7.4 | 7.5 | 0.263
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-9 | 25-AI-63039-01E01 CML-9 |  | FPSO 2014 | Pipe Wall Thickness | 1285 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.35 | CML-9 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.5 | 7 | 7.3 | 7.6 | 0.26458
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-7 | 25-AI-63039-01E01 CML-7 |  | FPSO 2014 | Pipe Wall Thickness | 1283 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.35 | CML-7 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 12 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.3 | 7.4 | 7.7 | 0.28868
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 1281 | Rope Access | 2014-03-23 09:30 | 2014-03-23 12:00 | [36 empty] | 7.1 | CML-5 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-23 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 250 | 6.35 | 250-WC-40026-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7 | 7.3 | 7.1 | 0.14142
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 1119 |  | 2014-03-21 11:30 | 2014-03-21 12:00 | [36 empty] | 7.1 | CML-4 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-21 11:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 9 O'Clock | 300 | 6.35 | 300-WC-40044-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.2 | 7 | 7.2 | 7 | 0.11547
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 1117 |  | 2014-03-21 11:30 | 2014-03-21 12:00 | [36 empty] | 7.45 | CML-2 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-03-21 11:30 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 7 | 3 O'Clock | 300 | 6.35 | 300-WC-40044-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7.9 | 7 | 7.4 | 7.5 | 0.36968
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2285 | Rope Access | 2014-03-17 08:00 | 2014-03-17 11:00 | [36 empty] | 7.875 | CML-4 | CML: type TBC | 3 | 2018-01-30 | 2017-06-19 | 2014-03-17 08:00 | 2.5 | 1.1606 | A1: Outside Quadrant |  | 4.92 | 2.5 | 3.215 | 7 | 12 O'Clock | 350 | 7.92 | 350-FL-43511-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.5 |  | 7 | 7.8 | 8.5 | 8.2 | 0.65
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-23 | 25-AI-63039-01E01 CML-23 |  | FPSO 2014 | Pipe Wall Thickness | 12986 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.5 | CML-23 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 3 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 6.6 | 6.6 | 0.11547
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-6 | 25-AI-63039-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8562 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.175 | CML-6 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.9 | 6 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.4 |  | 6.2 | 6.2 | 5.9 | 6.4 | 0.20616
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 8558 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.25 | CML-2 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6 | 9 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6 | 6.9 | 6.1 | 6 | 0.43589
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-20 | 25-AI-63039-01E01 CML-20 |  | FPSO 2014 | Pipe Wall Thickness | 12983 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.475 | CML-20 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.5 | 6.5 | 6.5 | 0.05
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-19 | 25-AI-63039-01E01 CML-19 |  | FPSO 2014 | Pipe Wall Thickness | 12982 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.5 | CML-19 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 6 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.5 | 6.4 | 6.6 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-10 | 25-AI-63039-01E01 CML-10 |  | FPSO 2015 | Pipe Wall Thickness | 8566 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.2 | CML-10 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 3 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.1 | 6.3 | 6.2 | 0.08165
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-8 | 25-AI-63039-01E01 CML-8 |  | FPSO 2015 | Pipe Wall Thickness | 8564 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.15 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.1 | 6 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.6 |  | 6.2 | 6.1 | 6.1 | 6.2 | 0.057735
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20040 | Rope access (Re-checking line) | 2014-05-29 07:00 | 2014-05-29 15:00 | [36 empty] | 21.85 | CML-2 | CML: Pipe Length | 3 | 2017-04-19 | 2016-04-25 | 2014-05-29 07:00 | 15.88 | 1.5616 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 20.4 | 9 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.52 | 0 | 22.4 | 23 | 21.6 | 20.4 | 1.124
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 13029 |  | 2014-01-11 09:00 | 2014-01-11 10:30 | [36 empty] | 22.025 | CML-3 | CML: Elbow | 3 | 2015-10-27 | 2015-03-19 | 2014-01-11 09:00 | 15.88 | 2.5215 | A3: Inside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.4 | 6 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.52 |  | 21.1 | 25.5 | 20.4 | 21.1 | 2.34
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63039-01E01 | CML-1 | 25-AI-63039-01E01 CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 13027 |  | 2014-01-11 09:00 | 2014-01-11 10:30 | [36 empty] | 20.975 | CML-1 | CML: Reducer | 3 | 2015-10-27 | 2015-03-19 | 2014-01-11 09:00 | 15.88 | 2.5215 | A1: Outside Quadrant |  | 18.95 | 15.88 | 17.415 | 20.4 | 12 O'Clock | 150 | 21.95 | 150-PG-23012-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.52 |  | 20.4 | 21.2 | 21.1 | 21.2 | 0.38622
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 13092 |  | 2014-01-10 09:00 | 2014-01-10 11:00 | [36 empty] | 21.775 | CML-2 | CML: Pipe Length | 3 | 2015-10-23 | 2015-03-16 | 2014-01-10 09:00 | 15.88 | 2.5327 | A4: Left Quadrant |  | 18.95 | 15.88 | 17.415 | 20.4 | 9 O'Clock | 150 | 21.95 | 150-PG-23037-25C02 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.52 |  | 22.4 | 23.2 | 21.1 | 20.4 | 1.2606
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63039-01E01 | CML-6 | 25-AI-63039-01E01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 2722 | Rope Access | 2014-03-13 09:00 | 2014-03-13 15:00 | [36 empty] | 11.625 | CML-6 | CML: Pipe Length | 6 | 2018-01-04 | 2018-03-26 | 2014-03-13 09:00 | 5.66 | 1.1895 | A3: Inside Quadrant |  | 5.13 | 5.66 | 5.395 | 10.2 | 6 O'Clock | 100 | 11.13 | 100-PG-23503-03C03 | 120 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.54 |  | 11.9 | 12.1 | 10.2 | 12.3 | 0.96393
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8590 | Line is FFS. Current RBI frequency is 36m. Action: CML’s to Inspect in 48m. RBI to be updated | 2015-02-08 11:00 | 2015-02-08 15:00 |  |  | Administrator | 2015-09-08 14:58 | [32 empty] | 20.575 | CML-4 | CML: Elbow | 3 | 2032-03-27 | 2029-12-13 | 2015-02-08 11:00 | 1.34 | 0.26601 | A4: Left Quadrant |  | 3.35 | 1.34 | 1.9481 | 5.9 | 9 O'Clock | 200 | 6.35 | 200-PL-43300-01C02-E | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.56 |  | 63 | 6.4 | 7 | 5.9 | 28.2869
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 2968 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.675 | CML-3 | CML: Elbow | 3 | 2025-01-15 | 2023-07-23 | 2014-05-01 14:00 | 0.54 | 0.42545 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.1 | 3 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.56 |  | 5.8 | 5.1 | 5.7 | 6.1 | 0.41932
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 22247 | Deck Level | 2014-05-01 14:00 | 2014-05-01 15:00 | [36 empty] | 5.675 | CML-3 | CML: Elbow | 3 | 2025-01-15 | 2023-07-23 | 2014-05-01 14:00 | 0.54 | 0.42545 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.1 | 3 O'Clock | 80 | 5.49 | 80-FL-43460-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.56 |  | 5.8 | 5.1 | 5.7 | 6.1 | 0.41932
AD01 | Montara_Topside | No | Closed Drain (57) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 12504 |  | 2014-02-04 16:00 | 2014-02-04 17:00 | Check Corrosion Rate of 0.572mm/ yr | [35 empty] | 5.55 | CML-2 | CML: Pipe Length | 3 | 2022-01-21 | 2020-12-14 | 2014-02-04 16:00 | 0.54 | 0.57245 | A2: Right Quadrant |  | 2.49 | 0.54 | 1.1719 | 5.1 | 3 O'Clock | 80 | 5.49 | 80-DC-57003-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.56 |  | 5.9 | 5.1 | 5.7 | 5.5 | 0.34157
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-18 | 25-AI-63039-01E01 CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 12981 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.95 | CML-18 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 12 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 7.4 | 6.6 | 7.4 | 0.52599
AD01 | Montara_Topside | No | Gas Compression (23) | Pipework | 25-AI-63039-01E01 | CML-13 | 25-AI-63039-01E01 CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 10997 | Rope Access | 2014-01-10 | 2014-01-10 | [36 empty] | 15 | CML-13 | CML: Pipe Length | 6 | 2014-07-04 | 2014-04-11 | 2014-01-10 | 10.22 | 9.526 | A2: Right Quadrant |  | 14.62 | 10.22 | 12.42 | 14.8 | 3 O'Clock | 80 | 20.62 | 200-PG-23013-09C03 | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.58 |  | 14.9 | 14.8 | 15.1 | 15.2 | 0.18257
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63039-01E01 | CML-24 | 25-AI-63039-01E01 CML-24 |  | FPSO 2014 | Pipe Wall Thickness | 21356 | Protective mesh removed | 2014-06-27 13:00 | 2014-06-27 15:00 | [36 empty] | 8.9 | CML-24 | CML: Reducer | 3 | 2059-02-11 | 2051-04-06 | 2014-06-27 13:00 | 3.61 | 0 | A1: Outside Quadrant |  | 5.18 | 3.61 | 4.395 | 8.2 | 12 O'Clock | 250 | 8.18 | 200-PL-20035-03C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.59 |  | 8.2 | 8.9 | 9 | 9.5 | 0.53541
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 3003 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.525 | CML-5 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.2 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.59 | 0 | 8.7 | 8.6 | 8.2 | 8.6 | 0.22174
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 |  | FPSO 2014 | Pipe Wall Thickness | 22282 | Rope Access | 2014-05-01 07:00 | 2014-05-01 09:00 | [36 empty] | 8.525 | CML-5 | CML: Pipe Length | 6 | 2059-02-11 | 2066-04-06 | 2014-05-01 07:00 | 3.61 | 0 | A3: Inside Quadrant |  | 2.18 | 3.61 | 2.895 | 8.2 | 6 O'Clock | 50 | 8.18 | 50-PF-20301-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.59 |  | 8.7 | 8.6 | 8.2 | 8.6 | 0.22174
AD01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 | yes | FPSO 2015 | Pipe Wall Thickness | 23688 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 7.3 | CML-4 | CML: Reducer | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A4: Left Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 9 O'Clock | 80 | 5.54 | 50-CG-38455-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.2 | 7.3 | 7.6 | 7.1 | 0.21602
AD01 | Montara_Topside | No | Glycol Regeneration (38) | Pipework | 25-AI-63039-01E01 | CML-5 | 25-AI-63039-01E01 CML-5 | yes | FPSO 2015 | Pipe Wall Thickness | 23669 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 7.225 | CML-5 | CML: Fitting | 3 | 2043-10-24 | 2047-01-28 | 2015-10-30 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 6 O'Clock | 100 | 5.54 | 50-CG-38454-01C02-H | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.3 | 7.3 | 7.1 | 7.2 | 0.095743
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-9 | 25-AI-63039-01E01 CML-9 |  | FPSO 2015 | Pipe Wall Thickness | 8565 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 6.275 | CML-9 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 6.2 | 6 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.3 | 6.3 | 6.2 | 6.3 | 0.05
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-17 | 25-AI-63039-01E01 CML-17 |  | FPSO 2014 | Pipe Wall Thickness | 12980 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.45 | CML-17 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A1: Outside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 3 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.4 | 6.4 | 6.5 | 6.5 | 0.057735
AD01 | Montara_Topside | No | Chemical Injection (42) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2015 | Pipe Wall Thickness | 7498 | No drawing to reference pipe schedule | 2015-04-13 07:00 | 2015-04-13 15:00 | [36 empty] | 7.7 | CML-2 | CML: type TBC | 1 | 2229-10-16 | 2165-09-23 | 2015-04-13 07:00 | 2.5 | 0.02143 | A2: Right Quadrant |  | 6.14 | 2.5 | 3.8737 | 7.1 | 3 O'Clock | 40 | 7.14 | 40-CI-42309-01S01 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.5 | 7.1 | 8 | 8.2 | 0.49666
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-16 | 25-AI-63039-01E01 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 12979 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.475 | CML-16 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 3 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.4 | 6.5 | 6.5 | 0.05
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-15 | 25-AI-63039-01E01 CML-15 |  | FPSO 2014 | Pipe Wall Thickness | 12978 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.425 | CML-15 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 9 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.5 | 6.4 | 6.4 | 6.4 | 0.05
AD01 | Montara_Topside | No | Steam (55) | Pipework | 25-AI-63039-01E01 | CML-4 | 25-AI-63039-01E01 CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8856 |  | 2015-02-24 11:00 | 2015-02-24 12:00 | [36 empty] | 7.25 | CML-4 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-24 11:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 7.1 | 9 O'Clock | 50 | 5.54 | 50-SL-55003-01C02-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.4 | 7.4 | 7.1 | 7.1 | 0.17321
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63039-01E01 | CML-27 | 25-AI-63039-01E01 CML-27 |  | FPSO 2015 | Pipe Wall Thickness | 8824 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 6.025 | CML-27 | CML: Fitting | 3 | 2027-05-09 | 2025-06-02 | 2015-02-21 07:00 | 1.1 | 0.37641 | A1: Outside Quadrant |  | 3.35 | 1.1 | 1.8281 | 5.7 | 12 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 5.7 | 6.4 | 5.9 | 6.1 | 0.29861
AD01 | Montara_Topside | No | Separation (20) | Pipework | 25-AI-63039-01E01 | CML-6 | 25-AI-63039-01E01 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 8803 | LAGGING REMOVAL REQUIRED | 2015-02-21 07:00 | 2015-02-21 12:00 | [36 empty] | 5.875 | CML-6 | CML: Equal Tee | 3 | 2027-05-09 | 2025-06-02 | 2015-02-21 07:00 | 1.1 | 0.37641 | A4: Left Quadrant |  | 3.35 | 1.1 | 1.8281 | 5.7 | 9 O'Clock | 200 | 6.35 | 200-PL-20008-01C02-H | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 5.8 | 5.9 | 6.1 | 5.7 | 0.17078
AD01 | Montara_Topside | No | Flare (43) | Pipework | 25-AI-63039-01E01 | CML-14 | 25-AI-63039-01E01 CML-14 |  | FPSO 2014 | Pipe Wall Thickness | 12977 |  | 2014-02-06 01:00 | 2014-02-06 10:00 | [36 empty] | 6.825 | CML-14 | CML: type TBC | 3 | 2051-11-30 | 2051-08-19 | 2014-02-06 01:00 | 2.5 | 0 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.4 | 6 O'Clock | 200 | 6.35 | 200-FH-43516-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.9 |  | 6.7 | 6.8 | 6.4 | 7.4 | 0.41932
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-3 | 25-AI-63039-01E01 CML-3 |  | FPSO 2015 | Pipe Wall Thickness | 8559 | All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [36 empty] | 8.625 | CML-3 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 8.4 | 6 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.9 |  | 8.7 | 8.7 | 8.4 | 8.7 | 0.15
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20382 |  | 2014-10-18 07:00 | 2014-10-18 15:00 | [36 empty] | 7.25 | CML-2 | CML: Elbow | 3 | 2048-08-12 | 2049-10-10 | 2014-10-18 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 7.1 | 9 O'Clock | 100 | 6.02 | 100-WC-40403-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.3 | 7.1 | 7.5 | 7.1 | 0.19149
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 20396 |  | 2014-10-17 07:00 | 2014-10-17 15:00 | [36 empty] | 7.25 | CML-2 | CML: Elbow | 3 | 273443 | 255293 | 2014-10-17 07:00 | 2.5 | 0.00725 | A1: Outside Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.1 | 12 O'Clock | 150 | 7.11 | 150-WC-40405-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.3 | 7.4 | 7.2 | 0.1291
AD01 | Montara_Topside | No | Produced Water (44) | Pipework | 25-AI-63039-01E01 | CML-10 | 25-AI-63039-01E01 CML-10 |  | FPSO 2014 | Pipe Wall Thickness | 22001 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.825 | CML-10 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.1 | 12 O'Clock | 80 | 5.49 | 80-PW-44001-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.1 | 7.9 | 8.7 | 7.6 | 0.6702
AD01 | Montara_Topside | No | Produced Water (44) | Pipework | 25-AI-63039-01E01 | CML-2 | 25-AI-63039-01E01 CML-2 |  | FPSO 2014 | Pipe Wall Thickness | 21984 |  | 2014-10-14 07:00 | 2014-10-14 15:00 | [36 empty] | 7.45 | CML-2 | CML: Elbow | 3 | 2043-04-25 | 2046-10-17 | 2014-10-14 07:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.49 | 2.5 | 2.1519 | 7.1 | 6 O'Clock | 20 | 5.49 | 80-PW-44034-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.5 | 7.6 | 7.1 | 7.6 | 0.23805
AD01 | Montara_Topside | No | Cooling Medium (40) | Pipework | 25-AI-63039-01E01 | CML-6 | 25-AI-63039-01E01 CML-6 |  | FPSO 2014 | Pipe Wall Thickness | 20335 |  | 2014-10-09 07:00 | 2014-10-09 15:00 | [36 empty] | 7.5 | CML-6 | CML: Elbow | 3 | 269755 | 251894 | 2014-10-09 07:00 | 2.5 | 0.00737 | A2: Right Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.1 | 3 O'Clock | 150 | 7.11 | 150-WC-40001-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.6 |  | 7.7 | 7.1 | 7.8 | 7.4 | 0.31623
AD01 | Montara_Topside | No | Compressed Air (63) | Pipework | 25-AI-63039-01E01 | CML-1 | 25-AI-63039-01E01 CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 8557 | Reducer not on site. All fittings CAST. Readings taken on piping directly adjacent to fitting. | 2015-02-04 07:30 | 2015-02-04 15:00 | [37 empty] | CML-1 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2015-02-04 07:30 | 2.5 | 0 |  |  | 2.54 | 2.5 | 2.1738 |  | 9 O'Clock | 50 | 5.54 | 50-AI-63039-01E01 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | [6 empty] | #DIV/0!
CG04 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38452-09C02-P | CML-12 | 50-CG-38452-09C02-P CML-12 |  | FPSO 2015 | Pipe Wall Thickness | 23752 |  | 2015-10-30 07:00 | 2015-10-30 15:00 | [36 empty] | 8.725 | CML-12 | CML: Elbow | 3 | 2047-08-20 | 2038-10-01 | 2015-10-30 07:00 | 2.5 | 0.18223 | A1: Outside Quadrant |  | 5.74 | 2.5 | 4.12 | 8.3 | 12 O'Clock | 50 | 8.74 | 50-CG-38452-09C02-H | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.8 |  | 8.3 | 8.5 | 9.1 | 9 | 0.38622
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40507-1CG | CML-4 | 200-WC-40507-1CG CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8673 | Material Class Not Selectable.Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m. RBI to be updated | 2015-02-12 14:00 | 2015-02-12 15:00 | Check Corrosion Rate of 0.705mm/ yr |  | Administrator | 2015-09-08 10:53 | [32 empty] | 12.075 | CML-4 | CML: Elbow | 3 | 2027-11-18 | 2022-10-10 | 2015-02-12 14:00 | 2.5 | 0.70465 | A2: Right Quadrant |  | 9.7 | 2.5 | 6.1 | 11.5 | 3 O'Clock | 200 | 12.7 | 200-WC-40507-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9 |  | 12.1 | 11.5 | 12.8 | 11.9 | 0.54391
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 150-FL-43084-01C02 | CML-4 | 150-FL-43084-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2569 | Rope Access | 2014-04-08 07:30 | 2014-04-08 08:30 | [36 empty] | 8.475 | CML-4 | CML: type TBC | 3 | 2059-07-07 | 2055-11-27 | 2014-04-08 07:30 | 2.5 | 0 | A4: Left Quadrant |  | 4.11 | 2.5 | 2.8606 | 7.9 | 9 O'Clock | 150 | 7.11 | 150-FL-43084-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 5.4 |  | 8.6 | 8.7 | 8.7 | 7.9 | 0.38622
CG02 | Montara_Topside | Yes | Glycol Regeneration (38) | Pipework | 50-CG-38001-09C02 | CML-27 | 50-CG-38001-09C02 CML-27 |  | FPSO 2014 | Pipe Wall Thickness | 10942 | Deck Level | 2014-01-08 | 2014-01-08 | [36 empty] | 8.475 | CML-27 | CML: type TBC | 3 |  |  | 2014-01-08 |  | 1.3873 | A2: Right Quadrant |  | 5.74 |  |  | 7.9 | 3 O'Clock | 50 | 8.74 | 50-CG-38001-09C02 | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock |  | 7.9 | 8.7 | 7.9 | 8.6 | 8.7 | 0.38622
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PG-20300-03C03-P | CML-1 | 200-PG-20300-03C03-P CML-1 |  | FPSO 2015 | Pipe Wall Thickness | 23356 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-20 07:00 | 2015-07-20 15:00 | [36 empty] | 10.825 | CML-1 | CML: Elbow | 6 | 2021-10-09 | 2020-04-05 | 2015-07-20 07:00 | 3.3 | 1.1241 | A1: Outside Quadrant |  | 6.7 | 3.3 | 5 | 10.3 | 12 O'Clock | 200 | 12.7 | 200-PG-20300-03C03-P | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7 | 0.28084 | 10.3 | 11.2 | 10.8 | 11 | 0.38622
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-13 | 50-PL-23052-09C03 CML-13 |  | FPSO 2013 | Pipe Wall Thickness | 10177 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.825 | CML-13 | CML: type TBC | 6 | 2018-02-22 | 2017-06-30 | 2013-11-09 | 2.81 | 1.7456 | A4: Left Quadrant |  | 5.07 | 2.81 | 3.94 | 10.3 | 9 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.49 |  | 11 | 11.2 | 10.8 | 10.3 | 0.38622
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-18 | 50-PF-20300-03C03-P CML-18 |  | FPSO 2014 | Pipe Wall Thickness | 21584 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.5 | CML-18 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 12 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.4 | 9.8 | 9.8 | 0.38297
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 50-PF-20300-03C03-P | CML-16 | 50-PF-20300-03C03-P CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21582 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.5 | CML-16 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A2: Right Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 3 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9.8 | 9 | 9.4 | 9.8 | 0.38297
VA01 | Montara_Topside | Yes | Separation (20) | Pipework | 25-VA-23054-01C02 | CML-4 | 25-VA-23054-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 21570 | Rope Access | 2014-05-26 09:30 | 2014-05-26 12:00 | [36 empty] | 9.5 | CML-4 | CML: type TBC | 6 | 2075-10-24 | 2074-08-12 | 2014-05-26 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.74 | 2.5 | 2.62 | 9 | 12 O'Clock | 50 | 8.74 | 50-PF-20300-03C03-P | 160 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.5 |  | 9 | 9.8 | 9.8 | 9.4 | 0.38297
FL02 | Montara_Topside | Yes | Fuel Gas (45) | Pipework | 50-FL-43454-01C02-P | CML-33 | 50-FL-43454-01C02-P CML-33 |  | FPSO 2014 | Pipe Wall Thickness | 1181 | Rope Access | 2014-03-22 09:30 | 2014-03-22 12:00 | [36 empty] | 9.4 | CML-33 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-22 09:30 | 2.5 | 0 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 9.1 | 9 O'Clock | 50 | 5.54 | 50-FG-45023-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.9 | 9.5 | 9.1 | 0.38297
FL02 | Montara_Topside | Yes | Closed Drain (57) | Pipework | 50-FL-43454-01C02-P | CML-8 | 50-FL-43454-01C02-P CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2316 | Rope Access | 2014-03-17 13:00 | 2014-03-17 15:00 | [36 empty] | 9.4 | CML-8 | CML: type TBC | 6 | 2074-01-04 | 2073-09-17 | 2014-03-17 13:00 | 2.5 | 0 | A1: Outside Quadrant |  | 2.56 | 2.5 | 2.53 | 9.1 | 3 O'Clock | 100 | 8.56 | 100-DC-57307-01C03 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 6.6 |  | 9.1 | 9.1 | 9.5 | 9.9 | 0.38297
PG01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PG-20005-03C03-P | CML-1 | 300-PG-20005-03C03-P CML-1 |  | FPSO 2014 | Pipe Wall Thickness | 6157 | Protective mesh removed | 2014-07-11 07:30 | 2014-07-11 15:00 | [36 empty] | 14.8 | CML-1 | CML: Reducing Tee | 6 | 2107-02-11 | 2090-04-05 | 2014-07-11 07:30 | 4.9 | 0 | A3: Inside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.5 | 9 O'Clock | 300 | 14.27 | 300-PG-20005-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 15.3 | 14.9 | 14.5 | 14.5 | 0.38297
PF01 | Montara_Topside | Yes | Separation (20) | Pipework | 300-PF-20500-03C03-P | CML-18 | 300-PF-20500-03C03-P CML-18 |  | FPSO 2015 | Pipe Wall Thickness | 23495 | Re-check on line / Selected CML''s as Per RBI 2014 Report | 2015-07-27 07:00 | 2015-07-27 15:00 | [36 empty] | 15 | CML-18 | CML: Elbow | 6 | 2107-02-11 | 2090-04-05 | 2015-07-27 07:00 | 4.9 | 0 | A1: Outside Quadrant |  | 8.27 | 4.9 | 6.585 | 14.5 | 12 O'Clock | 300 | 14.27 | 300-PF-20500-03C03-P | 60 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.6 |  | 14.5 | 15.3 | 15.3 | 14.9 | 0.38297
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-3 | 200-PG-23007-09C03-PA CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20690 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | [36 empty] | 20.7 | CML-3 | CML: Reducing Tee | 6 | 2040-02-29 | 2034-07-03 | 2014-06-30 13:00 | 10.22 | 0.38855 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 20.2 | 12 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.98 |  | 20.2 | 20.6 | 21 | 21 | 0.38297
PL01 | Montara_Topside | Yes | Separation (20) | Pipework | 200-PL-20019-01C02 | CML-31 | 200-PL-20019-01C02 CML-31 |  | FPSO 2014 | Pipe Wall Thickness | 21282 |  | 2014-09-30 07:00 | 2014-09-30 15:00 | [36 empty] | 7.15 | CML-31 | CML: Elbow | 3 | 2051-11-30 | 2051-08-19 | 2014-09-30 07:00 | 2.5 | 0 | A2: Right Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.8 | 3 O'Clock | 200 | 6.35 | 200-PL-20019-01C02 | 20 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 4.3 |  | 7.3 | 6.8 | 7.3 | 7.2 | 0.23805
FH01 | Montara_Topside | Yes | Flare (43) | Pipework | 80-FH-43005-01C02 | CML-4 | 80-FH-43005-01C02 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 12554 |  | 2014-01-20 10:00 | 2014-01-10 12:00 | [36 empty] | 5.9 | CML-4 | CML: type TBC | 3 | 2034-08-24 | 2037-02-12 | 2014-01-20 10:00 | 2.5 | 0.14074 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.4 | 9 O'Clock | 80 | 5.49 | 80-FH-43005-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.9 |  | 6.2 | 5.8 | 6.2 | 5.4 | 0.38297
DH01 | Montara_Topside | Yes | Open Drain (56) | Pipework | 50-DH-56137-01C02 | CML-16 | 50-DH-56137-01C02 CML-16 |  | FPSO 2014 | Pipe Wall Thickness | 21100 | Rope Access | 2014-05-18 09:30 | 2014-05-18 14:00 | [36 empty] | 6.3 | CML-16 | CML: type TBC | 3 |  |  | 2014-05-18 09:30 | 2.5 | 0 | A2: Right Quadrant |  |  | 2.5 |  | 6 | 6 O'Clock | 80 |  | 80-DH-56137-01C02 | 40STD | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.5 |  | 6.8 | 6 | 6 | 6.4 | 0.38297
FL01 | Montara_Topside | Yes | Flare (43) | Pipework | 300-FL-43510-01C02 | CML-3 | 300-FL-43510-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 20474 |  | 2014-09-28 07:00 | 2014-09-28 15:00 | [36 empty] | 6.7 | CML-3 | CML: Elbow | 3 | 2047-06-13 | 2047-03-14 | 2014-09-28 07:00 | 2.5 | 0.11305 | A3: Inside Quadrant |  | 3.35 | 2.5 | 2.5281 | 6.2 | 6 O'Clock | 300 | 6.35 | 300-FL-43510-01C02 |  | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.7 |  | 6.6 | 7 | 6.2 | 7 | 0.38297
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 50-PW-44012-01X01 | CML-4 | 50-PW-44012-01X01 CML-4 |  | FPSO 2014 | Pipe Wall Thickness | 2018 |  | 2014-03-27 09:30 | 2014-03-27 10:00 | [36 empty] | 5.3 | CML-4 | CML: Pipe Length | 3 | 2020-09-28 | 2021-07-13 | 2014-03-27 09:30 | 2.5 | 0.4145 | A2: Right Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 3 O'Clock | 50 | 5.54 | 50-PW-44012-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 |  | 5.3 | 5.2 | 5.4 | 5.3 | 0.08165
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-6 | 80-PW-44016-01C02-P CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 22908 | Rope Access | 2015-05-02 07:00 | 2015-05-02 15:00 | [36 empty] | 5.45 | CML-6 | CML: Pipe Length | 3 | 2043-08-03 | 2047-02-06 | 2015-05-02 07:00 | 2.5 | 0.09903 | A2: Right Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 3 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 | 0.17892 | 5.7 | 5.3 | 5.4 | 5.4 | 0.17321
PW01 | Montara_Topside | Yes | Produced Water (44) | Pipework | 80-PW-44016-01C02-P | CML-3 | 80-PW-44016-01C02-P CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 21935 |  | 2014-10-10 07:00 | 2014-10-10 15:00 | [36 empty] | 5.55 | CML-3 | CML: Elbow | 3 | 2034-10-19 | 2037-04-15 | 2014-10-10 07:00 | 2.5 | 0.13974 | A4: Left Quadrant |  | 2.49 | 2.5 | 2.1519 | 5.3 | 9 O'Clock | 80 | 5.49 | 80-PW-44016-01C02-P | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.8 |  | 5.7 | 5.6 | 5.6 | 5.3 | 0.17321
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-3 | 100-WC-40027-01C02 CML-3 |  | FPSO 2014 | Pipe Wall Thickness | 835 |  | 2014-04-02 09:00 | 2014-04-02 10:00 | Check Corrosion Rate of 0.382mm/ yr |  | Nestor | 2016-04-01 | [32 empty] | 5.95 | CML-3 | CML: Elbow | 3 | 2022-08-12 | 2022-12-01 | 2014-04-02 09:00 | 2.5 | 0.38248 | A3: Inside Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 6 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6 | 6.3 | 5.7 | 5.8 | 0.26458
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 100-WC-40027-01C02 | CML-6 | 100-WC-40027-01C02 CML-6 |  | FPSO 2015 | Pipe Wall Thickness | 23426 | Re-check on line as Per RBI 2014 Report | 2015-07-23 07:00 | 2015-07-23 15:00 |  |  | Nestor | 2016-04-01 | [32 empty] | 6.025 | CML-6 | CML: Pipe Length | 3 | 2036-12-22 | 2037-10-02 | 2015-07-23 07:00 | 2.5 | 0.1493 | A2: Right Quadrant |  | 3.02 | 2.5 | 2.3838 | 5.7 | 3 O'Clock | 100 | 6.02 | 100-WC-40027-01C02 | 40 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 | -0.15307 | 6.1 | 5.7 | 6.1 | 6.2 | 0.22174
PG03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 200-PG-23007-09C03-PA | CML-13 | 200-PG-23007-09C03-PA CML-13 |  | FPSO 2014 | Pipe Wall Thickness | 20700 | Protective mesh removed/Rope access | 2014-06-30 13:00 | 2014-06-30 15:00 | Check Corrosion Rate of 0.481mm/ yr |  | John Wilson | 2017-03-23 09:17 | Loss within CA no further action required. | [31 empty] | 20.6 | CML-13 | CML: Fitting | 6 | 2035-01-07 | 2030-06-13 | 2014-06-30 13:00 | 10.22 | 0.48106 | A1: Outside Quadrant |  | 14.62 | 10.22 | 12.42 | 20.1 | 12 O'Clock | 200 | 20.62 | 200-PG-23007-09C03-P | 140 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.88 |  | 20.1 | 20.9 | 20.9 | 20.5 | 0.38297
WC02 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 200-WC-40508-1CG | CML-4 | 200-WC-40508-1CG CML-4 |  | FPSO 2015 | Pipe Wall Thickness | 8669 | Material Class Not Selectable. Line is FFS. Current RBI frequency is 48m. Action: Inspect in 60m (Feb. 2020). RBI to be updated | 2015-02-12 13:00 | 2015-02-12 14:00 | Check Corrosion Rate of 0.529mm/ yr |  | Administrator | 2015-09-08 12:53 | [32 empty] | 12.325 | CML-4 | CML: Pipe Length | 3 | 2032-09-13 | 2025-11-22 | 2015-02-12 13:00 | 2.5 | 0.52852 | A2: Right Quadrant |  | 9.7 | 2.5 | 6.1 | 11.8 | 3 O'Clock | 200 | 12.7 | 200-WC-40508-1CG | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 9.3 |  | 12.1 | 11.8 | 12.7 | 12.7 | 0.45
PW03 | Montara_Topside | Yes | Produced Water (44) | Pipework | 200-PW-44018-01X01 | CML-13 | 200-PW-44018-01X01 CML-13 |  | FPSO 2015 | Pipe Wall Thickness | 23248 |  | 2015-05-11 07:00 | 2015-05-11 15:00 | [36 empty] | 5.25 | CML-13 | CML: Pipe Length | 3 | 2030-10-11 | 2032-08-22 | 2015-05-11 07:00 | 2.5 | 0.17496 | A1: Outside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.2 | 6 O'Clock | 50 | 5.54 | 50-PW-44040-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 2.7 | 0 | 5.2 | 5.3 | 5.2 | 5.3 | 0.057735
WC01 | Montara_Topside | Yes | Cooling Medium (40) | Pipework | 50-WC-40021-01C02 | CML-8 | 50-WC-40021-01C02 CML-8 |  | FPSO 2014 | Pipe Wall Thickness | 2103 | Rope Access | 2014-03-28 13:00 | 2014-03-28 14:00 | [36 empty] | 6.025 | CML-8 | CML: type TBC | 3 | 2043-10-24 | 2047-01-28 | 2014-03-28 13:00 | 2.5 | 0 | A3: Inside Quadrant |  | 2.54 | 2.5 | 2.1738 | 5.7 | 6 O'Clock | 50 | 5.54 | 50-WC-40021-01C02 | 80 | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 3.2 |  | 6.1 | 6.1 | 5.7 | 6.2 | 0.22174
PL03 | Montara_Topside | Yes | Gas Compression (23) | Pipework | 50-PL-23052-09C03 | CML-16 | 50-PL-23052-09C03 CML-16 |  | FPSO 2013 | Pipe Wall Thickness | 10180 | Deck Level | 2013-11-09 | 2013-11-09 | [36 empty] | 10.55 | CML-16 | CML: type TBC | 6 | 2016-10-25 | 2016-05-08 | 2013-11-09 | 2.81 | 2.4258 | A1: Outside Quadrant |  | 5.07 | 2.81 | 3.94 | 10 | 12 O'Clock | 50 | 11.07 | 50-PL-23052-09C03 | XXS | 12 O'Clock | 3 O'Clock | 6 O'Clock | 9 O'Clock | 7.19 |  | 10 | 10.8 | 10.8 | 10.6 | 0.37859